Titanium Analytics

Results Analysis and Recommendations

Test Building, AHU 1 (°F)  |  2025-08-01 to 2025-08-14

# Summary

This report reviews an exported results file from the Extreme & Change Analytics Lab using three methods: Extremes, Changes and Volatility. Each real abnormality is reported as location, condition, normal range, observed value, magnitude, duration and status.

Data gap: no readings from 2025-08-06 09:45 to 2025-08-06 22:00 (12 h 15 min).

Below typical from 2025-08-09 22:00 to 2025-08-10 06:45 (9 h), up to 7.56°F from typical.

The engine flagged 47 events with a 5.0-hour baseline; with a 24.0-hour baseline the same data gives 6.

| Source file | res.csv |
| --- | --- |
| Period | 2025-08-01 00:00 to 2025-08-14 23:45 |
| Readings | 1,296, about one every 15.0 minutes (660 Night, 636 Day) |
| Analysis settings in the file | Window 20 (about 5.0 h), K_E 2.0 |
| Reference | No reference document configured |

# 1. How this sensor normally behaves

The typical daily swing is 5.6-7.84°F; schedule transitions happen around hours 7, 8, 9, 10, 18, 19, 20, 21, 22.

| Hours | Typical value (°F) |
| --- | --- |
| 00:00-03:59 | 80.08 |
| 04:00-07:59 | 80.08 |
| 08:00-11:59 | 74.76-78.96 |
| 12:00-15:59 | 74.76-75.04 |
| 16:00-19:59 | 74.76-75.6 |
| 20:00-23:59 | 77.28-80.08 |

Shaded: abnormalities (orange) and data gaps (grey). Dashed line: typical value for each hour of the day.

# 2. Extremes: abnormalities found

Each reading was compared with the typical value for the same hour of the day. Deviations larger than 1.25°F lasting at least an hour are reported.

## Abnormality 1: Data gap

| Location | Test Building, AHU 1 |
| --- | --- |
| Condition | No readings received |
| Normal | A reading about every 15.0 minutes |
| Observed | Last reading 2025-08-06 09:45, next reading 2025-08-06 22:00 |
| Magnitude | About 48 readings missing |
| Duration | 12 h 15 min |
| Status | Resolved, readings resumed |

Readings resumed after the gap.

## Abnormality 2: Below typical for this time of day

| Location | Test Building, AHU 1 |
| --- | --- |
| Condition | Unusually low for the time of day |
| Normal range | 80.08-80.08°F |
| Observed | 72.52-72.52°F; 72.52°F at 2025-08-09 22:00 |
| Magnitude | Up to 7.56°F below typical |
| Duration | 9 h (2025-08-09 22:00 to 2025-08-10 06:45, Saturday) |
| Status | Resolved |

Observed 72.52-72.52°F where 80.08-80.08°F is typical.

Hypothesis to investigate (not a conclusion): Check schedules, overrides and equipment logs for this period - a hypothesis to check, not a conclusion.

# 3. Changes

Typical fastest change: -0.84°F down, 0.84°F up per reading.

70.0% of abnormal-change flags fall in schedule transition hours.

# 4. Volatility

Daily variability of changes stays between 0.32 and 0.83°F.

# 5. Why the engine flagged what it did

|  | Window 20 (about 5.0 h) - in file | Window 96 (about 24.0 h) |
| --- | --- | --- |
| Extreme readings | 246 | 46 |
| Non-normal readings | 485 | 170 |
| Separate events | 47 | 6 |

93.0% of extreme flags (228 of 246) fall in schedule transition hours, and 50 came from periods with almost no variability.

# 6. Recommendations

## Building operations

Review the abnormal periods. Check schedules, overrides and equipment logs for the periods listed.

Check the data gap. Find the cause and alert on missing data.

## Analytics engine and app

- Use a daily baseline. A window covering one day avoids flagging the normal cycle.

- Add a variability floor. At least one sensor step, so a single tick cannot trigger an extreme.

# Limitations

Causes are hypotheses for investigation.

The typical baseline uses only the period in this file.

# About this report

Generated 2026-10-09 16:09 by the Extreme & Change Analytics Lab.

All tables and numbers were computed by the app from the results data.

AI wording not used: no OpenAI API key is set ([openai] api_key in config.local.ini).