## Summary
Results analysis summary: Monthly overview |  |  | Report generated: 10/09/2026 16:09
Hello,
Below is a summary of the 1 month of readings for Test Building, AHU 1 (1,296 readings, 08/01/2025 – 08/14/2025), and our recommendations.
Use the tabs at the bottom to find more detail about each month, including event-level actions.
Read the Guide | See the charts (go to 'Dashboard') | Read the AI review (go to 'AI review')
AI summary |  | Plain built-in wording (AI not used). AI wording not used: no OpenAI API key is set ([openai] api_key in config.local.ini).
● Data gap: no readings from 2025-08-06 09:45 to 2025-08-06 22:00 (12 h 15 min).
● Below typical from 2025-08-09 22:00 to 2025-08-10 06:45 (9 h), up to 7.56°F from typical.
● The engine flagged 47 events with a 5.0-hour baseline; with a 24.0-hour baseline the same data gives 6.
August 2025 / Sensor: Test Building, AHU 1 (°F) |  | Rank by mean materiality: 1 out of 1 months · extremes 19% of readings | Status: | 3 recommendations
Improve | Recommendations | Why have we recommended this? |  | Learn more
Operating level | ● Review what changed when the level shifted | Confirmed shift share: 19% of readings (62 h). The value stayed away from its baseline for N_M readings in a row with a high mean ¦Z¦ - check setpoint or schedule changes, sensor drift or an equipment fault. |  | Confirmed/Materialized Shift
Sensitivity | ● Consider a longer baseline window | Extreme share is 19% of readings, well above the ~5% expected at K_E = 2. A longer Window (96 = 24 h) or a higher K_E would flag fewer routine swings. |  | K_E
Data quality | ● Fix the data gaps | Missing data: 12.2 h in gaps longer than three reading intervals. Events inside a gap cannot be detected. |  | Data gaps
Show events and benchmarks for this month (go to 'Aug 2025')
Data quality / Gaps in the readings |  | 1 gaps, 12.2 hours of missing data | Status: | Gaps to review
Show the gaps (go to 'Data gaps')

## AI review
AI review | Report generated: 10/09/2026 16:09
< Back to summary worksheet
Plain built-in wording (AI not used). AI wording not used: no OpenAI API key is set ([openai] api_key in config.local.ini).
Causes are hypotheses to check, not conclusions. The figures on the other tabs are computed by the app.
Summary
● Data gap: no readings from 2025-08-06 09:45 to 2025-08-06 22:00 (12 h 15 min).
● Below typical from 2025-08-09 22:00 to 2025-08-10 06:45 (9 h), up to 7.56°F from typical.
● The engine flagged 47 events with a 5.0-hour baseline; with a 24.0-hour baseline the same data gives 6.
Normal behaviour
The typical daily swing is 5.6-7.84°F; schedule transitions happen around hours 7, 8, 9, 10, 18, 19, 20, 21, 22.
Abnormal periods
Below typical for this time of day | Observed 72.52-72.52°F where 80.08-80.08°F is typical. Check schedules, overrides and equipment logs for this period - a hypothesis to check, not a conclusion.
Data gaps
Readings resumed after the gap.
Rate of change
● Typical fastest change: -0.84°F down, 0.84°F up per reading.
● 70.0% of abnormal-change flags fall in schedule transition hours.
Volatility
● Daily variability of changes stays between 0.32 and 0.83°F.
Why the engine flagged what it did
93.0% of extreme flags (228 of 246) fall in schedule transition hours, and 50 came from periods with almost no variability.
Recommendations: operations
Review the abnormal periods | Check schedules, overrides and equipment logs for the periods listed.
Check the data gap | Find the cause and alert on missing data.
Recommendations: analytics settings
Use a daily baseline | A window covering one day avoids flagging the normal cycle.
Add a variability floor | At least one sensor step, so a single tick cannot trigger an extreme.
Limitations
● Causes are hypotheses for investigation.
● The typical baseline uses only the period in this file.

## Dashboard
Dashboard | [11 empty] | Report generated: 10/09/2026 16:09
< Back to summary worksheet
Charts for the whole period. The monthly figures behind them are in the table below.
Monthly figures
Month | Extreme share | Confirmed share | Sustained deviation (h) | Material changes per day | Investigate | Review | Monitor | Upper – Day | Upper – Night | Lower – Day | Lower – Night
Aug 2025 | 18.98% | 19.21% | 89.75 | 1.9286 | 27 | 1 | 20 | 9 | 124 | 106 | 7
By month
Events and extremes
Time of day
By day

## Guide
Guide
This report summarises the Extreme & Change analysis of Test Building, AHU 1 and gives recommendations and benchmarks for each month.
It shows when the readings left their normal range, how long deviations lasted, how often the value changed abnormally fast, and how much data is missing.
How to use this report
Use the tabs at the bottom of the screen to move through the workbook.
Tab (at the bottom of the screen) | What is on the tab?
Summary | Overview of each month with recommendations, the AI summary, and links to the month tabs.
AI review | The written analysis: summary, normal behaviour, abnormal periods, changes, recommendations and limitations.
Dashboard | Charts: monthly measures, events and extremes, time-of-day heatmap and the daily overview.
Month tabs | ● Analysis funnel: extreme share, sustained deviation hours and material changes per day, with the month's rank.
● Recommendations with this month vs the best and worst month, and more benchmarks (also day vs night).
● A chart of the readings against the normal range, and every event sorted by materiality.
Data gaps | Every break in the data longer than three reading intervals, with the hours missing.
Events | All events in the whole period in one filterable list.
Daily overview | One row per day: readings, value range, extremes, persistent and confirmed periods, changes.
Monthly metrics | The monthly figures behind the Summary and month tabs.
Column descriptor | What every column of the results file means and which parameters drive it.
Data | Not included in this report (option off).
How are the results calculated?
Each reading is compared with a rolling baseline of the previous readings (Window 20, K_E 2). ¦Z¦ ≥ K_E flags an Extreme reading.
An event continues while ¦Z¦ ≥ K_P; after N_P readings it is Persistent, after N_M readings with mean ¦Z¦ ≥ K_M it is a Confirmed/Materialized Shift.
The rate of change has its own baseline; ¦Z_ROC¦ ≥ ROC_K is an Abnormal Change, and repeats within the frequency window make a Material Change.
The Materiality score (0–1) combines size (¦Z¦), duration and recurrence. Rank 1 = the month with the most issues.
Recommendations are rules applied to these figures; they point to what to check, they are not a diagnosis of the equipment.
Learn more: info_main\Statistical_calc_parameters\Statistical calc parameters manual.docx

## Data gaps
Data gaps | [6 empty] | Report generated: 10/09/2026 16:09
The analysis expects one reading about every 15 minutes.
A gap is any break of more than three reading intervals. No readings, and so no extremes or events, exist inside a gap.
This tab lists every gap and the time it covers, so missing data is not mistaken for normal operation.
Summary of gaps
Number of gaps |  | 1
Missing time (hours) |  | 12.25
From (last reading) | To (next reading) | Hours missing | Readings missing (approx.) | Day/Night at start | Severity | Action
2025-08-06 09:45 | 2025-08-06 22:00 | 12.25 | 48 | Day | Medium | Check the logger / network for this period

## Aug 2025
We compared each reading with its own rolling baseline using the settings below | [5 empty] | Rank by mean materiality: 1 of 1 months (1 = most issues)
Sensor: Test Building, AHU 1 (°F), Period: August 2025, Value range: 72.5 – 80.4 °F | [5 empty] | Report generated: 10/09/2026 16:09
< Back to summary worksheet
Analysis funnel
Readings in this month: 1,296 |  | vs other months (1) | Recommendations to improve |  |  |  | Why have we recommended this?
| Extreme readings |  |  | This month | Best month | Worst month
| Share of readings | Rank vs other months | ● Review what changed when the level shifted | 19.21% | 19.21% | 19.21% | Confirmed shift share: 19% of readings (62 h). The value stayed away from its baseline for N_M readings in a row with a high mean ¦Z¦ - check setpoint or schedule changes, sensor drift or an equipment fault.
| 18.98% | 1
| Sustained deviations |  | ● Consider a longer baseline window | 18.98% | 18.98% | 18.98% | Extreme share is 19% of readings, well above the ~5% expected at K_E = 2. A longer Window (96 = 24 h) or a higher K_E would flag fewer routine swings.
| Hours (Persistent + Confirmed) | Rank vs other months
| 89.75 | 1
|  |  | ● Fix the data gaps | 12.25 | 12.25 | 12.25 | Missing data: 12.2 h in gaps longer than three reading intervals. Events inside a gap cannot be detected.
Material changes
| Per day | Rank vs other months
| 1.9286 | 1
More benchmarks
|  |  | Measure | This month | Best month | Worst month | Whole period | This month – Day | This month – Night
|  |  | Mean value | 77.4183 | 77.4183 | 77.4183 | 77.4183 | 75.8474 | 78.932
|  |  | Min value | 72.52 | 72.52 | 72.52 | 72.52 | 74.48 | 72.52
|  |  | Max value | 80.36 | 80.36 | 80.36 | 80.36 | 80.36 | 80.36
|  |  | Extreme share | 18.98% | 18.98% | 18.98% | 18.98% | 18.08% | 19.85%
|  |  | Upper extremes | 133 | 133 | 133 | 133 | 9 | 124
|  |  | Lower extremes | 113 | 113 | 113 | 113 | 106 | 7
|  |  | Sustained deviation (h) | 89.75 | 89.75 | 89.75 | 89.75 | 39.5 | 50.25
|  |  | Confirmed share | 19.21% | 19.21% | 19.21% | 19.21% | 16.04% | 22.27%
|  |  | Material changes per day | 1.9286 | 1.9286 | 1.9286 | 1.9286 | Not relevant | Not relevant
|  |  | Mean materiality score | 0.19815 | 0.19815 | 0.19815 | 0.19815 | 0.18485 | 0.21096
|  |  | Max ¦Z¦ | 4.2485 | 4.2485 | 4.2485 | 4.2485 | 4.2485 | 3.4006
|  |  | Data gap hours | 12.25 | 12.25 | 12.25 | 12.25 | Not relevant | Not relevant
* Best = lowest month, Worst = highest month for each measure (for Mean/Min/Max value: simply the lowest and highest month).
* With a 20-reading rolling window ¦Z¦ cannot exceed (W−1)/√W = 4.25, so Max ¦Z¦ is similar in every month; use Extreme share and the events instead.
* Settings detected in the results: Window 20, K_E 2.
Readings against the normal range
Grey band = normal range (moving average ± K_E·σ). Dots outside it are Extreme readings: orange = upper, blue = lower.
Events in this month
View all events
* Sorted by materiality score (highest first). Action: Investigate = Confirmed shift, Review = Persistent, Monitor = shorter events.
Start | End | Duration (h) | Highest state | Direction | Peak value | Max ¦Z¦ | Mean ¦Z¦ | Max materiality | Day/Night | Action
2025-08-07 19:15 | 2025-08-07 23:15 | 4.25 | Confirmed/Materialized Shift | upper | 80.36 | 3.2738 | 2.1587 | 0.6466 | Night | Investigate
2025-08-12 08:15 | 2025-08-12 11:45 | 3.75 | Confirmed/Materialized Shift | lower | 74.76 | 3.4558 | 2.091 | 0.6422 | Day | Investigate
2025-08-04 19:15 | 2025-08-04 23:30 | 4.5 | Confirmed/Materialized Shift | upper | 80.36 | 3.1537 | 2.0856 | 0.6399 | Night | Investigate
2025-08-08 08:30 | 2025-08-08 11:30 | 3.25 | Confirmed/Materialized Shift | lower | 74.76 | 3.447 | 2.1739 | 0.6345 | Day | Investigate
2025-08-09 19:15 | 2025-08-09 23:45 | 4.75 | Confirmed/Materialized Shift | upper | 79.52 | 3.1409 | 2.0857 | 0.6252 | Night | Investigate
2025-08-01 19:30 | 2025-08-01 23:30 | 4.25 | Confirmed/Materialized Shift | upper | 80.08 | 3.4006 | 2.1014 | 0.6206 | Night | Investigate
2025-08-04 08:15 | 2025-08-04 11:45 | 3.75 | Confirmed/Materialized Shift | lower | 74.76 | 3.4305 | 2.1707 | 0.6142 | Day | Investigate
2025-08-03 08:15 | 2025-08-03 11:45 | 3.75 | Confirmed/Materialized Shift | lower | 74.48 | 3.5563 | 2.135 | 0.613 | Day | Investigate
2025-08-14 08:15 | 2025-08-14 11:45 | 3.75 | Confirmed/Materialized Shift | lower | 74.48 | 3.5738 | 2.1293 | 0.6118 | Day | Investigate
2025-08-11 08:15 | 2025-08-11 11:15 | 3.25 | Confirmed/Materialized Shift | lower | 74.48 | 3.2811 | 2.3065 | 0.611 | Day | Investigate
2025-08-01 08:30 | 2025-08-01 11:15 | 3 | Confirmed/Materialized Shift | lower | 74.76 | 3.445 | 2.2947 | 0.6102 | Day | Investigate
2025-08-13 19:15 | 2025-08-13 23:30 | 4.5 | Confirmed/Materialized Shift | upper | 80.08 | 3.0987 | 2.0645 | 0.6091 | Night | Investigate
2025-08-02 19:30 | 2025-08-02 23:15 | 4 | Confirmed/Materialized Shift | upper | 80.08 | 3.074 | 2.08 | 0.6044 | Night | Investigate
2025-08-08 19:15 | 2025-08-08 23:45 | 4.75 | Confirmed/Materialized Shift | upper | 80.36 | 3.2738 | 2.0293 | 0.6007 | Night | Investigate
2025-08-10 19:15 | 2025-08-10 23:15 | 4.25 | Confirmed/Materialized Shift | upper | 80.36 | 3.2738 | 2.1505 | 0.5969 | Night | Investigate
2025-08-06 08:15 | 2025-08-06 09:45 | 1.75 | Confirmed/Materialized Shift | lower | 75.32 | 3.205 | 2.852 | 0.5957 | Day | Investigate
2025-08-09 08:15 | 2025-08-09 11:45 | 3.75 | Confirmed/Materialized Shift | lower | 74.76 | 3.4598 | 2.1101 | 0.5951 | Day | Investigate
2025-08-11 19:30 | 2025-08-11 23:30 | 4.25 | Confirmed/Materialized Shift | upper | 80.08 | 3.2 | 2.0577 | 0.5943 | Night | Investigate
2025-08-12 19:15 | 2025-08-12 23:00 | 4 | Confirmed/Materialized Shift | upper | 80.36 | 3.3995 | 2.2293 | 0.591 | Night | Investigate
2025-08-05 08:15 | 2025-08-05 11:45 | 3.75 | Confirmed/Materialized Shift | lower | 74.76 | 3.2714 | 2.1095 | 0.5893 | Day | Investigate
2025-08-03 19:15 | 2025-08-03 23:30 | 4.5 | Confirmed/Materialized Shift | upper | 80.08 | 3.3593 | 2.0698 | 0.5868 | Night | Investigate
2025-08-07 08:15 | 2025-08-07 11:45 | 3.75 | Confirmed/Materialized Shift | lower | 74.76 | 3.4548 | 2.0886 | 0.586 | Day | Investigate
2025-08-05 19:30 | 2025-08-05 23:30 | 4.25 | Confirmed/Materialized Shift | upper | 80.08 | 3.2692 | 2.0696 | 0.5858 | Night | Investigate
2025-08-02 08:15 | 2025-08-02 11:45 | 3.75 | Confirmed/Materialized Shift | lower | 74.76 | 3.1152 | 2.0909 | 0.5648 | Day | Investigate
2025-08-13 08:15 | 2025-08-13 11:30 | 3.5 | Confirmed/Materialized Shift | lower | 74.76 | 3.223 | 2.1754 | 0.5576 | Day | Investigate
2025-08-14 19:30 | 2025-08-14 23:15 | 4 | Confirmed/Materialized Shift | upper | 80.36 | 3.0376 | 2.0818 | 0.5379 | Night | Investigate
2025-08-10 07:00 | 2025-08-10 08:30 | 1.75 | Confirmed/Materialized Shift | upper | 80.36 | 4.2485 | 2.2116 | 0.5018 | Day | Investigate
2025-08-11 04:30 | 2025-08-11 05:15 | 1 | Persistent | upper | 80.36 | 2.2993 | 1.327 | 0.324 | Night | Review
2025-08-01 06:00 | 2025-08-01 06:15 | 0.5 | Extreme/elevated | lower | 79.52 | 2.976 | 2.0415 | 0.2841 | Night | Monitor
2025-08-05 06:30 | 2025-08-05 06:30 | 0.25 | Extreme triggered | lower | 79.52 | 2.351 | 2.351 | 0.271 | Night | Monitor
2025-08-05 04:45 | 2025-08-05 05:00 | 0.5 | Extreme/elevated | upper | 80.36 | 2.2757 | 1.7506 | 0.2531 | Night | Monitor
2025-08-02 06:30 | 2025-08-02 06:30 | 0.25 | Extreme triggered | lower | 79.52 | 2.3202 | 2.3202 | 0.2404 | Night | Monitor
2025-08-02 03:00 | 2025-08-02 03:00 | 0.25 | Extreme triggered | upper | 80.36 | 2.2938 | 2.2938 | 0.2386 | Night | Monitor
2025-08-14 16:45 | 2025-08-14 16:45 | 0.25 | Extreme triggered | upper | 75.32 | 2.2757 | 2.2757 | 0.2374 | Day | Monitor
2025-08-02 15:30 | 2025-08-02 15:30 | 0.25 | Extreme triggered | lower | 74.48 | 2.2757 | 2.2757 | 0.2374 | Day | Monitor
2025-08-14 18:45 | 2025-08-14 18:45 | 0.25 | Extreme triggered | lower | 74.48 | 2.2584 | 2.2584 | 0.2363 | Day | Monitor
2025-08-02 17:30 | 2025-08-02 17:30 | 0.25 | Extreme triggered | upper | 75.32 | 2.1794 | 2.1794 | 0.231 | Day | Monitor
2025-08-13 16:15 | 2025-08-13 16:15 | 0.25 | Extreme triggered | upper | 75.32 | 2.5628 | 2.5628 | 0.228 | Day | Monitor
2025-08-07 03:30 | 2025-08-07 03:30 | 0.25 | Extreme triggered | lower | 79.52 | 2.0417 | 2.0417 | 0.2218 | Night | Monitor
2025-08-07 02:45 | 2025-08-07 02:45 | 0.25 | Extreme triggered | lower | 79.52 | 2.4597 | 2.4597 | 0.2211 | Night | Monitor
2025-08-11 15:00 | 2025-08-11 15:00 | 0.25 | Extreme triggered | upper | 75.32 | 2.3202 | 2.3202 | 0.2118 | Day | Monitor
2025-08-05 16:15 | 2025-08-05 16:15 | 0.25 | Extreme triggered | upper | 75.32 | 2.2993 | 2.2993 | 0.2104 | Day | Monitor
2025-08-04 02:30 | 2025-08-04 02:30 | 0.25 | Extreme triggered | upper | 80.36 | 2.2757 | 2.2757 | 0.2089 | Night | Monitor
2025-08-13 07:45 | 2025-08-13 07:45 | 0.25 | Extreme triggered | lower | 79.52 | 2.2253 | 2.2253 | 0.2055 | Day | Monitor
2025-08-08 04:15 | 2025-08-08 04:15 | 0.25 | Extreme triggered | lower | 79.52 | 2.1794 | 2.1794 | 0.2024 | Night | Monitor
2025-08-07 06:30 | 2025-08-07 06:30 | 0.25 | Extreme triggered | upper | 80.36 | 2.1222 | 2.1222 | 0.1986 | Night | Monitor
2025-08-11 18:00 | 2025-08-11 18:00 | 0.25 | Extreme triggered | upper | 75.32 | 2.0417 | 2.0417 | 0.1933 | Day | Monitor
2025-08-09 03:15 | 2025-08-09 03:15 | 0.25 | Extreme triggered | upper | 80.36 | 2.0125 | 2.0125 | 0.1913 | Night | Monitor

## Events
All events | [10 empty] | Report generated: 10/09/2026 16:09
< Back to summary worksheet
One row per event (from Extreme triggered until Persistence ends), sorted by start time. Use the filter buttons in the header row.
Start | End | Duration (h) | Direction | Peak value | Max ¦Z¦ | Mean ¦Z¦ (event) | Highest state | Max materiality score | Day/Night at start | Month | Action
2025-08-01 06:00 | 2025-08-01 06:15 | 0.5 | lower | 79.52 | 2.976 | 2.0415 | Extreme/elevated | 0.2841 | Night | Aug 2025 | Monitor
2025-08-01 08:30 | 2025-08-01 11:15 | 3 | lower | 74.76 | 3.445 | 2.2947 | Confirmed/Materialized Shift | 0.6102 | Day | Aug 2025 | Investigate
2025-08-01 19:30 | 2025-08-01 23:30 | 4.25 | upper | 80.08 | 3.4006 | 2.1014 | Confirmed/Materialized Shift | 0.6206 | Night | Aug 2025 | Investigate
2025-08-02 03:00 | 2025-08-02 03:00 | 0.25 | upper | 80.36 | 2.2938 | 2.2938 | Extreme triggered | 0.2386 | Night | Aug 2025 | Monitor
2025-08-02 06:30 | 2025-08-02 06:30 | 0.25 | lower | 79.52 | 2.3202 | 2.3202 | Extreme triggered | 0.2404 | Night | Aug 2025 | Monitor
2025-08-02 08:15 | 2025-08-02 11:45 | 3.75 | lower | 74.76 | 3.1152 | 2.0909 | Confirmed/Materialized Shift | 0.5648 | Day | Aug 2025 | Investigate
2025-08-02 15:30 | 2025-08-02 15:30 | 0.25 | lower | 74.48 | 2.2757 | 2.2757 | Extreme triggered | 0.2374 | Day | Aug 2025 | Monitor
2025-08-02 17:30 | 2025-08-02 17:30 | 0.25 | upper | 75.32 | 2.1794 | 2.1794 | Extreme triggered | 0.231 | Day | Aug 2025 | Monitor
2025-08-02 19:30 | 2025-08-02 23:15 | 4 | upper | 80.08 | 3.074 | 2.08 | Confirmed/Materialized Shift | 0.6044 | Night | Aug 2025 | Investigate
2025-08-03 08:15 | 2025-08-03 11:45 | 3.75 | lower | 74.48 | 3.5563 | 2.135 | Confirmed/Materialized Shift | 0.613 | Day | Aug 2025 | Investigate
2025-08-03 19:15 | 2025-08-03 23:30 | 4.5 | upper | 80.08 | 3.3593 | 2.0698 | Confirmed/Materialized Shift | 0.5868 | Night | Aug 2025 | Investigate
2025-08-04 02:30 | 2025-08-04 02:30 | 0.25 | upper | 80.36 | 2.2757 | 2.2757 | Extreme triggered | 0.2089 | Night | Aug 2025 | Monitor
2025-08-04 08:15 | 2025-08-04 11:45 | 3.75 | lower | 74.76 | 3.4305 | 2.1707 | Confirmed/Materialized Shift | 0.6142 | Day | Aug 2025 | Investigate
2025-08-04 19:15 | 2025-08-04 23:30 | 4.5 | upper | 80.36 | 3.1537 | 2.0856 | Confirmed/Materialized Shift | 0.6399 | Night | Aug 2025 | Investigate
2025-08-05 04:45 | 2025-08-05 05:00 | 0.5 | upper | 80.36 | 2.2757 | 1.7506 | Extreme/elevated | 0.2531 | Night | Aug 2025 | Monitor
2025-08-05 06:30 | 2025-08-05 06:30 | 0.25 | lower | 79.52 | 2.351 | 2.351 | Extreme triggered | 0.271 | Night | Aug 2025 | Monitor
2025-08-05 08:15 | 2025-08-05 11:45 | 3.75 | lower | 74.76 | 3.2714 | 2.1095 | Confirmed/Materialized Shift | 0.5893 | Day | Aug 2025 | Investigate
2025-08-05 16:15 | 2025-08-05 16:15 | 0.25 | upper | 75.32 | 2.2993 | 2.2993 | Extreme triggered | 0.2104 | Day | Aug 2025 | Monitor
2025-08-05 19:30 | 2025-08-05 23:30 | 4.25 | upper | 80.08 | 3.2692 | 2.0696 | Confirmed/Materialized Shift | 0.5858 | Night | Aug 2025 | Investigate
2025-08-06 08:15 | 2025-08-06 09:45 | 1.75 | lower | 75.32 | 3.205 | 2.852 | Confirmed/Materialized Shift | 0.5957 | Day | Aug 2025 | Investigate
2025-08-07 02:45 | 2025-08-07 02:45 | 0.25 | lower | 79.52 | 2.4597 | 2.4597 | Extreme triggered | 0.2211 | Night | Aug 2025 | Monitor
2025-08-07 03:30 | 2025-08-07 03:30 | 0.25 | lower | 79.52 | 2.0417 | 2.0417 | Extreme triggered | 0.2218 | Night | Aug 2025 | Monitor
2025-08-07 06:30 | 2025-08-07 06:30 | 0.25 | upper | 80.36 | 2.1222 | 2.1222 | Extreme triggered | 0.1986 | Night | Aug 2025 | Monitor
2025-08-07 08:15 | 2025-08-07 11:45 | 3.75 | lower | 74.76 | 3.4548 | 2.0886 | Confirmed/Materialized Shift | 0.586 | Day | Aug 2025 | Investigate
2025-08-07 19:15 | 2025-08-07 23:15 | 4.25 | upper | 80.36 | 3.2738 | 2.1587 | Confirmed/Materialized Shift | 0.6466 | Night | Aug 2025 | Investigate
2025-08-08 04:15 | 2025-08-08 04:15 | 0.25 | lower | 79.52 | 2.1794 | 2.1794 | Extreme triggered | 0.2024 | Night | Aug 2025 | Monitor
2025-08-08 08:30 | 2025-08-08 11:30 | 3.25 | lower | 74.76 | 3.447 | 2.1739 | Confirmed/Materialized Shift | 0.6345 | Day | Aug 2025 | Investigate
2025-08-08 19:15 | 2025-08-08 23:45 | 4.75 | upper | 80.36 | 3.2738 | 2.0293 | Confirmed/Materialized Shift | 0.6007 | Night | Aug 2025 | Investigate
2025-08-09 03:15 | 2025-08-09 03:15 | 0.25 | upper | 80.36 | 2.0125 | 2.0125 | Extreme triggered | 0.1913 | Night | Aug 2025 | Monitor
2025-08-09 08:15 | 2025-08-09 11:45 | 3.75 | lower | 74.76 | 3.4598 | 2.1101 | Confirmed/Materialized Shift | 0.5951 | Day | Aug 2025 | Investigate
2025-08-09 19:15 | 2025-08-09 23:45 | 4.75 | upper | 79.52 | 3.1409 | 2.0857 | Confirmed/Materialized Shift | 0.6252 | Night | Aug 2025 | Investigate
2025-08-10 07:00 | 2025-08-10 08:30 | 1.75 | upper | 80.36 | 4.2485 | 2.2116 | Confirmed/Materialized Shift | 0.5018 | Day | Aug 2025 | Investigate
2025-08-10 19:15 | 2025-08-10 23:15 | 4.25 | upper | 80.36 | 3.2738 | 2.1505 | Confirmed/Materialized Shift | 0.5969 | Night | Aug 2025 | Investigate
2025-08-11 04:30 | 2025-08-11 05:15 | 1 | upper | 80.36 | 2.2993 | 1.327 | Persistent | 0.324 | Night | Aug 2025 | Review
2025-08-11 08:15 | 2025-08-11 11:15 | 3.25 | lower | 74.48 | 3.2811 | 2.3065 | Confirmed/Materialized Shift | 0.611 | Day | Aug 2025 | Investigate
2025-08-11 15:00 | 2025-08-11 15:00 | 0.25 | upper | 75.32 | 2.3202 | 2.3202 | Extreme triggered | 0.2118 | Day | Aug 2025 | Monitor
2025-08-11 18:00 | 2025-08-11 18:00 | 0.25 | upper | 75.32 | 2.0417 | 2.0417 | Extreme triggered | 0.1933 | Day | Aug 2025 | Monitor
2025-08-11 19:30 | 2025-08-11 23:30 | 4.25 | upper | 80.08 | 3.2 | 2.0577 | Confirmed/Materialized Shift | 0.5943 | Night | Aug 2025 | Investigate
2025-08-12 08:15 | 2025-08-12 11:45 | 3.75 | lower | 74.76 | 3.4558 | 2.091 | Confirmed/Materialized Shift | 0.6422 | Day | Aug 2025 | Investigate
2025-08-12 19:15 | 2025-08-12 23:00 | 4 | upper | 80.36 | 3.3995 | 2.2293 | Confirmed/Materialized Shift | 0.591 | Night | Aug 2025 | Investigate
2025-08-13 07:45 | 2025-08-13 07:45 | 0.25 | lower | 79.52 | 2.2253 | 2.2253 | Extreme triggered | 0.2055 | Day | Aug 2025 | Monitor
2025-08-13 08:15 | 2025-08-13 11:30 | 3.5 | lower | 74.76 | 3.223 | 2.1754 | Confirmed/Materialized Shift | 0.5576 | Day | Aug 2025 | Investigate
2025-08-13 16:15 | 2025-08-13 16:15 | 0.25 | upper | 75.32 | 2.5628 | 2.5628 | Extreme triggered | 0.228 | Day | Aug 2025 | Monitor
2025-08-13 19:15 | 2025-08-13 23:30 | 4.5 | upper | 80.08 | 3.0987 | 2.0645 | Confirmed/Materialized Shift | 0.6091 | Night | Aug 2025 | Investigate
2025-08-14 08:15 | 2025-08-14 11:45 | 3.75 | lower | 74.48 | 3.5738 | 2.1293 | Confirmed/Materialized Shift | 0.6118 | Day | Aug 2025 | Investigate
2025-08-14 16:45 | 2025-08-14 16:45 | 0.25 | upper | 75.32 | 2.2757 | 2.2757 | Extreme triggered | 0.2374 | Day | Aug 2025 | Monitor
2025-08-14 18:45 | 2025-08-14 18:45 | 0.25 | lower | 74.48 | 2.2584 | 2.2584 | Extreme triggered | 0.2363 | Day | Aug 2025 | Monitor
2025-08-14 19:30 | 2025-08-14 23:15 | 4 | upper | 80.36 | 3.0376 | 2.0818 | Confirmed/Materialized Shift | 0.5379 | Night | Aug 2025 | Investigate

## Daily overview
Daily overview | [9 empty] | Report generated: 10/09/2026 16:09
< Back to summary worksheet
One row per day with data. Bars: share of extreme readings (red) and peak materiality (blue).
Date | Readings | Mean value | Min value | Max value | Extreme readings | Extreme share | Persistent periods | Confirmed shift periods | Abnormal changes | Material changes | Max materiality score
2025-08-01 | 96 | 77.5542 | 74.76 | 80.36 | 16 | 16.67% | 8 | 17 | 5 | 2 | 0.6206
2025-08-02 | 96 | 77.5338 | 74.48 | 80.36 | 21 | 21.88% | 8 | 19 | 5 | 1 | 0.6044
2025-08-03 | 96 | 77.5338 | 74.48 | 80.36 | 19 | 19.79% | 8 | 21 | 4 | 2 | 0.613
2025-08-04 | 96 | 77.5658 | 74.48 | 80.36 | 18 | 18.75% | 8 | 21 | 5 | 3 | 0.6399
2025-08-05 | 96 | 77.5688 | 74.76 | 80.36 | 21 | 21.88% | 8 | 20 | 5 | 1 | 0.5893
2025-08-06 | 48 | 79.6425 | 75.32 | 80.36 | 7 | 14.58% | 4 | 1 | 4 | 2 | 0.5957
2025-08-07 | 96 | 77.5367 | 74.48 | 80.36 | 21 | 21.88% | 8 | 20 | 6 | 3 | 0.6466
2025-08-08 | 96 | 77.5192 | 74.76 | 80.36 | 17 | 17.71% | 8 | 20 | 5 | 3 | 0.6345
2025-08-09 | 96 | 76.9125 | 72.52 | 80.36 | 19 | 19.79% | 8 | 22 | 6 | 2 | 0.6252
2025-08-10 | 96 | 75.3696 | 72.52 | 80.36 | 12 | 12.5% | 8 | 12 | 3 | 0 | 0.5969
2025-08-11 | 96 | 77.5221 | 74.48 | 80.36 | 20 | 20.83% | 10 | 18 | 5 | 2 | 0.611
2025-08-12 | 96 | 77.5746 | 74.76 | 80.36 | 18 | 18.75% | 8 | 19 | 6 | 3 | 0.6422
2025-08-13 | 96 | 77.5571 | 74.76 | 80.36 | 20 | 20.83% | 8 | 20 | 3 | 1 | 0.6091
2025-08-14 | 96 | 77.5775 | 74.48 | 80.36 | 17 | 17.71% | 8 | 19 | 4 | 2 | 0.6118

## Monthly metrics
Monthly metrics | [23 empty] | Report generated: 10/09/2026 16:09
< Back to summary worksheet
Computed from the results by the app. Reading interval: 15.00 minutes (median spacing of the timestamps). Rank 1 = the month with the most issues. Gap hours count in the month where the gap starts.
Month | Readings | Days with data | Mean value | Min value | Max value | Extreme readings | Extreme share | Upper extremes | Lower extremes | Persistent periods | Confirmed shift periods | Sustained deviation (h) | Confirmed share | Abnormal changes | Material changes | Material changes per day | Mean materiality score | Max materiality score | Max ¦Z¦ | Events | Data gap hours | Rank: extreme share | Rank: sustained (h) | Rank: material changes/day | Rank: mean materiality
Aug 2025 | 1296 | 14 | 77.4183 | 72.52 | 80.36 | 246 | 18.98% | 133 | 113 | 110 | 249 | 89.75 | 19.21% | 66 | 27 | 1.9286 | 0.19815 | 0.6466 | 4.2485 | 48 | 12.25 | 1 | 1 | 1 | 1
All | 1296 | 14 | 77.4183 | 72.52 | 80.36 | 246 | 18.98% | 133 | 113 | 110 | 249 | 89.75 | 19.21% | 66 | 27 | 1.9286 | 0.19815 | 0.6466 | 4.2485 | 48 | 12.25

## Column descriptor
Column descriptor |  |  | Report generated: 10/09/2026 16:09
< Back to summary worksheet
Meaning of every column in res.csv and the parameters that drive it. Full detail: Statistical calc parameters manual.
Column | Meaning | Driven by | Step
Timestamp | Time of the reading | — | Input
Value | The reading | — | Input
AbnormalChangeFlag | Unusually fast change: ¦ROC_ZScore¦ ≥ ROC_K | ROC_K | Change
ConfirmedShiftFlag | Reading is in a Confirmed/Materialized Shift | N_M, K_M | Materiality
DeltaLower | LowerLimit − Value (positive = below the band) | limits | Extreme
DeltaLower_pct | DeltaLower as % of LowerLimit | limits | Extreme
DeltaUpper | Value − UpperLimit (positive = above the band) | limits | Extreme
DeltaUpper_pct | DeltaUpper as % of UpperLimit | limits | Extreme
DeltaX | Change from the previous reading | — | Change
EventEndTime | End of the event this reading belongs to | K_P, N_EXIT | Persistence
EventStartTime | Start of the event this reading belongs to | K_E | Persistence
ExtremeDirection | upper / lower / none | Method, K_E | Extreme
ExtremeFlag | Reading outside the normal range | Method, Window, K_E, p, K_IQR | Extreme
FrequencyCount | Abnormal changes in the last frequency window | Frequency window | Change
LowerLimit | Lower edge of the normal range: MA − K_E·σ | Method, Window, K_E | Extreme
MaterialChangeFlag | Abnormal change that recurs (FrequencyCount ≥ min) | Min recurrences | Change
MaterialExtremeFlag | Extreme that also lasted N_P readings | N_P | Materiality
MaterialityScore | 0–1 ranking: Wm·magnitude + Wd·duration + Wf·frequency | Weights, K_E, N_M | Materiality
MeanZ_event | Average ¦Z¦ over the event so far | — | Persistence
MovingAverage | Baseline (rolling mean over Window) | Method, Window, α | Extreme
PersistenceCount | Readings in the current event | K_P, N_EXIT | Persistence
ROC | Rate of change: (x(t) − x(t−h)) / h | ROC horizon | Change
ROC_MeanBaseline | Rolling mean of ROC | ROC baseline window | Change
ROC_StdDev | Rolling std of ROC | ROC baseline window | Change
ROC_ZScore | (ROC − mean) / std | ROC baseline window | Change
RollingStdDev | σ used for the limits | Method, Window | Extreme
State | Normal, Extreme triggered, Extreme/elevated, Persistent, Confirmed/Materialized Shift, Persistence ends | K_E, K_P, N_P, N_M, K_M, N_EXIT | Persistence
UpperLimit | Upper edge of the normal range: MA + K_E·σ | Method, Window, K_E | Extreme
ZScore | (Value − MA) / σ | Method, Window | Extreme
Day/Night | Day or night category of the reading | time of day | Input
Settings detected in this results file
Window 20, K_E 2