## Summary
Results analysis summary: Monthly overview |  |  | Report generated: 10/09/2026 16:09
Hello,
Below is a summary of the 1 month of readings for Test Building, AHU 1 (1,296 readings, 08/01/2025 – 08/14/2025), and our recommendations.
Use the tabs at the bottom to find more detail about each month, including event-level actions.
Read the Guide | See the charts (go to 'Dashboard') | Read the AI review (go to 'AI review')
AI summary |  | Plain built-in wording (AI not used). AI wording not used: no OpenAI API key is set ([openai] api_key in config.local.ini).
● Data gap: no readings from 2025-08-06 09:45 to 2025-08-06 22:00 (12 h 15 min).
● Below typical from 2025-08-09 22:00 to 2025-08-10 06:45 (9 h), up to 7.56°F from typical.
● The engine flagged 47 events with a 5.0-hour baseline; with a 24.0-hour baseline the same data gives 6.
August 2025 / Sensor: Test Building, AHU 1 (°F) |  | Rank by mean materiality: 1 out of 1 months · extremes 19% of readings | Status: | 3 recommendations
Improve | Recommendations | Why have we recommended this? |  | Learn more
Operating level | ● Review what changed when the level shifted | Confirmed shift share: 19% of readings (62 h). The value stayed away from its baseline for N_M readings in a row with a high mean ¦Z¦ - check setpoint or schedule changes, sensor drift or an equipment fault. |  | Confirmed/Materialized Shift
Sensitivity | ● Consider a longer baseline window | Extreme share is 19% of readings, well above the ~5% expected at K_E = 2. A longer Window (96 = 24 h) or a higher K_E would flag fewer routine swings. |  | K_E
Data quality | ● Fix the data gaps | Missing data: 12.2 h in gaps longer than three reading intervals. Events inside a gap cannot be detected. |  | Data gaps
Show events and benchmarks for this month (go to 'Aug 2025')
Data quality / Gaps in the readings |  | 1 gaps, 12.2 hours of missing data | Status: | Gaps to review
Show the gaps (go to 'Data gaps')

## AI review
AI review | Report generated: 10/09/2026 16:09
< Back to summary worksheet
Plain built-in wording (AI not used). AI wording not used: no OpenAI API key is set ([openai] api_key in config.local.ini).
Causes are hypotheses to check, not conclusions. The figures on the other tabs are computed by the app.
Summary
● Data gap: no readings from 2025-08-06 09:45 to 2025-08-06 22:00 (12 h 15 min).
● Below typical from 2025-08-09 22:00 to 2025-08-10 06:45 (9 h), up to 7.56°F from typical.
● The engine flagged 47 events with a 5.0-hour baseline; with a 24.0-hour baseline the same data gives 6.
Normal behaviour
The typical daily swing is 5.6-7.84°F; schedule transitions happen around hours 7, 8, 9, 10, 18, 19, 20, 21, 22.
Abnormal periods
Below typical for this time of day | Observed 72.52-72.52°F where 80.08-80.08°F is typical. Check schedules, overrides and equipment logs for this period - a hypothesis to check, not a conclusion.
Data gaps
Readings resumed after the gap.
Rate of change
● Typical fastest change: -0.84°F down, 0.84°F up per reading.
● 70.0% of abnormal-change flags fall in schedule transition hours.
Volatility
● Daily variability of changes stays between 0.32 and 0.83°F.
Why the engine flagged what it did
93.0% of extreme flags (228 of 246) fall in schedule transition hours, and 50 came from periods with almost no variability.
Recommendations: operations
Review the abnormal periods | Check schedules, overrides and equipment logs for the periods listed.
Check the data gap | Find the cause and alert on missing data.
Recommendations: analytics settings
Use a daily baseline | A window covering one day avoids flagging the normal cycle.
Add a variability floor | At least one sensor step, so a single tick cannot trigger an extreme.
Limitations
● Causes are hypotheses for investigation.
● The typical baseline uses only the period in this file.

## Dashboard
Dashboard | [11 empty] | Report generated: 10/09/2026 16:09
< Back to summary worksheet
Charts for the whole period. The monthly figures behind them are in the table below.
Monthly figures
Month | Extreme share | Confirmed share | Sustained deviation (h) | Material changes per day | Investigate | Review | Monitor | Upper – Day | Upper – Night | Lower – Day | Lower – Night
Aug 2025 | 18.98% | 19.21% | 89.75 | 1.9286 | 27 | 1 | 20 | 9 | 124 | 106 | 7
By month
Events and extremes
Time of day
By day

## Guide
Guide
This report summarises the Extreme & Change analysis of Test Building, AHU 1 and gives recommendations and benchmarks for each month.
It shows when the readings left their normal range, how long deviations lasted, how often the value changed abnormally fast, and how much data is missing.
How to use this report
Use the tabs at the bottom of the screen to move through the workbook.
Tab (at the bottom of the screen) | What is on the tab?
Summary | Overview of each month with recommendations, the AI summary, and links to the month tabs.
AI review | The written analysis: summary, normal behaviour, abnormal periods, changes, recommendations and limitations.
Dashboard | Charts: monthly measures, events and extremes, time-of-day heatmap and the daily overview.
Month tabs | ● Analysis funnel: extreme share, sustained deviation hours and material changes per day, with the month's rank.
● Recommendations with this month vs the best and worst month, and more benchmarks (also day vs night).
● A chart of the readings against the normal range, and every event sorted by materiality.
Data gaps | Every break in the data longer than three reading intervals, with the hours missing.
Events | All events in the whole period in one filterable list.
Daily overview | One row per day: readings, value range, extremes, persistent and confirmed periods, changes.
Monthly metrics | The monthly figures behind the Summary and month tabs.
Column descriptor | What every column of the results file means and which parameters drive it.
Data | The results file as exported by the app.
How are the results calculated?
Each reading is compared with a rolling baseline of the previous readings (Window 20, K_E 2). ¦Z¦ ≥ K_E flags an Extreme reading.
An event continues while ¦Z¦ ≥ K_P; after N_P readings it is Persistent, after N_M readings with mean ¦Z¦ ≥ K_M it is a Confirmed/Materialized Shift.
The rate of change has its own baseline; ¦Z_ROC¦ ≥ ROC_K is an Abnormal Change, and repeats within the frequency window make a Material Change.
The Materiality score (0–1) combines size (¦Z¦), duration and recurrence. Rank 1 = the month with the most issues.
Recommendations are rules applied to these figures; they point to what to check, they are not a diagnosis of the equipment.
Learn more: info_main\Statistical_calc_parameters\Statistical calc parameters manual.docx

## Data gaps
Data gaps | [6 empty] | Report generated: 10/09/2026 16:09
The analysis expects one reading about every 15 minutes.
A gap is any break of more than three reading intervals. No readings, and so no extremes or events, exist inside a gap.
This tab lists every gap and the time it covers, so missing data is not mistaken for normal operation.
Summary of gaps
Number of gaps |  | 1
Missing time (hours) |  | 12.25
From (last reading) | To (next reading) | Hours missing | Readings missing (approx.) | Day/Night at start | Severity | Action
2025-08-06 09:45 | 2025-08-06 22:00 | 12.25 | 48 | Day | Medium | Check the logger / network for this period

## Aug 2025
We compared each reading with its own rolling baseline using the settings below | [5 empty] | Rank by mean materiality: 1 of 1 months (1 = most issues)
Sensor: Test Building, AHU 1 (°F), Period: August 2025, Value range: 72.5 – 80.4 °F | [5 empty] | Report generated: 10/09/2026 16:09
< Back to summary worksheet
Analysis funnel
Readings in this month: 1,296 |  | vs other months (1) | Recommendations to improve |  |  |  | Why have we recommended this?
| Extreme readings |  |  | This month | Best month | Worst month
| Share of readings | Rank vs other months | ● Review what changed when the level shifted | 19.21% | 19.21% | 19.21% | Confirmed shift share: 19% of readings (62 h). The value stayed away from its baseline for N_M readings in a row with a high mean ¦Z¦ - check setpoint or schedule changes, sensor drift or an equipment fault.
| 18.98% | 1
| Sustained deviations |  | ● Consider a longer baseline window | 18.98% | 18.98% | 18.98% | Extreme share is 19% of readings, well above the ~5% expected at K_E = 2. A longer Window (96 = 24 h) or a higher K_E would flag fewer routine swings.
| Hours (Persistent + Confirmed) | Rank vs other months
| 89.75 | 1
|  |  | ● Fix the data gaps | 12.25 | 12.25 | 12.25 | Missing data: 12.2 h in gaps longer than three reading intervals. Events inside a gap cannot be detected.
Material changes
| Per day | Rank vs other months
| 1.9286 | 1
More benchmarks
|  |  | Measure | This month | Best month | Worst month | Whole period | This month – Day | This month – Night
|  |  | Mean value | 77.4183 | 77.4183 | 77.4183 | 77.4183 | 75.8474 | 78.932
|  |  | Min value | 72.52 | 72.52 | 72.52 | 72.52 | 74.48 | 72.52
|  |  | Max value | 80.36 | 80.36 | 80.36 | 80.36 | 80.36 | 80.36
|  |  | Extreme share | 18.98% | 18.98% | 18.98% | 18.98% | 18.08% | 19.85%
|  |  | Upper extremes | 133 | 133 | 133 | 133 | 9 | 124
|  |  | Lower extremes | 113 | 113 | 113 | 113 | 106 | 7
|  |  | Sustained deviation (h) | 89.75 | 89.75 | 89.75 | 89.75 | 39.5 | 50.25
|  |  | Confirmed share | 19.21% | 19.21% | 19.21% | 19.21% | 16.04% | 22.27%
|  |  | Material changes per day | 1.9286 | 1.9286 | 1.9286 | 1.9286 | Not relevant | Not relevant
|  |  | Mean materiality score | 0.19815 | 0.19815 | 0.19815 | 0.19815 | 0.18485 | 0.21096
|  |  | Max ¦Z¦ | 4.2485 | 4.2485 | 4.2485 | 4.2485 | 4.2485 | 3.4006
|  |  | Data gap hours | 12.25 | 12.25 | 12.25 | 12.25 | Not relevant | Not relevant
* Best = lowest month, Worst = highest month for each measure (for Mean/Min/Max value: simply the lowest and highest month).
* With a 20-reading rolling window ¦Z¦ cannot exceed (W−1)/√W = 4.25, so Max ¦Z¦ is similar in every month; use Extreme share and the events instead.
* Settings detected in the results: Window 20, K_E 2.
Readings against the normal range
Grey band = normal range (moving average ± K_E·σ). Dots outside it are Extreme readings: orange = upper, blue = lower.
Events in this month
View all events
* Sorted by materiality score (highest first). Action: Investigate = Confirmed shift, Review = Persistent, Monitor = shorter events. Click the Action to see the readings.
Start | End | Duration (h) | Highest state | Direction | Peak value | Max ¦Z¦ | Mean ¦Z¦ | Max materiality | Day/Night | Action
2025-08-07 19:15 | 2025-08-07 23:15 | 4.25 | Confirmed/Materialized Shift | upper | 80.36 | 3.2738 | 2.1587 | 0.6466 | Night | Investigate
2025-08-12 08:15 | 2025-08-12 11:45 | 3.75 | Confirmed/Materialized Shift | lower | 74.76 | 3.4558 | 2.091 | 0.6422 | Day | Investigate
2025-08-04 19:15 | 2025-08-04 23:30 | 4.5 | Confirmed/Materialized Shift | upper | 80.36 | 3.1537 | 2.0856 | 0.6399 | Night | Investigate
2025-08-08 08:30 | 2025-08-08 11:30 | 3.25 | Confirmed/Materialized Shift | lower | 74.76 | 3.447 | 2.1739 | 0.6345 | Day | Investigate
2025-08-09 19:15 | 2025-08-09 23:45 | 4.75 | Confirmed/Materialized Shift | upper | 79.52 | 3.1409 | 2.0857 | 0.6252 | Night | Investigate
2025-08-01 19:30 | 2025-08-01 23:30 | 4.25 | Confirmed/Materialized Shift | upper | 80.08 | 3.4006 | 2.1014 | 0.6206 | Night | Investigate
2025-08-04 08:15 | 2025-08-04 11:45 | 3.75 | Confirmed/Materialized Shift | lower | 74.76 | 3.4305 | 2.1707 | 0.6142 | Day | Investigate
2025-08-03 08:15 | 2025-08-03 11:45 | 3.75 | Confirmed/Materialized Shift | lower | 74.48 | 3.5563 | 2.135 | 0.613 | Day | Investigate
2025-08-14 08:15 | 2025-08-14 11:45 | 3.75 | Confirmed/Materialized Shift | lower | 74.48 | 3.5738 | 2.1293 | 0.6118 | Day | Investigate
2025-08-11 08:15 | 2025-08-11 11:15 | 3.25 | Confirmed/Materialized Shift | lower | 74.48 | 3.2811 | 2.3065 | 0.611 | Day | Investigate
2025-08-01 08:30 | 2025-08-01 11:15 | 3 | Confirmed/Materialized Shift | lower | 74.76 | 3.445 | 2.2947 | 0.6102 | Day | Investigate
2025-08-13 19:15 | 2025-08-13 23:30 | 4.5 | Confirmed/Materialized Shift | upper | 80.08 | 3.0987 | 2.0645 | 0.6091 | Night | Investigate
2025-08-02 19:30 | 2025-08-02 23:15 | 4 | Confirmed/Materialized Shift | upper | 80.08 | 3.074 | 2.08 | 0.6044 | Night | Investigate
2025-08-08 19:15 | 2025-08-08 23:45 | 4.75 | Confirmed/Materialized Shift | upper | 80.36 | 3.2738 | 2.0293 | 0.6007 | Night | Investigate
2025-08-10 19:15 | 2025-08-10 23:15 | 4.25 | Confirmed/Materialized Shift | upper | 80.36 | 3.2738 | 2.1505 | 0.5969 | Night | Investigate
2025-08-06 08:15 | 2025-08-06 09:45 | 1.75 | Confirmed/Materialized Shift | lower | 75.32 | 3.205 | 2.852 | 0.5957 | Day | Investigate
2025-08-09 08:15 | 2025-08-09 11:45 | 3.75 | Confirmed/Materialized Shift | lower | 74.76 | 3.4598 | 2.1101 | 0.5951 | Day | Investigate
2025-08-11 19:30 | 2025-08-11 23:30 | 4.25 | Confirmed/Materialized Shift | upper | 80.08 | 3.2 | 2.0577 | 0.5943 | Night | Investigate
2025-08-12 19:15 | 2025-08-12 23:00 | 4 | Confirmed/Materialized Shift | upper | 80.36 | 3.3995 | 2.2293 | 0.591 | Night | Investigate
2025-08-05 08:15 | 2025-08-05 11:45 | 3.75 | Confirmed/Materialized Shift | lower | 74.76 | 3.2714 | 2.1095 | 0.5893 | Day | Investigate
2025-08-03 19:15 | 2025-08-03 23:30 | 4.5 | Confirmed/Materialized Shift | upper | 80.08 | 3.3593 | 2.0698 | 0.5868 | Night | Investigate
2025-08-07 08:15 | 2025-08-07 11:45 | 3.75 | Confirmed/Materialized Shift | lower | 74.76 | 3.4548 | 2.0886 | 0.586 | Day | Investigate
2025-08-05 19:30 | 2025-08-05 23:30 | 4.25 | Confirmed/Materialized Shift | upper | 80.08 | 3.2692 | 2.0696 | 0.5858 | Night | Investigate
2025-08-02 08:15 | 2025-08-02 11:45 | 3.75 | Confirmed/Materialized Shift | lower | 74.76 | 3.1152 | 2.0909 | 0.5648 | Day | Investigate
2025-08-13 08:15 | 2025-08-13 11:30 | 3.5 | Confirmed/Materialized Shift | lower | 74.76 | 3.223 | 2.1754 | 0.5576 | Day | Investigate
2025-08-14 19:30 | 2025-08-14 23:15 | 4 | Confirmed/Materialized Shift | upper | 80.36 | 3.0376 | 2.0818 | 0.5379 | Night | Investigate
2025-08-10 07:00 | 2025-08-10 08:30 | 1.75 | Confirmed/Materialized Shift | upper | 80.36 | 4.2485 | 2.2116 | 0.5018 | Day | Investigate
2025-08-11 04:30 | 2025-08-11 05:15 | 1 | Persistent | upper | 80.36 | 2.2993 | 1.327 | 0.324 | Night | Review
2025-08-01 06:00 | 2025-08-01 06:15 | 0.5 | Extreme/elevated | lower | 79.52 | 2.976 | 2.0415 | 0.2841 | Night | Monitor
2025-08-05 06:30 | 2025-08-05 06:30 | 0.25 | Extreme triggered | lower | 79.52 | 2.351 | 2.351 | 0.271 | Night | Monitor
2025-08-05 04:45 | 2025-08-05 05:00 | 0.5 | Extreme/elevated | upper | 80.36 | 2.2757 | 1.7506 | 0.2531 | Night | Monitor
2025-08-02 06:30 | 2025-08-02 06:30 | 0.25 | Extreme triggered | lower | 79.52 | 2.3202 | 2.3202 | 0.2404 | Night | Monitor
2025-08-02 03:00 | 2025-08-02 03:00 | 0.25 | Extreme triggered | upper | 80.36 | 2.2938 | 2.2938 | 0.2386 | Night | Monitor
2025-08-14 16:45 | 2025-08-14 16:45 | 0.25 | Extreme triggered | upper | 75.32 | 2.2757 | 2.2757 | 0.2374 | Day | Monitor
2025-08-02 15:30 | 2025-08-02 15:30 | 0.25 | Extreme triggered | lower | 74.48 | 2.2757 | 2.2757 | 0.2374 | Day | Monitor
2025-08-14 18:45 | 2025-08-14 18:45 | 0.25 | Extreme triggered | lower | 74.48 | 2.2584 | 2.2584 | 0.2363 | Day | Monitor
2025-08-02 17:30 | 2025-08-02 17:30 | 0.25 | Extreme triggered | upper | 75.32 | 2.1794 | 2.1794 | 0.231 | Day | Monitor
2025-08-13 16:15 | 2025-08-13 16:15 | 0.25 | Extreme triggered | upper | 75.32 | 2.5628 | 2.5628 | 0.228 | Day | Monitor
2025-08-07 03:30 | 2025-08-07 03:30 | 0.25 | Extreme triggered | lower | 79.52 | 2.0417 | 2.0417 | 0.2218 | Night | Monitor
2025-08-07 02:45 | 2025-08-07 02:45 | 0.25 | Extreme triggered | lower | 79.52 | 2.4597 | 2.4597 | 0.2211 | Night | Monitor
2025-08-11 15:00 | 2025-08-11 15:00 | 0.25 | Extreme triggered | upper | 75.32 | 2.3202 | 2.3202 | 0.2118 | Day | Monitor
2025-08-05 16:15 | 2025-08-05 16:15 | 0.25 | Extreme triggered | upper | 75.32 | 2.2993 | 2.2993 | 0.2104 | Day | Monitor
2025-08-04 02:30 | 2025-08-04 02:30 | 0.25 | Extreme triggered | upper | 80.36 | 2.2757 | 2.2757 | 0.2089 | Night | Monitor
2025-08-13 07:45 | 2025-08-13 07:45 | 0.25 | Extreme triggered | lower | 79.52 | 2.2253 | 2.2253 | 0.2055 | Day | Monitor
2025-08-08 04:15 | 2025-08-08 04:15 | 0.25 | Extreme triggered | lower | 79.52 | 2.1794 | 2.1794 | 0.2024 | Night | Monitor
2025-08-07 06:30 | 2025-08-07 06:30 | 0.25 | Extreme triggered | upper | 80.36 | 2.1222 | 2.1222 | 0.1986 | Night | Monitor
2025-08-11 18:00 | 2025-08-11 18:00 | 0.25 | Extreme triggered | upper | 75.32 | 2.0417 | 2.0417 | 0.1933 | Day | Monitor
2025-08-09 03:15 | 2025-08-09 03:15 | 0.25 | Extreme triggered | upper | 80.36 | 2.0125 | 2.0125 | 0.1913 | Night | Monitor

## Events
All events | [10 empty] | Report generated: 10/09/2026 16:09
< Back to summary worksheet
One row per event (from Extreme triggered until Persistence ends), sorted by start time. Use the filter buttons in the header row.
Start | End | Duration (h) | Direction | Peak value | Max ¦Z¦ | Mean ¦Z¦ (event) | Highest state | Max materiality score | Day/Night at start | Month | Action | Readings
2025-08-01 06:00 | 2025-08-01 06:15 | 0.5 | lower | 79.52 | 2.976 | 2.0415 | Extreme/elevated | 0.2841 | Night | Aug 2025 | Monitor | View readings
2025-08-01 08:30 | 2025-08-01 11:15 | 3 | lower | 74.76 | 3.445 | 2.2947 | Confirmed/Materialized Shift | 0.6102 | Day | Aug 2025 | Investigate | View readings
2025-08-01 19:30 | 2025-08-01 23:30 | 4.25 | upper | 80.08 | 3.4006 | 2.1014 | Confirmed/Materialized Shift | 0.6206 | Night | Aug 2025 | Investigate | View readings
2025-08-02 03:00 | 2025-08-02 03:00 | 0.25 | upper | 80.36 | 2.2938 | 2.2938 | Extreme triggered | 0.2386 | Night | Aug 2025 | Monitor | View readings
2025-08-02 06:30 | 2025-08-02 06:30 | 0.25 | lower | 79.52 | 2.3202 | 2.3202 | Extreme triggered | 0.2404 | Night | Aug 2025 | Monitor | View readings
2025-08-02 08:15 | 2025-08-02 11:45 | 3.75 | lower | 74.76 | 3.1152 | 2.0909 | Confirmed/Materialized Shift | 0.5648 | Day | Aug 2025 | Investigate | View readings
2025-08-02 15:30 | 2025-08-02 15:30 | 0.25 | lower | 74.48 | 2.2757 | 2.2757 | Extreme triggered | 0.2374 | Day | Aug 2025 | Monitor | View readings
2025-08-02 17:30 | 2025-08-02 17:30 | 0.25 | upper | 75.32 | 2.1794 | 2.1794 | Extreme triggered | 0.231 | Day | Aug 2025 | Monitor | View readings
2025-08-02 19:30 | 2025-08-02 23:15 | 4 | upper | 80.08 | 3.074 | 2.08 | Confirmed/Materialized Shift | 0.6044 | Night | Aug 2025 | Investigate | View readings
2025-08-03 08:15 | 2025-08-03 11:45 | 3.75 | lower | 74.48 | 3.5563 | 2.135 | Confirmed/Materialized Shift | 0.613 | Day | Aug 2025 | Investigate | View readings
2025-08-03 19:15 | 2025-08-03 23:30 | 4.5 | upper | 80.08 | 3.3593 | 2.0698 | Confirmed/Materialized Shift | 0.5868 | Night | Aug 2025 | Investigate | View readings
2025-08-04 02:30 | 2025-08-04 02:30 | 0.25 | upper | 80.36 | 2.2757 | 2.2757 | Extreme triggered | 0.2089 | Night | Aug 2025 | Monitor | View readings
2025-08-04 08:15 | 2025-08-04 11:45 | 3.75 | lower | 74.76 | 3.4305 | 2.1707 | Confirmed/Materialized Shift | 0.6142 | Day | Aug 2025 | Investigate | View readings
2025-08-04 19:15 | 2025-08-04 23:30 | 4.5 | upper | 80.36 | 3.1537 | 2.0856 | Confirmed/Materialized Shift | 0.6399 | Night | Aug 2025 | Investigate | View readings
2025-08-05 04:45 | 2025-08-05 05:00 | 0.5 | upper | 80.36 | 2.2757 | 1.7506 | Extreme/elevated | 0.2531 | Night | Aug 2025 | Monitor | View readings
2025-08-05 06:30 | 2025-08-05 06:30 | 0.25 | lower | 79.52 | 2.351 | 2.351 | Extreme triggered | 0.271 | Night | Aug 2025 | Monitor | View readings
2025-08-05 08:15 | 2025-08-05 11:45 | 3.75 | lower | 74.76 | 3.2714 | 2.1095 | Confirmed/Materialized Shift | 0.5893 | Day | Aug 2025 | Investigate | View readings
2025-08-05 16:15 | 2025-08-05 16:15 | 0.25 | upper | 75.32 | 2.2993 | 2.2993 | Extreme triggered | 0.2104 | Day | Aug 2025 | Monitor | View readings
2025-08-05 19:30 | 2025-08-05 23:30 | 4.25 | upper | 80.08 | 3.2692 | 2.0696 | Confirmed/Materialized Shift | 0.5858 | Night | Aug 2025 | Investigate | View readings
2025-08-06 08:15 | 2025-08-06 09:45 | 1.75 | lower | 75.32 | 3.205 | 2.852 | Confirmed/Materialized Shift | 0.5957 | Day | Aug 2025 | Investigate | View readings
2025-08-07 02:45 | 2025-08-07 02:45 | 0.25 | lower | 79.52 | 2.4597 | 2.4597 | Extreme triggered | 0.2211 | Night | Aug 2025 | Monitor | View readings
2025-08-07 03:30 | 2025-08-07 03:30 | 0.25 | lower | 79.52 | 2.0417 | 2.0417 | Extreme triggered | 0.2218 | Night | Aug 2025 | Monitor | View readings
2025-08-07 06:30 | 2025-08-07 06:30 | 0.25 | upper | 80.36 | 2.1222 | 2.1222 | Extreme triggered | 0.1986 | Night | Aug 2025 | Monitor | View readings
2025-08-07 08:15 | 2025-08-07 11:45 | 3.75 | lower | 74.76 | 3.4548 | 2.0886 | Confirmed/Materialized Shift | 0.586 | Day | Aug 2025 | Investigate | View readings
2025-08-07 19:15 | 2025-08-07 23:15 | 4.25 | upper | 80.36 | 3.2738 | 2.1587 | Confirmed/Materialized Shift | 0.6466 | Night | Aug 2025 | Investigate | View readings
2025-08-08 04:15 | 2025-08-08 04:15 | 0.25 | lower | 79.52 | 2.1794 | 2.1794 | Extreme triggered | 0.2024 | Night | Aug 2025 | Monitor | View readings
2025-08-08 08:30 | 2025-08-08 11:30 | 3.25 | lower | 74.76 | 3.447 | 2.1739 | Confirmed/Materialized Shift | 0.6345 | Day | Aug 2025 | Investigate | View readings
2025-08-08 19:15 | 2025-08-08 23:45 | 4.75 | upper | 80.36 | 3.2738 | 2.0293 | Confirmed/Materialized Shift | 0.6007 | Night | Aug 2025 | Investigate | View readings
2025-08-09 03:15 | 2025-08-09 03:15 | 0.25 | upper | 80.36 | 2.0125 | 2.0125 | Extreme triggered | 0.1913 | Night | Aug 2025 | Monitor | View readings
2025-08-09 08:15 | 2025-08-09 11:45 | 3.75 | lower | 74.76 | 3.4598 | 2.1101 | Confirmed/Materialized Shift | 0.5951 | Day | Aug 2025 | Investigate | View readings
2025-08-09 19:15 | 2025-08-09 23:45 | 4.75 | upper | 79.52 | 3.1409 | 2.0857 | Confirmed/Materialized Shift | 0.6252 | Night | Aug 2025 | Investigate | View readings
2025-08-10 07:00 | 2025-08-10 08:30 | 1.75 | upper | 80.36 | 4.2485 | 2.2116 | Confirmed/Materialized Shift | 0.5018 | Day | Aug 2025 | Investigate | View readings
2025-08-10 19:15 | 2025-08-10 23:15 | 4.25 | upper | 80.36 | 3.2738 | 2.1505 | Confirmed/Materialized Shift | 0.5969 | Night | Aug 2025 | Investigate | View readings
2025-08-11 04:30 | 2025-08-11 05:15 | 1 | upper | 80.36 | 2.2993 | 1.327 | Persistent | 0.324 | Night | Aug 2025 | Review | View readings
2025-08-11 08:15 | 2025-08-11 11:15 | 3.25 | lower | 74.48 | 3.2811 | 2.3065 | Confirmed/Materialized Shift | 0.611 | Day | Aug 2025 | Investigate | View readings
2025-08-11 15:00 | 2025-08-11 15:00 | 0.25 | upper | 75.32 | 2.3202 | 2.3202 | Extreme triggered | 0.2118 | Day | Aug 2025 | Monitor | View readings
2025-08-11 18:00 | 2025-08-11 18:00 | 0.25 | upper | 75.32 | 2.0417 | 2.0417 | Extreme triggered | 0.1933 | Day | Aug 2025 | Monitor | View readings
2025-08-11 19:30 | 2025-08-11 23:30 | 4.25 | upper | 80.08 | 3.2 | 2.0577 | Confirmed/Materialized Shift | 0.5943 | Night | Aug 2025 | Investigate | View readings
2025-08-12 08:15 | 2025-08-12 11:45 | 3.75 | lower | 74.76 | 3.4558 | 2.091 | Confirmed/Materialized Shift | 0.6422 | Day | Aug 2025 | Investigate | View readings
2025-08-12 19:15 | 2025-08-12 23:00 | 4 | upper | 80.36 | 3.3995 | 2.2293 | Confirmed/Materialized Shift | 0.591 | Night | Aug 2025 | Investigate | View readings
2025-08-13 07:45 | 2025-08-13 07:45 | 0.25 | lower | 79.52 | 2.2253 | 2.2253 | Extreme triggered | 0.2055 | Day | Aug 2025 | Monitor | View readings
2025-08-13 08:15 | 2025-08-13 11:30 | 3.5 | lower | 74.76 | 3.223 | 2.1754 | Confirmed/Materialized Shift | 0.5576 | Day | Aug 2025 | Investigate | View readings
2025-08-13 16:15 | 2025-08-13 16:15 | 0.25 | upper | 75.32 | 2.5628 | 2.5628 | Extreme triggered | 0.228 | Day | Aug 2025 | Monitor | View readings
2025-08-13 19:15 | 2025-08-13 23:30 | 4.5 | upper | 80.08 | 3.0987 | 2.0645 | Confirmed/Materialized Shift | 0.6091 | Night | Aug 2025 | Investigate | View readings
2025-08-14 08:15 | 2025-08-14 11:45 | 3.75 | lower | 74.48 | 3.5738 | 2.1293 | Confirmed/Materialized Shift | 0.6118 | Day | Aug 2025 | Investigate | View readings
2025-08-14 16:45 | 2025-08-14 16:45 | 0.25 | upper | 75.32 | 2.2757 | 2.2757 | Extreme triggered | 0.2374 | Day | Aug 2025 | Monitor | View readings
2025-08-14 18:45 | 2025-08-14 18:45 | 0.25 | lower | 74.48 | 2.2584 | 2.2584 | Extreme triggered | 0.2363 | Day | Aug 2025 | Monitor | View readings
2025-08-14 19:30 | 2025-08-14 23:15 | 4 | upper | 80.36 | 3.0376 | 2.0818 | Confirmed/Materialized Shift | 0.5379 | Night | Aug 2025 | Investigate | View readings

## Daily overview
Daily overview | [9 empty] | Report generated: 10/09/2026 16:09
< Back to summary worksheet
One row per day with data. Bars: share of extreme readings (red) and peak materiality (blue).
Date | Readings | Mean value | Min value | Max value | Extreme readings | Extreme share | Persistent periods | Confirmed shift periods | Abnormal changes | Material changes | Max materiality score
2025-08-01 | 96 | 77.5542 | 74.76 | 80.36 | 16 | 16.67% | 8 | 17 | 5 | 2 | 0.6206
2025-08-02 | 96 | 77.5338 | 74.48 | 80.36 | 21 | 21.88% | 8 | 19 | 5 | 1 | 0.6044
2025-08-03 | 96 | 77.5338 | 74.48 | 80.36 | 19 | 19.79% | 8 | 21 | 4 | 2 | 0.613
2025-08-04 | 96 | 77.5658 | 74.48 | 80.36 | 18 | 18.75% | 8 | 21 | 5 | 3 | 0.6399
2025-08-05 | 96 | 77.5688 | 74.76 | 80.36 | 21 | 21.88% | 8 | 20 | 5 | 1 | 0.5893
2025-08-06 | 48 | 79.6425 | 75.32 | 80.36 | 7 | 14.58% | 4 | 1 | 4 | 2 | 0.5957
2025-08-07 | 96 | 77.5367 | 74.48 | 80.36 | 21 | 21.88% | 8 | 20 | 6 | 3 | 0.6466
2025-08-08 | 96 | 77.5192 | 74.76 | 80.36 | 17 | 17.71% | 8 | 20 | 5 | 3 | 0.6345
2025-08-09 | 96 | 76.9125 | 72.52 | 80.36 | 19 | 19.79% | 8 | 22 | 6 | 2 | 0.6252
2025-08-10 | 96 | 75.3696 | 72.52 | 80.36 | 12 | 12.5% | 8 | 12 | 3 | 0 | 0.5969
2025-08-11 | 96 | 77.5221 | 74.48 | 80.36 | 20 | 20.83% | 10 | 18 | 5 | 2 | 0.611
2025-08-12 | 96 | 77.5746 | 74.76 | 80.36 | 18 | 18.75% | 8 | 19 | 6 | 3 | 0.6422
2025-08-13 | 96 | 77.5571 | 74.76 | 80.36 | 20 | 20.83% | 8 | 20 | 3 | 1 | 0.6091
2025-08-14 | 96 | 77.5775 | 74.48 | 80.36 | 17 | 17.71% | 8 | 19 | 4 | 2 | 0.6118

## Monthly metrics
Monthly metrics | [23 empty] | Report generated: 10/09/2026 16:09
< Back to summary worksheet
Computed from the results by the app. Reading interval: 15.00 minutes (median spacing of the timestamps). Rank 1 = the month with the most issues. Gap hours count in the month where the gap starts.
Month | Readings | Days with data | Mean value | Min value | Max value | Extreme readings | Extreme share | Upper extremes | Lower extremes | Persistent periods | Confirmed shift periods | Sustained deviation (h) | Confirmed share | Abnormal changes | Material changes | Material changes per day | Mean materiality score | Max materiality score | Max ¦Z¦ | Events | Data gap hours | Rank: extreme share | Rank: sustained (h) | Rank: material changes/day | Rank: mean materiality
Aug 2025 | 1296 | 14 | 77.4183 | 72.52 | 80.36 | 246 | 18.98% | 133 | 113 | 110 | 249 | 89.75 | 19.21% | 66 | 27 | 1.9286 | 0.19815 | 0.6466 | 4.2485 | 48 | 12.25 | 1 | 1 | 1 | 1
All | 1296 | 14 | 77.4183 | 72.52 | 80.36 | 246 | 18.98% | 133 | 113 | 110 | 249 | 89.75 | 19.21% | 66 | 27 | 1.9286 | 0.19815 | 0.6466 | 4.2485 | 48 | 12.25

## Column descriptor
Column descriptor |  |  | Report generated: 10/09/2026 16:09
< Back to summary worksheet
Meaning of every column in res.csv and the parameters that drive it. Full detail: Statistical calc parameters manual.
Column | Meaning | Driven by | Step
Timestamp | Time of the reading | — | Input
Value | The reading | — | Input
AbnormalChangeFlag | Unusually fast change: ¦ROC_ZScore¦ ≥ ROC_K | ROC_K | Change
ConfirmedShiftFlag | Reading is in a Confirmed/Materialized Shift | N_M, K_M | Materiality
DeltaLower | LowerLimit − Value (positive = below the band) | limits | Extreme
DeltaLower_pct | DeltaLower as % of LowerLimit | limits | Extreme
DeltaUpper | Value − UpperLimit (positive = above the band) | limits | Extreme
DeltaUpper_pct | DeltaUpper as % of UpperLimit | limits | Extreme
DeltaX | Change from the previous reading | — | Change
EventEndTime | End of the event this reading belongs to | K_P, N_EXIT | Persistence
EventStartTime | Start of the event this reading belongs to | K_E | Persistence
ExtremeDirection | upper / lower / none | Method, K_E | Extreme
ExtremeFlag | Reading outside the normal range | Method, Window, K_E, p, K_IQR | Extreme
FrequencyCount | Abnormal changes in the last frequency window | Frequency window | Change
LowerLimit | Lower edge of the normal range: MA − K_E·σ | Method, Window, K_E | Extreme
MaterialChangeFlag | Abnormal change that recurs (FrequencyCount ≥ min) | Min recurrences | Change
MaterialExtremeFlag | Extreme that also lasted N_P readings | N_P | Materiality
MaterialityScore | 0–1 ranking: Wm·magnitude + Wd·duration + Wf·frequency | Weights, K_E, N_M | Materiality
MeanZ_event | Average ¦Z¦ over the event so far | — | Persistence
MovingAverage | Baseline (rolling mean over Window) | Method, Window, α | Extreme
PersistenceCount | Readings in the current event | K_P, N_EXIT | Persistence
ROC | Rate of change: (x(t) − x(t−h)) / h | ROC horizon | Change
ROC_MeanBaseline | Rolling mean of ROC | ROC baseline window | Change
ROC_StdDev | Rolling std of ROC | ROC baseline window | Change
ROC_ZScore | (ROC − mean) / std | ROC baseline window | Change
RollingStdDev | σ used for the limits | Method, Window | Extreme
State | Normal, Extreme triggered, Extreme/elevated, Persistent, Confirmed/Materialized Shift, Persistence ends | K_E, K_P, N_P, N_M, K_M, N_EXIT | Persistence
UpperLimit | Upper edge of the normal range: MA + K_E·σ | Method, Window, K_E | Extreme
ZScore | (Value − MA) / σ | Method, Window | Extreme
Day/Night | Day or night category of the reading | time of day | Input
Settings detected in this results file
Window 20, K_E 2

## Data
| Data | [12 empty] | Report generated: 10/09/2026 16:09
< Back to summary worksheet
The results file res.csv as exported by the app: 1,296 readings, 31 columns. Meaning of each column: see Column descriptor.
Timestamp | Value | MovingAverage | RollingStdDev | UpperLimit | LowerLimit | ZScore | ExtremeFlag | ExtremeDirection | DeltaUpper | DeltaLower | DeltaUpper_pct | DeltaLower_pct | State | PersistenceCount | EventStartTime | EventEndTime | MeanZ_event | DeltaX | ROC | ROC_MeanBaseline | ROC_StdDev | ROC_ZScore | AbnormalChangeFlag | FrequencyCount | MaterialChangeFlag | MaterialExtremeFlag | ConfirmedShiftFlag | MaterialChangeFlag.1 | MaterialityScore | Day/Night
2025-08-01 | 80.08 | [5 empty] | FALSE | none |  |  |  |  | Normal | 0 | [8 empty] | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-01 00:15 | 80.08 | 80.08 | 0 | 80.08 | 80.08 |  | FALSE | none | 0 | 0 | 0 | 0 | Normal | 0 |  |  |  | 0 | 0 |  |  |  | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-01 00:30 | 80.08 | 80.08 | 0 | 80.08 | 80.08 |  | FALSE | none | 0 | 0 | 0 | 0 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0 |  | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-01 00:45 | 79.8 | 80.01 | 0.14 | 80.29 | 79.73 | -1.5 | FALSE | none | -0.49 | -0.07 | -0.61029 | -0.087796 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.093333 | 0.16166 | -1.1547 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1 | Night
2025-08-01 01:00 | 80.08 | 80.024 | 0.12522 | 80.2744 | 79.7736 | 0.44721 | FALSE | none | -0.19444 | -0.30644 | -0.24222 | -0.38414 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.22862 | 1.2247 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0298 | Night
2025-08-01 01:15 | 80.08 | 80.0333 | 0.11431 | 80.262 | 79.8047 | 0.40825 | FALSE | none | -0.18195 | -0.27529 | -0.2267 | -0.34495 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.19799 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0272 | Night
2025-08-01 01:30 | 79.8 | 80 | 0.13663 | 80.2733 | 79.7267 | -1.4639 | FALSE | none | -0.47325 | -0.073252 | -0.58955 | -0.091879 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.046667 | 0.21078 | -1.107 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0976 | Night
2025-08-01 01:45 | 80.08 | 80.01 | 0.12961 | 80.2692 | 79.7508 | 0.54006 | FALSE | none | -0.18923 | -0.32923 | -0.23574 | -0.41282 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.22862 | 1.2247 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.036 | Night
2025-08-01 02:00 | 80.08 | 80.0178 | 0.12347 | 80.2647 | 79.7708 | 0.50395 | FALSE | none | -0.18471 | -0.30916 | -0.23013 | -0.38756 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.21166 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0336 | Night
2025-08-01 02:15 | 80.08 | 80.024 | 0.11806 | 80.2601 | 79.7879 | 0.47434 | FALSE | none | -0.18012 | -0.29212 | -0.22442 | -0.36612 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.19799 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0316 | Night
2025-08-01 02:30 | 80.08 | 80.0291 | 0.11327 | 80.2556 | 79.8026 | 0.44947 | FALSE | none | -0.17562 | -0.27744 | -0.21883 | -0.34766 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.18667 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.03 | Night
2025-08-01 02:45 | 80.08 | 80.0333 | 0.10899 | 80.2513 | 79.8154 | 0.42817 | FALSE | none | -0.17131 | -0.26465 | -0.21347 | -0.33157 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.17709 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0285 | Night
2025-08-01 03:00 | 79.8 | 80.0154 | 0.12279 | 80.261 | 79.7698 | -1.7541 | FALSE | none | -0.46096 | -0.030192 | -0.57433 | -0.037848 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.023333 | 0.1872 | -1.3711 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1169 | Night
2025-08-01 03:15 | 80.08 | 80.02 | 0.11923 | 80.2585 | 79.7815 | 0.50324 | FALSE | none | -0.17846 | -0.29846 | -0.22235 | -0.37409 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.19799 | 1.4142 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0335 | Night
2025-08-01 03:30 | 79.8 | 80.0053 | 0.12817 | 80.2617 | 79.749 | -1.6021 | FALSE | none | -0.46167 | -0.051 | -0.5752 | -0.06395 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.02 | 0.20441 | -1.2719 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1068 | Night
2025-08-01 03:45 | 80.08 | 80.01 | 0.12522 | 80.2604 | 79.7596 | 0.55902 | FALSE | none | -0.18044 | -0.32044 | -0.22482 | -0.40176 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.21166 | 1.3229 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0373 | Night
2025-08-01 04:00 | 80.08 | 80.0141 | 0.12243 | 80.259 | 79.7693 | 0.53814 | FALSE | none | -0.17897 | -0.31074 | -0.22299 | -0.38954 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.20448 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0359 | Night
2025-08-01 04:15 | 80.08 | 80.0178 | 0.11978 | 80.2573 | 79.7782 | 0.51946 | FALSE | none | -0.17734 | -0.30179 | -0.22097 | -0.37828 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.19799 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0346 | Night
2025-08-01 04:30 | 79.8 | 80.0063 | 0.12668 | 80.2597 | 79.753 | -1.6287 | FALSE | none | -0.45967 | -0.047036 | -0.57273 | -0.058977 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.015556 | 0.2031 | -1.302 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1086 | Night
2025-08-01 04:45 | 80.08 | 80.01 | 0.12439 | 80.2588 | 79.7612 | 0.56273 | FALSE | none | -0.17879 | -0.31879 | -0.22276 | -0.39968 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.2087 | 1.3416 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0375 | Night
2025-08-01 05:00 | 80.08 | 80.01 | 0.12439 | 80.2588 | 79.7612 | 0.56273 | FALSE | none | -0.17879 | -0.31879 | -0.22276 | -0.39968 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.20313 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0375 | Night
2025-08-01 05:15 | 80.08 | 80.01 | 0.12439 | 80.2588 | 79.7612 | 0.56273 | FALSE | none | -0.17879 | -0.31879 | -0.22276 | -0.39968 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.20313 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0375 | Night
2025-08-01 05:30 | 80.08 | 80.01 | 0.12439 | 80.2588 | 79.7612 | 0.56273 | FALSE | none | -0.17879 | -0.31879 | -0.22276 | -0.39968 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.20313 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0375 | Night
2025-08-01 05:45 | 80.08 | 80.024 | 0.11491 | 80.2538 | 79.7942 | 0.48734 | FALSE | none | -0.17382 | -0.28582 | -0.21659 | -0.3582 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.19217 | -0.072851 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0325 | Night
2025-08-01 06:00 | 79.52 | 79.996 | 0.15995 | 80.3159 | 79.6761 | -2.976 | TRUE | lower | -0.79589 | 0.15611 | -0.99096 | 0.19592 | Extreme triggered | 1 | 2025-08-01 06:00 | 2025-08-01 06:30 | 2.976 | -0.56 | -0.56 | -0.028 | 0.22066 | -2.411 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.2841 | Night
2025-08-01 06:15 | 79.8 | 79.982 | 0.1644 | 80.3108 | 79.6532 | -1.1071 | FALSE | none | -0.5108 | -0.1468 | -0.63603 | -0.1843 | Extreme/elevated | 2 | 2025-08-01 06:00 |  | 2.0415 | 0.28 | 0.28 | -0.014 | 0.23116 | 1.2718 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.2167 | Night
2025-08-01 06:30 | 80.08 | 79.996 | 0.15995 | 80.3159 | 79.6761 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.29371 | -0.50692 | Persistence ends | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.23116 | 1.1507 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0636 | Night
2025-08-01 06:45 | 79.8 | 79.982 | 0.1644 | 80.3108 | 79.6532 | -1.1071 | FALSE | none | -0.5108 | -0.1468 | -0.63603 | -0.1843 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.23116 | -1.1507 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1024 | Night
2025-08-01 07:00 | 80.08 | 79.982 | 0.1644 | 80.3108 | 79.6532 | 0.59611 | FALSE | none | -0.2308 | -0.4268 | -0.28738 | -0.53582 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.24035 | 1.165 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0683 | Day
2025-08-01 07:15 | 80.08 | 79.982 | 0.1644 | 80.3108 | 79.6532 | 0.59611 | FALSE | none | -0.2308 | -0.4268 | -0.28738 | -0.53582 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.24035 | 0 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0683 | Day
2025-08-01 07:30 | 80.36 | 79.996 | 0.18395 | 80.3639 | 79.6281 | 1.9789 | FALSE | none | -0.0038901 | -0.73189 | -0.0048407 | -0.91914 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.24837 | 1.071 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1605 | Day
2025-08-01 07:45 | 79.8 | 79.982 | 0.18783 | 80.3577 | 79.6063 | -0.96896 | FALSE | none | -0.55766 | -0.19366 | -0.69397 | -0.24327 | Normal | 0 |  |  |  | -0.56 | -0.56 | -0.014 | 0.27963 | -1.9526 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0932 | Day
2025-08-01 08:00 | 80.08 | 79.996 | 0.18395 | 80.3639 | 79.6281 | 0.45666 | FALSE | none | -0.28389 | -0.45189 | -0.35326 | -0.5675 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.27963 | 0.95125 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.059 | Day
2025-08-01 08:15 | 79.8 | 79.982 | 0.18783 | 80.3577 | 79.6063 | -0.96896 | FALSE | none | -0.55766 | -0.19366 | -0.69397 | -0.24327 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.27963 | -0.95125 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0932 | Day
2025-08-01 08:30 | 78.96 | 79.94 | 0.29437 | 80.5287 | 79.3513 | -3.3292 | TRUE | lower | -1.5687 | 0.39126 | -1.948 | 0.49308 | Extreme triggered | 1 | 2025-08-01 08:30 | 2025-08-01 11:30 | 3.3292 | -0.84 | -0.84 | -0.042 | 0.33099 | -2.411 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.3077 | Day
2025-08-01 08:45 | 78.12 | 79.842 | 0.49985 | 80.8417 | 78.8423 | -3.445 | TRUE | lower | -2.7217 | 0.7223 | -3.3667 | 0.91614 | Extreme/elevated | 2 | 2025-08-01 08:30 |  | 3.3871 | -0.84 | -0.84 | -0.098 | 0.36649 | -2.0246 | TRUE | 2 | TRUE | FALSE | FALSE | TRUE | 0.4011 | Day
2025-08-01 09:00 | 77.28 | 79.702 | 0.75611 | 81.2142 | 78.1898 | -3.2032 | TRUE | lower | -3.9342 | 0.90978 | -4.8442 | 1.1636 | Persistent | 3 | 2025-08-01 08:30 |  | 3.3258 | -0.84 | -0.84 | -0.14 | 0.40116 | -1.745 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.4421 | Day
2025-08-01 09:15 | 76.44 | 79.52 | 1.0437 | 81.6074 | 77.4326 | -2.951 | TRUE | lower | -5.1674 | 0.99256 | -6.3321 | 1.2818 | Persistent | 4 | 2025-08-01 08:30 |  | 3.2321 | -0.84 | -0.84 | -0.182 | 0.42875 | -1.5347 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.4824 | Day
2025-08-01 09:30 | 76.16 | 79.338 | 1.2824 | 81.9028 | 76.7732 | -2.4782 | TRUE | lower | -5.7428 | 0.61321 | -7.0117 | 0.79872 | Persistent | 5 | 2025-08-01 08:30 |  | 3.0813 | -0.28 | -0.28 | -0.182 | 0.42875 | -0.22857 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.5081 | Day
2025-08-01 09:45 | 75.6 | 79.114 | 1.516 | 82.1459 | 76.0821 | -2.318 | TRUE | lower | -6.5459 | 0.48207 | -7.9687 | 0.63362 | Persistent | 6 | 2025-08-01 08:30 |  | 2.9541 | -0.56 | -0.56 | -0.224 | 0.4222 | -0.79582 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.5545 | Day
2025-08-01 10:00 | 74.76 | 78.848 | 1.7811 | 82.4102 | 75.2858 | -2.2952 | TRUE | lower | -7.6502 | 0.5258 | -9.2831 | 0.69841 | Confirmed/Materialized Shift | 7 | 2025-08-01 08:30 |  | 2.86 | -0.84 | -0.84 | -0.266 | 0.44015 | -1.3041 | FALSE | 2 | FALSE | TRUE | TRUE | FALSE | 0.6102 | Day
2025-08-01 10:15 | 74.76 | 78.582 | 1.9742 | 82.5304 | 74.6336 | -1.936 | FALSE | none | -7.7704 | -0.12642 | -9.4152 | -0.16939 | Confirmed/Materialized Shift | 8 | 2025-08-01 08:30 |  | 2.7445 | 0 | 0 | -0.266 | 0.44015 | 0.60434 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5862 | Day
2025-08-01 10:30 | 74.76 | 78.316 | 2.1151 | 82.5462 | 74.0858 | -1.6812 | FALSE | none | -7.7862 | -0.67425 | -9.4326 | -0.91009 | Confirmed/Materialized Shift | 9 | 2025-08-01 08:30 |  | 2.6263 | 0 | 0 | -0.266 | 0.44015 | 0.60434 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5692 | Day
2025-08-01 10:45 | 74.76 | 78.05 | 2.2138 | 82.4777 | 73.6223 | -1.4861 | FALSE | none | -7.7177 | -1.1377 | -9.3573 | -1.5453 | Confirmed/Materialized Shift | 10 | 2025-08-01 08:30 |  | 2.5123 | 0 | 0 | -0.266 | 0.44015 | 0.60434 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5562 | Day
2025-08-01 11:00 | 74.76 | 77.812 | 2.3016 | 82.4152 | 73.2088 | -1.326 | FALSE | none | -7.6552 | -1.5512 | -9.2886 | -2.1189 | Confirmed/Materialized Shift | 11 | 2025-08-01 08:30 |  | 2.4045 | 0 | 0 | -0.238 | 0.43827 | 0.54305 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.517 | Day
2025-08-01 11:15 | 75.04 | 77.574 | 2.3311 | 82.2363 | 72.9117 | -1.087 | FALSE | none | -7.1963 | -2.1283 | -8.7507 | -2.9189 | Confirmed/Materialized Shift | 12 | 2025-08-01 08:30 |  | 2.2947 | 0.28 | 0.28 | -0.238 | 0.43827 | 1.1819 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4725 | Day
2025-08-01 11:30 | 75.04 | 77.322 | 2.3183 | 81.9587 | 72.6853 | -0.98432 | FALSE | none | -6.9187 | -2.3547 | -8.4417 | -3.2396 | Persistence ends | 0 |  |  |  | 0 | 0 | -0.252 | 0.42513 | 0.59276 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0656 | Day
2025-08-01 11:45 | 74.76 | 77.07 | 2.3087 | 81.6874 | 72.4526 | -1.0006 | FALSE | none | -6.9274 | -2.3074 | -8.4804 | -3.1847 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.252 | 0.42513 | -0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0667 | Day
2025-08-01 12:00 | 75.04 | 76.818 | 2.2368 | 81.2916 | 72.3444 | -0.79488 | FALSE | none | -6.2516 | -2.6956 | -7.6904 | -3.7261 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.252 | 0.42513 | 1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.053 | Day
2025-08-01 12:15 | 75.04 | 76.566 | 2.1314 | 80.8288 | 72.3032 | -0.71596 | FALSE | none | -5.7888 | -2.7368 | -7.1618 | -3.7852 | Normal | 0 |  |  |  | 0 | 0 | -0.252 | 0.42513 | 0.59276 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0477 | Day
2025-08-01 12:30 | 75.04 | 76.3 | 1.9579 | 80.2158 | 72.3842 | -0.64355 | FALSE | none | -5.1758 | -2.6558 | -6.4523 | -3.669 | Normal | 0 |  |  |  | 0 | 0 | -0.266 | 0.41106 | 0.6471 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0429 | Day
2025-08-01 12:45 | 74.76 | 76.048 | 1.8018 | 79.6517 | 72.4443 | -0.71483 | FALSE | none | -4.8917 | -2.3157 | -6.1413 | -3.1965 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.252 | 0.40525 | -0.069093 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0477 | Day
2025-08-01 13:00 | 75.04 | 75.796 | 1.5419 | 78.8799 | 72.7121 | -0.49029 | FALSE | none | -3.8399 | -2.3279 | -4.868 | -3.2015 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.252 | 0.40525 | 1.3128 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0327 | Day
2025-08-01 13:15 | 74.76 | 75.544 | 1.2343 | 78.0126 | 73.0754 | -0.63519 | FALSE | none | -3.2526 | -1.6846 | -4.1693 | -2.3052 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.252 | 0.40525 | -0.069093 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0423 | Day
2025-08-01 13:30 | 75.04 | 75.348 | 0.93926 | 77.2265 | 73.4695 | -0.32792 | FALSE | none | -2.1865 | -1.5705 | -2.8313 | -2.1376 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.196 | 0.39702 | 1.1989 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0219 | Day
2025-08-01 13:45 | 74.76 | 75.18 | 0.68284 | 76.5457 | 73.8143 | -0.61508 | FALSE | none | -1.7857 | -0.94568 | -2.3328 | -1.2812 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.168 | 0.36789 | -0.30444 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.041 | Day
2025-08-01 14:00 | 75.04 | 75.068 | 0.47116 | 76.0103 | 74.1257 | -0.059427 | FALSE | none | -0.97033 | -0.91433 | -1.2766 | -1.2335 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.112 | 0.34473 | 1.1371 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.004 | Day
2025-08-01 14:15 | 74.76 | 74.984 | 0.34711 | 75.6782 | 74.2898 | -0.64532 | FALSE | none | -0.91823 | -0.47023 | -1.2133 | -0.63297 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.084 | 0.30266 | -0.64759 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.043 | Day
2025-08-01 14:30 | 74.76 | 74.914 | 0.21256 | 75.3391 | 74.4889 | -0.72449 | FALSE | none | -0.57913 | -0.27113 | -0.76869 | -0.36398 | Normal | 0 |  |  |  | 0 | 0 | -0.07 | 0.29958 | 0.23366 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0483 | Day
2025-08-01 14:45 | 74.76 | 74.872 | 0.14073 | 75.1535 | 74.5905 | -0.79582 | FALSE | none | -0.39347 | -0.16947 | -0.52356 | -0.2272 | Normal | 0 |  |  |  | 0 | 0 | -0.042 | 0.27666 | 0.15181 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-01 15:00 | 75.04 | 74.886 | 0.14292 | 75.1718 | 74.6002 | 1.0775 | FALSE | none | -0.13183 | -0.43983 | -0.17538 | -0.58959 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.21256 | 1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Day
2025-08-01 15:15 | 75.04 | 74.9 | 0.14364 | 75.1873 | 74.6127 | 0.97468 | FALSE | none | -0.14727 | -0.42727 | -0.19588 | -0.57266 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.21256 | -0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.065 | Day
2025-08-01 15:30 | 74.76 | 74.9 | 0.14364 | 75.1873 | 74.6127 | -0.97468 | FALSE | none | -0.42727 | -0.14727 | -0.56828 | -0.19738 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.22252 | -1.2583 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.065 | Day
2025-08-01 15:45 | 74.76 | 74.9 | 0.14364 | 75.1873 | 74.6127 | -0.97468 | FALSE | none | -0.42727 | -0.14727 | -0.56828 | -0.19738 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.22252 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.065 | Day
2025-08-01 16:00 | 75.04 | 74.914 | 0.14292 | 75.1998 | 74.6282 | 0.88163 | FALSE | none | -0.15983 | -0.41183 | -0.21255 | -0.55185 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.23116 | 1.1507 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-01 16:15 | 74.76 | 74.9 | 0.14364 | 75.1873 | 74.6127 | -0.97468 | FALSE | none | -0.42727 | -0.14727 | -0.56828 | -0.19738 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.23116 | -1.1507 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.065 | Day
2025-08-01 16:30 | 75.04 | 74.9 | 0.14364 | 75.1873 | 74.6127 | 0.97468 | FALSE | none | -0.14727 | -0.42727 | -0.19588 | -0.57266 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.24035 | 1.165 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.065 | Day
2025-08-01 16:45 | 75.04 | 74.914 | 0.14292 | 75.1998 | 74.6282 | 0.88163 | FALSE | none | -0.15983 | -0.41183 | -0.21255 | -0.55185 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.23116 | -0.060564 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-01 17:00 | 74.76 | 74.9 | 0.14364 | 75.1873 | 74.6127 | -0.97468 | FALSE | none | -0.42727 | -0.14727 | -0.56828 | -0.19738 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.23116 | -1.1507 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.065 | Day
2025-08-01 17:15 | 75.04 | 74.9 | 0.14364 | 75.1873 | 74.6127 | 0.97468 | FALSE | none | -0.14727 | -0.42727 | -0.19588 | -0.57266 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.24035 | 1.165 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.065 | Day
2025-08-01 17:30 | 75.04 | 74.9 | 0.14364 | 75.1873 | 74.6127 | 0.97468 | FALSE | none | -0.14727 | -0.42727 | -0.19588 | -0.57266 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.24035 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.065 | Day
2025-08-01 17:45 | 74.76 | 74.9 | 0.14364 | 75.1873 | 74.6127 | -0.97468 | FALSE | none | -0.42727 | -0.14727 | -0.56828 | -0.19738 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.24035 | -1.165 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.065 | Day
2025-08-01 18:00 | 74.76 | 74.886 | 0.14292 | 75.1718 | 74.6002 | -0.88163 | FALSE | none | -0.41183 | -0.15983 | -0.54786 | -0.21425 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.23116 | 0.060564 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-01 18:15 | 75.04 | 74.9 | 0.14364 | 75.1873 | 74.6127 | 0.97468 | FALSE | none | -0.14727 | -0.42727 | -0.19588 | -0.57266 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.23116 | 1.1507 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.065 | Day
2025-08-01 18:30 | 75.04 | 74.9 | 0.14364 | 75.1873 | 74.6127 | 0.97468 | FALSE | none | -0.14727 | -0.42727 | -0.19588 | -0.57266 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.22252 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.065 | Day
2025-08-01 18:45 | 75.04 | 74.914 | 0.14292 | 75.1998 | 74.6282 | 0.88163 | FALSE | none | -0.15983 | -0.41183 | -0.21255 | -0.55185 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.21256 | -0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-01 19:00 | 74.76 | 74.9 | 0.14364 | 75.1873 | 74.6127 | -0.97468 | FALSE | none | -0.42727 | -0.14727 | -0.56828 | -0.19738 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.21256 | -1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.065 | Night
2025-08-01 19:15 | 75.04 | 74.914 | 0.14292 | 75.1998 | 74.6282 | 0.88163 | FALSE | none | -0.15983 | -0.41183 | -0.21255 | -0.55185 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.21256 | 1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Night
2025-08-01 19:30 | 75.6 | 74.956 | 0.20515 | 75.3663 | 74.5457 | 3.1391 | TRUE | upper | 0.23369 | -1.0543 | 0.31007 | -1.4143 | Extreme triggered | 1 | 2025-08-01 19:30 | 2025-08-01 23:45 | 3.1391 | 0.56 | 0.56 | 0.042 | 0.24503 | 2.1141 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.295 | Night
2025-08-01 19:45 | 76.16 | 75.026 | 0.33347 | 75.6929 | 74.3591 | 3.4006 | TRUE | upper | 0.46705 | -1.8009 | 0.61704 | -2.422 | Extreme/elevated | 2 | 2025-08-01 19:30 |  | 3.2698 | 0.56 | 0.56 | 0.07 | 0.27063 | 1.8106 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.3696 | Night
2025-08-01 20:00 | 76.72 | 75.11 | 0.50478 | 76.1196 | 74.1004 | 3.1895 | TRUE | upper | 0.60045 | -2.6196 | 0.78882 | -3.5351 | Persistent | 3 | 2025-08-01 19:30 |  | 3.2431 | 0.56 | 0.56 | 0.084 | 0.28871 | 1.6487 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4126 | Night
2025-08-01 20:15 | 77 | 75.208 | 0.6576 | 76.5232 | 73.8928 | 2.7251 | TRUE | upper | 0.4768 | -3.1072 | 0.62308 | -4.205 | Persistent | 4 | 2025-08-01 19:30 |  | 3.1136 | 0.28 | 0.28 | 0.098 | 0.2912 | 0.62501 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4388 | Night
2025-08-01 20:30 | 77.28 | 75.334 | 0.79443 | 76.9229 | 73.7451 | 2.4496 | TRUE | upper | 0.35714 | -3.5349 | 0.46428 | -4.7933 | Persistent | 5 | 2025-08-01 19:30 |  | 2.9808 | 0.28 | 0.28 | 0.126 | 0.27963 | 0.55073 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4776 | Night
2025-08-01 20:45 | 77.56 | 75.474 | 0.92409 | 77.3222 | 73.6258 | 2.2574 | TRUE | upper | 0.23782 | -3.9342 | 0.30757 | -5.3435 | Persistent | 6 | 2025-08-01 19:30 |  | 2.8602 | 0.28 | 0.28 | 0.14 | 0.28 | 0.5 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.5219 | Night
2025-08-01 21:00 | 78.4 | 75.642 | 1.1247 | 77.8914 | 73.3926 | 2.4522 | TRUE | upper | 0.50862 | -5.0074 | 0.65299 | -6.8227 | Confirmed/Materialized Shift | 7 | 2025-08-01 19:30 |  | 2.8019 | 0.84 | 0.84 | 0.168 | 0.31989 | 2.1007 | TRUE | 2 | TRUE | TRUE | TRUE | TRUE | 0.6206 | Night
2025-08-01 21:15 | 78.96 | 75.852 | 1.3255 | 78.503 | 73.201 | 2.3448 | TRUE | upper | 0.45697 | -5.759 | 0.58211 | -7.8674 | Confirmed/Materialized Shift | 8 | 2025-08-01 19:30 |  | 2.7448 | 0.56 | 0.56 | 0.21 | 0.31305 | 1.118 | FALSE | 2 | FALSE | TRUE | TRUE | FALSE | 0.6135 | Night
2025-08-01 21:30 | 78.96 | 76.048 | 1.4799 | 79.0079 | 73.0881 | 1.9676 | FALSE | none | -0.047898 | -5.8719 | -0.060624 | -8.034 | Confirmed/Materialized Shift | 9 | 2025-08-01 19:30 |  | 2.6584 | 0 | 0 | 0.196 | 0.316 | -0.62025 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5883 | Night
2025-08-01 21:45 | 79.52 | 76.272 | 1.6488 | 79.5695 | 72.9745 | 1.97 | FALSE | none | -0.049524 | -6.5455 | -0.06224 | -8.9696 | Confirmed/Materialized Shift | 10 | 2025-08-01 19:30 |  | 2.5896 | 0.56 | 0.56 | 0.224 | 0.32246 | 1.042 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5885 | Night
2025-08-01 22:00 | 80.08 | 76.538 | 1.813 | 80.1639 | 72.9121 | 1.9537 | FALSE | none | -0.083916 | -7.1679 | -0.10468 | -9.8309 | Confirmed/Materialized Shift | 11 | 2025-08-01 19:30 |  | 2.5318 | 0.56 | 0.56 | 0.266 | 0.30773 | 0.95538 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5588 | Night
2025-08-01 22:15 | 80.08 | 76.79 | 1.9396 | 80.6693 | 72.9107 | 1.6962 | FALSE | none | -0.58926 | -7.1693 | -0.73047 | -9.8329 | Confirmed/Materialized Shift | 12 | 2025-08-01 19:30 |  | 2.4621 | 0 | 0 | 0.252 | 0.31338 | -0.80414 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5417 | Night
2025-08-01 22:30 | 80.08 | 77.042 | 2.0258 | 81.0936 | 72.9904 | 1.4997 | FALSE | none | -1.0136 | -7.0896 | -1.2499 | -9.713 | Confirmed/Materialized Shift | 13 | 2025-08-01 19:30 |  | 2.3881 | 0 | 0 | 0.252 | 0.31338 | -0.80414 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5285 | Night
2025-08-01 22:45 | 80.08 | 77.308 | 2.0594 | 81.4268 | 73.1892 | 1.346 | FALSE | none | -1.3468 | -6.8908 | -1.6539 | -9.415 | Confirmed/Materialized Shift | 14 | 2025-08-01 19:30 |  | 2.3137 | 0 | 0 | 0.266 | 0.29402 | -0.90471 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5183 | Night
2025-08-01 23:00 | 80.08 | 77.574 | 2.0565 | 81.687 | 73.461 | 1.2186 | FALSE | none | -1.607 | -6.619 | -1.9673 | -9.0103 | Confirmed/Materialized Shift | 15 | 2025-08-01 19:30 |  | 2.2407 | 0 | 0 | 0.266 | 0.29402 | -0.90471 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5098 | Night
2025-08-01 23:15 | 80.08 | 77.826 | 2.0384 | 81.9028 | 73.7492 | 1.1058 | FALSE | none | -1.8228 | -6.3308 | -2.2255 | -8.5842 | Confirmed/Materialized Shift | 16 | 2025-08-01 19:30 |  | 2.1697 | 0 | 0 | 0.252 | 0.29992 | -0.84022 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5023 | Night
2025-08-01 23:30 | 80.08 | 78.078 | 1.9867 | 82.0514 | 74.1046 | 1.0077 | FALSE | none | -1.9714 | -5.9754 | -2.4027 | -8.0635 | Confirmed/Materialized Shift | 17 | 2025-08-01 19:30 |  | 2.1014 | 0 | 0 | 0.252 | 0.29992 | -0.84022 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4672 | Night
2025-08-01 23:45 | 79.8 | 78.316 | 1.8862 | 82.0884 | 74.5436 | 0.78677 | FALSE | none | -2.2884 | -5.2564 | -2.7877 | -7.0514 | Persistence ends | 0 |  |  |  | -0.28 | -0.28 | 0.238 | 0.31828 | -1.6275 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0525 | Night
2025-08-02 | 80.08 | 78.582 | 1.7267 | 82.0354 | 75.1286 | 0.86755 | FALSE | none | -1.9554 | -4.9514 | -2.3836 | -6.5905 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.266 | 0.29402 | 0.047616 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0578 | Night
2025-08-02 00:15 | 80.08 | 78.834 | 1.5403 | 81.9145 | 75.7535 | 0.80895 | FALSE | none | -1.8345 | -4.3265 | -2.2396 | -5.7113 | Normal | 0 |  |  |  | 0 | 0 | 0.252 | 0.29992 | -0.84022 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0539 | Night
2025-08-02 00:30 | 79.8 | 79.044 | 1.3508 | 81.7456 | 76.3424 | 0.55967 | FALSE | none | -1.9456 | -3.4576 | -2.3801 | -4.5291 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.21 | 0.31305 | -1.5652 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0373 | Night
2025-08-02 00:45 | 80.08 | 79.24 | 1.1845 | 81.6089 | 76.8711 | 0.70918 | FALSE | none | -1.5289 | -3.2089 | -1.8735 | -4.1744 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.196 | 0.30266 | 0.27754 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0473 | Night
2025-08-02 01:00 | 79.8 | 79.394 | 1.0297 | 81.4534 | 77.3346 | 0.39429 | FALSE | none | -1.6534 | -2.4654 | -2.0298 | -3.1879 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.154 | 0.30773 | -1.4103 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0263 | Night
2025-08-02 01:15 | 80.08 | 79.548 | 0.87087 | 81.2897 | 77.8063 | 0.61088 | FALSE | none | -1.2097 | -2.2737 | -1.4882 | -2.9223 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.154 | 0.30773 | 0.40945 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0407 | Night
2025-08-02 01:30 | 80.08 | 79.688 | 0.69423 | 81.0765 | 78.2995 | 0.56466 | FALSE | none | -0.99646 | -1.7805 | -1.229 | -2.2739 | Normal | 0 |  |  |  | 0 | 0 | 0.14 | 0.30807 | -0.45445 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0376 | Night
2025-08-02 01:45 | 80.08 | 79.814 | 0.48476 | 80.7835 | 78.8445 | 0.54872 | FALSE | none | -0.70352 | -1.2355 | -0.87087 | -1.567 | Normal | 0 |  |  |  | 0 | 0 | 0.126 | 0.30773 | -0.40945 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0366 | Night
2025-08-02 02:00 | 80.08 | 79.898 | 0.35505 | 80.6081 | 79.1879 | 0.51261 | FALSE | none | -0.5281 | -0.8921 | -0.65514 | -1.1266 | Normal | 0 |  |  |  | 0 | 0 | 0.084 | 0.25855 | -0.32489 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0342 | Night
2025-08-02 02:15 | 80.08 | 79.954 | 0.27963 | 80.5133 | 79.3947 | 0.45059 | FALSE | none | -0.43326 | -0.68526 | -0.53813 | -0.86311 | Normal | 0 |  |  |  | 0 | 0 | 0.056 | 0.23338 | -0.23995 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.03 | Night
2025-08-02 02:30 | 79.8 | 79.996 | 0.15995 | 80.3159 | 79.6761 | -1.2254 | FALSE | none | -0.51589 | -0.12389 | -0.64233 | -0.1555 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.042 | 0.24503 | -1.3141 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0817 | Night
2025-08-02 02:45 | 79.8 | 80.01 | 0.12439 | 80.2588 | 79.7612 | -1.6882 | FALSE | none | -0.45879 | -0.038787 | -0.57163 | -0.048628 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.21256 | -0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1125 | Night
2025-08-02 03:00 | 80.36 | 80.024 | 0.14648 | 80.317 | 79.731 | 2.2938 | TRUE | upper | 0.043037 | -0.62896 | 0.053584 | -0.78886 | Extreme triggered | 1 | 2025-08-02 03:00 | 2025-08-02 03:15 | 2.2938 | 0.56 | 0.56 | 0.014 | 0.21256 | 2.5686 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.2386 | Night
2025-08-02 03:15 | 80.08 | 80.024 | 0.14648 | 80.317 | 79.731 | 0.3823 | FALSE | none | -0.23696 | -0.34896 | -0.29503 | -0.43768 | Persistence ends | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.22252 | -1.2583 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0541 | Night
2025-08-02 03:30 | 79.8 | 80.01 | 0.15403 | 80.3181 | 79.7019 | -1.3633 | FALSE | none | -0.51807 | -0.098067 | -0.64502 | -0.12304 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.23116 | -1.1507 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1195 | Night
2025-08-02 03:45 | 80.08 | 80.01 | 0.15403 | 80.3181 | 79.7019 | 0.45445 | FALSE | none | -0.23807 | -0.37807 | -0.29641 | -0.47435 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.24035 | 1.165 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0589 | Night
2025-08-02 04:00 | 80.08 | 80.01 | 0.15403 | 80.3181 | 79.7019 | 0.45445 | FALSE | none | -0.23807 | -0.37807 | -0.29641 | -0.47435 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.24035 | 0 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0589 | Night
2025-08-02 04:15 | 80.08 | 80.01 | 0.15403 | 80.3181 | 79.7019 | 0.45445 | FALSE | none | -0.23807 | -0.37807 | -0.29641 | -0.47435 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.24035 | 0 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0589 | Night
2025-08-02 04:30 | 80.08 | 80.01 | 0.15403 | 80.3181 | 79.7019 | 0.45445 | FALSE | none | -0.23807 | -0.37807 | -0.29641 | -0.47435 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.24035 | 0 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0589 | Night
2025-08-02 04:45 | 80.08 | 80.024 | 0.14648 | 80.317 | 79.731 | 0.3823 | FALSE | none | -0.23696 | -0.34896 | -0.29503 | -0.43768 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.23116 | -0.060564 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0541 | Night
2025-08-02 05:00 | 79.8 | 80.01 | 0.15403 | 80.3181 | 79.7019 | -1.3633 | FALSE | none | -0.51807 | -0.098067 | -0.64502 | -0.12304 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.23116 | -1.1507 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1195 | Night
2025-08-02 05:15 | 80.08 | 80.01 | 0.15403 | 80.3181 | 79.7019 | 0.45445 | FALSE | none | -0.23807 | -0.37807 | -0.29641 | -0.47435 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.24035 | 1.165 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0589 | Night
2025-08-02 05:30 | 79.8 | 80.01 | 0.15403 | 80.3181 | 79.7019 | -1.3633 | FALSE | none | -0.51807 | -0.098067 | -0.64502 | -0.12304 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.24035 | -1.165 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0909 | Night
2025-08-02 05:45 | 80.08 | 80.01 | 0.15403 | 80.3181 | 79.7019 | 0.45445 | FALSE | none | -0.23807 | -0.37807 | -0.29641 | -0.47435 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.24035 | 1.165 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0303 | Night
2025-08-02 06:00 | 80.36 | 80.038 | 0.1644 | 80.3668 | 79.7092 | 1.9586 | FALSE | none | -0.0068001 | -0.6508 | -0.0084613 | -0.81647 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.028 | 0.23863 | 1.056 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1306 | Night
2025-08-02 06:15 | 79.8 | 80.024 | 0.17236 | 80.3687 | 79.6793 | -1.2996 | FALSE | none | -0.56873 | -0.12073 | -0.70765 | -0.15152 | Normal | 0 |  |  |  | -0.56 | -0.56 | -0.014 | 0.26446 | -2.0646 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1152 | Night
2025-08-02 06:30 | 79.52 | 79.996 | 0.20515 | 80.4063 | 79.5857 | -2.3202 | TRUE | lower | -0.88631 | 0.065691 | -1.1023 | 0.082541 | Extreme triggered | 1 | 2025-08-02 06:30 | 2025-08-02 06:45 | 2.3202 | -0.28 | -0.28 | -0.028 | 0.27101 | -0.92984 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.2404 | Night
2025-08-02 06:45 | 80.08 | 79.996 | 0.20515 | 80.4063 | 79.5857 | 0.40945 | FALSE | none | -0.32631 | -0.49431 | -0.40583 | -0.6211 | Persistence ends | 0 |  |  |  | 0.56 | 0.56 | 0 | 0.3013 | 1.8586 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0559 | Night
2025-08-02 07:00 | 80.36 | 80.01 | 0.22019 | 80.4504 | 79.5696 | 1.5895 | FALSE | none | -0.090383 | -0.79038 | -0.11235 | -0.99332 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.30773 | 0.86439 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1345 | Day
2025-08-02 07:15 | 79.8 | 79.996 | 0.22437 | 80.4447 | 79.5473 | -0.87356 | FALSE | none | -0.64474 | -0.25274 | -0.80146 | -0.31772 | Normal | 0 |  |  |  | -0.56 | -0.56 | -0.014 | 0.33347 | -1.6373 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0868 | Day
2025-08-02 07:30 | 79.8 | 79.996 | 0.22437 | 80.4447 | 79.5473 | -0.87356 | FALSE | none | -0.64474 | -0.25274 | -0.80146 | -0.31772 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.32754 | 0 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0868 | Day
2025-08-02 07:45 | 80.08 | 80.01 | 0.22019 | 80.4504 | 79.5696 | 0.31791 | FALSE | none | -0.37038 | -0.51038 | -0.46039 | -0.64143 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.33347 | 0.79767 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0498 | Day
2025-08-02 08:00 | 79.8 | 79.982 | 0.20864 | 80.3993 | 79.5647 | -0.8723 | FALSE | none | -0.59929 | -0.23529 | -0.74539 | -0.29572 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.028 | 0.31338 | -0.80414 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0867 | Day
2025-08-02 08:15 | 79.24 | 79.94 | 0.26485 | 80.4697 | 79.4103 | -2.643 | TRUE | lower | -1.2297 | 0.17029 | -1.5282 | 0.21445 | Extreme triggered | 1 | 2025-08-02 08:15 | 2025-08-02 12:00 | 2.643 | -0.56 | -0.56 | -0.042 | 0.33099 | -1.565 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.2619 | Day
2025-08-02 08:30 | 78.68 | 79.884 | 0.38649 | 80.657 | 79.111 | -3.1152 | TRUE | lower | -1.977 | 0.43102 | -2.4511 | 0.54484 | Extreme/elevated | 2 | 2025-08-02 08:15 |  | 2.8791 | -0.56 | -0.56 | -0.056 | 0.34711 | -1.452 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.3505 | Day
2025-08-02 08:45 | 78.12 | 79.786 | 0.54865 | 80.8833 | 78.6887 | -3.0366 | TRUE | lower | -2.7633 | 0.5687 | -3.4164 | 0.72273 | Persistent | 3 | 2025-08-02 08:15 |  | 2.9316 | -0.56 | -0.56 | -0.098 | 0.35505 | -1.3012 | FALSE | 0 | FALSE | TRUE | FALSE | FALSE | 0.3739 | Day
2025-08-02 09:00 | 77.28 | 79.646 | 0.77869 | 81.2034 | 78.0886 | -3.0384 | TRUE | lower | -3.9234 | 0.80861 | -4.8316 | 1.0355 | Persistent | 4 | 2025-08-02 08:15 |  | 2.9583 | -0.84 | -0.84 | -0.14 | 0.39073 | -1.7915 | FALSE | 0 | FALSE | TRUE | FALSE | FALSE | 0.4311 | Day
2025-08-02 09:15 | 76.72 | 79.478 | 1.0086 | 81.4953 | 77.4607 | -2.7344 | TRUE | lower | -4.7753 | 0.74073 | -5.8596 | 0.95627 | Persistent | 5 | 2025-08-02 08:15 |  | 2.9135 | -0.56 | -0.56 | -0.168 | 0.40013 | -0.97969 | FALSE | 0 | FALSE | TRUE | FALSE | FALSE | 0.468 | Day
2025-08-02 09:30 | 76.16 | 79.282 | 1.2399 | 81.7617 | 76.8023 | -2.518 | TRUE | lower | -5.6017 | 0.64228 | -6.8513 | 0.83627 | Persistent | 6 | 2025-08-02 08:15 |  | 2.8476 | -0.56 | -0.56 | -0.196 | 0.40728 | -0.89373 | FALSE | 0 | FALSE | TRUE | FALSE | FALSE | 0.5107 | Day
2025-08-02 09:45 | 75.32 | 79.044 | 1.5068 | 82.0575 | 76.0305 | -2.4715 | TRUE | lower | -6.7375 | 0.7105 | -8.2107 | 0.93449 | Confirmed/Materialized Shift | 7 | 2025-08-02 08:15 |  | 2.7939 | -0.84 | -0.84 | -0.238 | 0.42875 | -1.4041 | FALSE | 0 | FALSE | TRUE | TRUE | FALSE | 0.5648 | Day
2025-08-02 10:00 | 74.76 | 78.792 | 1.7718 | 82.3356 | 75.2484 | -2.2756 | TRUE | lower | -7.5756 | 0.48839 | -9.2009 | 0.64903 | Confirmed/Materialized Shift | 8 | 2025-08-02 08:15 |  | 2.7291 | -0.56 | -0.56 | -0.252 | 0.43472 | -0.70849 | FALSE | 0 | FALSE | TRUE | TRUE | FALSE | 0.5517 | Day
2025-08-02 10:15 | 74.76 | 78.526 | 1.9578 | 82.4417 | 74.6103 | -1.9235 | FALSE | none | -7.6817 | -0.14968 | -9.3177 | -0.20062 | Confirmed/Materialized Shift | 9 | 2025-08-02 08:15 |  | 2.6396 | 0 | 0 | -0.266 | 0.42098 | 0.63186 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.5282 | Day
2025-08-02 10:30 | 75.04 | 78.288 | 2.0803 | 82.4486 | 74.1274 | -1.5613 | FALSE | none | -7.4086 | -0.91262 | -8.9857 | -1.2311 | Confirmed/Materialized Shift | 10 | 2025-08-02 08:15 |  | 2.5318 | 0.28 | 0.28 | -0.238 | 0.43827 | 1.1819 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.5041 | Day
2025-08-02 10:45 | 74.76 | 78.022 | 2.177 | 82.376 | 73.668 | -1.4984 | FALSE | none | -7.616 | -1.092 | -9.2454 | -1.4823 | Confirmed/Materialized Shift | 11 | 2025-08-02 08:15 |  | 2.4378 | -0.28 | -0.28 | -0.266 | 0.42098 | -0.033256 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4999 | Day
2025-08-02 11:00 | 74.76 | 77.742 | 2.2202 | 82.1823 | 73.3017 | -1.3431 | FALSE | none | -7.4223 | -1.4583 | -9.0315 | -1.9895 | Confirmed/Materialized Shift | 12 | 2025-08-02 08:15 |  | 2.3466 | 0 | 0 | -0.28 | 0.40627 | 0.6892 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4895 | Day
2025-08-02 11:15 | 75.04 | 77.504 | 2.2429 | 81.9899 | 73.0181 | -1.0986 | FALSE | none | -6.9499 | -2.0219 | -8.4765 | -2.769 | Confirmed/Materialized Shift | 13 | 2025-08-02 08:15 |  | 2.2506 | 0.28 | 0.28 | -0.238 | 0.41902 | 1.2362 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4732 | Day
2025-08-02 11:30 | 74.76 | 77.266 | 2.2701 | 81.8063 | 72.7257 | -1.1039 | FALSE | none | -7.0463 | -2.0343 | -8.6134 | -2.7972 | Confirmed/Materialized Shift | 14 | 2025-08-02 08:15 |  | 2.1687 | -0.28 | -0.28 | -0.238 | 0.41902 | -0.10023 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4736 | Day
2025-08-02 11:45 | 74.76 | 77 | 2.2345 | 81.4689 | 72.5311 | -1.0025 | FALSE | none | -6.7089 | -2.2289 | -8.235 | -3.0731 | Confirmed/Materialized Shift | 15 | 2025-08-02 08:15 |  | 2.0909 | 0 | 0 | -0.266 | 0.37976 | 0.70045 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4668 | Day
2025-08-02 12:00 | 75.04 | 76.734 | 2.1275 | 80.989 | 72.479 | -0.79623 | FALSE | none | -5.949 | -2.561 | -7.3455 | -3.5335 | Persistence ends | 0 |  |  |  | 0.28 | 0.28 | -0.266 | 0.37976 | 1.4378 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-02 12:15 | 74.76 | 76.482 | 2.042 | 80.566 | 72.398 | -0.84328 | FALSE | none | -5.806 | -2.362 | -7.2066 | -3.2626 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.252 | 0.37346 | -0.074975 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0562 | Day
2025-08-02 12:30 | 74.76 | 76.23 | 1.9182 | 80.0665 | 72.3935 | -0.76633 | FALSE | none | -5.3065 | -2.3665 | -6.6276 | -3.2689 | Normal | 0 |  |  |  | 0 | 0 | -0.252 | 0.37346 | 0.67478 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0511 | Day
2025-08-02 12:45 | 75.04 | 75.978 | 1.7051 | 79.3881 | 72.5679 | -0.55013 | FALSE | none | -4.3481 | -2.4721 | -5.477 | -3.4066 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.252 | 0.37346 | 1.4245 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0367 | Day
2025-08-02 13:00 | 75.04 | 75.74 | 1.4578 | 78.6555 | 72.8245 | -0.48019 | FALSE | none | -3.6155 | -2.2155 | -4.5966 | -3.0423 | Normal | 0 |  |  |  | 0 | 0 | -0.238 | 0.37758 | 0.63034 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.032 | Day
2025-08-02 13:15 | 74.76 | 75.516 | 1.2157 | 77.9475 | 73.0845 | -0.62184 | FALSE | none | -3.1875 | -1.6755 | -4.0893 | -2.2925 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.224 | 0.37013 | -0.1513 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0415 | Day
2025-08-02 13:30 | 75.04 | 75.334 | 0.96344 | 77.2609 | 73.4071 | -0.30516 | FALSE | none | -2.2209 | -1.6329 | -2.8745 | -2.2244 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.182 | 0.37758 | 1.2236 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0203 | Day
2025-08-02 13:45 | 74.76 | 75.166 | 0.71227 | 76.5905 | 73.7415 | -0.57001 | FALSE | none | -1.8305 | -1.0185 | -2.39 | -1.3812 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.168 | 0.36789 | -0.30444 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.038 | Day
2025-08-02 14:00 | 74.76 | 75.04 | 0.51389 | 76.0678 | 74.0122 | -0.54486 | FALSE | none | -1.3078 | -0.74778 | -1.7192 | -1.0104 | Normal | 0 |  |  |  | 0 | 0 | -0.126 | 0.33347 | 0.37784 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0363 | Day
2025-08-02 14:15 | 74.76 | 74.942 | 0.33099 | 75.604 | 74.28 | -0.54987 | FALSE | none | -0.84398 | -0.47998 | -1.1163 | -0.64617 | Normal | 0 |  |  |  | 0 | 0 | -0.098 | 0.31828 | 0.30791 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0367 | Day
2025-08-02 14:30 | 74.76 | 74.872 | 0.16751 | 75.207 | 74.537 | -0.66862 | FALSE | none | -0.44702 | -0.22302 | -0.59438 | -0.2992 | Normal | 0 |  |  |  | 0 | 0 | -0.07 | 0.29958 | 0.23366 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0446 | Day
2025-08-02 14:45 | 75.04 | 74.858 | 0.13702 | 75.132 | 74.584 | 1.3283 | FALSE | none | -0.092042 | -0.45604 | -0.12251 | -0.61145 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.014 | 0.24837 | 1.1837 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0886 | Day
2025-08-02 15:00 | 74.76 | 74.858 | 0.13702 | 75.132 | 74.584 | -0.71522 | FALSE | none | -0.37204 | -0.17604 | -0.49518 | -0.23603 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.22252 | -1.2583 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0477 | Day
2025-08-02 15:15 | 75.04 | 74.872 | 0.14073 | 75.1535 | 74.5905 | 1.1937 | FALSE | none | -0.11347 | -0.44947 | -0.15098 | -0.60258 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.23116 | 1.1507 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0796 | Day
2025-08-02 15:30 | 74.48 | 74.844 | 0.15995 | 75.1639 | 74.5241 | -2.2757 | TRUE | lower | -0.68389 | 0.044105 | -0.90987 | 0.059183 | Extreme triggered | 1 | 2025-08-02 15:30 | 2025-08-02 15:45 | 2.2757 | -0.56 | -0.56 | -0.028 | 0.25533 | -2.0835 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.2374 | Day
2025-08-02 15:45 | 74.76 | 74.844 | 0.15995 | 75.1639 | 74.5241 | -0.52517 | FALSE | none | -0.40389 | -0.23589 | -0.53735 | -0.31653 | Persistence ends | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.25695 | 1.0897 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0636 | Day
2025-08-02 16:00 | 75.04 | 74.858 | 0.1644 | 75.1868 | 74.5292 | 1.1071 | FALSE | none | -0.1468 | -0.5108 | -0.19525 | -0.68537 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.26446 | 1.0058 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1024 | Day
2025-08-02 16:15 | 74.76 | 74.844 | 0.15995 | 75.1639 | 74.5241 | -0.52517 | FALSE | none | -0.40389 | -0.23589 | -0.53735 | -0.31653 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.26446 | -1.0058 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0636 | Day
2025-08-02 16:30 | 74.76 | 74.844 | 0.15995 | 75.1639 | 74.5241 | -0.52517 | FALSE | none | -0.40389 | -0.23589 | -0.53735 | -0.31653 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.25695 | 0 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0636 | Day
2025-08-02 16:45 | 75.04 | 74.858 | 0.1644 | 75.1868 | 74.5292 | 1.1071 | FALSE | none | -0.1468 | -0.5108 | -0.19525 | -0.68537 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.26446 | 1.0058 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1024 | Day
2025-08-02 17:00 | 75.04 | 74.858 | 0.1644 | 75.1868 | 74.5292 | 1.1071 | FALSE | none | -0.1468 | -0.5108 | -0.19525 | -0.68537 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.25695 | 0 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1024 | Day
2025-08-02 17:15 | 75.04 | 74.872 | 0.16751 | 75.207 | 74.537 | 1.0029 | FALSE | none | -0.16702 | -0.50302 | -0.22208 | -0.67485 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.24837 | -0.056367 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0954 | Day
2025-08-02 17:30 | 75.32 | 74.9 | 0.19271 | 75.2854 | 74.5146 | 2.1794 | TRUE | upper | 0.034582 | -0.80542 | 0.045934 | -1.0809 | Extreme triggered | 1 | 2025-08-02 17:30 | 2025-08-02 17:45 | 2.1794 | 0.28 | 0.28 | 0.028 | 0.25533 | 0.98694 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.231 | Day
2025-08-02 17:45 | 75.04 | 74.9 | 0.19271 | 75.2854 | 74.5146 | 0.72648 | FALSE | none | -0.24542 | -0.52542 | -0.32598 | -0.70512 | Persistence ends | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.25695 | -1.0897 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.077 | Day
2025-08-02 18:00 | 74.76 | 74.886 | 0.19217 | 75.2703 | 74.5017 | -0.65566 | FALSE | none | -0.51035 | -0.25835 | -0.67802 | -0.34677 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.26446 | -1.0058 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0437 | Day
2025-08-02 18:15 | 74.76 | 74.886 | 0.19217 | 75.2703 | 74.5017 | -0.65566 | FALSE | none | -0.51035 | -0.25835 | -0.67802 | -0.34677 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.25695 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0437 | Day
2025-08-02 18:30 | 74.76 | 74.872 | 0.19056 | 75.2531 | 74.4909 | -0.58775 | FALSE | none | -0.49311 | -0.26911 | -0.65527 | -0.36127 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.24837 | 0.056367 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0392 | Day
2025-08-02 18:45 | 75.04 | 74.886 | 0.19217 | 75.2703 | 74.5017 | 0.80136 | FALSE | none | -0.23035 | -0.53835 | -0.30603 | -0.7226 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.24837 | 1.071 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0534 | Day
2025-08-02 19:00 | 74.76 | 74.886 | 0.19217 | 75.2703 | 74.5017 | -0.65566 | FALSE | none | -0.51035 | -0.25835 | -0.67802 | -0.34677 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.25695 | -1.0897 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0437 | Night
2025-08-02 19:15 | 75.32 | 74.914 | 0.21256 | 75.3391 | 74.4889 | 1.91 | FALSE | none | -0.019127 | -0.83113 | -0.025387 | -1.1158 | Normal | 0 |  |  |  | 0.56 | 0.56 | 0.028 | 0.28583 | 1.8612 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1273 | Night
2025-08-02 19:30 | 75.6 | 74.956 | 0.25855 | 75.4731 | 74.4389 | 2.4908 | TRUE | upper | 0.12691 | -1.1611 | 0.16815 | -1.5598 | Extreme triggered | 1 | 2025-08-02 19:30 | 2025-08-02 23:30 | 2.4908 | 0.28 | 0.28 | 0.042 | 0.2912 | 0.81732 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.2232 | Night
2025-08-02 19:45 | 76.16 | 75.012 | 0.37346 | 75.7589 | 74.2651 | 3.074 | TRUE | upper | 0.40109 | -1.8949 | 0.52943 | -2.5516 | Extreme/elevated | 2 | 2025-08-02 19:30 |  | 2.7824 | 0.56 | 0.56 | 0.056 | 0.3094 | 1.6289 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.3192 | Night
2025-08-02 20:00 | 76.44 | 75.096 | 0.48582 | 76.0676 | 74.1244 | 2.7664 | TRUE | upper | 0.37235 | -2.3156 | 0.4895 | -3.124 | Persistent | 3 | 2025-08-02 19:30 |  | 2.7771 | 0.28 | 0.28 | 0.084 | 0.30266 | 0.64759 | FALSE | 0 | FALSE | TRUE | FALSE | FALSE | 0.3559 | Night
2025-08-02 20:15 | 76.72 | 75.18 | 0.60601 | 76.392 | 73.968 | 2.5412 | TRUE | upper | 0.32799 | -2.752 | 0.42935 | -3.7205 | Persistent | 4 | 2025-08-02 19:30 |  | 2.7181 | 0.28 | 0.28 | 0.084 | 0.30266 | 0.64759 | FALSE | 0 | FALSE | TRUE | FALSE | FALSE | 0.398 | Night
2025-08-02 20:30 | 77.56 | 75.334 | 0.78397 | 76.9019 | 73.7661 | 2.8394 | TRUE | upper | 0.65805 | -3.7939 | 0.8557 | -5.1432 | Persistent | 5 | 2025-08-02 19:30 |  | 2.7424 | 0.84 | 0.84 | 0.154 | 0.30773 | 2.2292 | TRUE | 1 | FALSE | TRUE | FALSE | FALSE | 0.5036 | Night
2025-08-02 20:45 | 78.12 | 75.502 | 0.98797 | 77.4779 | 73.5261 | 2.6499 | TRUE | upper | 0.64206 | -4.5939 | 0.82871 | -6.248 | Persistent | 6 | 2025-08-02 19:30 |  | 2.727 | 0.56 | 0.56 | 0.168 | 0.31989 | 1.2254 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.5481 | Night
2025-08-02 21:00 | 78.4 | 75.67 | 1.1735 | 78.017 | 73.323 | 2.3263 | TRUE | upper | 0.38295 | -5.077 | 0.49086 | -6.9242 | Confirmed/Materialized Shift | 7 | 2025-08-02 19:30 |  | 2.6697 | 0.28 | 0.28 | 0.168 | 0.31989 | 0.35012 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5837 | Night
2025-08-02 21:15 | 78.68 | 75.866 | 1.3304 | 78.5268 | 73.2052 | 2.1151 | TRUE | upper | 0.15319 | -5.4748 | 0.19507 | -7.4787 | Confirmed/Materialized Shift | 8 | 2025-08-02 19:30 |  | 2.6004 | 0.28 | 0.28 | 0.196 | 0.30266 | 0.27754 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5696 | Night
2025-08-02 21:30 | 78.96 | 76.076 | 1.4707 | 79.0174 | 73.1346 | 1.9609 | FALSE | none | -0.057438 | -5.8254 | -0.072691 | -7.9654 | Confirmed/Materialized Shift | 9 | 2025-08-02 19:30 |  | 2.5294 | 0.28 | 0.28 | 0.21 | 0.29958 | 0.23366 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5593 | Night
2025-08-02 21:45 | 80.08 | 76.328 | 1.6981 | 79.7242 | 72.9318 | 2.2096 | TRUE | upper | 0.35584 | -7.1482 | 0.44634 | -9.8011 | Confirmed/Materialized Shift | 10 | 2025-08-02 19:30 |  | 2.4974 | 1.12 | 1.12 | 0.252 | 0.36224 | 2.3962 | TRUE | 2 | TRUE | TRUE | TRUE | TRUE | 0.6044 | Night
2025-08-02 22:00 | 80.08 | 76.58 | 1.8629 | 80.3057 | 72.8543 | 1.8788 | FALSE | none | -0.22571 | -7.2257 | -0.28107 | -9.918 | Confirmed/Materialized Shift | 11 | 2025-08-02 19:30 |  | 2.4411 | 0 | 0 | 0.252 | 0.36224 | -0.69567 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5824 | Night
2025-08-02 22:15 | 79.8 | 76.818 | 1.9574 | 80.7328 | 72.9032 | 1.5234 | FALSE | none | -0.93284 | -6.8968 | -1.1555 | -9.4603 | Confirmed/Materialized Shift | 12 | 2025-08-02 19:30 |  | 2.3647 | -0.28 | -0.28 | 0.238 | 0.37758 | -1.3719 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5587 | Night
2025-08-02 22:30 | 79.8 | 77.042 | 2.0319 | 81.1058 | 72.9782 | 1.3574 | FALSE | none | -1.3058 | -6.8218 | -1.61 | -9.3477 | Confirmed/Materialized Shift | 13 | 2025-08-02 19:30 |  | 2.2872 | 0 | 0 | 0.224 | 0.38111 | -0.58775 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5476 | Night
2025-08-02 22:45 | 80.08 | 77.294 | 2.0824 | 81.4589 | 73.1291 | 1.3379 | FALSE | none | -1.3789 | -6.9509 | -1.6927 | -9.5049 | Confirmed/Materialized Shift | 14 | 2025-08-02 19:30 |  | 2.2194 | 0.28 | 0.28 | 0.252 | 0.36224 | 0.077297 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5463 | Night
2025-08-02 23:00 | 79.8 | 77.546 | 2.0645 | 81.6751 | 73.4169 | 1.0918 | FALSE | none | -1.8751 | -6.3831 | -2.2958 | -8.6943 | Confirmed/Materialized Shift | 15 | 2025-08-02 19:30 |  | 2.1442 | -0.28 | -0.28 | 0.252 | 0.36224 | -1.4686 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5014 | Night
2025-08-02 23:15 | 80.08 | 77.812 | 2.0291 | 81.8702 | 73.7538 | 1.1177 | FALSE | none | -1.7902 | -6.3262 | -2.1866 | -8.5774 | Confirmed/Materialized Shift | 16 | 2025-08-02 19:30 |  | 2.08 | 0.28 | 0.28 | 0.266 | 0.35736 | 0.039176 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5031 | Night
2025-08-02 23:30 | 79.8 | 78.064 | 1.9412 | 81.9463 | 74.1817 | 0.8943 | FALSE | none | -2.1463 | -5.6183 | -2.6192 | -7.5738 | Persistence ends | 0 |  |  |  | -0.28 | -0.28 | 0.252 | 0.37346 | -1.4245 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0882 | Night
2025-08-02 23:45 | 80.08 | 78.316 | 1.8531 | 82.0222 | 74.6098 | 0.95193 | FALSE | none | -1.9422 | -5.4702 | -2.3679 | -7.3317 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.252 | 0.37346 | 0.074975 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.092 | Night
2025-08-03 | 80.08 | 78.582 | 1.6905 | 81.9629 | 75.2011 | 0.88615 | FALSE | none | -1.8829 | -4.8789 | -2.2973 | -6.4879 | Normal | 0 |  |  |  | 0 | 0 | 0.266 | 0.35736 | -0.74434 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0876 | Night
2025-08-03 00:15 | 79.52 | 78.792 | 1.5158 | 81.8235 | 75.7605 | 0.48029 | FALSE | none | -2.3035 | -3.7595 | -2.8152 | -4.9624 | Normal | 0 |  |  |  | -0.56 | -0.56 | 0.21 | 0.39468 | -1.951 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.032 | Night
2025-08-03 00:30 | 80.08 | 79.016 | 1.3401 | 81.6961 | 76.3359 | 0.79399 | FALSE | none | -1.6161 | -3.7441 | -1.9782 | -4.9048 | Normal | 0 |  |  |  | 0.56 | 0.56 | 0.224 | 0.40218 | 0.83544 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0529 | Night
2025-08-03 00:45 | 79.8 | 79.198 | 1.1679 | 81.5338 | 76.8622 | 0.51546 | FALSE | none | -1.7338 | -2.9378 | -2.1264 | -3.8221 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.182 | 0.40905 | -1.1294 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0344 | Night
2025-08-03 01:00 | 80.08 | 79.38 | 0.98473 | 81.3495 | 77.4105 | 0.71086 | FALSE | none | -1.2695 | -2.6695 | -1.5605 | -3.4484 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.182 | 0.40905 | 0.23958 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0474 | Night
2025-08-03 01:15 | 80.08 | 79.548 | 0.7703 | 81.0886 | 78.0074 | 0.69064 | FALSE | none | -1.0086 | -2.0726 | -1.2438 | -2.6569 | Normal | 0 |  |  |  | 0 | 0 | 0.168 | 0.41031 | -0.40945 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.046 | Night
2025-08-03 01:30 | 80.08 | 79.674 | 0.61931 | 80.9126 | 78.4354 | 0.65557 | FALSE | none | -0.83261 | -1.6446 | -1.029 | -2.0968 | Normal | 0 |  |  |  | 0 | 0 | 0.126 | 0.37976 | -0.33179 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0437 | Night
2025-08-03 01:45 | 79.8 | 79.758 | 0.49985 | 80.7577 | 78.7583 | 0.084025 | FALSE | none | -0.9577 | -1.0417 | -1.1859 | -1.3227 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.084 | 0.37566 | -0.96896 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0056 | Night
2025-08-03 02:00 | 80.36 | 79.856 | 0.40218 | 80.6604 | 79.0516 | 1.2532 | FALSE | none | -0.30037 | -1.3084 | -0.37238 | -1.6551 | Normal | 0 |  |  |  | 0.56 | 0.56 | 0.098 | 0.38835 | 1.1896 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0835 | Night
2025-08-03 02:15 | 80.36 | 79.94 | 0.30807 | 80.5561 | 79.3239 | 1.3633 | FALSE | none | -0.19613 | -1.0361 | -0.24347 | -1.3062 | Normal | 0 |  |  |  | 0 | 0 | 0.084 | 0.38649 | -0.21734 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0909 | Night
2025-08-03 02:30 | 79.8 | 79.982 | 0.20864 | 80.3993 | 79.5647 | -0.8723 | FALSE | none | -0.59929 | -0.23529 | -0.74539 | -0.29572 | Normal | 0 |  |  |  | -0.56 | -0.56 | 0.042 | 0.40905 | -1.4717 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0582 | Night
2025-08-03 02:45 | 80.08 | 79.982 | 0.20864 | 80.3993 | 79.5647 | 0.4697 | FALSE | none | -0.31929 | -0.51529 | -0.39713 | -0.64764 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.32754 | 0.85485 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0313 | Night
2025-08-03 03:00 | 79.8 | 79.968 | 0.2111 | 80.3902 | 79.5458 | -0.79582 | FALSE | none | -0.5902 | -0.2542 | -0.73417 | -0.31957 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.33347 | -0.79767 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Night
2025-08-03 03:15 | 80.08 | 79.982 | 0.20864 | 80.3993 | 79.5647 | 0.4697 | FALSE | none | -0.31929 | -0.51529 | -0.39713 | -0.64764 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.33347 | 0.79767 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0313 | Night
2025-08-03 03:30 | 79.8 | 79.982 | 0.20864 | 80.3993 | 79.5647 | -0.8723 | FALSE | none | -0.59929 | -0.23529 | -0.74539 | -0.29572 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.33991 | -0.82375 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0582 | Night
2025-08-03 03:45 | 80.36 | 79.996 | 0.22437 | 80.4447 | 79.5473 | 1.6223 | FALSE | none | -0.084736 | -0.81274 | -0.10533 | -1.0217 | Normal | 0 |  |  |  | 0.56 | 0.56 | 0.014 | 0.35736 | 1.5279 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1082 | Night
2025-08-03 04:00 | 79.8 | 79.996 | 0.22437 | 80.4447 | 79.5473 | -0.87356 | FALSE | none | -0.64474 | -0.25274 | -0.80146 | -0.31772 | Normal | 0 |  |  |  | -0.56 | -0.56 | 0 | 0.37456 | -1.4951 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0582 | Night
2025-08-03 04:15 | 80.08 | 79.996 | 0.22437 | 80.4447 | 79.5473 | 0.37438 | FALSE | none | -0.36474 | -0.53274 | -0.4534 | -0.66971 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.37456 | 0.74755 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.025 | Night
2025-08-03 04:30 | 80.08 | 80.01 | 0.22019 | 80.4504 | 79.5696 | 0.31791 | FALSE | none | -0.37038 | -0.51038 | -0.46039 | -0.64143 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.36873 | -0.037968 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0212 | Night
2025-08-03 04:45 | 79.8 | 79.996 | 0.22437 | 80.4447 | 79.5473 | -0.87356 | FALSE | none | -0.64474 | -0.25274 | -0.80146 | -0.31772 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.36873 | -0.72139 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0582 | Night
2025-08-03 05:00 | 80.08 | 79.996 | 0.22437 | 80.4447 | 79.5473 | 0.37438 | FALSE | none | -0.36474 | -0.53274 | -0.4534 | -0.66971 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.37456 | 0.74755 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.025 | Night
2025-08-03 05:15 | 79.8 | 80.01 | 0.20058 | 80.4112 | 79.6088 | -1.047 | FALSE | none | -0.61116 | -0.19116 | -0.76004 | -0.24012 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.014 | 0.35736 | -0.82269 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0698 | Night
2025-08-03 05:30 | 80.08 | 80.01 | 0.20058 | 80.4112 | 79.6088 | 0.34899 | FALSE | none | -0.33116 | -0.47116 | -0.41183 | -0.59184 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.33991 | 0.82375 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0233 | Night
2025-08-03 05:45 | 79.8 | 80.01 | 0.20058 | 80.4112 | 79.6088 | -1.047 | FALSE | none | -0.61116 | -0.19116 | -0.76004 | -0.24012 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.33991 | -0.82375 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0698 | Night
2025-08-03 06:00 | 79.8 | 79.996 | 0.20515 | 80.4063 | 79.5857 | -0.95538 | FALSE | none | -0.60631 | -0.21431 | -0.75406 | -0.26928 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.33347 | 0.041982 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0637 | Night
2025-08-03 06:15 | 80.08 | 79.996 | 0.20515 | 80.4063 | 79.5857 | 0.40945 | FALSE | none | -0.32631 | -0.49431 | -0.40583 | -0.6211 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.33991 | 0.82375 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0273 | Night
2025-08-03 06:30 | 80.08 | 79.996 | 0.20515 | 80.4063 | 79.5857 | 0.40945 | FALSE | none | -0.32631 | -0.49431 | -0.40583 | -0.6211 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.33991 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0273 | Night
2025-08-03 06:45 | 80.08 | 80.01 | 0.20058 | 80.4112 | 79.6088 | 0.34899 | FALSE | none | -0.33116 | -0.47116 | -0.41183 | -0.59184 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.33347 | -0.041982 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0233 | Night
2025-08-03 07:00 | 80.08 | 79.996 | 0.18395 | 80.3639 | 79.6281 | 0.45666 | FALSE | none | -0.28389 | -0.45189 | -0.35326 | -0.5675 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.30773 | 0.045494 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0304 | Day
2025-08-03 07:15 | 80.08 | 79.982 | 0.1644 | 80.3108 | 79.6532 | 0.59611 | FALSE | none | -0.2308 | -0.4268 | -0.28738 | -0.53582 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.30773 | 0.045494 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0397 | Day
2025-08-03 07:30 | 80.08 | 79.996 | 0.15995 | 80.3159 | 79.6761 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.29371 | -0.50692 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.27963 | -0.050066 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.035 | Day
2025-08-03 07:45 | 80.08 | 79.996 | 0.15995 | 80.3159 | 79.6761 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.29371 | -0.50692 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.27253 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.035 | Day
2025-08-03 08:00 | 79.8 | 79.996 | 0.15995 | 80.3159 | 79.6761 | -1.2254 | FALSE | none | -0.51589 | -0.12389 | -0.64233 | -0.1555 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.27253 | -1.0274 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0817 | Day
2025-08-03 08:15 | 79.24 | 79.954 | 0.23116 | 80.4163 | 79.4917 | -3.0887 | TRUE | lower | -1.1763 | 0.25168 | -1.4628 | 0.31661 | Extreme triggered | 1 | 2025-08-03 08:15 | 2025-08-03 12:00 | 3.0887 | -0.56 | -0.56 | -0.042 | 0.2912 | -1.7789 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.2631 | Day
2025-08-03 08:30 | 78.4 | 79.884 | 0.41729 | 80.7186 | 79.0494 | -3.5563 | TRUE | lower | -2.3186 | 0.64942 | -2.8724 | 0.82154 | Extreme/elevated | 2 | 2025-08-03 08:15 |  | 3.3225 | -0.84 | -0.84 | -0.07 | 0.33839 | -2.2755 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.3799 | Day
2025-08-03 08:45 | 78.12 | 79.772 | 0.55926 | 80.8905 | 78.6535 | -2.9539 | TRUE | lower | -2.7705 | 0.53347 | -3.425 | 0.67826 | Persistent | 3 | 2025-08-03 08:15 |  | 3.1996 | -0.28 | -0.28 | -0.112 | 0.30672 | -0.54772 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.3969 | Day
2025-08-03 09:00 | 77.28 | 79.646 | 0.78922 | 81.2244 | 78.0676 | -2.9979 | TRUE | lower | -3.9444 | 0.78756 | -4.8562 | 1.0088 | Persistent | 4 | 2025-08-03 08:15 |  | 3.1492 | -0.84 | -0.84 | -0.126 | 0.33347 | -2.1411 | TRUE | 2 | TRUE | TRUE | FALSE | TRUE | 0.4856 | Day
2025-08-03 09:15 | 76.72 | 79.478 | 1.0168 | 81.5116 | 77.4444 | -2.7125 | TRUE | lower | -4.7916 | 0.72443 | -5.8784 | 0.93542 | Persistent | 5 | 2025-08-03 08:15 |  | 3.0619 | -0.56 | -0.56 | -0.168 | 0.33254 | -1.1788 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.5237 | Day
2025-08-03 09:30 | 76.16 | 79.282 | 1.2465 | 81.775 | 76.789 | -2.5046 | TRUE | lower | -5.615 | 0.629 | -6.8664 | 0.81913 | Persistent | 6 | 2025-08-03 08:15 |  | 2.969 | -0.56 | -0.56 | -0.196 | 0.34112 | -1.0671 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.567 | Day
2025-08-03 09:45 | 75.6 | 79.072 | 1.4855 | 82.043 | 76.101 | -2.3372 | TRUE | lower | -6.443 | 0.50097 | -7.8532 | 0.6583 | Confirmed/Materialized Shift | 7 | 2025-08-03 08:15 |  | 2.8787 | -0.56 | -0.56 | -0.21 | 0.35037 | -0.99895 | FALSE | 2 | FALSE | TRUE | TRUE | FALSE | 0.613 | Day
2025-08-03 10:00 | 74.76 | 78.806 | 1.7485 | 82.3031 | 75.3089 | -2.3139 | TRUE | lower | -7.5431 | 0.54892 | -9.165 | 0.72889 | Confirmed/Materialized Shift | 8 | 2025-08-03 08:15 |  | 2.8081 | -0.84 | -0.84 | -0.266 | 0.35736 | -1.6062 | FALSE | 2 | FALSE | TRUE | TRUE | FALSE | 0.6114 | Day
2025-08-03 10:15 | 74.48 | 78.54 | 1.9789 | 82.4977 | 74.5823 | -2.0517 | TRUE | lower | -8.0177 | 0.10229 | -9.7187 | 0.13715 | Confirmed/Materialized Shift | 9 | 2025-08-03 08:15 |  | 2.7241 | -0.28 | -0.28 | -0.266 | 0.35736 | -0.039176 | FALSE | 2 | FALSE | TRUE | TRUE | FALSE | 0.5939 | Day
2025-08-03 10:30 | 75.04 | 78.288 | 2.0902 | 82.4684 | 74.1076 | -1.5539 | FALSE | none | -7.4284 | -0.9324 | -9.0076 | -1.2582 | Confirmed/Materialized Shift | 10 | 2025-08-03 08:15 |  | 2.6071 | 0.56 | 0.56 | -0.252 | 0.38435 | 2.1127 | TRUE | 3 | TRUE | FALSE | TRUE | TRUE | 0.5893 | Day
2025-08-03 10:45 | 75.04 | 78.05 | 2.1781 | 82.4063 | 73.6937 | -1.3819 | FALSE | none | -7.3663 | -1.3463 | -8.9389 | -1.8268 | Confirmed/Materialized Shift | 11 | 2025-08-03 08:15 |  | 2.4957 | 0 | 0 | -0.238 | 0.38835 | 0.61285 | FALSE | 3 | FALSE | FALSE | TRUE | FALSE | 0.5778 | Day
2025-08-03 11:00 | 74.76 | 77.798 | 2.2552 | 82.3084 | 73.2876 | -1.3471 | FALSE | none | -7.5484 | -1.4724 | -9.1709 | -2.009 | Confirmed/Materialized Shift | 12 | 2025-08-03 08:15 |  | 2.4 | -0.28 | -0.28 | -0.252 | 0.38435 | -0.072851 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.547 | Day
2025-08-03 11:15 | 75.04 | 77.546 | 2.2683 | 82.0827 | 73.0093 | -1.1048 | FALSE | none | -7.0427 | -2.0307 | -8.58 | -2.7814 | Confirmed/Materialized Shift | 13 | 2025-08-03 08:15 |  | 2.3003 | 0.28 | 0.28 | -0.252 | 0.38435 | 1.3842 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5308 | Day
2025-08-03 11:30 | 74.76 | 77.28 | 2.2675 | 81.8149 | 72.7451 | -1.1114 | FALSE | none | -7.0549 | -2.0149 | -8.623 | -2.7698 | Confirmed/Materialized Shift | 14 | 2025-08-03 08:15 |  | 2.2154 | -0.28 | -0.28 | -0.266 | 0.37976 | -0.036866 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5027 | Day
2025-08-03 11:45 | 74.76 | 77.014 | 2.2335 | 81.481 | 72.547 | -1.0092 | FALSE | none | -6.721 | -2.213 | -8.2485 | -3.0504 | Confirmed/Materialized Shift | 15 | 2025-08-03 08:15 |  | 2.135 | 0 | 0 | -0.266 | 0.37976 | 0.70045 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.4959 | Day
2025-08-03 12:00 | 75.04 | 76.762 | 2.1522 | 81.0664 | 72.4576 | -0.80011 | FALSE | none | -6.0264 | -2.5824 | -7.4339 | -3.564 | Persistence ends | 0 |  |  |  | 0.28 | 0.28 | -0.252 | 0.39494 | 1.3471 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0819 | Day
2025-08-03 12:15 | 74.76 | 76.496 | 2.0467 | 80.5894 | 72.4026 | -0.84819 | FALSE | none | -5.8294 | -2.3574 | -7.2335 | -3.256 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.266 | 0.39047 | -0.035854 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0851 | Day
2025-08-03 12:30 | 75.04 | 76.244 | 1.8862 | 80.0164 | 72.4716 | -0.63832 | FALSE | none | -4.9764 | -2.5684 | -6.2192 | -3.544 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.252 | 0.40525 | 1.3128 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0711 | Day
2025-08-03 12:45 | 74.76 | 75.978 | 1.6807 | 79.3394 | 72.6166 | -0.72471 | FALSE | none | -4.5794 | -2.1434 | -5.7719 | -2.9516 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.266 | 0.4009 | -0.034922 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0769 | Day
2025-08-03 13:00 | 75.04 | 75.74 | 1.4292 | 78.5983 | 72.8817 | -0.48979 | FALSE | none | -3.5583 | -2.1583 | -4.5272 | -2.9614 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.238 | 0.41902 | 1.2362 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0327 | Day
2025-08-03 13:15 | 74.76 | 75.516 | 1.1813 | 77.8786 | 73.1534 | -0.63996 | FALSE | none | -3.1186 | -1.6066 | -4.0045 | -2.1963 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.224 | 0.41232 | -0.13582 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0427 | Day
2025-08-03 13:30 | 74.76 | 75.334 | 0.9762 | 77.2864 | 73.3816 | -0.58799 | FALSE | none | -2.5264 | -1.3784 | -3.2689 | -1.8784 | Normal | 0 |  |  |  | 0 | 0 | -0.182 | 0.38835 | 0.46865 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0392 | Day
2025-08-03 13:45 | 75.04 | 75.18 | 0.72391 | 76.6278 | 73.7322 | -0.19339 | FALSE | none | -1.5878 | -1.3078 | -2.0721 | -1.7737 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.154 | 0.4009 | 1.0826 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0129 | Day
2025-08-03 14:00 | 74.76 | 75.054 | 0.53339 | 76.1208 | 73.9872 | -0.55119 | FALSE | none | -1.3608 | -0.77279 | -1.7877 | -1.0445 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.126 | 0.36873 | -0.41765 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0367 | Day
2025-08-03 14:15 | 75.04 | 74.97 | 0.36195 | 75.6939 | 74.2461 | 0.19339 | FALSE | none | -0.65391 | -0.79391 | -0.86388 | -1.0693 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.084 | 0.36451 | 0.9986 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0129 | Day
2025-08-03 14:30 | 74.76 | 74.9 | 0.23161 | 75.3632 | 74.4368 | -0.60447 | FALSE | none | -0.60322 | -0.32322 | -0.80041 | -0.43421 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.07 | 0.35037 | -0.59937 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0403 | Day
2025-08-03 14:45 | 74.76 | 74.858 | 0.1644 | 75.1868 | 74.5292 | -0.59611 | FALSE | none | -0.4268 | -0.2308 | -0.56765 | -0.30968 | Normal | 0 |  |  |  | 0 | 0 | -0.042 | 0.33099 | 0.12689 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0397 | Day
2025-08-03 15:00 | 75.04 | 74.872 | 0.16751 | 75.207 | 74.537 | 1.0029 | FALSE | none | -0.16702 | -0.50302 | -0.22208 | -0.67485 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.27963 | 0.95125 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0669 | Day
2025-08-03 15:15 | 74.76 | 74.886 | 0.14292 | 75.1718 | 74.6002 | -0.88163 | FALSE | none | -0.41183 | -0.15983 | -0.54786 | -0.21425 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.014 | 0.27963 | -1.0514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-03 15:30 | 75.04 | 74.886 | 0.14292 | 75.1718 | 74.6002 | 1.0775 | FALSE | none | -0.13183 | -0.43983 | -0.17538 | -0.58959 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.25695 | 1.0897 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Day
2025-08-03 15:45 | 74.76 | 74.872 | 0.14073 | 75.1535 | 74.5905 | -0.79582 | FALSE | none | -0.39347 | -0.16947 | -0.52356 | -0.2272 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.26446 | -1.0058 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-03 16:00 | 74.76 | 74.872 | 0.14073 | 75.1535 | 74.5905 | -0.79582 | FALSE | none | -0.39347 | -0.16947 | -0.52356 | -0.2272 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.25695 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-03 16:15 | 75.04 | 74.872 | 0.14073 | 75.1535 | 74.5905 | 1.1937 | FALSE | none | -0.11347 | -0.44947 | -0.15098 | -0.60258 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.25695 | 1.0897 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0796 | Day
2025-08-03 16:30 | 75.04 | 74.886 | 0.14292 | 75.1718 | 74.6002 | 1.0775 | FALSE | none | -0.13183 | -0.43983 | -0.17538 | -0.58959 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.24837 | -0.056367 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Day
2025-08-03 16:45 | 74.76 | 74.886 | 0.14292 | 75.1718 | 74.6002 | -0.88163 | FALSE | none | -0.41183 | -0.15983 | -0.54786 | -0.21425 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.25695 | -1.0897 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-03 17:00 | 74.76 | 74.872 | 0.14073 | 75.1535 | 74.5905 | -0.79582 | FALSE | none | -0.39347 | -0.16947 | -0.52356 | -0.2272 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.24837 | 0.056367 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-03 17:15 | 75.04 | 74.886 | 0.14292 | 75.1718 | 74.6002 | 1.0775 | FALSE | none | -0.13183 | -0.43983 | -0.17538 | -0.58959 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.24837 | 1.071 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Day
2025-08-03 17:30 | 74.76 | 74.872 | 0.14073 | 75.1535 | 74.5905 | -0.79582 | FALSE | none | -0.39347 | -0.16947 | -0.52356 | -0.2272 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.24837 | -1.071 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-03 17:45 | 74.76 | 74.872 | 0.14073 | 75.1535 | 74.5905 | -0.79582 | FALSE | none | -0.39347 | -0.16947 | -0.52356 | -0.2272 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.24035 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-03 18:00 | 75.04 | 74.872 | 0.14073 | 75.1535 | 74.5905 | 1.1937 | FALSE | none | -0.11347 | -0.44947 | -0.15098 | -0.60258 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.24035 | 1.165 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0796 | Day
2025-08-03 18:15 | 74.76 | 74.872 | 0.14073 | 75.1535 | 74.5905 | -0.79582 | FALSE | none | -0.39347 | -0.16947 | -0.52356 | -0.2272 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.24035 | -1.165 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-03 18:30 | 75.04 | 74.886 | 0.14292 | 75.1718 | 74.6002 | 1.0775 | FALSE | none | -0.13183 | -0.43983 | -0.17538 | -0.58959 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.24837 | 1.071 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Day
2025-08-03 18:45 | 74.76 | 74.872 | 0.14073 | 75.1535 | 74.5905 | -0.79582 | FALSE | none | -0.39347 | -0.16947 | -0.52356 | -0.2272 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.24837 | -1.071 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-03 19:00 | 75.04 | 74.886 | 0.14292 | 75.1718 | 74.6002 | 1.0775 | FALSE | none | -0.13183 | -0.43983 | -0.17538 | -0.58959 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.24837 | 1.071 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Night
2025-08-03 19:15 | 75.32 | 74.9 | 0.16995 | 75.2399 | 74.5601 | 2.4713 | TRUE | upper | 0.080093 | -0.75991 | 0.10645 | -1.0192 | Extreme triggered | 1 | 2025-08-03 19:15 | 2025-08-03 23:45 | 2.4713 | 0.28 | 0.28 | 0.014 | 0.24837 | 1.071 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.2219 | Night
2025-08-03 19:30 | 75.6 | 74.942 | 0.22756 | 75.3971 | 74.4869 | 2.8915 | TRUE | upper | 0.20287 | -1.1131 | 0.26907 | -1.4944 | Extreme/elevated | 2 | 2025-08-03 19:15 |  | 2.6814 | 0.28 | 0.28 | 0.042 | 0.24503 | 0.97132 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.3071 | Night
2025-08-03 19:45 | 76.16 | 75.012 | 0.35066 | 75.7133 | 74.3107 | 3.2738 | TRUE | upper | 0.44667 | -1.8493 | 0.58996 | -2.4886 | Persistent | 3 | 2025-08-03 19:15 |  | 2.8789 | 0.56 | 0.56 | 0.07 | 0.27063 | 1.8106 | FALSE | 0 | FALSE | TRUE | FALSE | FALSE | 0.3897 | Night
2025-08-03 20:00 | 76.16 | 75.068 | 0.43472 | 75.9374 | 74.1986 | 2.5119 | TRUE | upper | 0.22255 | -1.9614 | 0.29307 | -2.6435 | Persistent | 4 | 2025-08-03 19:15 |  | 2.7871 | 0 | 0 | 0.056 | 0.26641 | -0.2102 | FALSE | 0 | FALSE | TRUE | FALSE | FALSE | 0.396 | Night
2025-08-03 20:15 | 77.56 | 75.208 | 0.70015 | 76.6083 | 73.8077 | 3.3593 | TRUE | upper | 0.95171 | -3.7523 | 1.2423 | -5.0839 | Persistent | 5 | 2025-08-03 19:15 |  | 2.9016 | 1.4 | 1.4 | 0.14 | 0.39073 | 3.2247 | TRUE | 1 | FALSE | TRUE | FALSE | FALSE | 0.5382 | Night
2025-08-03 20:30 | 77.28 | 75.32 | 0.83754 | 76.9951 | 73.6449 | 2.3402 | TRUE | upper | 0.28492 | -3.6351 | 0.37005 | -4.936 | Persistent | 6 | 2025-08-03 19:15 |  | 2.808 | -0.28 | -0.28 | 0.112 | 0.40013 | -0.97969 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.5274 | Night
2025-08-03 20:45 | 77.84 | 75.474 | 0.99711 | 77.4682 | 73.4798 | 2.3728 | TRUE | upper | 0.37177 | -4.3602 | 0.4799 | -5.9339 | Confirmed/Materialized Shift | 7 | 2025-08-03 19:15 |  | 2.7458 | 0.56 | 0.56 | 0.154 | 0.4009 | 1.0127 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5868 | Night
2025-08-03 21:00 | 78.4 | 75.656 | 1.1761 | 78.0081 | 73.3039 | 2.3332 | TRUE | upper | 0.39186 | -5.0961 | 0.50233 | -6.9521 | Confirmed/Materialized Shift | 8 | 2025-08-03 19:15 |  | 2.6943 | 0.56 | 0.56 | 0.182 | 0.40905 | 0.92409 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5841 | Night
2025-08-03 21:15 | 78.68 | 75.838 | 1.3452 | 78.5284 | 73.1476 | 2.1127 | TRUE | upper | 0.15158 | -5.5324 | 0.19302 | -7.5634 | Confirmed/Materialized Shift | 9 | 2025-08-03 19:15 |  | 2.6296 | 0.28 | 0.28 | 0.182 | 0.40905 | 0.23958 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5694 | Night
2025-08-03 21:30 | 78.96 | 76.034 | 1.4995 | 79.0331 | 73.0349 | 1.9513 | FALSE | none | -0.07309 | -5.9251 | -0.092481 | -8.1127 | Confirmed/Materialized Shift | 10 | 2025-08-03 19:15 |  | 2.5618 | 0.28 | 0.28 | 0.196 | 0.40728 | 0.20625 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5587 | Night
2025-08-03 21:45 | 79.8 | 76.286 | 1.6861 | 79.6581 | 72.9139 | 2.0841 | TRUE | upper | 0.14186 | -6.8861 | 0.17809 | -9.4442 | Confirmed/Materialized Shift | 11 | 2025-08-03 19:15 |  | 2.5184 | 0.84 | 0.84 | 0.252 | 0.41531 | 1.4158 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5675 | Night
2025-08-03 22:00 | 80.08 | 76.552 | 1.8448 | 80.2417 | 72.8623 | 1.9124 | FALSE | none | -0.16165 | -7.2177 | -0.20146 | -9.9059 | Confirmed/Materialized Shift | 12 | 2025-08-03 19:15 |  | 2.4679 | 0.28 | 0.28 | 0.266 | 0.41106 | 0.034058 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5561 | Night
2025-08-03 22:15 | 79.8 | 76.79 | 1.9439 | 80.6778 | 72.9022 | 1.5484 | FALSE | none | -0.87776 | -6.8978 | -1.088 | -9.4617 | Confirmed/Materialized Shift | 13 | 2025-08-03 19:15 |  | 2.3971 | -0.28 | -0.28 | 0.238 | 0.42875 | -1.2082 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5318 | Night
2025-08-03 22:30 | 80.08 | 77.056 | 2.0142 | 81.0844 | 73.0276 | 1.5013 | FALSE | none | -1.0044 | -7.0524 | -1.2387 | -9.6572 | Confirmed/Materialized Shift | 14 | 2025-08-03 19:15 |  | 2.3332 | 0.28 | 0.28 | 0.266 | 0.41106 | 0.034058 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5287 | Night
2025-08-03 22:45 | 80.08 | 77.322 | 2.0461 | 81.4141 | 73.2299 | 1.348 | FALSE | none | -1.3341 | -6.8501 | -1.6387 | -9.3543 | Confirmed/Materialized Shift | 15 | 2025-08-03 19:15 |  | 2.2675 | 0 | 0 | 0.266 | 0.41106 | -0.6471 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4899 | Night
2025-08-03 23:00 | 79.8 | 77.56 | 2.0435 | 81.647 | 73.473 | 1.0962 | FALSE | none | -1.847 | -6.327 | -2.2621 | -8.6113 | Confirmed/Materialized Shift | 16 | 2025-08-03 19:15 |  | 2.1943 | -0.28 | -0.28 | 0.238 | 0.42875 | -1.2082 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4731 | Night
2025-08-03 23:15 | 80.08 | 77.826 | 2.0057 | 81.8375 | 73.8145 | 1.1238 | FALSE | none | -1.7575 | -6.2655 | -2.1475 | -8.4881 | Confirmed/Materialized Shift | 17 | 2025-08-03 19:15 |  | 2.1313 | 0.28 | 0.28 | 0.266 | 0.41106 | 0.034058 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4749 | Night
2025-08-03 23:30 | 80.08 | 78.078 | 1.9532 | 81.9844 | 74.1716 | 1.025 | FALSE | none | -1.9044 | -5.9084 | -2.3229 | -7.9658 | Confirmed/Materialized Shift | 18 | 2025-08-03 19:15 |  | 2.0698 | 0 | 0 | 0.252 | 0.41531 | -0.60678 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4683 | Night
2025-08-03 23:45 | 79.8 | 78.33 | 1.8234 | 81.9768 | 74.6832 | 0.80619 | FALSE | none | -2.1768 | -5.1168 | -2.6554 | -6.8513 | Persistence ends | 0 |  |  |  | -0.28 | -0.28 | 0.252 | 0.41531 | -1.281 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0537 | Night
2025-08-04 | 79.8 | 78.568 | 1.6761 | 81.9201 | 75.2159 | 0.73505 | FALSE | none | -2.1201 | -4.5841 | -2.588 | -6.0946 | Normal | 0 |  |  |  | 0 | 0 | 0.238 | 0.41902 | -0.568 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.049 | Night
2025-08-04 00:15 | 80.08 | 78.806 | 1.5214 | 81.8488 | 75.7632 | 0.83739 | FALSE | none | -1.7688 | -4.3168 | -2.1611 | -5.6978 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.238 | 0.41902 | 0.10023 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0558 | Night
2025-08-04 00:30 | 79.8 | 79.016 | 1.3339 | 81.6838 | 76.3482 | 0.58775 | FALSE | none | -1.8838 | -3.4518 | -2.3062 | -4.5211 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.21 | 0.43449 | -1.1278 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0392 | Night
2025-08-04 00:45 | 80.08 | 79.212 | 1.1701 | 81.5522 | 76.8718 | 0.74182 | FALSE | none | -1.4722 | -3.2082 | -1.8052 | -4.1734 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.196 | 0.42706 | 0.19669 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0495 | Night
2025-08-04 01:00 | 80.08 | 79.408 | 0.93706 | 81.2821 | 77.5339 | 0.71714 | FALSE | none | -1.2021 | -2.5461 | -1.4789 | -3.2839 | Normal | 0 |  |  |  | 0 | 0 | 0.196 | 0.42706 | -0.45895 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0478 | Night
2025-08-04 01:15 | 80.08 | 79.534 | 0.83988 | 81.2138 | 77.8542 | 0.6501 | FALSE | none | -1.1338 | -2.2258 | -1.396 | -2.8589 | Normal | 0 |  |  |  | 0 | 0 | 0.126 | 0.32086 | -0.39269 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0433 | Night
2025-08-04 01:30 | 80.08 | 79.674 | 0.65807 | 80.9901 | 78.3579 | 0.61696 | FALSE | none | -0.91014 | -1.7221 | -1.1238 | -2.1978 | Normal | 0 |  |  |  | 0 | 0 | 0.14 | 0.30807 | -0.45445 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0411 | Night
2025-08-04 01:45 | 80.08 | 79.786 | 0.5015 | 80.789 | 78.783 | 0.58625 | FALSE | none | -0.70899 | -1.297 | -0.87759 | -1.6463 | Normal | 0 |  |  |  | 0 | 0 | 0.112 | 0.29296 | -0.3823 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0391 | Night
2025-08-04 02:00 | 79.8 | 79.856 | 0.38111 | 80.6182 | 79.0938 | -0.14694 | FALSE | none | -0.81822 | -0.70622 | -1.0149 | -0.89289 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.07 | 0.28547 | -1.226 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0098 | Night
2025-08-04 02:15 | 80.08 | 79.926 | 0.26446 | 80.4549 | 79.3971 | 0.58231 | FALSE | none | -0.37493 | -0.68293 | -0.46601 | -0.86014 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.07 | 0.28547 | 0.73562 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0388 | Night
2025-08-04 02:30 | 80.36 | 79.996 | 0.15995 | 80.3159 | 79.6761 | 2.2757 | TRUE | upper | 0.044105 | -0.68389 | 0.054915 | -0.85834 | Extreme triggered | 1 | 2025-08-04 02:30 | 2025-08-04 02:45 | 2.2757 | 0.28 | 0.28 | 0.07 | 0.28547 | 0.73562 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.2089 | Night
2025-08-04 02:45 | 80.08 | 80.01 | 0.15403 | 80.3181 | 79.7019 | 0.45445 | FALSE | none | -0.23807 | -0.37807 | -0.29641 | -0.47435 | Persistence ends | 0 |  |  |  | -0.28 | -0.28 | 0.014 | 0.23116 | -1.2718 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0303 | Night
2025-08-04 03:00 | 79.8 | 79.996 | 0.15995 | 80.3159 | 79.6761 | -1.2254 | FALSE | none | -0.51589 | -0.12389 | -0.64233 | -0.1555 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.23116 | -1.1507 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0817 | Night
2025-08-04 03:15 | 80.08 | 80.01 | 0.15403 | 80.3181 | 79.7019 | 0.45445 | FALSE | none | -0.23807 | -0.37807 | -0.29641 | -0.47435 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.23116 | 1.1507 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0303 | Night
2025-08-04 03:30 | 79.8 | 79.996 | 0.15995 | 80.3159 | 79.6761 | -1.2254 | FALSE | none | -0.51589 | -0.12389 | -0.64233 | -0.1555 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.23116 | -1.1507 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0817 | Night
2025-08-04 03:45 | 79.8 | 79.982 | 0.1644 | 80.3108 | 79.6532 | -1.1071 | FALSE | none | -0.5108 | -0.1468 | -0.63603 | -0.1843 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.23116 | 0.060564 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0738 | Night
2025-08-04 04:00 | 80.08 | 79.996 | 0.15995 | 80.3159 | 79.6761 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.29371 | -0.50692 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.23116 | 1.1507 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.035 | Night
2025-08-04 04:15 | 80.08 | 79.996 | 0.15995 | 80.3159 | 79.6761 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.29371 | -0.50692 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.22252 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.035 | Night
2025-08-04 04:30 | 80.08 | 79.996 | 0.15995 | 80.3159 | 79.6761 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.29371 | -0.50692 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.22252 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.035 | Night
2025-08-04 04:45 | 80.08 | 80.01 | 0.15403 | 80.3181 | 79.7019 | 0.45445 | FALSE | none | -0.23807 | -0.37807 | -0.29641 | -0.47435 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.21256 | -0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0303 | Night
2025-08-04 05:00 | 80.08 | 80.024 | 0.14648 | 80.317 | 79.731 | 0.3823 | FALSE | none | -0.23696 | -0.34896 | -0.29503 | -0.43768 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.21256 | -0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0255 | Night
2025-08-04 05:15 | 80.08 | 80.024 | 0.14648 | 80.317 | 79.731 | 0.3823 | FALSE | none | -0.23696 | -0.34896 | -0.29503 | -0.43768 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.20313 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0255 | Night
2025-08-04 05:30 | 80.08 | 80.038 | 0.13702 | 80.312 | 79.764 | 0.30652 | FALSE | none | -0.23204 | -0.31604 | -0.28893 | -0.39622 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.19217 | -0.072851 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0204 | Night
2025-08-04 05:45 | 80.08 | 80.038 | 0.13702 | 80.312 | 79.764 | 0.30652 | FALSE | none | -0.23204 | -0.31604 | -0.28893 | -0.39622 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.18169 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0204 | Night
2025-08-04 06:00 | 79.8 | 80.024 | 0.14648 | 80.317 | 79.731 | -1.5292 | FALSE | none | -0.51696 | -0.068963 | -0.64365 | -0.086495 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.19217 | -1.3842 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1019 | Night
2025-08-04 06:15 | 79.8 | 80.01 | 0.15403 | 80.3181 | 79.7019 | -1.3633 | FALSE | none | -0.51807 | -0.098067 | -0.64502 | -0.12304 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.19217 | 0.072851 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0909 | Night
2025-08-04 06:30 | 80.08 | 80.01 | 0.15403 | 80.3181 | 79.7019 | 0.45445 | FALSE | none | -0.23807 | -0.37807 | -0.29641 | -0.47435 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.20313 | 1.3784 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0303 | Night
2025-08-04 06:45 | 80.08 | 80.01 | 0.15403 | 80.3181 | 79.7019 | 0.45445 | FALSE | none | -0.23807 | -0.37807 | -0.29641 | -0.47435 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.20313 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0303 | Night
2025-08-04 07:00 | 79.8 | 80.01 | 0.15403 | 80.3181 | 79.7019 | -1.3633 | FALSE | none | -0.51807 | -0.098067 | -0.64502 | -0.12304 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.20313 | -1.3784 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0909 | Day
2025-08-04 07:15 | 80.08 | 80.01 | 0.15403 | 80.3181 | 79.7019 | 0.45445 | FALSE | none | -0.23807 | -0.37807 | -0.29641 | -0.47435 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.20313 | 1.3784 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0303 | Day
2025-08-04 07:30 | 79.8 | 79.982 | 0.13702 | 80.256 | 79.708 | -1.3283 | FALSE | none | -0.45604 | -0.092042 | -0.56823 | -0.11547 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.028 | 0.20109 | -1.2532 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0886 | Day
2025-08-04 07:45 | 80.08 | 79.982 | 0.13702 | 80.256 | 79.708 | 0.71522 | FALSE | none | -0.17604 | -0.37204 | -0.21935 | -0.46676 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.20313 | 1.3784 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0477 | Day
2025-08-04 08:00 | 80.08 | 79.996 | 0.13165 | 80.2593 | 79.7327 | 0.63808 | FALSE | none | -0.17929 | -0.34729 | -0.22339 | -0.43557 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.19217 | -0.072851 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0425 | Day
2025-08-04 08:15 | 79.24 | 79.954 | 0.21256 | 80.3791 | 79.5289 | -3.359 | TRUE | lower | -1.1391 | 0.28887 | -1.4172 | 0.36323 | Extreme triggered | 1 | 2025-08-04 08:15 | 2025-08-04 12:00 | 3.359 | -0.84 | -0.84 | -0.042 | 0.26132 | -3.0537 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.3096 | Day
2025-08-04 08:30 | 78.68 | 79.898 | 0.35505 | 80.6081 | 79.1879 | -3.4305 | TRUE | lower | -1.9281 | 0.5079 | -2.3919 | 0.64139 | Extreme/elevated | 2 | 2025-08-04 08:15 |  | 3.3948 | -0.56 | -0.56 | -0.056 | 0.28147 | -1.7906 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.3716 | Day
2025-08-04 08:45 | 78.12 | 79.814 | 0.53339 | 80.8808 | 78.7472 | -3.1759 | TRUE | lower | -2.7608 | 0.62721 | -3.4134 | 0.79649 | Persistent | 3 | 2025-08-04 08:15 |  | 3.3218 | -0.56 | -0.56 | -0.084 | 0.30266 | -1.5727 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4117 | Day
2025-08-04 09:00 | 77.28 | 79.674 | 0.77338 | 81.2208 | 78.1272 | -3.0955 | TRUE | lower | -3.9408 | 0.84725 | -4.8519 | 1.0844 | Persistent | 4 | 2025-08-04 08:15 |  | 3.2652 | -0.84 | -0.84 | -0.14 | 0.33378 | -2.0972 | TRUE | 2 | TRUE | TRUE | FALSE | TRUE | 0.4921 | Day
2025-08-04 09:15 | 76.72 | 79.506 | 1.0095 | 81.5249 | 77.4871 | -2.7599 | TRUE | lower | -4.8049 | 0.7671 | -5.8938 | 0.98997 | Persistent | 5 | 2025-08-04 08:15 |  | 3.1642 | -0.56 | -0.56 | -0.168 | 0.34473 | -1.1371 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.5269 | Day
2025-08-04 09:30 | 76.16 | 79.31 | 1.2452 | 81.8004 | 76.8196 | -2.5298 | TRUE | lower | -5.6404 | 0.65965 | -6.8953 | 0.8587 | Persistent | 6 | 2025-08-04 08:15 |  | 3.0584 | -0.56 | -0.56 | -0.196 | 0.35301 | -1.0311 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.5687 | Day
2025-08-04 09:45 | 75.6 | 79.086 | 1.4802 | 82.0463 | 76.1257 | -2.3552 | TRUE | lower | -6.4463 | 0.52568 | -7.8569 | 0.69055 | Confirmed/Materialized Shift | 7 | 2025-08-04 08:15 |  | 2.958 | -0.56 | -0.56 | -0.224 | 0.35881 | -0.93644 | FALSE | 2 | FALSE | TRUE | TRUE | FALSE | 0.6142 | Day
2025-08-04 10:00 | 74.76 | 78.82 | 1.7462 | 82.3125 | 75.3275 | -2.325 | TRUE | lower | -7.5525 | 0.56752 | -9.1754 | 0.75341 | Confirmed/Materialized Shift | 8 | 2025-08-04 08:15 |  | 2.8788 | -0.84 | -0.84 | -0.266 | 0.37976 | -1.5115 | FALSE | 2 | FALSE | TRUE | TRUE | FALSE | 0.6121 | Day
2025-08-04 10:15 | 75.04 | 78.568 | 1.9107 | 82.3895 | 74.7465 | -1.8464 | FALSE | none | -7.3495 | -0.2935 | -8.9204 | -0.39266 | Confirmed/Materialized Shift | 9 | 2025-08-04 08:15 |  | 2.7641 | 0.28 | 0.28 | -0.252 | 0.39494 | 1.3471 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5802 | Day
2025-08-04 10:30 | 75.04 | 78.316 | 2.0295 | 82.375 | 74.257 | -1.6142 | FALSE | none | -7.335 | -0.78301 | -8.9044 | -1.0545 | Confirmed/Materialized Shift | 10 | 2025-08-04 08:15 |  | 2.6491 | 0 | 0 | -0.252 | 0.39494 | 0.63808 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5648 | Day
2025-08-04 10:45 | 75.04 | 78.064 | 2.1102 | 82.2845 | 73.8435 | -1.433 | FALSE | none | -7.2445 | -1.1965 | -8.8042 | -1.6203 | Confirmed/Materialized Shift | 11 | 2025-08-04 08:15 |  | 2.5386 | 0 | 0 | -0.252 | 0.39494 | 0.63808 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5241 | Day
2025-08-04 11:00 | 75.04 | 77.826 | 2.1717 | 82.1694 | 73.4826 | -1.2829 | FALSE | none | -7.1294 | -1.5574 | -8.6764 | -2.1193 | Confirmed/Materialized Shift | 12 | 2025-08-04 08:15 |  | 2.4339 | 0 | 0 | -0.238 | 0.39884 | 0.59674 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5141 | Day
2025-08-04 11:15 | 74.76 | 77.574 | 2.2224 | 82.0188 | 73.1292 | -1.2662 | FALSE | none | -7.2588 | -1.6308 | -8.8501 | -2.23 | Confirmed/Materialized Shift | 13 | 2025-08-04 08:15 |  | 2.3441 | -0.28 | -0.28 | -0.252 | 0.39494 | -0.070897 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.513 | Day
2025-08-04 11:30 | 75.04 | 77.322 | 2.209 | 81.74 | 72.904 | -1.0331 | FALSE | none | -6.7 | -2.136 | -8.1967 | -2.9298 | Confirmed/Materialized Shift | 14 | 2025-08-04 08:15 |  | 2.2505 | 0.28 | 0.28 | -0.252 | 0.39494 | 1.3471 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4689 | Day
2025-08-04 11:45 | 74.76 | 77.056 | 2.1795 | 81.415 | 72.697 | -1.0535 | FALSE | none | -6.655 | -2.063 | -8.1742 | -2.8378 | Confirmed/Materialized Shift | 15 | 2025-08-04 08:15 |  | 2.1707 | -0.28 | -0.28 | -0.266 | 0.39047 | -0.035854 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4702 | Day
2025-08-04 12:00 | 75.04 | 76.818 | 2.1233 | 81.0645 | 72.5715 | -0.83739 | FALSE | none | -6.0245 | -2.4685 | -7.4317 | -3.4015 | Persistence ends | 0 |  |  |  | 0.28 | 0.28 | -0.238 | 0.40905 | 1.2663 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0558 | Day
2025-08-04 12:15 | 75.04 | 76.566 | 2.0119 | 80.5898 | 72.5422 | -0.75849 | FALSE | none | -5.5498 | -2.4978 | -6.8865 | -3.4432 | Normal | 0 |  |  |  | 0 | 0 | -0.252 | 0.39494 | 0.63808 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0506 | Day
2025-08-04 12:30 | 74.48 | 76.3 | 1.911 | 80.1219 | 72.4781 | -0.9524 | FALSE | none | -5.6419 | -2.0019 | -7.0417 | -2.7621 | Normal | 0 |  |  |  | -0.56 | -0.56 | -0.266 | 0.4009 | -0.73335 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0635 | Day
2025-08-04 12:45 | 75.04 | 76.048 | 1.7078 | 79.4635 | 72.6325 | -0.59024 | FALSE | none | -4.4235 | -2.4075 | -5.5668 | -3.3147 | Normal | 0 |  |  |  | 0.56 | 0.56 | -0.252 | 0.42513 | 1.91 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0393 | Day
2025-08-04 13:00 | 74.76 | 75.782 | 1.44 | 78.6621 | 72.9019 | -0.70971 | FALSE | none | -3.9021 | -1.8581 | -4.9605 | -2.5487 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.266 | 0.42098 | -0.033256 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0473 | Day
2025-08-04 13:15 | 75.04 | 75.572 | 1.1945 | 77.961 | 73.183 | -0.44537 | FALSE | none | -2.921 | -1.857 | -3.7468 | -2.5375 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.21 | 0.41506 | 1.1806 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0297 | Day
2025-08-04 13:30 | 74.76 | 75.376 | 0.95537 | 77.2867 | 73.4653 | -0.64477 | FALSE | none | -2.5267 | -1.2947 | -3.2693 | -1.7624 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.196 | 0.40728 | -0.20625 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.043 | Day
2025-08-04 13:45 | 74.76 | 75.208 | 0.71184 | 76.6317 | 73.7843 | -0.62936 | FALSE | none | -1.8717 | -0.97567 | -2.4424 | -1.3223 | Normal | 0 |  |  |  | 0 | 0 | -0.168 | 0.40013 | 0.41987 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.042 | Day
2025-08-04 14:00 | 75.04 | 75.096 | 0.51869 | 76.1334 | 74.0586 | -0.10797 | FALSE | none | -1.0934 | -0.98137 | -1.4361 | -1.3251 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.112 | 0.37894 | 1.0345 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0072 | Day
2025-08-04 14:15 | 75.04 | 75.012 | 0.35066 | 75.7133 | 74.3107 | 0.079849 | FALSE | none | -0.67333 | -0.72933 | -0.88931 | -0.98145 | Normal | 0 |  |  |  | 0 | 0 | -0.084 | 0.36451 | 0.23045 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0053 | Day
2025-08-04 14:30 | 75.04 | 74.956 | 0.22437 | 75.4047 | 74.5073 | 0.37438 | FALSE | none | -0.36474 | -0.53274 | -0.4837 | -0.71501 | Normal | 0 |  |  |  | 0 | 0 | -0.056 | 0.34711 | 0.16133 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.025 | Day
2025-08-04 14:45 | 74.76 | 74.914 | 0.16935 | 75.2527 | 74.5753 | -0.90938 | FALSE | none | -0.49269 | -0.18469 | -0.65472 | -0.24766 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.042 | 0.33099 | -0.71906 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0606 | Day
2025-08-04 15:00 | 74.76 | 74.914 | 0.16935 | 75.2527 | 74.5753 | -0.90938 | FALSE | none | -0.49269 | -0.18469 | -0.65472 | -0.24766 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.27253 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0606 | Day
2025-08-04 15:15 | 75.04 | 74.914 | 0.16935 | 75.2527 | 74.5753 | 0.74404 | FALSE | none | -0.21269 | -0.46469 | -0.28264 | -0.62312 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.27253 | 1.0274 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0496 | Day
2025-08-04 15:30 | 74.76 | 74.9 | 0.16995 | 75.2399 | 74.5601 | -0.82375 | FALSE | none | -0.47991 | -0.19991 | -0.63784 | -0.26812 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.27963 | -0.95125 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0549 | Day
2025-08-04 15:45 | 74.76 | 74.886 | 0.16935 | 75.2247 | 74.5473 | -0.74404 | FALSE | none | -0.46469 | -0.21269 | -0.61774 | -0.28531 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.27963 | 0.050066 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0496 | Day
2025-08-04 16:00 | 75.04 | 74.886 | 0.16935 | 75.2247 | 74.5473 | 0.90938 | FALSE | none | -0.18469 | -0.49269 | -0.24552 | -0.66091 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.28727 | 0.97468 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0606 | Day
2025-08-04 16:15 | 75.04 | 74.9 | 0.16995 | 75.2399 | 74.5601 | 0.82375 | FALSE | none | -0.19991 | -0.47991 | -0.26569 | -0.64365 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.27963 | -0.050066 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0549 | Day
2025-08-04 16:30 | 75.04 | 74.9 | 0.16995 | 75.2399 | 74.5601 | 0.82375 | FALSE | none | -0.19991 | -0.47991 | -0.26569 | -0.64365 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.27253 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0549 | Day
2025-08-04 16:45 | 74.76 | 74.9 | 0.16995 | 75.2399 | 74.5601 | -0.82375 | FALSE | none | -0.47991 | -0.19991 | -0.63784 | -0.26812 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.27253 | -1.0274 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0549 | Day
2025-08-04 17:00 | 75.04 | 74.9 | 0.16995 | 75.2399 | 74.5601 | 0.82375 | FALSE | none | -0.19991 | -0.47991 | -0.26569 | -0.64365 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.27253 | 1.0274 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0549 | Day
2025-08-04 17:15 | 74.76 | 74.886 | 0.16935 | 75.2247 | 74.5473 | -0.74404 | FALSE | none | -0.46469 | -0.21269 | -0.61774 | -0.28531 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.27963 | -0.95125 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0496 | Day
2025-08-04 17:30 | 75.04 | 74.914 | 0.14292 | 75.1998 | 74.6282 | 0.88163 | FALSE | none | -0.15983 | -0.41183 | -0.21255 | -0.55185 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.028 | 0.25533 | 0.98694 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-04 17:45 | 74.76 | 74.9 | 0.14364 | 75.1873 | 74.6127 | -0.97468 | FALSE | none | -0.42727 | -0.14727 | -0.56828 | -0.19738 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.23116 | -1.1507 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.065 | Day
2025-08-04 18:00 | 75.04 | 74.914 | 0.14292 | 75.1998 | 74.6282 | 0.88163 | FALSE | none | -0.15983 | -0.41183 | -0.21255 | -0.55185 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.23116 | 1.1507 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-04 18:15 | 75.04 | 74.914 | 0.14292 | 75.1998 | 74.6282 | 0.88163 | FALSE | none | -0.15983 | -0.41183 | -0.21255 | -0.55185 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.22252 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-04 18:30 | 74.76 | 74.914 | 0.14292 | 75.1998 | 74.6282 | -1.0775 | FALSE | none | -0.43983 | -0.13183 | -0.58489 | -0.17665 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.22252 | -1.2583 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Day
2025-08-04 18:45 | 74.76 | 74.914 | 0.14292 | 75.1998 | 74.6282 | -1.0775 | FALSE | none | -0.43983 | -0.13183 | -0.58489 | -0.17665 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.22252 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Day
2025-08-04 19:00 | 75.04 | 74.914 | 0.14292 | 75.1998 | 74.6282 | 0.88163 | FALSE | none | -0.15983 | -0.41183 | -0.21255 | -0.55185 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.22252 | 1.2583 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Night
2025-08-04 19:15 | 75.6 | 74.942 | 0.20864 | 75.3593 | 74.5247 | 3.1537 | TRUE | upper | 0.24071 | -1.0753 | 0.31942 | -1.4429 | Extreme triggered | 1 | 2025-08-04 19:15 | 2025-08-04 23:45 | 3.1537 | 0.56 | 0.56 | 0.028 | 0.25533 | 2.0835 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.296 | Night
2025-08-04 19:30 | 75.88 | 74.984 | 0.29577 | 75.5755 | 74.3925 | 3.0294 | TRUE | upper | 0.30447 | -1.4875 | 0.40286 | -1.9996 | Extreme/elevated | 2 | 2025-08-04 19:15 |  | 3.0916 | 0.28 | 0.28 | 0.042 | 0.26132 | 0.91074 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.3448 | Night
2025-08-04 19:45 | 75.88 | 75.04 | 0.35184 | 75.7437 | 74.3363 | 2.3875 | TRUE | upper | 0.13633 | -1.5437 | 0.17998 | -2.0766 | Persistent | 3 | 2025-08-04 19:15 |  | 2.8569 | 0 | 0 | 0.056 | 0.25044 | -0.22361 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.3592 | Night
2025-08-04 20:00 | 76.72 | 75.138 | 0.50804 | 76.1541 | 74.1219 | 3.1139 | TRUE | upper | 0.56593 | -2.5981 | 0.74313 | -3.5051 | Persistent | 4 | 2025-08-04 19:15 |  | 2.9211 | 0.84 | 0.84 | 0.098 | 0.30504 | 2.4325 | TRUE | 2 | TRUE | TRUE | FALSE | TRUE | 0.4933 | Night
2025-08-04 20:15 | 77 | 75.236 | 0.65571 | 76.5474 | 73.9246 | 2.6902 | TRUE | upper | 0.45257 | -3.0754 | 0.59123 | -4.1602 | Persistent | 5 | 2025-08-04 19:15 |  | 2.8749 | 0.28 | 0.28 | 0.098 | 0.30504 | 0.59665 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.5222 | Night
2025-08-04 20:30 | 77.84 | 75.39 | 0.866 | 77.122 | 73.658 | 2.8291 | TRUE | upper | 0.718 | -4.182 | 0.93099 | -5.6776 | Persistent | 6 | 2025-08-04 19:15 |  | 2.8673 | 0.84 | 0.84 | 0.154 | 0.33347 | 2.0571 | TRUE | 3 | TRUE | TRUE | FALSE | TRUE | 0.6172 | Night
2025-08-04 20:45 | 77.56 | 75.53 | 0.97789 | 77.4858 | 73.5742 | 2.0759 | TRUE | upper | 0.074215 | -3.9858 | 0.095779 | -5.4174 | Confirmed/Materialized Shift | 7 | 2025-08-04 19:15 |  | 2.7542 | -0.28 | -0.28 | 0.14 | 0.34592 | -1.2141 | FALSE | 3 | FALSE | TRUE | TRUE | FALSE | 0.6241 | Night
2025-08-04 21:00 | 78.12 | 75.684 | 1.1277 | 77.9394 | 73.4286 | 2.1601 | TRUE | upper | 0.18058 | -4.6914 | 0.23169 | -6.3891 | Confirmed/Materialized Shift | 8 | 2025-08-04 19:15 |  | 2.68 | 0.56 | 0.56 | 0.154 | 0.35736 | 1.1361 | FALSE | 3 | FALSE | TRUE | TRUE | FALSE | 0.6297 | Night
2025-08-04 21:15 | 78.96 | 75.88 | 1.332 | 78.5441 | 73.2159 | 2.3123 | TRUE | upper | 0.41593 | -5.7441 | 0.52955 | -7.8454 | Confirmed/Materialized Shift | 9 | 2025-08-04 19:15 |  | 2.6391 | 0.84 | 0.84 | 0.196 | 0.38649 | 1.6663 | FALSE | 3 | FALSE | TRUE | TRUE | FALSE | 0.6399 | Night
2025-08-04 21:30 | 78.96 | 76.076 | 1.4819 | 79.0398 | 73.1122 | 1.9462 | FALSE | none | -0.079798 | -5.8478 | -0.10096 | -7.9984 | Confirmed/Materialized Shift | 10 | 2025-08-04 19:15 |  | 2.5698 | 0 | 0 | 0.196 | 0.38649 | -0.50713 | FALSE | 3 | FALSE | FALSE | TRUE | FALSE | 0.6155 | Night
2025-08-04 21:45 | 79.52 | 76.314 | 1.6339 | 79.5817 | 73.0463 | 1.9622 | FALSE | none | -0.061733 | -6.4737 | -0.077572 | -8.8625 | Confirmed/Materialized Shift | 11 | 2025-08-04 19:15 |  | 2.5146 | 0.56 | 0.56 | 0.238 | 0.37758 | 0.85281 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.588 | Night
2025-08-04 22:00 | 80.08 | 76.566 | 1.8066 | 80.1791 | 72.9529 | 1.9451 | FALSE | none | -0.099148 | -7.1271 | -0.12366 | -9.7695 | Confirmed/Materialized Shift | 12 | 2025-08-04 19:15 |  | 2.4671 | 0.56 | 0.56 | 0.252 | 0.38435 | 0.80136 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5868 | Night
2025-08-04 22:15 | 80.08 | 76.832 | 1.9151 | 80.6621 | 73.0019 | 1.696 | FALSE | none | -0.58213 | -7.0781 | -0.72169 | -9.6958 | Confirmed/Materialized Shift | 13 | 2025-08-04 19:15 |  | 2.4078 | 0 | 0 | 0.266 | 0.36873 | -0.72139 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5702 | Night
2025-08-04 22:30 | 79.8 | 77.07 | 1.9755 | 81.0209 | 73.1191 | 1.382 | FALSE | none | -1.2209 | -6.6809 | -1.5069 | -9.1371 | Confirmed/Materialized Shift | 14 | 2025-08-04 19:15 |  | 2.3345 | -0.28 | -0.28 | 0.238 | 0.38835 | -1.3338 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5207 | Night
2025-08-04 22:45 | 80.08 | 77.336 | 2.006 | 81.348 | 73.324 | 1.3679 | FALSE | none | -1.268 | -6.756 | -1.5587 | -9.2139 | Confirmed/Materialized Shift | 15 | 2025-08-04 19:15 |  | 2.2701 | 0.28 | 0.28 | 0.266 | 0.36873 | 0.037968 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5198 | Night
2025-08-04 23:00 | 80.08 | 77.588 | 2.0189 | 81.6258 | 73.5502 | 1.2343 | FALSE | none | -1.5458 | -6.5298 | -1.8938 | -8.878 | Confirmed/Materialized Shift | 16 | 2025-08-04 19:15 |  | 2.2054 | 0 | 0 | 0.252 | 0.37346 | -0.67478 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4823 | Night
2025-08-04 23:15 | 80.36 | 77.854 | 2.016 | 81.886 | 73.822 | 1.2431 | FALSE | none | -1.526 | -6.538 | -1.8635 | -8.8564 | Confirmed/Materialized Shift | 17 | 2025-08-04 19:15 |  | 2.1488 | 0.28 | 0.28 | 0.266 | 0.36873 | 0.037968 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4829 | Night
2025-08-04 23:30 | 80.08 | 78.12 | 1.9356 | 81.9913 | 74.2487 | 1.0126 | FALSE | none | -1.9113 | -5.8313 | -2.3311 | -7.8537 | Confirmed/Materialized Shift | 18 | 2025-08-04 19:15 |  | 2.0856 | -0.28 | -0.28 | 0.266 | 0.36873 | -1.4808 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4675 | Night
2025-08-04 23:45 | 80.08 | 78.386 | 1.8111 | 82.0083 | 74.7637 | 0.93532 | FALSE | none | -1.9283 | -5.3163 | -2.3513 | -7.1108 | Persistence ends | 0 |  |  |  | 0 | 0 | 0.266 | 0.36873 | -0.72139 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0624 | Night
2025-08-05 | 79.8 | 78.624 | 1.6543 | 81.9325 | 75.3155 | 0.71089 | FALSE | none | -2.1325 | -4.4845 | -2.6028 | -5.9543 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.238 | 0.38835 | -1.3338 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0474 | Night
2025-08-05 00:15 | 80.08 | 78.848 | 1.5212 | 81.8904 | 75.8056 | 0.80989 | FALSE | none | -1.8104 | -4.2744 | -2.2108 | -5.6386 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.224 | 0.38111 | 0.14694 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.054 | Night
2025-08-05 00:30 | 80.08 | 79.058 | 1.3725 | 81.8031 | 76.3129 | 0.7446 | FALSE | none | -1.7231 | -3.7671 | -2.1064 | -4.9364 | Normal | 0 |  |  |  | 0 | 0 | 0.21 | 0.38408 | -0.54676 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0496 | Night
2025-08-05 00:45 | 80.08 | 79.268 | 1.1666 | 81.6011 | 76.9349 | 0.69606 | FALSE | none | -1.5211 | -3.1451 | -1.8641 | -4.088 | Normal | 0 |  |  |  | 0 | 0 | 0.21 | 0.38408 | -0.54676 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0464 | Night
2025-08-05 01:00 | 80.08 | 79.436 | 1.012 | 81.46 | 77.412 | 0.63636 | FALSE | none | -1.38 | -2.668 | -1.6941 | -3.4465 | Normal | 0 |  |  |  | 0 | 0 | 0.168 | 0.3565 | -0.47125 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0424 | Night
2025-08-05 01:15 | 79.8 | 79.576 | 0.83557 | 81.2471 | 77.9049 | 0.26808 | FALSE | none | -1.4471 | -1.8951 | -1.7812 | -2.4326 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.14 | 0.36901 | -1.1382 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0179 | Night
2025-08-05 01:30 | 80.08 | 79.688 | 0.73466 | 81.1573 | 78.2187 | 0.53358 | FALSE | none | -1.0773 | -1.8613 | -1.3274 | -2.3796 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.112 | 0.33254 | 0.5052 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0356 | Night
2025-08-05 01:45 | 80.08 | 79.814 | 0.54107 | 80.8961 | 78.7319 | 0.49161 | FALSE | none | -0.81615 | -1.3481 | -1.0089 | -1.7123 | Normal | 0 |  |  |  | 0 | 0 | 0.126 | 0.32086 | -0.39269 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0328 | Night
2025-08-05 02:00 | 80.08 | 79.912 | 0.36789 | 80.6478 | 79.1762 | 0.45666 | FALSE | none | -0.56778 | -0.90378 | -0.70402 | -1.1415 | Normal | 0 |  |  |  | 0 | 0 | 0.098 | 0.30504 | -0.32127 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0304 | Night
2025-08-05 02:15 | 80.08 | 79.968 | 0.29296 | 80.5539 | 79.3821 | 0.3823 | FALSE | none | -0.47393 | -0.69793 | -0.58833 | -0.8792 | Normal | 0 |  |  |  | 0 | 0 | 0.056 | 0.25044 | -0.22361 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0255 | Night
2025-08-05 02:30 | 80.08 | 80.024 | 0.17236 | 80.3687 | 79.6793 | 0.32489 | FALSE | none | -0.28873 | -0.40073 | -0.35926 | -0.50293 | Normal | 0 |  |  |  | 0 | 0 | 0.056 | 0.25044 | -0.22361 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0217 | Night
2025-08-05 02:45 | 79.8 | 80.038 | 0.13702 | 80.312 | 79.764 | -1.737 | FALSE | none | -0.51204 | -0.036042 | -0.63757 | -0.045186 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.014 | 0.23116 | -1.2718 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1158 | Night
2025-08-05 03:00 | 80.08 | 80.038 | 0.13702 | 80.312 | 79.764 | 0.30652 | FALSE | none | -0.23204 | -0.31604 | -0.28893 | -0.39622 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.20313 | 1.3784 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0204 | Night
2025-08-05 03:15 | 80.08 | 80.038 | 0.13702 | 80.312 | 79.764 | 0.30652 | FALSE | none | -0.23204 | -0.31604 | -0.28893 | -0.39622 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.20313 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0204 | Night
2025-08-05 03:30 | 79.8 | 80.038 | 0.13702 | 80.312 | 79.764 | -1.737 | FALSE | none | -0.51204 | -0.036042 | -0.63757 | -0.045186 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.20313 | -1.3784 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1158 | Night
2025-08-05 03:45 | 80.08 | 80.038 | 0.13702 | 80.312 | 79.764 | 0.30652 | FALSE | none | -0.23204 | -0.31604 | -0.28893 | -0.39622 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.20313 | 1.3784 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0204 | Night
2025-08-05 04:00 | 79.8 | 80.024 | 0.14648 | 80.317 | 79.731 | -1.5292 | FALSE | none | -0.51696 | -0.068963 | -0.64365 | -0.086495 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.21256 | -1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1019 | Night
2025-08-05 04:15 | 79.8 | 79.996 | 0.13165 | 80.2593 | 79.7327 | -1.4888 | FALSE | none | -0.45929 | -0.067291 | -0.57226 | -0.084396 | Normal | 0 |  |  |  | 0 | 0 | -0.028 | 0.20109 | 0.13924 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0993 | Night
2025-08-05 04:30 | 79.8 | 79.982 | 0.13702 | 80.256 | 79.708 | -1.3283 | FALSE | none | -0.45604 | -0.092042 | -0.56823 | -0.11547 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.19217 | 0.072851 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0886 | Night
2025-08-05 04:45 | 80.36 | 79.996 | 0.15995 | 80.3159 | 79.6761 | 2.2757 | TRUE | upper | 0.044105 | -0.68389 | 0.054915 | -0.85834 | Extreme triggered | 1 | 2025-08-05 04:45 | 2025-08-05 05:15 | 2.2757 | 0.56 | 0.56 | 0.014 | 0.23116 | 2.362 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.2374 | Night
2025-08-05 05:00 | 79.8 | 79.996 | 0.15995 | 80.3159 | 79.6761 | -1.2254 | FALSE | none | -0.51589 | -0.12389 | -0.64233 | -0.1555 | Extreme/elevated | 2 | 2025-08-05 04:45 |  | 1.7506 | -0.56 | -0.56 | 0 | 0.25695 | -2.1794 | TRUE | 2 | TRUE | FALSE | FALSE | TRUE | 0.2531 | Night
2025-08-05 05:15 | 80.08 | 79.996 | 0.15995 | 80.3159 | 79.6761 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.29371 | -0.50692 | Persistence ends | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.25695 | 1.0897 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.0922 | Night
2025-08-05 05:30 | 80.08 | 79.996 | 0.15995 | 80.3159 | 79.6761 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.29371 | -0.50692 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.25695 | 0 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.0922 | Night
2025-08-05 05:45 | 80.08 | 79.996 | 0.15995 | 80.3159 | 79.6761 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.29371 | -0.50692 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.25695 | 0 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.0922 | Night
2025-08-05 06:00 | 80.08 | 79.996 | 0.15995 | 80.3159 | 79.6761 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.29371 | -0.50692 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.25695 | 0 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.0922 | Night
2025-08-05 06:15 | 79.8 | 79.996 | 0.15995 | 80.3159 | 79.6761 | -1.2254 | FALSE | none | -0.51589 | -0.12389 | -0.64233 | -0.1555 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.25695 | -1.0897 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.1388 | Night
2025-08-05 06:30 | 79.52 | 79.968 | 0.19056 | 80.3491 | 79.5869 | -2.351 | TRUE | lower | -0.82911 | 0.066888 | -1.0319 | 0.084044 | Extreme triggered | 1 | 2025-08-05 06:30 | 2025-08-05 06:45 | 2.351 | -0.28 | -0.28 | -0.028 | 0.25533 | -0.98694 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.271 | Night
2025-08-05 06:45 | 80.08 | 79.968 | 0.19056 | 80.3491 | 79.5869 | 0.58775 | FALSE | none | -0.26911 | -0.49311 | -0.33493 | -0.61959 | Persistence ends | 0 |  |  |  | 0.56 | 0.56 | 0 | 0.28727 | 1.9494 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.0963 | Night
2025-08-05 07:00 | 79.8 | 79.954 | 0.19217 | 80.3383 | 79.5697 | -0.80136 | FALSE | none | -0.53835 | -0.23035 | -0.6701 | -0.28949 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.29402 | -0.90471 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.1106 | Day
2025-08-05 07:15 | 80.08 | 79.954 | 0.19217 | 80.3383 | 79.5697 | 0.65566 | FALSE | none | -0.25835 | -0.51035 | -0.32157 | -0.64138 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.3013 | 0.92932 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0723 | Day
2025-08-05 07:30 | 79.8 | 79.94 | 0.19271 | 80.3254 | 79.5546 | -0.72648 | FALSE | none | -0.52542 | -0.24542 | -0.65411 | -0.30849 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.30773 | -0.86439 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0484 | Day
2025-08-05 07:45 | 80.08 | 79.954 | 0.19217 | 80.3383 | 79.5697 | 0.65566 | FALSE | none | -0.25835 | -0.51035 | -0.32157 | -0.64138 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.30773 | 0.86439 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0437 | Day
2025-08-05 08:00 | 80.08 | 79.954 | 0.19217 | 80.3383 | 79.5697 | 0.65566 | FALSE | none | -0.25835 | -0.51035 | -0.32157 | -0.64138 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.3013 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0437 | Day
2025-08-05 08:15 | 79.24 | 79.912 | 0.24712 | 80.4062 | 79.4178 | -2.7193 | TRUE | lower | -1.1662 | 0.17776 | -1.4504 | 0.22382 | Extreme triggered | 1 | 2025-08-05 08:15 | 2025-08-05 12:00 | 2.7193 | -0.84 | -0.84 | -0.042 | 0.35505 | -2.2476 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.267 | Day
2025-08-05 08:30 | 78.96 | 79.87 | 0.32596 | 80.5219 | 79.2181 | -2.7917 | TRUE | lower | -1.5619 | 0.25807 | -1.9398 | 0.32577 | Extreme/elevated | 2 | 2025-08-05 08:15 |  | 2.7555 | -0.28 | -0.28 | -0.042 | 0.35505 | -0.67033 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.329 | Day
2025-08-05 08:45 | 78.12 | 79.772 | 0.50498 | 80.782 | 78.762 | -3.2714 | TRUE | lower | -2.662 | 0.64204 | -3.2952 | 0.81516 | Persistent | 3 | 2025-08-05 08:15 |  | 2.9275 | -0.84 | -0.84 | -0.098 | 0.38835 | -1.9106 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4181 | Day
2025-08-05 09:00 | 77.56 | 79.66 | 0.7066 | 81.0732 | 78.2468 | -2.972 | TRUE | lower | -3.5132 | 0.6868 | -4.3334 | 0.87773 | Persistent | 4 | 2025-08-05 08:15 |  | 2.9386 | -0.56 | -0.56 | -0.112 | 0.40013 | -1.1196 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4553 | Day
2025-08-05 09:15 | 76.72 | 79.506 | 0.96344 | 81.4329 | 77.5791 | -2.8917 | TRUE | lower | -4.7129 | 0.85912 | -5.7874 | 1.1074 | Persistent | 5 | 2025-08-05 08:15 |  | 2.9292 | -0.84 | -0.84 | -0.154 | 0.43067 | -1.5929 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.5071 | Day
2025-08-05 09:30 | 76.16 | 79.324 | 1.2157 | 81.7555 | 76.8925 | -2.6025 | TRUE | lower | -5.5955 | 0.7325 | -6.8442 | 0.95263 | Persistent | 6 | 2025-08-05 08:15 |  | 2.8748 | -0.56 | -0.56 | -0.182 | 0.43827 | -0.86248 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.5449 | Day
2025-08-05 09:45 | 75.6 | 79.086 | 1.4463 | 81.9786 | 76.1934 | -2.4103 | TRUE | lower | -6.3786 | 0.59336 | -7.7809 | 0.77876 | Confirmed/Materialized Shift | 7 | 2025-08-05 08:15 |  | 2.8084 | -0.56 | -0.56 | -0.238 | 0.40905 | -0.78719 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5893 | Day
2025-08-05 10:00 | 75.04 | 78.848 | 1.6932 | 82.2344 | 75.4616 | -2.249 | TRUE | lower | -7.1944 | 0.42158 | -8.7487 | 0.55867 | Confirmed/Materialized Shift | 8 | 2025-08-05 08:15 |  | 2.7385 | -0.56 | -0.56 | -0.238 | 0.40905 | -0.78719 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5785 | Day
2025-08-05 10:15 | 74.76 | 78.582 | 1.8953 | 82.3726 | 74.7914 | -2.0166 | TRUE | lower | -7.6126 | 0.031399 | -9.2417 | 0.041982 | Confirmed/Materialized Shift | 9 | 2025-08-05 08:15 |  | 2.6583 | -0.28 | -0.28 | -0.266 | 0.39047 | -0.035854 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.563 | Day
2025-08-05 10:30 | 75.04 | 78.33 | 2.0168 | 82.3636 | 74.2964 | -1.6313 | FALSE | none | -7.3236 | -0.74362 | -8.8918 | -1.0009 | Confirmed/Materialized Shift | 10 | 2025-08-05 08:15 |  | 2.5556 | 0.28 | 0.28 | -0.252 | 0.40525 | 1.3128 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5373 | Day
2025-08-05 10:45 | 74.76 | 78.064 | 2.1219 | 82.3079 | 73.8201 | -1.5571 | FALSE | none | -7.5479 | -0.93988 | -9.1703 | -1.2732 | Confirmed/Materialized Shift | 11 | 2025-08-05 08:15 |  | 2.4648 | -0.28 | -0.28 | -0.266 | 0.4009 | -0.034922 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.5038 | Day
2025-08-05 11:00 | 75.04 | 77.812 | 2.1687 | 82.1494 | 73.4746 | -1.2782 | FALSE | none | -7.1094 | -1.5654 | -8.6542 | -2.1305 | Confirmed/Materialized Shift | 12 | 2025-08-05 08:15 |  | 2.3659 | 0.28 | 0.28 | -0.252 | 0.41531 | 1.281 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4852 | Day
2025-08-05 11:15 | 75.04 | 77.574 | 2.2 | 81.974 | 73.174 | -1.1518 | FALSE | none | -6.934 | -1.866 | -8.4588 | -2.5501 | Confirmed/Materialized Shift | 13 | 2025-08-05 08:15 |  | 2.2725 | 0 | 0 | -0.238 | 0.41902 | 0.568 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4768 | Day
2025-08-05 11:30 | 75.04 | 77.35 | 2.2194 | 81.7888 | 72.9112 | -1.0408 | FALSE | none | -6.7488 | -2.1288 | -8.2515 | -2.9197 | Confirmed/Materialized Shift | 14 | 2025-08-05 08:15 |  | 2.1845 | 0 | 0 | -0.224 | 0.4222 | 0.53055 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4694 | Day
2025-08-05 11:45 | 74.76 | 77.084 | 2.1937 | 81.4713 | 72.6967 | -1.0594 | FALSE | none | -6.7113 | -2.0633 | -8.2376 | -2.8382 | Confirmed/Materialized Shift | 15 | 2025-08-05 08:15 |  | 2.1095 | -0.28 | -0.28 | -0.266 | 0.37976 | -0.036866 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4706 | Day
2025-08-05 12:00 | 75.04 | 76.846 | 2.1411 | 81.1281 | 72.5639 | -0.84351 | FALSE | none | -6.0881 | -2.4761 | -7.5043 | -3.4123 | Persistence ends | 0 |  |  |  | 0.28 | 0.28 | -0.238 | 0.39884 | 1.2988 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0562 | Day
2025-08-05 12:15 | 75.04 | 76.594 | 2.0343 | 80.6627 | 72.5253 | -0.76389 | FALSE | none | -5.6227 | -2.5147 | -6.9706 | -3.4673 | Normal | 0 |  |  |  | 0 | 0 | -0.252 | 0.38435 | 0.65566 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0509 | Day
2025-08-05 12:30 | 74.76 | 76.342 | 1.9255 | 80.1931 | 72.4909 | -0.82159 | FALSE | none | -5.4331 | -2.2691 | -6.775 | -3.1302 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.252 | 0.38435 | -0.072851 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0548 | Day
2025-08-05 12:45 | 74.76 | 76.076 | 1.7406 | 79.5571 | 72.5949 | -0.75608 | FALSE | none | -4.7971 | -2.1651 | -6.0298 | -2.9825 | Normal | 0 |  |  |  | 0 | 0 | -0.266 | 0.36873 | 0.72139 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0504 | Day
2025-08-05 13:00 | 75.04 | 75.824 | 1.4749 | 78.7738 | 72.8742 | -0.53155 | FALSE | none | -3.7338 | -2.1658 | -4.74 | -2.972 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.252 | 0.38435 | 1.3842 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0354 | Day
2025-08-05 13:15 | 75.04 | 75.614 | 1.2438 | 78.1017 | 73.1263 | -0.46147 | FALSE | none | -3.0617 | -1.9137 | -3.9201 | -2.617 | Normal | 0 |  |  |  | 0 | 0 | -0.21 | 0.36195 | 0.58018 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0308 | Day
2025-08-05 13:30 | 74.76 | 75.404 | 0.97462 | 77.3532 | 73.4548 | -0.66077 | FALSE | none | -2.5932 | -1.3052 | -3.3525 | -1.7769 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.21 | 0.36195 | -0.19339 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0441 | Day
2025-08-05 13:45 | 74.76 | 75.236 | 0.74414 | 76.7243 | 73.7477 | -0.63966 | FALSE | none | -1.9643 | -1.0123 | -2.5602 | -1.3726 | Normal | 0 |  |  |  | 0 | 0 | -0.168 | 0.33254 | 0.5052 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0426 | Day
2025-08-05 14:00 | 74.76 | 75.096 | 0.51067 | 76.1173 | 74.0747 | -0.65796 | FALSE | none | -1.3573 | -0.68534 | -1.7832 | -0.9252 | Normal | 0 |  |  |  | 0 | 0 | -0.14 | 0.32118 | 0.43589 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0439 | Day
2025-08-05 14:15 | 74.76 | 74.998 | 0.34323 | 75.6845 | 74.3115 | -0.69341 | FALSE | none | -0.92446 | -0.44846 | -1.2215 | -0.60348 | Normal | 0 |  |  |  | 0 | 0 | -0.098 | 0.27666 | 0.35422 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0462 | Day
2025-08-05 14:30 | 75.04 | 74.942 | 0.20864 | 75.3593 | 74.5247 | 0.4697 | FALSE | none | -0.31929 | -0.51529 | -0.42369 | -0.69143 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.056 | 0.26641 | 1.2612 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0313 | Day
2025-08-05 14:45 | 75.04 | 74.914 | 0.14292 | 75.1998 | 74.6282 | 0.88163 | FALSE | none | -0.15983 | -0.41183 | -0.21255 | -0.55185 | Normal | 0 |  |  |  | 0 | 0 | -0.028 | 0.23863 | 0.11734 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-05 15:00 | 75.04 | 74.914 | 0.14292 | 75.1998 | 74.6282 | 0.88163 | FALSE | none | -0.15983 | -0.41183 | -0.21255 | -0.55185 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.20313 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-05 15:15 | 75.04 | 74.928 | 0.14073 | 75.2095 | 74.6465 | 0.79582 | FALSE | none | -0.16947 | -0.39347 | -0.22533 | -0.52711 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.19217 | -0.072851 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-05 15:30 | 74.76 | 74.914 | 0.14292 | 75.1998 | 74.6282 | -1.0775 | FALSE | none | -0.43983 | -0.13183 | -0.58489 | -0.17665 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.19217 | -1.3842 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Day
2025-08-05 15:45 | 75.04 | 74.928 | 0.14073 | 75.2095 | 74.6465 | 0.79582 | FALSE | none | -0.16947 | -0.39347 | -0.22533 | -0.52711 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.19217 | 1.3842 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-05 16:00 | 75.04 | 74.928 | 0.14073 | 75.2095 | 74.6465 | 0.79582 | FALSE | none | -0.16947 | -0.39347 | -0.22533 | -0.52711 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.18169 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-05 16:15 | 75.32 | 74.942 | 0.1644 | 75.2708 | 74.6132 | 2.2993 | TRUE | upper | 0.0492 | -0.7068 | 0.065364 | -0.94729 | Extreme triggered | 1 | 2025-08-05 16:15 | 2025-08-05 16:30 | 2.2993 | 0.28 | 0.28 | 0.014 | 0.19217 | 1.3842 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.2104 | Day
2025-08-05 16:30 | 75.04 | 74.942 | 0.1644 | 75.2708 | 74.6132 | 0.59611 | FALSE | none | -0.2308 | -0.4268 | -0.30663 | -0.57202 | Persistence ends | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.20313 | -1.3784 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0397 | Day
2025-08-05 16:45 | 74.76 | 74.942 | 0.1644 | 75.2708 | 74.6132 | -1.1071 | FALSE | none | -0.5108 | -0.1468 | -0.67862 | -0.19675 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.20313 | -1.3784 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0738 | Day
2025-08-05 17:00 | 75.04 | 74.942 | 0.1644 | 75.2708 | 74.6132 | 0.59611 | FALSE | none | -0.2308 | -0.4268 | -0.30663 | -0.57202 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.20313 | 1.3784 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0397 | Day
2025-08-05 17:15 | 74.76 | 74.928 | 0.16751 | 75.263 | 74.593 | -1.0029 | FALSE | none | -0.50302 | -0.16702 | -0.66834 | -0.2239 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.21256 | -1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0669 | Day
2025-08-05 17:30 | 74.76 | 74.928 | 0.16751 | 75.263 | 74.593 | -1.0029 | FALSE | none | -0.50302 | -0.16702 | -0.66834 | -0.2239 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.20313 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0669 | Day
2025-08-05 17:45 | 74.76 | 74.928 | 0.16751 | 75.263 | 74.593 | -1.0029 | FALSE | none | -0.50302 | -0.16702 | -0.66834 | -0.2239 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.20313 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0669 | Day
2025-08-05 18:00 | 75.04 | 74.928 | 0.16751 | 75.263 | 74.593 | 0.66862 | FALSE | none | -0.22302 | -0.44702 | -0.29632 | -0.59927 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.20313 | 1.3784 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0446 | Day
2025-08-05 18:15 | 75.04 | 74.928 | 0.16751 | 75.263 | 74.593 | 0.66862 | FALSE | none | -0.22302 | -0.44702 | -0.29632 | -0.59927 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.20313 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0446 | Day
2025-08-05 18:30 | 75.04 | 74.942 | 0.1644 | 75.2708 | 74.6132 | 0.59611 | FALSE | none | -0.2308 | -0.4268 | -0.30663 | -0.57202 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.19217 | -0.072851 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0397 | Day
2025-08-05 18:45 | 75.04 | 74.956 | 0.15995 | 75.2759 | 74.6361 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.31337 | -0.54115 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.19217 | -0.072851 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.035 | Day
2025-08-05 19:00 | 75.04 | 74.97 | 0.15403 | 75.2781 | 74.6619 | 0.45445 | FALSE | none | -0.23807 | -0.37807 | -0.31625 | -0.50637 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.19217 | -0.072851 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0303 | Night
2025-08-05 19:15 | 75.32 | 74.998 | 0.1644 | 75.3268 | 74.6692 | 1.9586 | FALSE | none | -0.0068001 | -0.6508 | -0.0090274 | -0.87158 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.028 | 0.20109 | 1.2532 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1306 | Night
2025-08-05 19:30 | 75.88 | 75.04 | 0.25695 | 75.5539 | 74.5261 | 3.2692 | TRUE | upper | 0.32611 | -1.3539 | 0.43162 | -1.8167 | Extreme triggered | 1 | 2025-08-05 19:30 | 2025-08-05 23:45 | 3.2692 | 0.56 | 0.56 | 0.042 | 0.22756 | 2.2763 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.3037 | Night
2025-08-05 19:45 | 76.16 | 75.096 | 0.35881 | 75.8136 | 74.3784 | 2.9654 | TRUE | upper | 0.34639 | -1.7816 | 0.4569 | -2.3953 | Extreme/elevated | 2 | 2025-08-05 19:30 |  | 3.1173 | 0.28 | 0.28 | 0.056 | 0.23338 | 0.9598 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.3406 | Night
2025-08-05 20:00 | 76.44 | 75.166 | 0.46743 | 76.1009 | 74.2311 | 2.7256 | TRUE | upper | 0.33915 | -2.2089 | 0.44565 | -2.9756 | Persistent | 3 | 2025-08-05 19:30 |  | 2.9867 | 0.28 | 0.28 | 0.07 | 0.23819 | 0.88163 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.3817 | Night
2025-08-05 20:15 | 77 | 75.264 | 0.62014 | 76.5043 | 74.0237 | 2.7994 | TRUE | upper | 0.49572 | -2.9763 | 0.64797 | -4.0207 | Persistent | 4 | 2025-08-05 19:30 |  | 2.9399 | 0.56 | 0.56 | 0.098 | 0.26132 | 1.7679 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4438 | Night
2025-08-05 20:30 | 77.56 | 75.404 | 0.79248 | 76.989 | 73.819 | 2.7206 | TRUE | upper | 0.57104 | -3.741 | 0.74172 | -5.0677 | Persistent | 5 | 2025-08-05 19:30 |  | 2.896 | 0.56 | 0.56 | 0.14 | 0.26485 | 1.5858 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4957 | Night
2025-08-05 20:45 | 77.84 | 75.544 | 0.95537 | 77.4547 | 73.6333 | 2.4032 | TRUE | upper | 0.38525 | -4.2067 | 0.49739 | -5.7131 | Persistent | 6 | 2025-08-05 19:30 |  | 2.8139 | 0.28 | 0.28 | 0.14 | 0.26485 | 0.52859 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.5316 | Night
2025-08-05 21:00 | 78.4 | 75.712 | 1.1397 | 77.9914 | 73.4326 | 2.3585 | TRUE | upper | 0.40856 | -4.9674 | 0.52385 | -6.7646 | Confirmed/Materialized Shift | 7 | 2025-08-05 19:30 |  | 2.7488 | 0.56 | 0.56 | 0.168 | 0.27852 | 1.4074 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5858 | Night
2025-08-05 21:15 | 78.68 | 75.88 | 1.3133 | 78.5066 | 73.2534 | 2.132 | TRUE | upper | 0.17337 | -5.4266 | 0.22083 | -7.408 | Confirmed/Materialized Shift | 8 | 2025-08-05 19:30 |  | 2.6717 | 0.28 | 0.28 | 0.168 | 0.27852 | 0.40212 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5707 | Night
2025-08-05 21:30 | 79.24 | 76.09 | 1.4951 | 79.0803 | 73.0997 | 2.1068 | TRUE | upper | 0.15973 | -6.1403 | 0.20198 | -8.3999 | Confirmed/Materialized Shift | 9 | 2025-08-05 19:30 |  | 2.609 | 0.56 | 0.56 | 0.21 | 0.27063 | 1.2933 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.569 | Night
2025-08-05 21:45 | 79.52 | 76.328 | 1.6437 | 79.6155 | 73.0405 | 1.9419 | FALSE | none | -0.095498 | -6.4795 | -0.11995 | -8.8711 | Confirmed/Materialized Shift | 10 | 2025-08-05 19:30 |  | 2.5423 | 0.28 | 0.28 | 0.238 | 0.24503 | 0.17141 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.558 | Night
2025-08-05 22:00 | 80.08 | 76.58 | 1.8135 | 80.2069 | 72.9531 | 1.93 | FALSE | none | -0.12694 | -7.1269 | -0.15827 | -9.7692 | Confirmed/Materialized Shift | 11 | 2025-08-05 19:30 |  | 2.4866 | 0.56 | 0.56 | 0.252 | 0.25533 | 1.2063 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.5287 | Night
2025-08-05 22:15 | 79.8 | 76.832 | 1.8956 | 80.6231 | 73.0409 | 1.5658 | FALSE | none | -0.82315 | -6.7591 | -1.021 | -9.2539 | Confirmed/Materialized Shift | 12 | 2025-08-05 19:30 |  | 2.4099 | -0.28 | -0.28 | 0.252 | 0.25533 | -2.0835 | TRUE | 1 | FALSE | FALSE | TRUE | FALSE | 0.533 | Night
2025-08-05 22:30 | 80.08 | 77.098 | 1.9616 | 81.0213 | 73.1747 | 1.5202 | FALSE | none | -0.94126 | -6.9053 | -1.1617 | -9.4367 | Confirmed/Materialized Shift | 13 | 2025-08-05 19:30 |  | 2.3414 | 0.28 | 0.28 | 0.266 | 0.24837 | 0.056367 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5299 | Night
2025-08-05 22:45 | 80.08 | 77.364 | 1.9884 | 81.3409 | 73.3871 | 1.3659 | FALSE | none | -1.2609 | -6.6929 | -1.5501 | -9.1199 | Confirmed/Materialized Shift | 14 | 2025-08-05 19:30 |  | 2.2717 | 0 | 0 | 0.266 | 0.24837 | -1.071 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5196 | Night
2025-08-05 23:00 | 80.08 | 77.616 | 1.9977 | 81.6115 | 73.6205 | 1.2334 | FALSE | none | -1.5315 | -6.4595 | -1.8766 | -8.774 | Confirmed/Materialized Shift | 15 | 2025-08-05 19:30 |  | 2.2025 | 0 | 0 | 0.252 | 0.25533 | -0.98694 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5108 | Night
2025-08-05 23:15 | 80.08 | 77.868 | 1.9734 | 81.8149 | 73.9211 | 1.1209 | FALSE | none | -1.7349 | -6.1589 | -2.1205 | -8.3317 | Confirmed/Materialized Shift | 16 | 2025-08-05 19:30 |  | 2.1349 | 0 | 0 | 0.252 | 0.25533 | -0.98694 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5033 | Night
2025-08-05 23:30 | 80.08 | 78.12 | 1.9142 | 81.9484 | 74.2916 | 1.0239 | FALSE | none | -1.8684 | -5.7884 | -2.28 | -7.7915 | Confirmed/Materialized Shift | 17 | 2025-08-05 19:30 |  | 2.0696 | 0 | 0 | 0.252 | 0.25533 | -0.98694 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.4968 | Night
2025-08-05 23:45 | 79.8 | 78.358 | 1.8038 | 81.9657 | 74.7503 | 0.79941 | FALSE | none | -2.1657 | -5.0497 | -2.6422 | -6.7554 | Persistence ends | 0 |  |  |  | -0.28 | -0.28 | 0.238 | 0.27666 | -1.8723 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0819 | Night
2025-08-06 | 80.08 | 78.61 | 1.6624 | 81.9348 | 75.2852 | 0.88426 | FALSE | none | -1.8548 | -4.7948 | -2.2638 | -6.3689 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.252 | 0.27101 | 0.10332 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0875 | Night
2025-08-06 00:15 | 80.08 | 78.848 | 1.4993 | 81.8467 | 75.8493 | 0.8217 | FALSE | none | -1.7667 | -4.2307 | -2.1585 | -5.5777 | Normal | 0 |  |  |  | 0 | 0 | 0.238 | 0.27666 | -0.86025 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0834 | Night
2025-08-06 00:30 | 80.08 | 79.058 | 1.3483 | 81.7546 | 76.3614 | 0.758 | FALSE | none | -1.6746 | -3.7186 | -2.0483 | -4.8697 | Normal | 0 |  |  |  | 0 | 0 | 0.21 | 0.27063 | -0.77596 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0791 | Night
2025-08-06 00:45 | 80.08 | 79.254 | 1.1791 | 81.6123 | 76.8957 | 0.70051 | FALSE | none | -1.5323 | -3.1843 | -1.8775 | -4.141 | Normal | 0 |  |  |  | 0 | 0 | 0.196 | 0.27404 | -0.71522 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0467 | Night
2025-08-06 01:00 | 80.36 | 79.45 | 0.99877 | 81.4475 | 77.4525 | 0.91112 | FALSE | none | -1.0875 | -2.9075 | -1.3353 | -3.754 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.196 | 0.27404 | 0.30652 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0607 | Night
2025-08-06 01:15 | 80.08 | 79.604 | 0.82313 | 81.2503 | 77.9577 | 0.57828 | FALSE | none | -1.1703 | -2.1223 | -1.4403 | -2.7223 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.154 | 0.27963 | -1.552 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0386 | Night
2025-08-06 01:30 | 80.08 | 79.73 | 0.67295 | 81.0759 | 78.3841 | 0.5201 | FALSE | none | -0.9959 | -1.6959 | -1.2284 | -2.1636 | Normal | 0 |  |  |  | 0 | 0 | 0.126 | 0.26446 | -0.47644 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0347 | Night
2025-08-06 01:45 | 80.08 | 79.842 | 0.50804 | 80.8581 | 78.8259 | 0.46847 | FALSE | none | -0.77807 | -1.2541 | -0.96227 | -1.5909 | Normal | 0 |  |  |  | 0 | 0 | 0.112 | 0.26329 | -0.42538 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0312 | Night
2025-08-06 02:00 | 80.08 | 79.926 | 0.37976 | 80.6855 | 79.1665 | 0.40552 | FALSE | none | -0.60551 | -0.91351 | -0.75046 | -1.1539 | Normal | 0 |  |  |  | 0 | 0 | 0.084 | 0.24206 | -0.34702 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.027 | Night
2025-08-06 02:15 | 79.8 | 79.982 | 0.24503 | 80.4721 | 79.4919 | -0.74278 | FALSE | none | -0.67205 | -0.30805 | -0.83514 | -0.38753 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.056 | 0.25044 | -1.3416 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0495 | Night
2025-08-06 02:30 | 79.8 | 80.01 | 0.17883 | 80.3677 | 79.6523 | -1.1743 | FALSE | none | -0.56765 | -0.14765 | -0.70632 | -0.18537 | Normal | 0 |  |  |  | 0 | 0 | 0.028 | 0.22066 | -0.12689 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0783 | Night
2025-08-06 02:45 | 80.08 | 80.038 | 0.13702 | 80.312 | 79.764 | 0.30652 | FALSE | none | -0.23204 | -0.31604 | -0.28893 | -0.39622 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.028 | 0.22066 | 1.142 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0204 | Night
2025-08-06 03:00 | 80.08 | 80.038 | 0.13702 | 80.312 | 79.764 | 0.30652 | FALSE | none | -0.23204 | -0.31604 | -0.28893 | -0.39622 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.18169 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0204 | Night
2025-08-06 03:15 | 80.08 | 80.052 | 0.12522 | 80.3024 | 79.8016 | 0.22361 | FALSE | none | -0.22244 | -0.27844 | -0.277 | -0.34891 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.16935 | -0.082671 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0149 | Night
2025-08-06 03:30 | 80.08 | 80.052 | 0.12522 | 80.3024 | 79.8016 | 0.22361 | FALSE | none | -0.22244 | -0.27844 | -0.277 | -0.34891 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.15735 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0149 | Night
2025-08-06 03:45 | 80.08 | 80.052 | 0.12522 | 80.3024 | 79.8016 | 0.22361 | FALSE | none | -0.22244 | -0.27844 | -0.277 | -0.34891 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.15735 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0149 | Night
2025-08-06 04:00 | 80.08 | 80.052 | 0.12522 | 80.3024 | 79.8016 | 0.22361 | FALSE | none | -0.22244 | -0.27844 | -0.277 | -0.34891 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.15735 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0149 | Night
2025-08-06 04:15 | 79.8 | 80.038 | 0.13702 | 80.312 | 79.764 | -1.737 | FALSE | none | -0.51204 | -0.036042 | -0.63757 | -0.045186 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.16935 | -1.5708 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1158 | Night
2025-08-06 04:30 | 80.08 | 80.038 | 0.13702 | 80.312 | 79.764 | 0.30652 | FALSE | none | -0.23204 | -0.31604 | -0.28893 | -0.39622 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.18169 | 1.5411 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0204 | Night
2025-08-06 04:45 | 80.08 | 80.052 | 0.12522 | 80.3024 | 79.8016 | 0.22361 | FALSE | none | -0.22244 | -0.27844 | -0.277 | -0.34891 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.16935 | -0.082671 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0149 | Night
2025-08-06 05:00 | 79.8 | 80.038 | 0.13702 | 80.312 | 79.764 | -1.737 | FALSE | none | -0.51204 | -0.036042 | -0.63757 | -0.045186 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.16935 | -1.5708 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1158 | Night
2025-08-06 05:15 | 80.36 | 80.052 | 0.1547 | 80.3614 | 79.7426 | 1.9909 | FALSE | none | -0.0014035 | -0.6174 | -0.0017465 | -0.77425 | Normal | 0 |  |  |  | 0.56 | 0.56 | 0.014 | 0.21256 | 2.5686 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1613 | Night
2025-08-06 05:30 | 79.8 | 80.038 | 0.1644 | 80.3668 | 79.7092 | -1.4477 | FALSE | none | -0.5668 | -0.0908 | -0.70527 | -0.11391 | Normal | 0 |  |  |  | -0.56 | -0.56 | -0.014 | 0.24837 | -2.1983 | TRUE | 2 | TRUE | FALSE | FALSE | TRUE | 0.1537 | Night
2025-08-06 05:45 | 79.8 | 80.024 | 0.17236 | 80.3687 | 79.6793 | -1.2996 | FALSE | none | -0.56873 | -0.12073 | -0.70765 | -0.15152 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.24837 | 0.056367 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.1438 | Night
2025-08-06 06:00 | 79.8 | 79.996 | 0.15995 | 80.3159 | 79.6761 | -1.2254 | FALSE | none | -0.51589 | -0.12389 | -0.64233 | -0.1555 | Normal | 0 |  |  |  | 0 | 0 | -0.028 | 0.23863 | 0.11734 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.1388 | Night
2025-08-06 06:15 | 80.08 | 79.996 | 0.15995 | 80.3159 | 79.6761 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.29371 | -0.50692 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.24035 | 1.165 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.0922 | Night
2025-08-06 06:30 | 79.8 | 79.982 | 0.1644 | 80.3108 | 79.6532 | -1.1071 | FALSE | none | -0.5108 | -0.1468 | -0.63603 | -0.1843 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.24837 | -1.071 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.1309 | Night
2025-08-06 06:45 | 80.08 | 79.982 | 0.1644 | 80.3108 | 79.6532 | 0.59611 | FALSE | none | -0.2308 | -0.4268 | -0.28738 | -0.53582 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.25695 | 1.0897 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.0969 | Night
2025-08-06 07:00 | 80.08 | 79.982 | 0.1644 | 80.3108 | 79.6532 | 0.59611 | FALSE | none | -0.2308 | -0.4268 | -0.28738 | -0.53582 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.25695 | 0 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.0969 | Day
2025-08-06 07:15 | 80.08 | 79.996 | 0.15995 | 80.3159 | 79.6761 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.29371 | -0.50692 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.24837 | -0.056367 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.0922 | Day
2025-08-06 07:30 | 79.8 | 79.996 | 0.15995 | 80.3159 | 79.6761 | -1.2254 | FALSE | none | -0.51589 | -0.12389 | -0.64233 | -0.1555 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.25695 | -1.0897 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.1388 | Day
2025-08-06 07:45 | 79.8 | 79.982 | 0.1644 | 80.3108 | 79.6532 | -1.1071 | FALSE | none | -0.5108 | -0.1468 | -0.63603 | -0.1843 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.24837 | 0.056367 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1024 | Day
2025-08-06 08:00 | 80.36 | 79.996 | 0.18395 | 80.3639 | 79.6281 | 1.9789 | FALSE | none | -0.0038901 | -0.73189 | -0.0048407 | -0.91914 | Normal | 0 |  |  |  | 0.56 | 0.56 | 0.014 | 0.27963 | 1.9526 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1319 | Day
2025-08-06 08:15 | 79.24 | 79.954 | 0.24837 | 80.4507 | 79.4573 | -2.8747 | TRUE | lower | -1.2107 | 0.21726 | -1.5049 | 0.27343 | Extreme triggered | 1 | 2025-08-06 08:15 | 2025-08-06 22:00 | 2.8747 | -1.12 | -1.12 | -0.042 | 0.37758 | -2.855 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.2774 | Day
2025-08-06 08:30 | 78.68 | 79.884 | 0.37566 | 80.6353 | 79.1327 | -3.205 | TRUE | lower | -1.9553 | 0.45268 | -2.4249 | 0.57205 | Extreme/elevated | 2 | 2025-08-06 08:15 |  | 3.0399 | -0.56 | -0.56 | -0.07 | 0.39468 | -1.2415 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.3565 | Day
2025-08-06 08:45 | 78.12 | 79.786 | 0.54107 | 80.8681 | 78.7039 | -3.0791 | TRUE | lower | -2.7481 | 0.58385 | -3.3983 | 0.74183 | Persistent | 3 | 2025-08-06 08:15 |  | 3.0529 | -0.56 | -0.56 | -0.098 | 0.40905 | -1.1294 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4053 | Day
2025-08-06 09:00 | 77.56 | 79.66 | 0.72959 | 81.1192 | 78.2008 | -2.8783 | TRUE | lower | -3.5592 | 0.64083 | -4.3876 | 0.81947 | Persistent | 4 | 2025-08-06 08:15 |  | 3.0093 | -0.56 | -0.56 | -0.126 | 0.42098 | -1.0309 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.449 | Day
2025-08-06 09:15 | 76.72 | 79.506 | 0.98042 | 81.4668 | 77.5452 | -2.8416 | TRUE | lower | -4.7468 | 0.82516 | -5.8267 | 1.0641 | Persistent | 5 | 2025-08-06 08:15 |  | 2.9758 | -0.84 | -0.84 | -0.154 | 0.44943 | -1.5264 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.5037 | Day
2025-08-06 09:30 | 76.16 | 79.31 | 1.2218 | 81.7535 | 76.8665 | -2.5783 | TRUE | lower | -5.5935 | 0.70648 | -6.8419 | 0.9191 | Persistent | 6 | 2025-08-06 08:15 |  | 2.9095 | -0.56 | -0.56 | -0.196 | 0.44597 | -0.8162 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.5433 | Day
2025-08-06 09:45 | 75.32 | 79.072 | 1.4966 | 82.0652 | 76.0788 | -2.507 | TRUE | lower | -6.7452 | 0.75883 | -8.2193 | 0.99743 | Confirmed/Materialized Shift | 7 | 2025-08-06 08:15 |  | 2.852 | -0.84 | -0.84 | -0.238 | 0.46566 | -1.2928 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5957 | Day
2025-08-06 22:00 | 80.08 | 79.086 | 1.505 | 82.0961 | 76.0759 | 0.66045 | FALSE | none | -2.0161 | -4.0041 | -2.4558 | -5.2633 | Persistence ends | 0 |  |  |  | 4.76 | 4.76 | 0.014 | 1.2102 | 3.9216 | TRUE | 2 | TRUE | FALSE | FALSE | TRUE | 0.1012 | Night
2025-08-06 22:15 | 79.8 | 79.058 | 1.4852 | 82.0283 | 76.0877 | 0.49961 | FALSE | none | -2.2283 | -3.7123 | -2.7165 | -4.879 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.028 | 1.2048 | -0.20916 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.0904 | Night
2025-08-06 22:30 | 80.08 | 79.072 | 1.4938 | 82.0596 | 76.0844 | 0.67478 | FALSE | none | -1.9796 | -3.9956 | -2.4125 | -5.2516 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 1.1999 | 0.22168 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.1021 | Night
2025-08-06 22:45 | 80.36 | 79.1 | 1.5133 | 82.1266 | 76.0734 | 0.83261 | FALSE | none | -1.7666 | -4.2866 | -2.1511 | -5.6348 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.028 | 1.2014 | 0.20975 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0841 | Night
2025-08-06 23:00 | 80.08 | 79.114 | 1.5214 | 82.1568 | 76.0712 | 0.63494 | FALSE | none | -2.0768 | -4.0088 | -2.5278 | -5.2698 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.014 | 1.2034 | -0.24431 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0709 | Night
2025-08-06 23:15 | 80.08 | 79.114 | 1.5214 | 82.1568 | 76.0712 | 0.63494 | FALSE | none | -2.0768 | -4.0088 | -2.5278 | -5.2698 | Normal | 0 |  |  |  | 0 | 0 | 0 | 1.2018 | 0 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0709 | Night
2025-08-06 23:30 | 80.08 | 79.128 | 1.5293 | 82.1866 | 76.0694 | 0.6225 | FALSE | none | -2.1066 | -4.0106 | -2.5632 | -5.2723 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 1.1999 | -0.011667 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0701 | Night
2025-08-06 23:45 | 79.8 | 79.114 | 1.5214 | 82.1568 | 76.0712 | 0.4509 | FALSE | none | -2.3568 | -3.7288 | -2.8687 | -4.9017 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 1.1999 | -0.22168 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0586 | Night
2025-08-07 | 79.8 | 79.1 | 1.5133 | 82.1266 | 76.0734 | 0.46256 | FALSE | none | -2.3266 | -3.7266 | -2.833 | -4.8987 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 1.1999 | 0.011667 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0594 | Night
2025-08-07 00:15 | 79.8 | 79.086 | 1.505 | 82.0961 | 76.0759 | 0.47441 | FALSE | none | -2.2961 | -3.7241 | -2.7968 | -4.8952 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 1.1999 | 0.011667 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0602 | Night
2025-08-07 00:30 | 80.08 | 79.1 | 1.5133 | 82.1266 | 76.0734 | 0.64759 | FALSE | none | -2.0466 | -4.0066 | -2.492 | -5.2668 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 1.1999 | 0.22168 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0432 | Night
2025-08-07 00:45 | 80.08 | 79.114 | 1.5214 | 82.1568 | 76.0712 | 0.63494 | FALSE | none | -2.0768 | -4.0088 | -2.5278 | -5.2698 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 1.1999 | -0.011667 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0423 | Night
2025-08-07 01:00 | 80.08 | 79.1 | 1.5106 | 82.1212 | 76.0788 | 0.64876 | FALSE | none | -2.0412 | -4.0012 | -2.4855 | -5.2592 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 1.1931 | 0.011735 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0433 | Night
2025-08-07 01:15 | 80.08 | 79.142 | 1.5263 | 82.1945 | 76.0895 | 0.61457 | FALSE | none | -2.1145 | -3.9905 | -2.5726 | -5.2445 | Normal | 0 |  |  |  | 0 | 0 | 0.042 | 1.1643 | -0.036072 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.041 | Night
2025-08-07 01:30 | 80.08 | 79.212 | 1.536 | 82.2841 | 76.1399 | 0.56509 | FALSE | none | -2.2041 | -3.9401 | -2.6786 | -5.1748 | Normal | 0 |  |  |  | 0 | 0 | 0.07 | 1.1558 | -0.060564 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0377 | Night
2025-08-07 01:45 | 80.08 | 79.31 | 1.5252 | 82.3604 | 76.2596 | 0.50485 | FALSE | none | -2.2804 | -3.8204 | -2.7688 | -5.0097 | Normal | 0 |  |  |  | 0 | 0 | 0.098 | 1.1465 | -0.085478 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0337 | Night
2025-08-07 02:00 | 79.8 | 79.422 | 1.4712 | 82.3644 | 76.4796 | 0.25693 | FALSE | none | -2.5644 | -3.3204 | -3.1135 | -4.3416 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.112 | 1.1397 | -0.34394 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0171 | Night
2025-08-07 02:15 | 80.08 | 79.59 | 1.3316 | 82.2533 | 76.9267 | 0.36797 | FALSE | none | -2.1733 | -3.1533 | -2.6422 | -4.0991 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.168 | 1.1178 | 0.1002 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0245 | Night
2025-08-07 02:30 | 79.8 | 79.772 | 1.059 | 81.89 | 77.654 | 0.026439 | FALSE | none | -2.09 | -2.146 | -2.5523 | -2.7636 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.182 | 1.1099 | -0.41625 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0018 | Night
2025-08-07 02:45 | 79.52 | 79.982 | 0.18783 | 80.3577 | 79.6063 | -2.4597 | TRUE | lower | -0.83766 | 0.086341 | -1.0424 | 0.10846 | Extreme triggered | 1 | 2025-08-07 02:45 | 2025-08-07 03:00 | 2.4597 | -0.28 | -0.28 | 0.21 | 1.0897 | -0.44968 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.2211 | Night
2025-08-07 03:00 | 79.8 | 79.968 | 0.19056 | 80.3491 | 79.5869 | -0.88163 | FALSE | none | -0.54911 | -0.21311 | -0.68341 | -0.26777 | Persistence ends | 0 |  |  |  | 0.28 | 0.28 | -0.014 | 0.21256 | 1.3831 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Night
2025-08-07 03:15 | 80.08 | 79.982 | 0.18783 | 80.3577 | 79.6063 | 0.52175 | FALSE | none | -0.27766 | -0.47366 | -0.34553 | -0.595 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.21256 | 1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0348 | Night
2025-08-07 03:30 | 79.52 | 79.954 | 0.21256 | 80.3791 | 79.5289 | -2.0417 | TRUE | lower | -0.85913 | 0.0088734 | -1.0688 | 0.011157 | Extreme triggered | 1 | 2025-08-07 03:30 | 2025-08-07 03:45 | 2.0417 | -0.56 | -0.56 | -0.028 | 0.23863 | -2.2294 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.2218 | Night
2025-08-07 03:45 | 80.08 | 79.94 | 0.19271 | 80.3254 | 79.5546 | 0.72648 | FALSE | none | -0.24542 | -0.52542 | -0.30553 | -0.66045 | Persistence ends | 0 |  |  |  | 0.56 | 0.56 | -0.014 | 0.26446 | 2.1704 | TRUE | 2 | TRUE | FALSE | FALSE | TRUE | 0.1056 | Night
2025-08-07 04:00 | 80.08 | 79.94 | 0.19271 | 80.3254 | 79.5546 | 0.72648 | FALSE | none | -0.24542 | -0.52542 | -0.30553 | -0.66045 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.25695 | 0 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.1056 | Night
2025-08-07 04:15 | 79.8 | 79.926 | 0.19217 | 80.3103 | 79.5417 | -0.65566 | FALSE | none | -0.51035 | -0.25835 | -0.63547 | -0.32479 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.26446 | -1.0058 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.1009 | Night
2025-08-07 04:30 | 79.8 | 79.912 | 0.19056 | 80.2931 | 79.5309 | -0.58775 | FALSE | none | -0.49311 | -0.26911 | -0.61414 | -0.33837 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.26446 | 0.052937 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.0963 | Night
2025-08-07 04:45 | 79.8 | 79.912 | 0.19056 | 80.2931 | 79.5309 | -0.58775 | FALSE | none | -0.49311 | -0.26911 | -0.61414 | -0.33837 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.25695 | 0 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.0963 | Night
2025-08-07 05:00 | 79.8 | 79.912 | 0.19056 | 80.2931 | 79.5309 | -0.58775 | FALSE | none | -0.49311 | -0.26911 | -0.61414 | -0.33837 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.25695 | 0 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.0963 | Night
2025-08-07 05:15 | 80.08 | 79.926 | 0.19217 | 80.3103 | 79.5417 | 0.80136 | FALSE | none | -0.23035 | -0.53835 | -0.28682 | -0.67681 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.26446 | 1.0058 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.1106 | Night
2025-08-07 05:30 | 80.08 | 79.926 | 0.19217 | 80.3103 | 79.5417 | 0.80136 | FALSE | none | -0.23035 | -0.53835 | -0.28682 | -0.67681 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.25695 | 0 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.1106 | Night
2025-08-07 05:45 | 79.8 | 79.912 | 0.19056 | 80.2931 | 79.5309 | -0.58775 | FALSE | none | -0.49311 | -0.26911 | -0.61414 | -0.33837 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.26446 | -1.0058 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.0963 | Night
2025-08-07 06:00 | 79.8 | 79.898 | 0.18783 | 80.2737 | 79.5223 | -0.52175 | FALSE | none | -0.47366 | -0.27766 | -0.59006 | -0.34916 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.26446 | 0.052937 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0634 | Night
2025-08-07 06:15 | 80.08 | 79.898 | 0.18783 | 80.2737 | 79.5223 | 0.96896 | FALSE | none | -0.19366 | -0.55766 | -0.24125 | -0.70126 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.27253 | 1.0274 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0646 | Night
2025-08-07 06:30 | 80.36 | 79.912 | 0.2111 | 80.3342 | 79.4898 | 2.1222 | TRUE | upper | 0.025795 | -0.8702 | 0.03211 | -1.0947 | Extreme triggered | 1 | 2025-08-07 06:30 | 2025-08-07 06:45 | 2.1222 | 0.28 | 0.28 | 0.014 | 0.27963 | 0.95125 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1986 | Night
2025-08-07 06:45 | 80.08 | 79.912 | 0.2111 | 80.3342 | 79.4898 | 0.79582 | FALSE | none | -0.2542 | -0.5902 | -0.31643 | -0.74249 | Persistence ends | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.28727 | -0.97468 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Night
2025-08-07 07:00 | 80.08 | 79.926 | 0.21256 | 80.3511 | 79.5009 | 0.72449 | FALSE | none | -0.27113 | -0.57913 | -0.33743 | -0.72845 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.27963 | -0.050066 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0483 | Day
2025-08-07 07:15 | 80.36 | 79.94 | 0.23161 | 80.4032 | 79.4768 | 1.8134 | FALSE | none | -0.043215 | -0.88322 | -0.053748 | -1.1113 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.27963 | 0.95125 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1209 | Day
2025-08-07 07:30 | 80.08 | 79.954 | 0.23116 | 80.4163 | 79.4917 | 0.54507 | FALSE | none | -0.33632 | -0.58832 | -0.41823 | -0.74011 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.014 | 0.27963 | -1.0514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0363 | Day
2025-08-07 07:45 | 80.08 | 79.982 | 0.20864 | 80.3993 | 79.5647 | 0.4697 | FALSE | none | -0.31929 | -0.51529 | -0.39713 | -0.64764 | Normal | 0 |  |  |  | 0 | 0 | 0.028 | 0.27101 | -0.10332 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0313 | Day
2025-08-07 08:00 | 79.8 | 79.982 | 0.20864 | 80.3993 | 79.5647 | -0.8723 | FALSE | none | -0.59929 | -0.23529 | -0.74539 | -0.29572 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.27253 | -1.0274 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0582 | Day
2025-08-07 08:15 | 79.24 | 79.94 | 0.26485 | 80.4697 | 79.4103 | -2.643 | TRUE | lower | -1.2297 | 0.17029 | -1.5282 | 0.21445 | Extreme triggered | 1 | 2025-08-07 08:15 | 2025-08-07 12:00 | 2.643 | -0.56 | -0.56 | -0.042 | 0.2912 | -1.7789 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.2333 | Day
2025-08-07 08:30 | 78.96 | 79.912 | 0.33254 | 80.5771 | 79.2469 | -2.8628 | TRUE | lower | -1.6171 | 0.28691 | -2.0069 | 0.36205 | Extreme/elevated | 2 | 2025-08-07 08:15 |  | 2.7529 | -0.28 | -0.28 | -0.028 | 0.27101 | -0.92984 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.3051 | Day
2025-08-07 08:45 | 77.84 | 79.8 | 0.56732 | 80.9346 | 78.6654 | -3.4548 | TRUE | lower | -3.0946 | 0.82536 | -3.8236 | 1.0492 | Persistent | 3 | 2025-08-07 08:15 |  | 2.9869 | -1.12 | -1.12 | -0.112 | 0.33254 | -3.0312 | TRUE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4303 | Day
2025-08-07 09:00 | 77.56 | 79.674 | 0.75173 | 81.1775 | 78.1705 | -2.8122 | TRUE | lower | -3.6175 | 0.61054 | -4.4562 | 0.78103 | Persistent | 4 | 2025-08-07 08:15 |  | 2.9432 | -0.28 | -0.28 | -0.126 | 0.33347 | -0.46181 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4446 | Day
2025-08-07 09:15 | 76.72 | 79.52 | 0.99928 | 81.5186 | 77.5214 | -2.802 | TRUE | lower | -4.7986 | 0.80143 | -5.8865 | 1.0338 | Persistent | 5 | 2025-08-07 08:15 |  | 2.915 | -0.84 | -0.84 | -0.154 | 0.36873 | -1.8604 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.5011 | Day
2025-08-07 09:30 | 76.16 | 79.338 | 1.2465 | 81.831 | 76.845 | -2.5495 | TRUE | lower | -5.671 | 0.685 | -6.9301 | 0.8914 | Persistent | 6 | 2025-08-07 08:15 |  | 2.8541 | -0.56 | -0.56 | -0.182 | 0.37758 | -1.0011 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.5414 | Day
2025-08-07 09:45 | 75.6 | 79.128 | 1.4938 | 82.1156 | 76.1404 | -2.3617 | TRUE | lower | -6.5156 | 0.54035 | -7.9347 | 0.70968 | Confirmed/Materialized Shift | 7 | 2025-08-07 08:15 |  | 2.7837 | -0.56 | -0.56 | -0.21 | 0.38408 | -0.91127 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.586 | Day
2025-08-07 10:00 | 74.76 | 78.876 | 1.7734 | 82.4229 | 75.3291 | -2.3209 | TRUE | lower | -7.6629 | 0.56913 | -9.297 | 0.75552 | Confirmed/Materialized Shift | 8 | 2025-08-07 08:15 |  | 2.7259 | -0.84 | -0.84 | -0.252 | 0.40525 | -1.451 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5833 | Day
2025-08-07 10:15 | 75.04 | 78.624 | 1.9433 | 82.5106 | 74.7374 | -1.8443 | FALSE | none | -7.4706 | -0.30259 | -9.0541 | -0.40488 | Confirmed/Materialized Shift | 9 | 2025-08-07 08:15 |  | 2.6279 | 0.28 | 0.28 | -0.252 | 0.40525 | 1.3128 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5515 | Day
2025-08-07 10:30 | 75.04 | 78.372 | 2.0674 | 82.5067 | 74.2373 | -1.6117 | FALSE | none | -7.4667 | -0.80275 | -9.0499 | -1.0813 | Confirmed/Materialized Shift | 10 | 2025-08-07 08:15 |  | 2.5263 | 0 | 0 | -0.252 | 0.40525 | 0.62184 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.536 | Day
2025-08-07 10:45 | 75.04 | 78.134 | 2.166 | 82.4659 | 73.8021 | -1.4285 | FALSE | none | -7.4259 | -1.2379 | -9.0049 | -1.6774 | Confirmed/Materialized Shift | 11 | 2025-08-07 08:15 |  | 2.4265 | 0 | 0 | -0.238 | 0.40905 | 0.58184 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5238 | Day
2025-08-07 11:00 | 75.04 | 77.896 | 2.2337 | 82.3635 | 73.4285 | -1.2786 | FALSE | none | -7.3235 | -1.6115 | -8.8916 | -2.1946 | Confirmed/Materialized Shift | 12 | 2025-08-07 08:15 |  | 2.3308 | 0 | 0 | -0.238 | 0.40905 | 0.58184 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5138 | Day
2025-08-07 11:15 | 75.04 | 77.644 | 2.2585 | 82.1611 | 73.1269 | -1.153 | FALSE | none | -7.1211 | -1.9131 | -8.6672 | -2.6161 | Confirmed/Materialized Shift | 13 | 2025-08-07 08:15 |  | 2.2402 | 0 | 0 | -0.252 | 0.39494 | 0.63808 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4769 | Day
2025-08-07 11:30 | 74.76 | 77.364 | 2.2512 | 81.8664 | 72.8616 | -1.1567 | FALSE | none | -7.1064 | -1.8984 | -8.6805 | -2.6055 | Confirmed/Materialized Shift | 14 | 2025-08-07 08:15 |  | 2.1628 | -0.28 | -0.28 | -0.28 | 0.37456 | -1.9267e-15 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4771 | Day
2025-08-07 11:45 | 74.76 | 77.098 | 2.2276 | 81.5532 | 72.6428 | -1.0496 | FALSE | none | -6.7932 | -2.1172 | -8.3297 | -2.9145 | Confirmed/Materialized Shift | 15 | 2025-08-07 08:15 |  | 2.0886 | 0 | 0 | -0.266 | 0.37976 | 0.70045 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.47 | Day
2025-08-07 12:00 | 74.76 | 76.832 | 2.1696 | 81.1713 | 72.4927 | -0.955 | FALSE | none | -6.4113 | -2.2673 | -7.8984 | -3.1276 | Persistence ends | 0 |  |  |  | 0 | 0 | -0.266 | 0.37976 | 0.70045 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0637 | Day
2025-08-07 12:15 | 75.04 | 76.566 | 2.0364 | 80.6387 | 72.4933 | -0.74938 | FALSE | none | -5.5987 | -2.5467 | -6.943 | -3.513 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.266 | 0.37976 | 1.4378 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.05 | Day
2025-08-07 12:30 | 74.76 | 76.3 | 1.8958 | 80.0916 | 72.5084 | -0.81233 | FALSE | none | -5.3316 | -2.2516 | -6.6569 | -3.1053 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.266 | 0.37976 | -0.036866 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0542 | Day
2025-08-07 12:45 | 75.32 | 76.062 | 1.6831 | 79.4283 | 72.6957 | -0.44085 | FALSE | none | -4.1083 | -2.6243 | -5.1723 | -3.6099 | Normal | 0 |  |  |  | 0.56 | 0.56 | -0.238 | 0.41902 | 1.9045 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0294 | Day
2025-08-07 13:00 | 75.04 | 75.824 | 1.4467 | 78.7173 | 72.9307 | -0.54193 | FALSE | none | -3.6773 | -2.1093 | -4.6716 | -2.8923 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.238 | 0.41902 | -0.10023 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0361 | Day
2025-08-07 13:15 | 74.76 | 75.6 | 1.2188 | 78.0376 | 73.1624 | -0.6892 | FALSE | none | -3.2776 | -1.5976 | -4.2 | -2.1836 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.224 | 0.41232 | -0.13582 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0459 | Day
2025-08-07 13:30 | 74.76 | 75.39 | 0.93915 | 77.2683 | 73.5117 | -0.67082 | FALSE | none | -2.5083 | -1.2483 | -3.2462 | -1.6981 | Normal | 0 |  |  |  | 0 | 0 | -0.21 | 0.41506 | 0.50595 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0447 | Day
2025-08-07 13:45 | 75.04 | 75.25 | 0.7429 | 76.7358 | 73.7642 | -0.28268 | FALSE | none | -1.6958 | -1.2758 | -2.2099 | -1.7296 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.14 | 0.36901 | 1.1382 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0188 | Day
2025-08-07 14:00 | 74.48 | 75.096 | 0.52658 | 76.1492 | 74.0428 | -1.1698 | FALSE | none | -1.6692 | -0.43716 | -2.192 | -0.59042 | Normal | 0 |  |  |  | -0.56 | -0.56 | -0.154 | 0.37976 | -1.0691 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.078 | Day
2025-08-07 14:15 | 74.76 | 74.998 | 0.36649 | 75.731 | 74.265 | -0.64941 | FALSE | none | -0.97097 | -0.49497 | -1.2821 | -0.66649 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.098 | 0.35505 | 1.0646 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0433 | Day
2025-08-07 14:30 | 75.04 | 74.942 | 0.24503 | 75.4321 | 74.4519 | 0.39996 | FALSE | none | -0.39205 | -0.58805 | -0.51974 | -0.78984 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.056 | 0.34711 | 0.96798 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0267 | Day
2025-08-07 14:45 | 74.76 | 74.9 | 0.19271 | 75.2854 | 74.5146 | -0.72648 | FALSE | none | -0.52542 | -0.24542 | -0.6979 | -0.32936 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.042 | 0.33099 | -0.71906 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0484 | Day
2025-08-07 15:00 | 74.76 | 74.9 | 0.19271 | 75.2854 | 74.5146 | -0.72648 | FALSE | none | -0.52542 | -0.24542 | -0.6979 | -0.32936 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.27253 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0484 | Day
2025-08-07 15:15 | 74.76 | 74.886 | 0.19217 | 75.2703 | 74.5017 | -0.65566 | FALSE | none | -0.51035 | -0.25835 | -0.67802 | -0.34677 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.26446 | 0.052937 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0437 | Day
2025-08-07 15:30 | 75.04 | 74.886 | 0.19217 | 75.2703 | 74.5017 | 0.80136 | FALSE | none | -0.23035 | -0.53835 | -0.30603 | -0.7226 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.27253 | 1.0274 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0534 | Day
2025-08-07 15:45 | 75.04 | 74.886 | 0.19217 | 75.2703 | 74.5017 | 0.80136 | FALSE | none | -0.23035 | -0.53835 | -0.30603 | -0.7226 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.27253 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0534 | Day
2025-08-07 16:00 | 75.04 | 74.886 | 0.19217 | 75.2703 | 74.5017 | 0.80136 | FALSE | none | -0.23035 | -0.53835 | -0.30603 | -0.7226 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.27253 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0534 | Day
2025-08-07 16:15 | 75.04 | 74.886 | 0.19217 | 75.2703 | 74.5017 | 0.80136 | FALSE | none | -0.23035 | -0.53835 | -0.30603 | -0.7226 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.27253 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0534 | Day
2025-08-07 16:30 | 75.04 | 74.9 | 0.19271 | 75.2854 | 74.5146 | 0.72648 | FALSE | none | -0.24542 | -0.52542 | -0.32598 | -0.70512 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.26446 | -0.052937 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0484 | Day
2025-08-07 16:45 | 75.04 | 74.914 | 0.19217 | 75.2983 | 74.5297 | 0.65566 | FALSE | none | -0.25835 | -0.51035 | -0.3431 | -0.68476 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.26446 | -0.052937 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0437 | Day
2025-08-07 17:00 | 74.76 | 74.914 | 0.19217 | 75.2983 | 74.5297 | -0.80136 | FALSE | none | -0.53835 | -0.23035 | -0.71495 | -0.30907 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.27253 | -1.0274 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0534 | Day
2025-08-07 17:15 | 74.76 | 74.9 | 0.19271 | 75.2854 | 74.5146 | -0.72648 | FALSE | none | -0.52542 | -0.24542 | -0.6979 | -0.32936 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.26446 | 0.052937 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0484 | Day
2025-08-07 17:30 | 74.76 | 74.9 | 0.19271 | 75.2854 | 74.5146 | -0.72648 | FALSE | none | -0.52542 | -0.24542 | -0.6979 | -0.32936 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.25695 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0484 | Day
2025-08-07 17:45 | 74.76 | 74.872 | 0.16751 | 75.207 | 74.537 | -0.66862 | FALSE | none | -0.44702 | -0.22302 | -0.59438 | -0.2992 | Normal | 0 |  |  |  | 0 | 0 | -0.028 | 0.22066 | 0.12689 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0446 | Day
2025-08-07 18:00 | 74.76 | 74.858 | 0.1644 | 75.1868 | 74.5292 | -0.59611 | FALSE | none | -0.4268 | -0.2308 | -0.56765 | -0.30968 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.21256 | 0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0397 | Day
2025-08-07 18:15 | 75.04 | 74.872 | 0.16751 | 75.207 | 74.537 | 1.0029 | FALSE | none | -0.16702 | -0.50302 | -0.22208 | -0.67485 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.21256 | 1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0669 | Day
2025-08-07 18:30 | 75.04 | 74.886 | 0.16935 | 75.2247 | 74.5473 | 0.90938 | FALSE | none | -0.18469 | -0.49269 | -0.24552 | -0.66091 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.21256 | -0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0606 | Day
2025-08-07 18:45 | 74.76 | 74.872 | 0.16751 | 75.207 | 74.537 | -0.66862 | FALSE | none | -0.44702 | -0.22302 | -0.59438 | -0.2992 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.21256 | -1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0446 | Day
2025-08-07 19:00 | 74.76 | 74.886 | 0.14292 | 75.1718 | 74.6002 | -0.88163 | FALSE | none | -0.41183 | -0.15983 | -0.54786 | -0.21425 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.16935 | -0.082671 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Night
2025-08-07 19:15 | 75.32 | 74.914 | 0.16935 | 75.2527 | 74.5753 | 2.3975 | TRUE | upper | 0.067309 | -0.74469 | 0.089444 | -0.99858 | Extreme triggered | 1 | 2025-08-07 19:15 | 2025-08-07 23:30 | 2.3975 | 0.56 | 0.56 | 0.028 | 0.20109 | 2.6456 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.2455 | Night
2025-08-07 19:30 | 75.6 | 74.942 | 0.22756 | 75.3971 | 74.4869 | 2.8915 | TRUE | upper | 0.20287 | -1.1131 | 0.26907 | -1.4944 | Extreme/elevated | 2 | 2025-08-07 19:15 |  | 2.6445 | 0.28 | 0.28 | 0.028 | 0.20109 | 1.2532 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.3356 | Night
2025-08-07 19:45 | 76.16 | 75.012 | 0.35066 | 75.7133 | 74.3107 | 3.2738 | TRUE | upper | 0.44667 | -1.8493 | 0.58996 | -2.4886 | Persistent | 3 | 2025-08-07 19:15 |  | 2.8543 | 0.56 | 0.56 | 0.07 | 0.22019 | 2.2253 | TRUE | 2 | TRUE | TRUE | FALSE | TRUE | 0.4468 | Night
2025-08-07 20:00 | 76.44 | 75.096 | 0.46853 | 76.0331 | 74.1589 | 2.8685 | TRUE | upper | 0.40694 | -2.2811 | 0.53522 | -3.0759 | Persistent | 4 | 2025-08-07 19:15 |  | 2.8578 | 0.28 | 0.28 | 0.084 | 0.22437 | 0.87356 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.477 | Night
2025-08-07 20:15 | 77 | 75.208 | 0.62544 | 76.4589 | 73.9571 | 2.8652 | TRUE | upper | 0.54112 | -3.0429 | 0.70773 | -4.1144 | Persistent | 5 | 2025-08-07 19:15 |  | 2.8593 | 0.56 | 0.56 | 0.112 | 0.24712 | 1.8129 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.5339 | Night
2025-08-07 20:30 | 77.56 | 75.334 | 0.81494 | 76.9639 | 73.7041 | 2.7315 | TRUE | upper | 0.59612 | -3.8559 | 0.77454 | -5.2316 | Persistent | 6 | 2025-08-07 19:15 |  | 2.838 | 0.56 | 0.56 | 0.126 | 0.26446 | 1.6411 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.5821 | Night
2025-08-07 20:45 | 77.56 | 75.46 | 0.95061 | 77.3612 | 73.5588 | 2.2091 | TRUE | upper | 0.19878 | -4.0012 | 0.25695 | -5.4395 | Confirmed/Materialized Shift | 7 | 2025-08-07 19:15 |  | 2.7482 | 0 | 0 | 0.126 | 0.26446 | -0.47644 | FALSE | 2 | FALSE | TRUE | TRUE | FALSE | 0.6044 | Night
2025-08-07 21:00 | 78.4 | 75.628 | 1.1487 | 77.9255 | 73.3305 | 2.4131 | TRUE | upper | 0.47453 | -5.0695 | 0.60895 | -6.9132 | Confirmed/Materialized Shift | 8 | 2025-08-07 19:15 |  | 2.7063 | 0.84 | 0.84 | 0.168 | 0.30672 | 2.1909 | TRUE | 3 | TRUE | TRUE | TRUE | TRUE | 0.6466 | Night
2025-08-07 21:15 | 78.4 | 75.796 | 1.2946 | 78.3853 | 73.2067 | 2.0114 | TRUE | upper | 0.014707 | -5.1933 | 0.018763 | -7.094 | Confirmed/Materialized Shift | 9 | 2025-08-07 19:15 |  | 2.6291 | 0 | 0 | 0.168 | 0.30672 | -0.54772 | FALSE | 3 | FALSE | TRUE | TRUE | FALSE | 0.6198 | Night
2025-08-07 21:30 | 79.24 | 76.006 | 1.4913 | 78.9885 | 73.0235 | 2.1686 | TRUE | upper | 0.25147 | -6.2165 | 0.31836 | -8.5131 | Confirmed/Materialized Shift | 10 | 2025-08-07 19:15 |  | 2.583 | 0.84 | 0.84 | 0.21 | 0.33839 | 1.8618 | FALSE | 3 | FALSE | TRUE | TRUE | FALSE | 0.6303 | Night
2025-08-07 21:45 | 79.52 | 76.23 | 1.6649 | 79.5598 | 72.9002 | 1.9761 | FALSE | none | -0.039776 | -6.6198 | -0.049996 | -9.0806 | Confirmed/Materialized Shift | 11 | 2025-08-07 19:15 |  | 2.5278 | 0.28 | 0.28 | 0.224 | 0.33502 | 0.16716 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5889 | Night
2025-08-07 22:00 | 79.8 | 76.482 | 1.8061 | 80.0942 | 72.8698 | 1.8371 | FALSE | none | -0.29423 | -6.9302 | -0.36736 | -9.5104 | Confirmed/Materialized Shift | 12 | 2025-08-07 19:15 |  | 2.4703 | 0.28 | 0.28 | 0.252 | 0.31338 | 0.089349 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5796 | Night
2025-08-07 22:15 | 80.08 | 76.748 | 1.9269 | 80.6018 | 72.8942 | 1.7292 | FALSE | none | -0.52176 | -7.1858 | -0.64733 | -9.8578 | Confirmed/Materialized Shift | 13 | 2025-08-07 19:15 |  | 2.4133 | 0.28 | 0.28 | 0.266 | 0.30773 | 0.045494 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5439 | Night
2025-08-07 22:30 | 80.36 | 77.028 | 2.0271 | 81.0821 | 72.9739 | 1.6438 | FALSE | none | -0.72213 | -7.3861 | -0.89061 | -10.1216 | Confirmed/Materialized Shift | 14 | 2025-08-07 19:15 |  | 2.3583 | 0.28 | 0.28 | 0.28 | 0.3013 | 2.3951e-15 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5382 | Night
2025-08-07 22:45 | 80.08 | 77.294 | 2.0625 | 81.4191 | 73.1689 | 1.3508 | FALSE | none | -1.3391 | -6.9111 | -1.6446 | -9.4453 | Confirmed/Materialized Shift | 15 | 2025-08-07 19:15 |  | 2.2911 | -0.28 | -0.28 | 0.266 | 0.32086 | -1.7017 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5186 | Night
2025-08-07 23:00 | 80.08 | 77.56 | 2.0616 | 81.6832 | 73.4368 | 1.2224 | FALSE | none | -1.6032 | -6.6432 | -1.9627 | -9.0461 | Confirmed/Materialized Shift | 16 | 2025-08-07 19:15 |  | 2.2243 | 0 | 0 | 0.266 | 0.32086 | -0.82902 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5101 | Night
2025-08-07 23:15 | 80.08 | 77.812 | 2.0453 | 81.9026 | 73.7214 | 1.1089 | FALSE | none | -1.8226 | -6.3586 | -2.2253 | -8.6252 | Confirmed/Materialized Shift | 17 | 2025-08-07 19:15 |  | 2.1587 | 0 | 0 | 0.252 | 0.32628 | -0.77234 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5025 | Night
2025-08-07 23:30 | 79.8 | 78.05 | 1.9817 | 82.0134 | 74.0866 | 0.88307 | FALSE | none | -2.2134 | -5.7134 | -2.6989 | -7.7118 | Persistence ends | 0 |  |  |  | -0.28 | -0.28 | 0.238 | 0.34323 | -1.5092 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0589 | Night
2025-08-07 23:45 | 80.08 | 78.316 | 1.8708 | 82.0576 | 74.5744 | 0.94291 | FALSE | none | -1.9776 | -5.5056 | -2.41 | -7.3827 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.266 | 0.32086 | 0.043633 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0629 | Night
2025-08-08 | 79.8 | 78.568 | 1.6981 | 81.9642 | 75.1718 | 0.72553 | FALSE | none | -2.1642 | -4.6282 | -2.6404 | -6.1568 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.252 | 0.33869 | -1.5708 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0484 | Night
2025-08-08 00:15 | 79.8 | 78.792 | 1.5347 | 81.8614 | 75.7226 | 0.65681 | FALSE | none | -2.0614 | -4.0774 | -2.5182 | -5.3847 | Normal | 0 |  |  |  | 0 | 0 | 0.224 | 0.33502 | -0.66862 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0438 | Night
2025-08-08 00:30 | 80.08 | 79.016 | 1.3614 | 81.7389 | 76.2931 | 0.78152 | FALSE | none | -1.6589 | -3.7869 | -2.0295 | -4.9636 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.224 | 0.33502 | 0.16716 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0521 | Night
2025-08-08 00:45 | 80.08 | 79.212 | 1.2014 | 81.6148 | 76.8092 | 0.72248 | FALSE | none | -1.5348 | -3.2708 | -1.8806 | -4.2584 | Normal | 0 |  |  |  | 0 | 0 | 0.196 | 0.3288 | -0.59611 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0482 | Night
2025-08-08 01:00 | 79.8 | 79.38 | 1.0136 | 81.4073 | 77.3527 | 0.41435 | FALSE | none | -1.6073 | -2.4473 | -1.9744 | -3.1638 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.168 | 0.34473 | -1.2996 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0276 | Night
2025-08-08 01:15 | 80.08 | 79.534 | 0.85449 | 81.243 | 77.825 | 0.63898 | FALSE | none | -1.163 | -2.255 | -1.4315 | -2.8975 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.154 | 0.33347 | 0.37784 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0426 | Night
2025-08-08 01:30 | 79.8 | 79.646 | 0.71804 | 81.0821 | 78.2099 | 0.21447 | FALSE | none | -1.2821 | -1.5901 | -1.5812 | -2.0331 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.112 | 0.33254 | -1.1788 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0143 | Night
2025-08-08 01:45 | 80.08 | 79.772 | 0.52893 | 80.8299 | 78.7141 | 0.58231 | FALSE | none | -0.74985 | -1.3659 | -0.9277 | -1.7352 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.126 | 0.33347 | 0.46181 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0388 | Night
2025-08-08 02:00 | 79.8 | 79.842 | 0.41902 | 80.68 | 79.004 | -0.10023 | FALSE | none | -0.88003 | -0.79603 | -1.0908 | -1.0076 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.07 | 0.29958 | -1.1683 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0067 | Night
2025-08-08 02:15 | 80.08 | 79.926 | 0.24837 | 80.4227 | 79.4293 | 0.62004 | FALSE | none | -0.34274 | -0.65074 | -0.42618 | -0.81927 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.084 | 0.30266 | 0.64759 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0413 | Night
2025-08-08 02:30 | 79.8 | 79.954 | 0.19217 | 80.3383 | 79.5697 | -0.80136 | FALSE | none | -0.53835 | -0.23035 | -0.6701 | -0.28949 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.028 | 0.25533 | -1.2063 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0534 | Night
2025-08-08 02:45 | 80.36 | 79.996 | 0.18395 | 80.3639 | 79.6281 | 1.9789 | FALSE | none | -0.0038901 | -0.73189 | -0.0048407 | -0.91914 | Normal | 0 |  |  |  | 0.56 | 0.56 | 0.042 | 0.27666 | 1.8723 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1319 | Night
2025-08-08 03:00 | 80.08 | 80.01 | 0.17883 | 80.3677 | 79.6523 | 0.39144 | FALSE | none | -0.28765 | -0.42765 | -0.35792 | -0.5369 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.014 | 0.27963 | -1.0514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0261 | Night
2025-08-08 03:15 | 80.08 | 80.01 | 0.17883 | 80.3677 | 79.6523 | 0.39144 | FALSE | none | -0.28765 | -0.42765 | -0.35792 | -0.5369 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.27253 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0261 | Night
2025-08-08 03:30 | 79.8 | 79.982 | 0.1644 | 80.3108 | 79.6532 | -1.1071 | FALSE | none | -0.5108 | -0.1468 | -0.63603 | -0.1843 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.028 | 0.27101 | -0.92984 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0738 | Night
2025-08-08 03:45 | 79.8 | 79.968 | 0.16751 | 80.303 | 79.633 | -1.0029 | FALSE | none | -0.50302 | -0.16702 | -0.6264 | -0.20973 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.26446 | 0.052937 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0669 | Night
2025-08-08 04:00 | 80.08 | 79.968 | 0.16751 | 80.303 | 79.633 | 0.66862 | FALSE | none | -0.22302 | -0.44702 | -0.27772 | -0.56135 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.27253 | 1.0274 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0446 | Night
2025-08-08 04:15 | 79.52 | 79.94 | 0.19271 | 80.3254 | 79.5546 | -2.1794 | TRUE | lower | -0.80542 | 0.034582 | -1.0027 | 0.043469 | Extreme triggered | 1 | 2025-08-08 04:15 | 2025-08-08 04:30 | 2.1794 | -0.56 | -0.56 | -0.028 | 0.29992 | -1.7738 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.2024 | Night
2025-08-08 04:30 | 79.8 | 79.94 | 0.19271 | 80.3254 | 79.5546 | -0.72648 | FALSE | none | -0.52542 | -0.24542 | -0.65411 | -0.30849 | Persistence ends | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.3013 | 0.92932 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0484 | Night
2025-08-08 04:45 | 80.08 | 79.94 | 0.19271 | 80.3254 | 79.5546 | 0.72648 | FALSE | none | -0.24542 | -0.52542 | -0.30553 | -0.66045 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.3013 | 0.92932 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0484 | Night
2025-08-08 05:00 | 80.08 | 79.954 | 0.19217 | 80.3383 | 79.5697 | 0.65566 | FALSE | none | -0.25835 | -0.51035 | -0.32157 | -0.64138 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.29402 | -0.047616 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0437 | Night
2025-08-08 05:15 | 80.08 | 79.968 | 0.19056 | 80.3491 | 79.5869 | 0.58775 | FALSE | none | -0.26911 | -0.49311 | -0.33493 | -0.61959 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.29402 | -0.047616 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0392 | Night
2025-08-08 05:30 | 80.08 | 79.968 | 0.19056 | 80.3491 | 79.5869 | 0.58775 | FALSE | none | -0.26911 | -0.49311 | -0.33493 | -0.61959 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.28727 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0392 | Night
2025-08-08 05:45 | 80.08 | 79.968 | 0.19056 | 80.3491 | 79.5869 | 0.58775 | FALSE | none | -0.26911 | -0.49311 | -0.33493 | -0.61959 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.28727 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0392 | Night
2025-08-08 06:00 | 79.8 | 79.968 | 0.19056 | 80.3491 | 79.5869 | -0.88163 | FALSE | none | -0.54911 | -0.21311 | -0.68341 | -0.26777 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.28727 | -0.97468 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Night
2025-08-08 06:15 | 79.8 | 79.954 | 0.19217 | 80.3383 | 79.5697 | -0.80136 | FALSE | none | -0.53835 | -0.23035 | -0.6701 | -0.28949 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.27963 | 0.050066 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0534 | Night
2025-08-08 06:30 | 79.8 | 79.954 | 0.19217 | 80.3383 | 79.5697 | -0.80136 | FALSE | none | -0.53835 | -0.23035 | -0.6701 | -0.28949 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.27253 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0534 | Night
2025-08-08 06:45 | 79.8 | 79.94 | 0.19271 | 80.3254 | 79.5546 | -0.72648 | FALSE | none | -0.52542 | -0.24542 | -0.65411 | -0.30849 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.26446 | 0.052937 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0484 | Night
2025-08-08 07:00 | 79.8 | 79.94 | 0.19271 | 80.3254 | 79.5546 | -0.72648 | FALSE | none | -0.52542 | -0.24542 | -0.65411 | -0.30849 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.25695 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0484 | Day
2025-08-08 07:15 | 79.8 | 79.926 | 0.19217 | 80.3103 | 79.5417 | -0.65566 | FALSE | none | -0.51035 | -0.25835 | -0.63547 | -0.32479 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.24837 | 0.056367 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0437 | Day
2025-08-08 07:30 | 79.52 | 79.912 | 0.2111 | 80.3342 | 79.4898 | -1.8569 | FALSE | none | -0.8142 | -0.030205 | -1.0135 | -0.037998 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.24837 | -1.071 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1238 | Day
2025-08-08 07:45 | 79.8 | 79.884 | 0.18395 | 80.2519 | 79.5161 | -0.45666 | FALSE | none | -0.45189 | -0.28389 | -0.56309 | -0.35702 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.028 | 0.22066 | 1.3958 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0304 | Day
2025-08-08 08:00 | 79.8 | 79.87 | 0.17883 | 80.2277 | 79.5123 | -0.39144 | FALSE | none | -0.42765 | -0.28765 | -0.53305 | -0.36177 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.21256 | 0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0261 | Day
2025-08-08 08:15 | 79.52 | 79.842 | 0.18783 | 80.2177 | 79.4663 | -1.7143 | FALSE | none | -0.69766 | -0.053659 | -0.86971 | -0.067525 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.028 | 0.22066 | -1.142 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1143 | Day
2025-08-08 08:30 | 78.68 | 79.786 | 0.32086 | 80.4277 | 79.1443 | -3.447 | TRUE | lower | -1.7477 | 0.46428 | -2.173 | 0.58662 | Extreme triggered | 1 | 2025-08-08 08:30 | 2025-08-08 11:45 | 3.447 | -0.84 | -0.84 | -0.056 | 0.28147 | -2.7854 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.3155 | Day
2025-08-08 08:45 | 77.84 | 79.688 | 0.5405 | 80.769 | 78.607 | -3.419 | TRUE | lower | -2.929 | 0.76699 | -3.6264 | 0.97573 | Extreme/elevated | 2 | 2025-08-08 08:30 |  | 3.433 | -0.84 | -0.84 | -0.098 | 0.33099 | -2.2418 | TRUE | 2 | TRUE | FALSE | FALSE | TRUE | 0.3994 | Day
2025-08-08 09:00 | 77 | 79.534 | 0.79961 | 81.1332 | 77.9348 | -3.1691 | TRUE | lower | -4.1332 | 0.93478 | -5.0944 | 1.1994 | Persistent | 3 | 2025-08-08 08:30 |  | 3.345 | -0.84 | -0.84 | -0.154 | 0.35736 | -1.9196 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.4398 | Day
2025-08-08 09:15 | 77 | 79.408 | 0.98011 | 81.3682 | 77.4478 | -2.4569 | TRUE | lower | -4.3682 | 0.44779 | -5.3684 | 0.57818 | Persistent | 4 | 2025-08-08 08:30 |  | 3.123 | 0 | 0 | -0.126 | 0.34563 | 0.36456 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.4495 | Day
2025-08-08 09:30 | 75.88 | 79.212 | 1.2519 | 81.7157 | 76.7083 | -2.6616 | TRUE | lower | -5.8357 | 0.82826 | -7.1415 | 1.0798 | Persistent | 5 | 2025-08-08 08:30 |  | 3.0307 | -1.12 | -1.12 | -0.196 | 0.39702 | -2.3273 | TRUE | 3 | TRUE | TRUE | FALSE | TRUE | 0.5489 | Day
2025-08-08 09:45 | 75.88 | 79.002 | 1.4372 | 81.8763 | 76.1277 | -2.1723 | TRUE | lower | -5.9963 | 0.24768 | -7.3236 | 0.32535 | Persistent | 6 | 2025-08-08 08:30 |  | 2.8877 | 0 | 0 | -0.21 | 0.38408 | 0.54676 | FALSE | 3 | FALSE | TRUE | FALSE | FALSE | 0.5734 | Day
2025-08-08 10:00 | 75.04 | 78.75 | 1.6624 | 82.0748 | 75.4252 | -2.2317 | TRUE | lower | -7.0348 | 0.38518 | -8.5712 | 0.51068 | Confirmed/Materialized Shift | 7 | 2025-08-08 08:30 |  | 2.7939 | -0.84 | -0.84 | -0.252 | 0.40525 | -1.451 | FALSE | 3 | FALSE | TRUE | TRUE | FALSE | 0.6345 | Day
2025-08-08 10:15 | 75.04 | 78.498 | 1.8243 | 82.1466 | 74.8494 | -1.8955 | FALSE | none | -7.1066 | -0.19061 | -8.6511 | -0.25465 | Confirmed/Materialized Shift | 8 | 2025-08-08 08:30 |  | 2.6816 | 0 | 0 | -0.252 | 0.40525 | 0.62184 | FALSE | 3 | FALSE | FALSE | TRUE | FALSE | 0.6121 | Day
2025-08-08 10:30 | 74.76 | 78.232 | 1.964 | 82.16 | 74.304 | -1.7678 | FALSE | none | -7.4 | -0.45599 | -9.0068 | -0.61368 | Confirmed/Materialized Shift | 9 | 2025-08-08 08:30 |  | 2.5801 | -0.28 | -0.28 | -0.266 | 0.4009 | -0.034922 | FALSE | 3 | FALSE | FALSE | TRUE | FALSE | 0.6036 | Day
2025-08-08 10:45 | 75.04 | 77.98 | 2.0364 | 82.0528 | 73.9072 | -1.4437 | FALSE | none | -7.0128 | -1.1328 | -8.5467 | -1.5327 | Confirmed/Materialized Shift | 10 | 2025-08-08 08:30 |  | 2.4665 | 0.28 | 0.28 | -0.252 | 0.41531 | 1.281 | FALSE | 3 | FALSE | FALSE | TRUE | FALSE | 0.582 | Day
2025-08-08 11:00 | 74.76 | 77.728 | 2.1099 | 81.9477 | 73.5083 | -1.4067 | FALSE | none | -7.1877 | -1.2517 | -8.7711 | -1.7028 | Confirmed/Materialized Shift | 11 | 2025-08-08 08:30 |  | 2.3701 | -0.28 | -0.28 | -0.252 | 0.41531 | -0.06742 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5509 | Day
2025-08-08 11:15 | 75.04 | 77.49 | 2.1322 | 81.7543 | 73.2257 | -1.1491 | FALSE | none | -6.7143 | -1.8143 | -8.2128 | -2.4778 | Confirmed/Materialized Shift | 12 | 2025-08-08 08:30 |  | 2.2684 | 0.28 | 0.28 | -0.238 | 0.42875 | 1.2082 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5052 | Day
2025-08-08 11:30 | 75.04 | 77.252 | 2.1264 | 81.5048 | 72.9992 | -1.0403 | FALSE | none | -6.4648 | -2.0408 | -7.9318 | -2.7957 | Confirmed/Materialized Shift | 13 | 2025-08-08 08:30 |  | 2.1739 | 0 | 0 | -0.238 | 0.42875 | 0.5551 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.4979 | Day
2025-08-08 11:45 | 75.04 | 77.014 | 2.0923 | 81.1986 | 72.8294 | -0.94345 | FALSE | none | -6.1586 | -2.2106 | -7.5847 | -3.0354 | Persistence ends | 0 |  |  |  | 0 | 0 | -0.238 | 0.42875 | 0.5551 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0915 | Day
2025-08-08 12:00 | 75.04 | 76.776 | 2.0285 | 80.833 | 72.719 | -0.85581 | FALSE | none | -5.793 | -2.321 | -7.1666 | -3.1917 | Normal | 0 |  |  |  | 0 | 0 | -0.238 | 0.42875 | 0.5551 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0571 | Day
2025-08-08 12:15 | 75.04 | 76.538 | 1.932 | 80.4019 | 72.6741 | -0.77538 | FALSE | none | -5.3619 | -2.3659 | -6.6689 | -3.2555 | Normal | 0 |  |  |  | 0 | 0 | -0.238 | 0.42875 | 0.5551 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0517 | Day
2025-08-08 12:30 | 74.76 | 76.3 | 1.8361 | 79.9722 | 72.6278 | -0.83874 | FALSE | none | -5.2122 | -2.1322 | -6.5175 | -2.9357 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.238 | 0.42875 | -0.097959 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0559 | Day
2025-08-08 12:45 | 75.04 | 76.062 | 1.6584 | 79.3789 | 72.7451 | -0.61624 | FALSE | none | -4.3389 | -2.2949 | -5.466 | -3.1547 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.238 | 0.42875 | 1.2082 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0411 | Day
2025-08-08 13:00 | 74.76 | 75.81 | 1.4274 | 78.6647 | 72.9553 | -0.73562 | FALSE | none | -3.9047 | -1.8047 | -4.9638 | -2.4737 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.252 | 0.42513 | -0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.049 | Day
2025-08-08 13:15 | 74.76 | 75.572 | 1.1451 | 77.8623 | 73.2817 | -0.70908 | FALSE | none | -3.1023 | -1.4783 | -3.9843 | -2.0173 | Normal | 0 |  |  |  | 0 | 0 | -0.238 | 0.42875 | 0.5551 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0473 | Day
2025-08-08 13:30 | 74.76 | 75.376 | 0.89286 | 77.1617 | 73.5903 | -0.68992 | FALSE | none | -2.4017 | -1.1697 | -3.1126 | -1.5895 | Normal | 0 |  |  |  | 0 | 0 | -0.196 | 0.40728 | 0.48124 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.046 | Day
2025-08-08 13:45 | 74.76 | 75.222 | 0.68751 | 76.597 | 73.847 | -0.67199 | FALSE | none | -1.837 | -0.91302 | -2.3983 | -1.2364 | Normal | 0 |  |  |  | 0 | 0 | -0.154 | 0.37976 | 0.40552 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0448 | Day
2025-08-08 14:00 | 75.04 | 75.124 | 0.54582 | 76.2156 | 74.0324 | -0.1539 | FALSE | none | -1.1756 | -1.0076 | -1.5425 | -1.3611 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.098 | 0.35505 | 1.0646 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0103 | Day
2025-08-08 14:15 | 75.04 | 75.026 | 0.32086 | 75.6677 | 74.3843 | 0.043633 | FALSE | none | -0.62772 | -0.65572 | -0.82958 | -0.88153 | Normal | 0 |  |  |  | 0 | 0 | -0.098 | 0.35505 | 0.27602 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0029 | Day
2025-08-08 14:30 | 75.04 | 74.984 | 0.25044 | 75.4849 | 74.4831 | 0.22361 | FALSE | none | -0.44488 | -0.55688 | -0.58936 | -0.74766 | Normal | 0 |  |  |  | 0 | 0 | -0.042 | 0.26132 | 0.16072 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0149 | Day
2025-08-08 14:45 | 74.76 | 74.928 | 0.14073 | 75.2095 | 74.6465 | -1.1937 | FALSE | none | -0.44947 | -0.11347 | -0.59762 | -0.15201 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.056 | 0.26641 | -0.84082 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0796 | Day
2025-08-08 15:00 | 75.04 | 74.928 | 0.14073 | 75.2095 | 74.6465 | 0.79582 | FALSE | none | -0.16947 | -0.39347 | -0.22533 | -0.52711 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.20313 | 1.3784 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-08 15:15 | 74.76 | 74.914 | 0.14292 | 75.1998 | 74.6282 | -1.0775 | FALSE | none | -0.43983 | -0.13183 | -0.58489 | -0.17665 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.21256 | -1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Day
2025-08-08 15:30 | 74.76 | 74.914 | 0.14292 | 75.1998 | 74.6282 | -1.0775 | FALSE | none | -0.43983 | -0.13183 | -0.58489 | -0.17665 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.20313 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Day
2025-08-08 15:45 | 75.04 | 74.914 | 0.14292 | 75.1998 | 74.6282 | 0.88163 | FALSE | none | -0.15983 | -0.41183 | -0.21255 | -0.55185 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.20313 | 1.3784 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-08 16:00 | 75.04 | 74.928 | 0.14073 | 75.2095 | 74.6465 | 0.79582 | FALSE | none | -0.16947 | -0.39347 | -0.22533 | -0.52711 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.19217 | -0.072851 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-08 16:15 | 74.76 | 74.914 | 0.14292 | 75.1998 | 74.6282 | -1.0775 | FALSE | none | -0.43983 | -0.13183 | -0.58489 | -0.17665 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.19217 | -1.3842 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Day
2025-08-08 16:30 | 75.04 | 74.914 | 0.14292 | 75.1998 | 74.6282 | 0.88163 | FALSE | none | -0.15983 | -0.41183 | -0.21255 | -0.55185 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.20313 | 1.3784 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-08 16:45 | 74.76 | 74.9 | 0.14364 | 75.1873 | 74.6127 | -0.97468 | FALSE | none | -0.42727 | -0.14727 | -0.56828 | -0.19738 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.21256 | -1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.065 | Day
2025-08-08 17:00 | 74.76 | 74.886 | 0.14292 | 75.1718 | 74.6002 | -0.88163 | FALSE | none | -0.41183 | -0.15983 | -0.54786 | -0.21425 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.21256 | 0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-08 17:15 | 74.76 | 74.872 | 0.14073 | 75.1535 | 74.5905 | -0.79582 | FALSE | none | -0.39347 | -0.16947 | -0.52356 | -0.2272 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.21256 | 0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-08 17:30 | 74.76 | 74.872 | 0.14073 | 75.1535 | 74.5905 | -0.79582 | FALSE | none | -0.39347 | -0.16947 | -0.52356 | -0.2272 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.20313 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-08 17:45 | 74.76 | 74.858 | 0.13702 | 75.132 | 74.584 | -0.71522 | FALSE | none | -0.37204 | -0.17604 | -0.49518 | -0.23603 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.19217 | 0.072851 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0477 | Day
2025-08-08 18:00 | 75.04 | 74.872 | 0.14073 | 75.1535 | 74.5905 | 1.1937 | FALSE | none | -0.11347 | -0.44947 | -0.15098 | -0.60258 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.19217 | 1.3842 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0796 | Day
2025-08-08 18:15 | 75.04 | 74.886 | 0.14292 | 75.1718 | 74.6002 | 1.0775 | FALSE | none | -0.13183 | -0.43983 | -0.17538 | -0.58959 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.19217 | -0.072851 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Day
2025-08-08 18:30 | 75.04 | 74.9 | 0.14364 | 75.1873 | 74.6127 | 0.97468 | FALSE | none | -0.14727 | -0.42727 | -0.19588 | -0.57266 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.19217 | -0.072851 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.065 | Day
2025-08-08 18:45 | 75.04 | 74.914 | 0.14292 | 75.1998 | 74.6282 | 0.88163 | FALSE | none | -0.15983 | -0.41183 | -0.21255 | -0.55185 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.19217 | -0.072851 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-08 19:00 | 74.76 | 74.9 | 0.14364 | 75.1873 | 74.6127 | -0.97468 | FALSE | none | -0.42727 | -0.14727 | -0.56828 | -0.19738 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.19217 | -1.3842 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.065 | Night
2025-08-08 19:15 | 75.32 | 74.914 | 0.16935 | 75.2527 | 74.5753 | 2.3975 | TRUE | upper | 0.067309 | -0.74469 | 0.089444 | -0.99858 | Extreme triggered | 1 | 2025-08-08 19:15 | 2025-08-09 | 2.3975 | 0.56 | 0.56 | 0.014 | 0.23116 | 2.362 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.2455 | Night
2025-08-08 19:30 | 75.6 | 74.942 | 0.22756 | 75.3971 | 74.4869 | 2.8915 | TRUE | upper | 0.20287 | -1.1131 | 0.26907 | -1.4944 | Extreme/elevated | 2 | 2025-08-08 19:15 |  | 2.6445 | 0.28 | 0.28 | 0.028 | 0.23863 | 1.056 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.3356 | Night
2025-08-08 19:45 | 76.16 | 75.012 | 0.35066 | 75.7133 | 74.3107 | 3.2738 | TRUE | upper | 0.44667 | -1.8493 | 0.58996 | -2.4886 | Persistent | 3 | 2025-08-08 19:15 |  | 2.8543 | 0.56 | 0.56 | 0.07 | 0.25493 | 1.9221 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4183 | Night
2025-08-08 20:00 | 76.72 | 75.096 | 0.51869 | 76.1334 | 74.0586 | 3.131 | TRUE | upper | 0.58663 | -2.6614 | 0.77053 | -3.5936 | Persistent | 4 | 2025-08-08 19:15 |  | 2.9234 | 0.56 | 0.56 | 0.084 | 0.27404 | 1.737 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4659 | Night
2025-08-08 20:15 | 77 | 75.208 | 0.66385 | 76.5357 | 73.8803 | 2.6994 | TRUE | upper | 0.46431 | -3.1197 | 0.60666 | -4.2226 | Persistent | 5 | 2025-08-08 19:15 |  | 2.8786 | 0.28 | 0.28 | 0.112 | 0.26329 | 0.63808 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4942 | Night
2025-08-08 20:30 | 77.28 | 75.334 | 0.79961 | 76.9332 | 73.7348 | 2.4337 | TRUE | upper | 0.34678 | -3.5452 | 0.45076 | -4.8081 | Persistent | 6 | 2025-08-08 19:15 |  | 2.8045 | 0.28 | 0.28 | 0.126 | 0.26446 | 0.58231 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.5337 | Night
2025-08-08 20:45 | 77.84 | 75.474 | 0.97197 | 77.4179 | 73.5301 | 2.4342 | TRUE | upper | 0.42207 | -4.3099 | 0.54518 | -5.8615 | Confirmed/Materialized Shift | 7 | 2025-08-08 19:15 |  | 2.7516 | 0.56 | 0.56 | 0.14 | 0.28 | 1.5 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5909 | Night
2025-08-08 21:00 | 78.4 | 75.642 | 1.1643 | 77.9707 | 73.3133 | 2.3687 | TRUE | upper | 0.42931 | -5.0867 | 0.5506 | -6.9383 | Confirmed/Materialized Shift | 8 | 2025-08-08 19:15 |  | 2.7037 | 0.56 | 0.56 | 0.168 | 0.29296 | 1.3381 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5865 | Night
2025-08-08 21:15 | 78.4 | 75.824 | 1.2962 | 78.4165 | 73.2315 | 1.9873 | FALSE | none | -0.016478 | -5.1685 | -0.021014 | -7.0577 | Confirmed/Materialized Shift | 9 | 2025-08-08 19:15 |  | 2.6241 | 0 | 0 | 0.182 | 0.27666 | -0.65784 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5611 | Night
2025-08-08 21:30 | 79.24 | 76.034 | 1.4885 | 79.011 | 73.057 | 2.1538 | TRUE | upper | 0.229 | -6.183 | 0.28984 | -8.4632 | Confirmed/Materialized Shift | 10 | 2025-08-08 19:15 |  | 2.5771 | 0.84 | 0.84 | 0.21 | 0.31305 | 2.0125 | TRUE | 2 | TRUE | TRUE | TRUE | TRUE | 0.6007 | Night
2025-08-08 21:45 | 79.52 | 76.272 | 1.6463 | 79.5645 | 72.9795 | 1.973 | FALSE | none | -0.044515 | -6.5405 | -0.055949 | -8.9621 | Confirmed/Materialized Shift | 11 | 2025-08-08 19:15 |  | 2.5222 | 0.28 | 0.28 | 0.238 | 0.2912 | 0.14423 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5601 | Night
2025-08-08 22:00 | 79.8 | 76.524 | 1.7827 | 80.0894 | 72.9586 | 1.8376 | FALSE | none | -0.28944 | -6.8414 | -0.36139 | -9.3772 | Confirmed/Materialized Shift | 12 | 2025-08-08 19:15 |  | 2.4651 | 0.28 | 0.28 | 0.252 | 0.28583 | 0.097959 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5511 | Night
2025-08-08 22:15 | 79.8 | 76.776 | 1.8741 | 80.5242 | 73.0278 | 1.6136 | FALSE | none | -0.72424 | -6.7722 | -0.8994 | -9.2735 | Confirmed/Materialized Shift | 13 | 2025-08-08 19:15 |  | 2.3996 | 0 | 0 | 0.252 | 0.28583 | -0.88163 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5361 | Night
2025-08-08 22:30 | 80.08 | 77.042 | 1.949 | 80.9399 | 73.1441 | 1.5588 | FALSE | none | -0.85994 | -6.9359 | -1.0624 | -9.4826 | Confirmed/Materialized Shift | 14 | 2025-08-08 19:15 |  | 2.3396 | 0.28 | 0.28 | 0.266 | 0.27963 | 0.050066 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5325 | Night
2025-08-08 22:45 | 79.8 | 77.294 | 1.9642 | 81.2223 | 73.3657 | 1.2759 | FALSE | none | -1.4223 | -6.4343 | -1.7511 | -8.7702 | Confirmed/Materialized Shift | 15 | 2025-08-08 19:15 |  | 2.2687 | -0.28 | -0.28 | 0.252 | 0.29992 | -1.7738 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5136 | Night
2025-08-08 23:00 | 79.8 | 77.532 | 1.965 | 81.4621 | 73.6019 | 1.1542 | FALSE | none | -1.6621 | -6.1981 | -2.0403 | -8.4211 | Confirmed/Materialized Shift | 16 | 2025-08-08 19:15 |  | 2.199 | 0 | 0 | 0.238 | 0.30504 | -0.78023 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5055 | Night
2025-08-08 23:15 | 80.08 | 77.784 | 1.9518 | 81.6875 | 73.8805 | 1.1764 | FALSE | none | -1.6075 | -6.1995 | -1.9679 | -8.3913 | Confirmed/Materialized Shift | 17 | 2025-08-08 19:15 |  | 2.1388 | 0.28 | 0.28 | 0.252 | 0.29992 | 0.093357 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.507 | Night
2025-08-08 23:30 | 80.08 | 78.036 | 1.9036 | 81.8432 | 74.2288 | 1.0737 | FALSE | none | -1.7632 | -5.8512 | -2.1544 | -7.8827 | Confirmed/Materialized Shift | 18 | 2025-08-08 19:15 |  | 2.0797 | 0 | 0 | 0.252 | 0.29992 | -0.84022 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5002 | Night
2025-08-08 23:45 | 80.36 | 78.302 | 1.8333 | 81.9687 | 74.6353 | 1.1225 | FALSE | none | -1.6087 | -5.7247 | -1.9625 | -7.6702 | Confirmed/Materialized Shift | 19 | 2025-08-08 19:15 |  | 2.0293 | 0.28 | 0.28 | 0.266 | 0.29402 | 0.047616 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5034 | Night
2025-08-09 | 79.8 | 78.554 | 1.6589 | 81.8719 | 75.2361 | 0.75109 | FALSE | none | -2.0719 | -4.5639 | -2.5306 | -6.066 | Persistence ends | 0 |  |  |  | -0.56 | -0.56 | 0.252 | 0.32628 | -2.4887 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0786 | Night
2025-08-09 00:15 | 79.8 | 78.778 | 1.4935 | 81.765 | 75.791 | 0.68431 | FALSE | none | -1.965 | -4.009 | -2.4032 | -5.2895 | Normal | 0 |  |  |  | 0 | 0 | 0.224 | 0.32246 | -0.69465 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0742 | Night
2025-08-09 00:30 | 80.08 | 79.002 | 1.3173 | 81.6366 | 76.3674 | 0.81833 | FALSE | none | -1.5566 | -3.7126 | -1.9068 | -4.8615 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.224 | 0.32246 | 0.17366 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0831 | Night
2025-08-09 00:45 | 80.08 | 79.198 | 1.1537 | 81.5053 | 76.8907 | 0.76452 | FALSE | none | -1.4253 | -3.1893 | -1.7488 | -4.1479 | Normal | 0 |  |  |  | 0 | 0 | 0.196 | 0.316 | -0.62025 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0795 | Night
2025-08-09 01:00 | 79.8 | 79.352 | 1.0009 | 81.3539 | 77.3501 | 0.44758 | FALSE | none | -1.5539 | -2.4499 | -1.91 | -3.1672 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.154 | 0.32086 | -1.3526 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0584 | Night
2025-08-09 01:15 | 79.8 | 79.492 | 0.83705 | 81.1661 | 77.8179 | 0.36796 | FALSE | none | -1.3661 | -1.9821 | -1.6831 | -2.5471 | Normal | 0 |  |  |  | 0 | 0 | 0.14 | 0.32118 | -0.43589 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Night
2025-08-09 01:30 | 80.08 | 79.632 | 0.66385 | 80.9597 | 78.3043 | 0.67486 | FALSE | none | -0.87969 | -1.7757 | -1.0866 | -2.2677 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.14 | 0.32118 | 0.43589 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0736 | Night
2025-08-09 01:45 | 79.8 | 79.73 | 0.51289 | 80.7558 | 78.7042 | 0.13648 | FALSE | none | -0.95577 | -1.0958 | -1.1835 | -1.3923 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.098 | 0.31828 | -1.1876 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0377 | Night
2025-08-09 02:00 | 80.08 | 79.814 | 0.41106 | 80.6361 | 78.9919 | 0.6471 | FALSE | none | -0.55613 | -1.0881 | -0.68967 | -1.3775 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.084 | 0.30266 | 0.64759 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0717 | Night
2025-08-09 02:15 | 79.8 | 79.884 | 0.24206 | 80.3681 | 79.3999 | -0.34702 | FALSE | none | -0.56812 | -0.40012 | -0.7069 | -0.50393 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.07 | 0.31305 | -1.118 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0517 | Night
2025-08-09 02:30 | 80.08 | 79.926 | 0.19217 | 80.3103 | 79.5417 | 0.80136 | FALSE | none | -0.23035 | -0.53835 | -0.28682 | -0.67681 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.042 | 0.26132 | 0.91074 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0534 | Night
2025-08-09 02:45 | 79.8 | 79.94 | 0.16995 | 80.2799 | 79.6001 | -0.82375 | FALSE | none | -0.47991 | -0.19991 | -0.59779 | -0.25114 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.014 | 0.26446 | -1.1117 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0549 | Night
2025-08-09 03:00 | 80.08 | 79.954 | 0.16935 | 80.2927 | 79.6153 | 0.74404 | FALSE | none | -0.21269 | -0.46469 | -0.26489 | -0.58367 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.26446 | 1.0058 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0496 | Night
2025-08-09 03:15 | 80.36 | 79.982 | 0.18783 | 80.3577 | 79.6063 | 2.0125 | TRUE | upper | 0.0023406 | -0.75366 | 0.0029127 | -0.94673 | Extreme triggered | 1 | 2025-08-09 03:15 | 2025-08-09 03:30 | 2.0125 | 0.28 | 0.28 | 0.028 | 0.27101 | 0.92984 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1913 | Night
2025-08-09 03:30 | 80.08 | 79.982 | 0.18783 | 80.3577 | 79.6063 | 0.52175 | FALSE | none | -0.27766 | -0.47366 | -0.34553 | -0.595 | Persistence ends | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.27253 | -1.0274 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0348 | Night
2025-08-09 03:45 | 80.08 | 79.996 | 0.18395 | 80.3639 | 79.6281 | 0.45666 | FALSE | none | -0.28389 | -0.45189 | -0.35326 | -0.5675 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.26446 | -0.052937 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0304 | Night
2025-08-09 04:00 | 79.8 | 79.996 | 0.18395 | 80.3639 | 79.6281 | -1.0655 | FALSE | none | -0.56389 | -0.17189 | -0.70167 | -0.21587 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.27253 | -1.0274 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.071 | Night
2025-08-09 04:15 | 79.8 | 79.982 | 0.18783 | 80.3577 | 79.6063 | -0.96896 | FALSE | none | -0.55766 | -0.19366 | -0.69397 | -0.24327 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.26446 | 0.052937 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0646 | Night
2025-08-09 04:30 | 79.8 | 79.968 | 0.19056 | 80.3491 | 79.5869 | -0.88163 | FALSE | none | -0.54911 | -0.21311 | -0.68341 | -0.26777 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.26446 | 0.052937 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Night
2025-08-09 04:45 | 80.08 | 79.954 | 0.16935 | 80.2927 | 79.6153 | 0.74404 | FALSE | none | -0.21269 | -0.46469 | -0.26489 | -0.58367 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.014 | 0.26446 | 1.1117 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0496 | Night
2025-08-09 05:00 | 80.08 | 79.968 | 0.16751 | 80.303 | 79.633 | 0.66862 | FALSE | none | -0.22302 | -0.44702 | -0.27772 | -0.56135 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.23116 | -0.060564 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0446 | Night
2025-08-09 05:15 | 80.36 | 79.996 | 0.18395 | 80.3639 | 79.6281 | 1.9789 | FALSE | none | -0.0038901 | -0.73189 | -0.0048407 | -0.91914 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.028 | 0.23863 | 1.056 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1319 | Night
2025-08-09 05:30 | 79.8 | 79.982 | 0.18783 | 80.3577 | 79.6063 | -0.96896 | FALSE | none | -0.55766 | -0.19366 | -0.69397 | -0.24327 | Normal | 0 |  |  |  | -0.56 | -0.56 | -0.014 | 0.26446 | -2.0646 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0932 | Night
2025-08-09 05:45 | 80.08 | 79.982 | 0.18783 | 80.3577 | 79.6063 | 0.52175 | FALSE | none | -0.27766 | -0.47366 | -0.34553 | -0.595 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.27253 | 1.0274 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0634 | Night
2025-08-09 06:00 | 80.08 | 79.996 | 0.18395 | 80.3639 | 79.6281 | 0.45666 | FALSE | none | -0.28389 | -0.45189 | -0.35326 | -0.5675 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.26446 | -0.052937 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.059 | Night
2025-08-09 06:15 | 80.08 | 80.01 | 0.17883 | 80.3677 | 79.6523 | 0.39144 | FALSE | none | -0.28765 | -0.42765 | -0.35792 | -0.5369 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.26446 | -0.052937 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0547 | Night
2025-08-09 06:30 | 80.36 | 80.024 | 0.19484 | 80.4137 | 79.6343 | 1.7245 | FALSE | none | -0.053677 | -0.72568 | -0.066751 | -0.91126 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.26446 | 1.0058 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1435 | Night
2025-08-09 06:45 | 79.8 | 80.024 | 0.19484 | 80.4137 | 79.6343 | -1.1497 | FALSE | none | -0.61368 | -0.16568 | -0.76315 | -0.20805 | Normal | 0 |  |  |  | -0.56 | -0.56 | 0 | 0.28727 | -1.9494 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1052 | Night
2025-08-09 07:00 | 79.8 | 80.01 | 0.20058 | 80.4112 | 79.6088 | -1.047 | FALSE | none | -0.61116 | -0.19116 | -0.76004 | -0.24012 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.27963 | 0.050066 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0984 | Day
2025-08-09 07:15 | 79.8 | 80.01 | 0.20058 | 80.4112 | 79.6088 | -1.047 | FALSE | none | -0.61116 | -0.19116 | -0.76004 | -0.24012 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.27253 | 0 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0984 | Day
2025-08-09 07:30 | 80.08 | 80.01 | 0.20058 | 80.4112 | 79.6088 | 0.34899 | FALSE | none | -0.33116 | -0.47116 | -0.41183 | -0.59184 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.27253 | 1.0274 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0518 | Day
2025-08-09 07:45 | 80.08 | 80.024 | 0.19484 | 80.4137 | 79.6343 | 0.28742 | FALSE | none | -0.33368 | -0.44568 | -0.41495 | -0.55965 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.26446 | -0.052937 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0477 | Day
2025-08-09 08:00 | 79.8 | 80.01 | 0.20058 | 80.4112 | 79.6088 | -1.047 | FALSE | none | -0.61116 | -0.19116 | -0.76004 | -0.24012 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.26446 | -1.0058 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0698 | Day
2025-08-09 08:15 | 79.24 | 79.954 | 0.24837 | 80.4507 | 79.4573 | -2.8747 | TRUE | lower | -1.2107 | 0.21726 | -1.5049 | 0.27343 | Extreme triggered | 1 | 2025-08-09 08:15 | 2025-08-09 12:00 | 2.8747 | -0.56 | -0.56 | -0.056 | 0.28147 | -1.7906 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.2488 | Day
2025-08-09 08:30 | 78.4 | 79.87 | 0.42488 | 80.7198 | 79.0202 | -3.4598 | TRUE | lower | -2.3198 | 0.62023 | -2.8739 | 0.7849 | Extreme/elevated | 2 | 2025-08-09 08:15 |  | 3.1672 | -0.84 | -0.84 | -0.084 | 0.3288 | -2.2993 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.3735 | Day
2025-08-09 08:45 | 77.84 | 79.758 | 0.61797 | 80.9939 | 78.5221 | -3.1037 | TRUE | lower | -3.1539 | 0.68205 | -3.8941 | 0.86861 | Persistent | 3 | 2025-08-09 08:15 |  | 3.1461 | -0.56 | -0.56 | -0.112 | 0.34473 | -1.2996 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4069 | Day
2025-08-09 09:00 | 77.56 | 79.646 | 0.78922 | 81.2244 | 78.0676 | -2.6431 | TRUE | lower | -3.6644 | 0.50756 | -4.5115 | 0.65016 | Persistent | 4 | 2025-08-09 08:15 |  | 3.0203 | -0.28 | -0.28 | -0.112 | 0.34473 | -0.48734 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4334 | Day
2025-08-09 09:15 | 77 | 79.506 | 0.98462 | 81.4752 | 77.5368 | -2.5451 | TRUE | lower | -4.4752 | 0.53676 | -5.4928 | 0.69226 | Persistent | 5 | 2025-08-09 08:15 |  | 2.9253 | -0.56 | -0.56 | -0.14 | 0.35765 | -1.1743 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.484 | Day
2025-08-09 09:30 | 76.16 | 79.324 | 1.2326 | 81.7892 | 76.8588 | -2.5669 | TRUE | lower | -5.6292 | 0.69879 | -6.8826 | 0.90919 | Persistent | 6 | 2025-08-09 08:15 |  | 2.8656 | -0.84 | -0.84 | -0.182 | 0.38835 | -1.6943 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.5426 | Day
2025-08-09 09:45 | 75.32 | 79.086 | 1.5078 | 82.1016 | 76.0704 | -2.4977 | TRUE | lower | -6.7816 | 0.75044 | -8.26 | 0.98651 | Confirmed/Materialized Shift | 7 | 2025-08-09 08:15 |  | 2.813 | -0.84 | -0.84 | -0.238 | 0.39884 | -1.5094 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5951 | Day
2025-08-09 10:00 | 75.04 | 78.834 | 1.7367 | 82.3074 | 75.3606 | -2.1846 | TRUE | lower | -7.2674 | 0.3206 | -8.8296 | 0.42542 | Confirmed/Materialized Shift | 8 | 2025-08-09 08:15 |  | 2.7345 | -0.28 | -0.28 | -0.252 | 0.39494 | -0.070897 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5742 | Day
2025-08-09 10:15 | 75.04 | 78.568 | 1.8912 | 82.3504 | 74.7856 | -1.8655 | FALSE | none | -7.3104 | -0.25443 | -8.8772 | -0.34021 | Confirmed/Materialized Shift | 9 | 2025-08-09 08:15 |  | 2.6379 | 0 | 0 | -0.266 | 0.37976 | 0.70045 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5529 | Day
2025-08-09 10:30 | 74.76 | 78.316 | 2.0477 | 82.4114 | 74.2206 | -1.7366 | FALSE | none | -7.6514 | -0.53944 | -9.2844 | -0.72681 | Confirmed/Materialized Shift | 10 | 2025-08-09 08:15 |  | 2.5478 | -0.28 | -0.28 | -0.252 | 0.37346 | -0.074975 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5443 | Day
2025-08-09 10:45 | 74.76 | 78.05 | 2.1495 | 82.349 | 73.751 | -1.5306 | FALSE | none | -7.589 | -1.009 | -9.2157 | -1.3682 | Confirmed/Materialized Shift | 11 | 2025-08-09 08:15 |  | 2.4553 | 0 | 0 | -0.266 | 0.35736 | 0.74434 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5306 | Day
2025-08-09 11:00 | 74.76 | 77.784 | 2.2133 | 82.2106 | 73.3574 | -1.3663 | FALSE | none | -7.4506 | -1.4026 | -9.0629 | -1.912 | Confirmed/Materialized Shift | 12 | 2025-08-09 08:15 |  | 2.3645 | 0 | 0 | -0.266 | 0.35736 | 0.74434 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4911 | Day
2025-08-09 11:15 | 75.04 | 77.532 | 2.225 | 81.9821 | 73.0819 | -1.12 | FALSE | none | -6.9421 | -1.9581 | -8.4678 | -2.6793 | Confirmed/Materialized Shift | 13 | 2025-08-09 08:15 |  | 2.2688 | 0.28 | 0.28 | -0.252 | 0.37346 | 1.4245 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4747 | Day
2025-08-09 11:30 | 74.76 | 77.252 | 2.2027 | 81.6573 | 72.8467 | -1.1314 | FALSE | none | -6.8973 | -1.9133 | -8.4467 | -2.6265 | Confirmed/Materialized Shift | 14 | 2025-08-09 08:15 |  | 2.1876 | -0.28 | -0.28 | -0.28 | 0.35184 | -2.0511e-15 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4754 | Day
2025-08-09 11:45 | 74.76 | 77 | 2.184 | 81.3681 | 72.6319 | -1.0256 | FALSE | none | -6.6081 | -2.1281 | -8.1212 | -2.9299 | Confirmed/Materialized Shift | 15 | 2025-08-09 08:15 |  | 2.1101 | 0 | 0 | -0.252 | 0.35066 | 0.71864 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4684 | Day
2025-08-09 12:00 | 74.76 | 76.748 | 2.1342 | 81.0163 | 72.4797 | -0.93152 | FALSE | none | -6.2563 | -2.2803 | -7.7223 | -3.1461 | Persistence ends | 0 |  |  |  | 0 | 0 | -0.252 | 0.35066 | 0.71864 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0621 | Day
2025-08-09 12:15 | 74.76 | 76.496 | 2.0507 | 80.5975 | 72.3945 | -0.84652 | FALSE | none | -5.8375 | -2.3655 | -7.2428 | -3.2675 | Normal | 0 |  |  |  | 0 | 0 | -0.252 | 0.35066 | 0.71864 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0564 | Day
2025-08-09 12:30 | 74.76 | 76.23 | 1.901 | 80.0319 | 72.4281 | -0.7733 | FALSE | none | -5.2719 | -2.3319 | -6.5873 | -3.2196 | Normal | 0 |  |  |  | 0 | 0 | -0.266 | 0.33347 | 0.79767 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0516 | Day
2025-08-09 12:45 | 74.76 | 75.964 | 1.6949 | 79.3538 | 72.5742 | -0.71036 | FALSE | none | -4.5938 | -2.1858 | -5.789 | -3.0119 | Normal | 0 |  |  |  | 0 | 0 | -0.266 | 0.33347 | 0.79767 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0474 | Day
2025-08-09 13:00 | 74.76 | 75.712 | 1.4518 | 78.6156 | 72.8084 | -0.65574 | FALSE | none | -3.8556 | -1.9516 | -4.9044 | -2.6805 | Normal | 0 |  |  |  | 0 | 0 | -0.252 | 0.33869 | 0.74404 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0437 | Day
2025-08-09 13:15 | 75.04 | 75.502 | 1.1958 | 77.8936 | 73.1104 | -0.38635 | FALSE | none | -2.8536 | -1.9296 | -3.6635 | -2.6393 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.21 | 0.35037 | 1.3985 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0258 | Day
2025-08-09 13:30 | 74.76 | 75.32 | 0.99099 | 77.302 | 73.338 | -0.56509 | FALSE | none | -2.542 | -1.422 | -3.2884 | -1.9389 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.182 | 0.31828 | -0.30791 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0377 | Day
2025-08-09 13:45 | 74.76 | 75.166 | 0.79961 | 76.7652 | 73.5668 | -0.50775 | FALSE | none | -2.0052 | -1.1932 | -2.6121 | -1.6219 | Normal | 0 |  |  |  | 0 | 0 | -0.154 | 0.30773 | 0.50044 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0338 | Day
2025-08-09 14:00 | 75.04 | 75.04 | 0.56732 | 76.1746 | 73.9054 | 0 | FALSE | none | -1.1346 | -1.1346 | -1.4895 | -1.5353 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.126 | 0.32086 | 1.2653 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Day
2025-08-09 14:15 | 74.76 | 74.928 | 0.33254 | 75.5931 | 74.2629 | -0.5052 | FALSE | none | -0.83309 | -0.49709 | -1.1021 | -0.66936 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.112 | 0.30672 | -0.54772 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0337 | Day
2025-08-09 14:30 | 74.76 | 74.858 | 0.1644 | 75.1868 | 74.5292 | -0.59611 | FALSE | none | -0.4268 | -0.2308 | -0.56765 | -0.30968 | Normal | 0 |  |  |  | 0 | 0 | -0.07 | 0.25493 | 0.27458 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0397 | Day
2025-08-09 14:45 | 75.04 | 74.844 | 0.13165 | 75.1073 | 74.5807 | 1.4888 | FALSE | none | -0.067291 | -0.45929 | -0.089593 | -0.61583 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.014 | 0.19217 | 1.5299 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0993 | Day
2025-08-09 15:00 | 75.04 | 74.844 | 0.13165 | 75.1073 | 74.5807 | 1.4888 | FALSE | none | -0.067291 | -0.45929 | -0.089593 | -0.61583 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.18169 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0993 | Day
2025-08-09 15:15 | 75.04 | 74.844 | 0.13165 | 75.1073 | 74.5807 | 1.4888 | FALSE | none | -0.067291 | -0.45929 | -0.089593 | -0.61583 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.18169 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0993 | Day
2025-08-09 15:30 | 75.04 | 74.858 | 0.13702 | 75.132 | 74.584 | 1.3283 | FALSE | none | -0.092042 | -0.45604 | -0.12251 | -0.61145 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.16935 | -0.082671 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0886 | Day
2025-08-09 15:45 | 74.76 | 74.858 | 0.13702 | 75.132 | 74.584 | -0.71522 | FALSE | none | -0.37204 | -0.17604 | -0.49518 | -0.23603 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.18169 | -1.5411 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0477 | Day
2025-08-09 16:00 | 75.04 | 74.872 | 0.14073 | 75.1535 | 74.5905 | 1.1937 | FALSE | none | -0.11347 | -0.44947 | -0.15098 | -0.60258 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.19217 | 1.3842 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0796 | Day
2025-08-09 16:15 | 75.04 | 74.872 | 0.14073 | 75.1535 | 74.5905 | 1.1937 | FALSE | none | -0.11347 | -0.44947 | -0.15098 | -0.60258 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.18169 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0796 | Day
2025-08-09 16:30 | 75.04 | 74.886 | 0.14292 | 75.1718 | 74.6002 | 1.0775 | FALSE | none | -0.13183 | -0.43983 | -0.17538 | -0.58959 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.16935 | -0.082671 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Day
2025-08-09 16:45 | 74.76 | 74.886 | 0.14292 | 75.1718 | 74.6002 | -0.88163 | FALSE | none | -0.41183 | -0.15983 | -0.54786 | -0.21425 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.18169 | -1.5411 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-09 17:00 | 75.04 | 74.9 | 0.14364 | 75.1873 | 74.6127 | 0.97468 | FALSE | none | -0.14727 | -0.42727 | -0.19588 | -0.57266 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.19217 | 1.3842 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.065 | Day
2025-08-09 17:15 | 74.76 | 74.9 | 0.14364 | 75.1873 | 74.6127 | -0.97468 | FALSE | none | -0.42727 | -0.14727 | -0.56828 | -0.19738 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.20313 | -1.3784 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.065 | Day
2025-08-09 17:30 | 74.76 | 74.9 | 0.14364 | 75.1873 | 74.6127 | -0.97468 | FALSE | none | -0.42727 | -0.14727 | -0.56828 | -0.19738 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.20313 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.065 | Day
2025-08-09 17:45 | 75.04 | 74.914 | 0.14292 | 75.1998 | 74.6282 | 0.88163 | FALSE | none | -0.15983 | -0.41183 | -0.21255 | -0.55185 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.21256 | 1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-09 18:00 | 74.76 | 74.914 | 0.14292 | 75.1998 | 74.6282 | -1.0775 | FALSE | none | -0.43983 | -0.13183 | -0.58489 | -0.17665 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.22252 | -1.2583 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Day
2025-08-09 18:15 | 75.04 | 74.914 | 0.14292 | 75.1998 | 74.6282 | 0.88163 | FALSE | none | -0.15983 | -0.41183 | -0.21255 | -0.55185 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.22252 | 1.2583 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-09 18:30 | 74.76 | 74.914 | 0.14292 | 75.1998 | 74.6282 | -1.0775 | FALSE | none | -0.43983 | -0.13183 | -0.58489 | -0.17665 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.22252 | -1.2583 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Day
2025-08-09 18:45 | 75.04 | 74.928 | 0.14073 | 75.2095 | 74.6465 | 0.79582 | FALSE | none | -0.16947 | -0.39347 | -0.22533 | -0.52711 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.23116 | 1.1507 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-09 19:00 | 75.04 | 74.928 | 0.14073 | 75.2095 | 74.6465 | 0.79582 | FALSE | none | -0.16947 | -0.39347 | -0.22533 | -0.52711 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.22252 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Night
2025-08-09 19:15 | 75.6 | 74.97 | 0.20058 | 75.3712 | 74.5688 | 3.1409 | TRUE | upper | 0.22884 | -1.0312 | 0.30362 | -1.3828 | Extreme triggered | 1 | 2025-08-09 19:15 | 2025-08-10 | 3.1409 | 0.56 | 0.56 | 0.042 | 0.24503 | 2.1141 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.2951 | Night
2025-08-09 19:30 | 75.88 | 75.026 | 0.27963 | 75.5853 | 74.4667 | 3.054 | TRUE | upper | 0.29474 | -1.4133 | 0.38994 | -1.8978 | Extreme/elevated | 2 | 2025-08-09 19:15 |  | 3.0975 | 0.28 | 0.28 | 0.056 | 0.25044 | 0.89443 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.3465 | Night
2025-08-09 19:45 | 75.88 | 75.068 | 0.33869 | 75.7454 | 74.3906 | 2.3975 | TRUE | upper | 0.13462 | -1.4894 | 0.17772 | -2.0021 | Persistent | 3 | 2025-08-09 19:15 |  | 2.8641 | 0 | 0 | 0.042 | 0.24503 | -0.17141 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.3598 | Night
2025-08-09 20:00 | 76.72 | 75.152 | 0.50088 | 76.1538 | 74.1502 | 3.1305 | TRUE | upper | 0.56624 | -2.5698 | 0.74355 | -3.4656 | Persistent | 4 | 2025-08-09 19:15 |  | 2.9307 | 0.84 | 0.84 | 0.084 | 0.30266 | 2.4978 | TRUE | 2 | TRUE | TRUE | FALSE | TRUE | 0.4944 | Night
2025-08-09 20:15 | 76.72 | 75.236 | 0.61008 | 76.4562 | 74.0158 | 2.4325 | TRUE | upper | 0.26385 | -2.7042 | 0.3451 | -3.6535 | Persistent | 5 | 2025-08-09 19:15 |  | 2.8311 | 0 | 0 | 0.084 | 0.30266 | -0.27754 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.505 | Night
2025-08-09 20:30 | 77.28 | 75.348 | 0.75951 | 76.867 | 73.829 | 2.5437 | TRUE | upper | 0.41298 | -3.451 | 0.53726 | -4.6743 | Persistent | 6 | 2025-08-09 19:15 |  | 2.7832 | 0.56 | 0.56 | 0.112 | 0.31989 | 1.4005 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.5696 | Night
2025-08-09 20:45 | 77.84 | 75.502 | 0.92765 | 77.3573 | 73.6467 | 2.5203 | TRUE | upper | 0.48269 | -4.1933 | 0.62398 | -5.6938 | Confirmed/Materialized Shift | 7 | 2025-08-09 19:15 |  | 2.7456 | 0.56 | 0.56 | 0.154 | 0.32086 | 1.2653 | FALSE | 2 | FALSE | TRUE | TRUE | FALSE | 0.6252 | Night
2025-08-09 21:00 | 78.4 | 75.67 | 1.1232 | 77.9164 | 73.4236 | 2.4305 | TRUE | upper | 0.48356 | -4.9764 | 0.62062 | -6.7777 | Confirmed/Materialized Shift | 8 | 2025-08-09 19:15 |  | 2.7062 | 0.56 | 0.56 | 0.168 | 0.33254 | 1.1788 | FALSE | 2 | FALSE | TRUE | TRUE | FALSE | 0.6192 | Night
2025-08-09 21:15 | 78.96 | 75.866 | 1.3304 | 78.5268 | 73.2052 | 2.3256 | TRUE | upper | 0.43319 | -5.7548 | 0.55164 | -7.8612 | Confirmed/Materialized Shift | 9 | 2025-08-09 19:15 |  | 2.664 | 0.56 | 0.56 | 0.196 | 0.34112 | 1.0671 | FALSE | 2 | FALSE | TRUE | TRUE | FALSE | 0.6122 | Night
2025-08-09 21:30 | 78.96 | 76.062 | 1.4824 | 79.0268 | 73.0972 | 1.955 | FALSE | none | -0.066773 | -5.8628 | -0.084494 | -8.0205 | Confirmed/Materialized Shift | 10 | 2025-08-09 19:15 |  | 2.5931 | 0 | 0 | 0.196 | 0.34112 | -0.57458 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5875 | Night
2025-08-09 21:45 | 79.52 | 76.3 | 1.6365 | 79.5729 | 73.0271 | 1.9677 | FALSE | none | -0.052906 | -6.4929 | -0.066488 | -8.8911 | Confirmed/Materialized Shift | 11 | 2025-08-09 19:15 |  | 2.5362 | 0.56 | 0.56 | 0.238 | 0.33099 | 0.97284 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5597 | Night
2025-08-09 22:00 | 72.52 | 76.174 | 1.8248 | 79.8235 | 72.5245 | -2.0025 | TRUE | lower | -7.3035 | 0.0044902 | -9.1496 | 0.0061912 | Confirmed/Materialized Shift | 12 | 2025-08-09 19:15 |  | 2.4917 | -7 | -7 | -0.126 | 1.6515 | -4.1624 | TRUE | 2 | TRUE | TRUE | TRUE | TRUE | 0.5906 | Night
2025-08-09 22:15 | 72.52 | 76.062 | 1.9784 | 80.0188 | 72.1052 | -1.7903 | FALSE | none | -7.4988 | -0.41477 | -9.3713 | -0.57524 | Confirmed/Materialized Shift | 13 | 2025-08-09 19:15 |  | 2.4378 | 0 | 0 | -0.112 | 1.6513 | 0.067827 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5765 | Night
2025-08-09 22:30 | 72.52 | 75.95 | 2.1147 | 80.1794 | 71.7206 | -1.622 | FALSE | none | -7.6594 | -0.79937 | -9.5528 | -1.1146 | Confirmed/Materialized Shift | 14 | 2025-08-09 19:15 |  | 2.3795 | 0 | 0 | -0.112 | 1.6513 | 0.067827 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5367 | Night
2025-08-09 22:45 | 72.52 | 75.824 | 2.2429 | 80.3099 | 71.3381 | -1.4731 | FALSE | none | -7.7899 | -1.1819 | -9.6998 | -1.6567 | Confirmed/Materialized Shift | 15 | 2025-08-09 19:15 |  | 2.3191 | 0 | 0 | -0.126 | 1.6489 | 0.076412 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5268 | Night
2025-08-09 23:00 | 72.52 | 75.712 | 2.3521 | 80.4163 | 71.0077 | -1.3571 | FALSE | none | -7.8963 | -1.5123 | -9.8193 | -2.1297 | Confirmed/Materialized Shift | 16 | 2025-08-09 19:15 |  | 2.2589 | 0 | 0 | -0.112 | 1.6488 | 0.06793 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.519 | Night
2025-08-09 23:15 | 72.52 | 75.586 | 2.4553 | 80.4965 | 70.6755 | -1.2487 | FALSE | none | -7.9765 | -1.8445 | -9.9092 | -2.6099 | Confirmed/Materialized Shift | 17 | 2025-08-09 19:15 |  | 2.1995 | 0 | 0 | -0.126 | 1.6464 | 0.076528 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5118 | Night
2025-08-09 23:30 | 72.52 | 75.474 | 2.5444 | 80.5628 | 70.3852 | -1.161 | FALSE | none | -8.0428 | -2.1348 | -9.9833 | -3.033 | Confirmed/Materialized Shift | 18 | 2025-08-09 19:15 |  | 2.1418 | 0 | 0 | -0.112 | 1.6463 | 0.068033 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.506 | Night
2025-08-09 23:45 | 72.52 | 75.348 | 2.628 | 80.6041 | 70.0919 | -1.0761 | FALSE | none | -8.0841 | -2.4281 | -10.0294 | -3.4642 | Confirmed/Materialized Shift | 19 | 2025-08-09 19:15 |  | 2.0857 | 0 | 0 | -0.126 | 1.6439 | 0.076645 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5003 | Night
2025-08-10 | 72.52 | 75.222 | 2.7029 | 80.6279 | 69.8161 | -0.99965 | FALSE | none | -8.1079 | -2.7039 | -10.0559 | -3.8728 | Persistence ends | 0 |  |  |  | 0 | 0 | -0.126 | 1.6439 | 0.076645 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0952 | Night
2025-08-10 00:15 | 72.52 | 75.068 | 2.7672 | 80.6025 | 69.5335 | -0.92077 | FALSE | none | -8.0825 | -2.9865 | -10.0276 | -4.295 | Normal | 0 |  |  |  | 0 | 0 | -0.154 | 1.6364 | 0.09411 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.09 | Night
2025-08-10 00:30 | 72.52 | 74.9 | 2.8169 | 80.5338 | 69.2662 | -0.8449 | FALSE | none | -8.0138 | -3.2538 | -9.9508 | -4.6975 | Normal | 0 |  |  |  | 0 | 0 | -0.168 | 1.6337 | 0.10284 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0563 | Night
2025-08-10 00:45 | 72.52 | 74.732 | 2.8553 | 80.4426 | 69.0214 | -0.7747 | FALSE | none | -7.9226 | -3.4986 | -9.8488 | -5.0689 | Normal | 0 |  |  |  | 0 | 0 | -0.168 | 1.6337 | 0.10284 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0516 | Night
2025-08-10 01:00 | 72.52 | 74.522 | 2.8558 | 80.2337 | 68.8103 | -0.70102 | FALSE | none | -7.7137 | -3.7097 | -9.614 | -5.3912 | Normal | 0 |  |  |  | 0 | 0 | -0.21 | 1.6171 | 0.12986 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0467 | Night
2025-08-10 01:15 | 72.52 | 74.312 | 2.8401 | 79.9922 | 68.6318 | -0.63097 | FALSE | none | -7.4722 | -3.8882 | -9.3411 | -5.6653 | Normal | 0 |  |  |  | 0 | 0 | -0.21 | 1.6171 | 0.12986 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0421 | Night
2025-08-10 01:30 | 72.52 | 74.074 | 2.777 | 79.6281 | 68.5199 | -0.55959 | FALSE | none | -7.1081 | -4.0001 | -8.9266 | -5.8378 | Normal | 0 |  |  |  | 0 | 0 | -0.238 | 1.6079 | 0.14802 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0373 | Night
2025-08-10 01:45 | 72.52 | 73.808 | 2.6492 | 79.1063 | 68.5097 | -0.48619 | FALSE | none | -6.5863 | -4.0103 | -8.3259 | -5.8536 | Normal | 0 |  |  |  | 0 | 0 | -0.266 | 1.5981 | 0.16645 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0324 | Night
2025-08-10 02:00 | 72.52 | 73.514 | 2.4299 | 78.3739 | 68.6541 | -0.40907 | FALSE | none | -5.8539 | -3.8659 | -7.4691 | -5.6309 | Normal | 0 |  |  |  | 0 | 0 | -0.294 | 1.5878 | 0.18517 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0273 | Night
2025-08-10 02:15 | 72.52 | 73.192 | 2.0704 | 77.3327 | 69.0513 | -0.32458 | FALSE | none | -4.8127 | -3.4687 | -6.2234 | -5.0234 | Normal | 0 |  |  |  | 0 | 0 | -0.322 | 1.5768 | 0.20421 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0216 | Night
2025-08-10 02:30 | 72.52 | 72.87 | 1.5652 | 76.0005 | 69.7395 | -0.22361 | FALSE | none | -3.4805 | -2.7805 | -4.5796 | -3.987 | Normal | 0 |  |  |  | 0 | 0 | -0.322 | 1.5768 | 0.20421 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0149 | Night
2025-08-10 02:45 | 72.52 | 72.52 | 0 | 72.52 | 72.52 |  | FALSE | none | 0 | 0 | 0 | 0 | Normal | 0 |  |  |  | 0 | 0 | -0.35 | 1.5652 | 0.22361 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-10 03:00 | 72.52 | 72.52 | 0 | 72.52 | 72.52 |  | FALSE | none | 0 | 0 | 0 | 0 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0 |  | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-10 03:15 | 72.52 | 72.52 | 0 | 72.52 | 72.52 |  | FALSE | none | 0 | 0 | 0 | 0 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0 |  | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-10 03:30 | 72.52 | 72.52 | 0 | 72.52 | 72.52 |  | FALSE | none | 0 | 0 | 0 | 0 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0 |  | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-10 03:45 | 72.52 | 72.52 | 0 | 72.52 | 72.52 |  | FALSE | none | 0 | 0 | 0 | 0 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0 |  | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-10 04:00 | 72.52 | 72.52 | 0 | 72.52 | 72.52 |  | FALSE | none | 0 | 0 | 0 | 0 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0 |  | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-10 04:15 | 72.52 | 72.52 | 0 | 72.52 | 72.52 |  | FALSE | none | 0 | 0 | 0 | 0 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0 |  | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-10 04:30 | 72.52 | 72.52 | 0 | 72.52 | 72.52 |  | FALSE | none | 0 | 0 | 0 | 0 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0 |  | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-10 04:45 | 72.52 | 72.52 | 0 | 72.52 | 72.52 |  | FALSE | none | 0 | 0 | 0 | 0 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0 |  | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-10 05:00 | 72.52 | 72.52 | 0 | 72.52 | 72.52 |  | FALSE | none | 0 | 0 | 0 | 0 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0 |  | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-10 05:15 | 72.52 | 72.52 | 0 | 72.52 | 72.52 |  | FALSE | none | 0 | 0 | 0 | 0 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0 |  | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-10 05:30 | 72.52 | 72.52 | 0 | 72.52 | 72.52 |  | FALSE | none | 0 | 0 | 0 | 0 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0 |  | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-10 05:45 | 72.52 | 72.52 | 0 | 72.52 | 72.52 |  | FALSE | none | 0 | 0 | 0 | 0 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0 |  | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-10 06:00 | 72.52 | 72.52 | 0 | 72.52 | 72.52 |  | FALSE | none | 0 | 0 | 0 | 0 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0 |  | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-10 06:15 | 72.52 | 72.52 | 0 | 72.52 | 72.52 |  | FALSE | none | 0 | 0 | 0 | 0 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0 |  | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-10 06:30 | 72.52 | 72.52 | 0 | 72.52 | 72.52 |  | FALSE | none | 0 | 0 | 0 | 0 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0 |  | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-10 06:45 | 72.52 | 72.52 | 0 | 72.52 | 72.52 |  | FALSE | none | 0 | 0 | 0 | 0 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0 |  | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-10 07:00 | 80.08 | 72.898 | 1.6905 | 76.2789 | 69.5171 | 4.2485 | TRUE | upper | 3.8011 | -10.5629 | 4.9831 | -15.1947 | Extreme triggered | 1 | 2025-08-10 07:00 | 2025-08-10 08:45 | 4.2485 | 7.56 | 7.56 | 0.378 | 1.6905 | 4.2485 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.3689 | Day
2025-08-10 07:15 | 79.8 | 73.262 | 2.2843 | 77.8306 | 68.6934 | 2.8622 | TRUE | upper | 1.9694 | -11.1066 | 2.5304 | -16.1683 | Extreme/elevated | 2 | 2025-08-10 07:00 |  | 3.5554 | -0.28 | -0.28 | 0.364 | 1.6949 | -0.37996 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.3337 | Day
2025-08-10 07:30 | 80.36 | 73.654 | 2.7711 | 79.1962 | 68.1118 | 2.42 | TRUE | upper | 1.1638 | -12.2482 | 1.4696 | -17.9824 | Persistent | 3 | 2025-08-10 07:00 |  | 3.1769 | 0.56 | 0.56 | 0.392 | 1.6932 | 0.09922 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.3613 | Day
2025-08-10 07:45 | 80.08 | 74.032 | 3.1039 | 80.2398 | 67.8242 | 1.9485 | FALSE | none | -0.15978 | -12.2558 | -0.19912 | -18.0699 | Persistent | 4 | 2025-08-10 07:00 |  | 2.8698 | -0.28 | -0.28 | 0.378 | 1.6978 | -0.38757 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.387 | Day
2025-08-10 08:00 | 80.08 | 74.41 | 3.3598 | 81.1297 | 67.6903 | 1.6876 | FALSE | none | -1.0497 | -12.3897 | -1.2938 | -18.3035 | Persistent | 5 | 2025-08-10 07:00 |  | 2.6334 | 0 | 0 | 0.378 | 1.6978 | -0.22264 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.4268 | Day
2025-08-10 08:15 | 78.96 | 74.732 | 3.4758 | 81.6836 | 67.7804 | 1.2164 | FALSE | none | -2.7236 | -11.1796 | -3.3343 | -16.4938 | Persistent | 6 | 2025-08-10 07:00 |  | 2.3972 | -1.12 | -1.12 | 0.322 | 1.7291 | -0.83397 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.4525 | Day
2025-08-10 08:30 | 78.96 | 75.054 | 3.5574 | 82.1688 | 67.9392 | 1.098 | FALSE | none | -3.2088 | -11.0208 | -3.9052 | -16.2216 | Confirmed/Materialized Shift | 7 | 2025-08-10 07:00 |  | 2.2116 | 0 | 0 | 0.322 | 1.7291 | -0.18623 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5018 | Day
2025-08-10 08:45 | 77.84 | 75.32 | 3.5569 | 82.4337 | 68.2063 | 0.70849 | FALSE | none | -4.5937 | -9.6337 | -5.5726 | -14.1244 | Persistence ends | 0 |  |  |  | -1.12 | -1.12 | 0.266 | 1.758 | -0.78842 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0758 | Day
2025-08-10 09:00 | 77.28 | 75.558 | 3.5187 | 82.5954 | 68.5206 | 0.48939 | FALSE | none | -5.3154 | -8.7594 | -6.4355 | -12.7836 | Normal | 0 |  |  |  | -0.56 | -0.56 | 0.238 | 1.7669 | -0.45165 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0612 | Day
2025-08-10 09:15 | 77 | 75.782 | 3.4572 | 82.6964 | 68.8676 | 0.35231 | FALSE | none | -5.6964 | -8.1324 | -6.8883 | -11.8087 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.224 | 1.7699 | -0.28475 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0521 | Day
2025-08-10 09:30 | 76.16 | 75.964 | 3.3712 | 82.7063 | 69.2217 | 0.05814 | FALSE | none | -6.5463 | -6.9383 | -7.9151 | -10.0233 | Normal | 0 |  |  |  | -0.84 | -0.84 | 0.182 | 1.7854 | -0.57241 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0039 | Day
2025-08-10 09:45 | 75.6 | 76.118 | 3.2745 | 82.667 | 69.569 | -0.15819 | FALSE | none | -7.067 | -6.031 | -8.5488 | -8.6691 | Normal | 0 |  |  |  | -0.56 | -0.56 | 0.154 | 1.7928 | -0.39826 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0105 | Day
2025-08-10 10:00 | 75.04 | 76.244 | 3.1758 | 82.5955 | 69.8925 | -0.37912 | FALSE | none | -7.5555 | -5.1475 | -9.1476 | -7.365 | Normal | 0 |  |  |  | -0.56 | -0.56 | 0.126 | 1.7997 | -0.38117 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0253 | Day
2025-08-10 10:15 | 74.76 | 76.356 | 3.0754 | 82.5069 | 70.2051 | -0.51895 | FALSE | none | -7.7469 | -4.5549 | -9.3894 | -6.488 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.112 | 1.8018 | -0.21756 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0346 | Day
2025-08-10 10:30 | 74.76 | 76.468 | 2.9673 | 82.4026 | 70.5334 | -0.57561 | FALSE | none | -7.6426 | -4.2266 | -9.2747 | -5.9923 | Normal | 0 |  |  |  | 0 | 0 | 0.112 | 1.8018 | -0.062159 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0384 | Day
2025-08-10 10:45 | 74.76 | 76.58 | 2.8504 | 82.2808 | 70.8792 | -0.63851 | FALSE | none | -7.5208 | -3.8808 | -9.1404 | -5.4752 | Normal | 0 |  |  |  | 0 | 0 | 0.112 | 1.8018 | -0.062159 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0426 | Day
2025-08-10 11:00 | 74.76 | 76.692 | 2.7237 | 82.1393 | 71.2447 | -0.70934 | FALSE | none | -7.3793 | -3.5153 | -8.9839 | -4.9341 | Normal | 0 |  |  |  | 0 | 0 | 0.112 | 1.8018 | -0.062159 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0473 | Day
2025-08-10 11:15 | 75.04 | 76.818 | 2.5747 | 81.9674 | 71.6686 | -0.69056 | FALSE | none | -6.9274 | -3.3714 | -8.4514 | -4.7042 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.126 | 1.802 | 0.085461 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.046 | Day
2025-08-10 11:30 | 74.76 | 76.93 | 2.4221 | 81.7742 | 72.0858 | -0.89592 | FALSE | none | -7.0142 | -2.6742 | -8.5775 | -3.7098 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.112 | 1.8041 | -0.21728 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0597 | Day
2025-08-10 11:45 | 75.04 | 77.056 | 2.2393 | 81.5345 | 72.5775 | -0.9003 | FALSE | none | -6.4945 | -2.4625 | -7.9654 | -3.393 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.126 | 1.8043 | 0.085352 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.06 | Day
2025-08-10 12:00 | 74.76 | 76.79 | 2.1762 | 81.1425 | 72.4375 | -0.93281 | FALSE | none | -6.3825 | -2.3225 | -7.8657 | -3.2062 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.266 | 0.44015 | -0.031807 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0622 | Day
2025-08-10 12:15 | 74.76 | 76.538 | 2.0998 | 80.7376 | 72.3384 | -0.84675 | FALSE | none | -5.9776 | -2.4216 | -7.4037 | -3.3476 | Normal | 0 |  |  |  | 0 | 0 | -0.252 | 0.44411 | 0.56742 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0564 | Day
2025-08-10 12:30 | 74.76 | 76.258 | 1.9298 | 80.1176 | 72.3984 | -0.77624 | FALSE | none | -5.3576 | -2.3616 | -6.6872 | -3.262 | Normal | 0 |  |  |  | 0 | 0 | -0.28 | 0.40627 | 0.6892 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0517 | Day
2025-08-10 12:45 | 75.04 | 76.006 | 1.7224 | 79.4508 | 72.5612 | -0.56085 | FALSE | none | -4.4108 | -2.4788 | -5.5516 | -3.4161 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.252 | 0.42513 | 1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0374 | Day
2025-08-10 13:00 | 74.76 | 75.74 | 1.4492 | 78.6385 | 72.8415 | -0.67622 | FALSE | none | -3.8785 | -1.9185 | -4.932 | -2.6338 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.266 | 0.42098 | -0.033256 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0451 | Day
2025-08-10 13:15 | 74.76 | 75.53 | 1.2485 | 78.027 | 73.033 | -0.61675 | FALSE | none | -3.267 | -1.727 | -4.187 | -2.3646 | Normal | 0 |  |  |  | 0 | 0 | -0.21 | 0.37318 | 0.56273 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0411 | Day
2025-08-10 13:30 | 74.76 | 75.32 | 0.9614 | 77.2428 | 73.3972 | -0.58248 | FALSE | none | -2.4828 | -1.3628 | -3.2143 | -1.8568 | Normal | 0 |  |  |  | 0 | 0 | -0.21 | 0.37318 | 0.56273 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0388 | Day
2025-08-10 13:45 | 75.04 | 75.18 | 0.75734 | 76.6947 | 73.6653 | -0.18486 | FALSE | none | -1.6547 | -1.3747 | -2.1575 | -1.8661 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.14 | 0.32118 | 1.3077 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0123 | Day
2025-08-10 14:00 | 75.04 | 75.068 | 0.57383 | 76.2157 | 73.9203 | -0.048795 | FALSE | none | -1.1757 | -1.1197 | -1.5425 | -1.5147 | Normal | 0 |  |  |  | 0 | 0 | -0.112 | 0.30672 | 0.36515 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0033 | Day
2025-08-10 14:15 | 74.76 | 74.956 | 0.35301 | 75.662 | 74.25 | -0.55523 | FALSE | none | -0.90202 | -0.51002 | -1.1922 | -0.68689 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.112 | 0.30672 | -0.54772 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.037 | Day
2025-08-10 14:30 | 75.04 | 74.9 | 0.21305 | 75.3261 | 74.4739 | 0.65713 | FALSE | none | -0.2861 | -0.5661 | -0.37981 | -0.76013 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.056 | 0.26641 | 1.2612 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0438 | Day
2025-08-10 14:45 | 74.76 | 74.858 | 0.13702 | 75.132 | 74.584 | -0.71522 | FALSE | none | -0.37204 | -0.17604 | -0.49518 | -0.23603 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.042 | 0.24503 | -0.97132 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0477 | Day
2025-08-10 15:00 | 74.76 | 74.844 | 0.13165 | 75.1073 | 74.5807 | -0.63808 | FALSE | none | -0.34729 | -0.17929 | -0.46239 | -0.2404 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.21256 | 0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0425 | Day
2025-08-10 15:15 | 75.04 | 74.858 | 0.13702 | 75.132 | 74.584 | 1.3283 | FALSE | none | -0.092042 | -0.45604 | -0.12251 | -0.61145 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.21256 | 1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0886 | Day
2025-08-10 15:30 | 74.76 | 74.858 | 0.13702 | 75.132 | 74.584 | -0.71522 | FALSE | none | -0.37204 | -0.17604 | -0.49518 | -0.23603 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.22252 | -1.2583 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0477 | Day
2025-08-10 15:45 | 75.04 | 74.872 | 0.14073 | 75.1535 | 74.5905 | 1.1937 | FALSE | none | -0.11347 | -0.44947 | -0.15098 | -0.60258 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.23116 | 1.1507 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0796 | Day
2025-08-10 16:00 | 75.04 | 74.886 | 0.14292 | 75.1718 | 74.6002 | 1.0775 | FALSE | none | -0.13183 | -0.43983 | -0.17538 | -0.58959 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.23116 | -0.060564 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Day
2025-08-10 16:15 | 74.76 | 74.872 | 0.14073 | 75.1535 | 74.5905 | -0.79582 | FALSE | none | -0.39347 | -0.16947 | -0.52356 | -0.2272 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.23116 | -1.1507 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-10 16:30 | 74.76 | 74.872 | 0.14073 | 75.1535 | 74.5905 | -0.79582 | FALSE | none | -0.39347 | -0.16947 | -0.52356 | -0.2272 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.22252 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-10 16:45 | 75.04 | 74.872 | 0.14073 | 75.1535 | 74.5905 | 1.1937 | FALSE | none | -0.11347 | -0.44947 | -0.15098 | -0.60258 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.22252 | 1.2583 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0796 | Day
2025-08-10 17:00 | 74.76 | 74.872 | 0.14073 | 75.1535 | 74.5905 | -0.79582 | FALSE | none | -0.39347 | -0.16947 | -0.52356 | -0.2272 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.22252 | -1.2583 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-10 17:15 | 74.76 | 74.872 | 0.14073 | 75.1535 | 74.5905 | -0.79582 | FALSE | none | -0.39347 | -0.16947 | -0.52356 | -0.2272 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.22252 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-10 17:30 | 74.76 | 74.872 | 0.14073 | 75.1535 | 74.5905 | -0.79582 | FALSE | none | -0.39347 | -0.16947 | -0.52356 | -0.2272 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.22252 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-10 17:45 | 74.76 | 74.858 | 0.13702 | 75.132 | 74.584 | -0.71522 | FALSE | none | -0.37204 | -0.17604 | -0.49518 | -0.23603 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.21256 | 0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0477 | Day
2025-08-10 18:00 | 75.04 | 74.872 | 0.14073 | 75.1535 | 74.5905 | 1.1937 | FALSE | none | -0.11347 | -0.44947 | -0.15098 | -0.60258 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.21256 | 1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0796 | Day
2025-08-10 18:15 | 75.04 | 74.886 | 0.14292 | 75.1718 | 74.6002 | 1.0775 | FALSE | none | -0.13183 | -0.43983 | -0.17538 | -0.58959 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.21256 | -0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Day
2025-08-10 18:30 | 75.04 | 74.9 | 0.14364 | 75.1873 | 74.6127 | 0.97468 | FALSE | none | -0.14727 | -0.42727 | -0.19588 | -0.57266 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.21256 | -0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.065 | Day
2025-08-10 18:45 | 74.76 | 74.886 | 0.14292 | 75.1718 | 74.6002 | -0.88163 | FALSE | none | -0.41183 | -0.15983 | -0.54786 | -0.21425 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.21256 | -1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-10 19:00 | 75.04 | 74.886 | 0.14292 | 75.1718 | 74.6002 | 1.0775 | FALSE | none | -0.13183 | -0.43983 | -0.17538 | -0.58959 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.22252 | 1.2583 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Night
2025-08-10 19:15 | 75.32 | 74.914 | 0.16935 | 75.2527 | 74.5753 | 2.3975 | TRUE | upper | 0.067309 | -0.74469 | 0.089444 | -0.99858 | Extreme triggered | 1 | 2025-08-10 19:15 | 2025-08-10 23:30 | 2.3975 | 0.28 | 0.28 | 0.028 | 0.22066 | 1.142 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.217 | Night
2025-08-10 19:30 | 75.6 | 74.942 | 0.22756 | 75.3971 | 74.4869 | 2.8915 | TRUE | upper | 0.20287 | -1.1131 | 0.26907 | -1.4944 | Extreme/elevated | 2 | 2025-08-10 19:15 |  | 2.6445 | 0.28 | 0.28 | 0.028 | 0.22066 | 1.142 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.3071 | Night
2025-08-10 19:45 | 76.16 | 75.012 | 0.35066 | 75.7133 | 74.3107 | 3.2738 | TRUE | upper | 0.44667 | -1.8493 | 0.58996 | -2.4886 | Persistent | 3 | 2025-08-10 19:15 |  | 2.8543 | 0.56 | 0.56 | 0.07 | 0.23819 | 2.0571 | TRUE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4183 | Night
2025-08-10 20:00 | 76.72 | 75.11 | 0.51289 | 76.1358 | 74.0842 | 3.1391 | TRUE | upper | 0.58423 | -2.6358 | 0.76735 | -3.5578 | Persistent | 4 | 2025-08-10 19:15 |  | 2.9255 | 0.56 | 0.56 | 0.098 | 0.26132 | 1.7679 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4664 | Night
2025-08-10 20:15 | 77 | 75.208 | 0.66385 | 76.5357 | 73.8803 | 2.6994 | TRUE | upper | 0.46431 | -3.1197 | 0.60666 | -4.2226 | Persistent | 5 | 2025-08-10 19:15 |  | 2.8803 | 0.28 | 0.28 | 0.098 | 0.26132 | 0.69645 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4942 | Night
2025-08-10 20:30 | 77.56 | 75.348 | 0.83705 | 77.0221 | 73.6739 | 2.6426 | TRUE | upper | 0.53791 | -3.8861 | 0.69838 | -5.2747 | Persistent | 6 | 2025-08-10 19:15 |  | 2.8407 | 0.56 | 0.56 | 0.14 | 0.26485 | 1.5858 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.5476 | Night
2025-08-10 20:45 | 78.12 | 75.502 | 1.0369 | 77.5758 | 73.4282 | 2.5249 | TRUE | upper | 0.54425 | -4.6918 | 0.70157 | -6.3896 | Confirmed/Materialized Shift | 7 | 2025-08-10 19:15 |  | 2.7955 | 0.56 | 0.56 | 0.154 | 0.27963 | 1.4519 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5969 | Night
2025-08-10 21:00 | 78.4 | 75.67 | 1.215 | 78.1 | 73.24 | 2.2469 | TRUE | upper | 0.30003 | -5.16 | 0.38416 | -7.0453 | Confirmed/Materialized Shift | 8 | 2025-08-10 19:15 |  | 2.727 | 0.28 | 0.28 | 0.168 | 0.27852 | 0.40212 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5784 | Night
2025-08-10 21:15 | 78.68 | 75.866 | 1.3671 | 78.6002 | 73.1318 | 2.0583 | TRUE | upper | 0.079762 | -5.5482 | 0.10148 | -7.5866 | Confirmed/Materialized Shift | 9 | 2025-08-10 19:15 |  | 2.6527 | 0.28 | 0.28 | 0.196 | 0.25855 | 0.32489 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5658 | Night
2025-08-10 21:30 | 78.96 | 76.076 | 1.504 | 79.084 | 73.068 | 1.9175 | FALSE | none | -0.12402 | -5.892 | -0.15682 | -8.0638 | Confirmed/Materialized Shift | 10 | 2025-08-10 19:15 |  | 2.5792 | 0.28 | 0.28 | 0.21 | 0.25493 | 0.27458 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5564 | Night
2025-08-10 21:45 | 79.52 | 76.3 | 1.6664 | 79.6329 | 72.9671 | 1.9323 | FALSE | none | -0.11287 | -6.5529 | -0.14174 | -8.9806 | Confirmed/Materialized Shift | 11 | 2025-08-10 19:15 |  | 2.5204 | 0.56 | 0.56 | 0.224 | 0.26641 | 1.2612 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5574 | Night
2025-08-10 22:00 | 80.08 | 76.566 | 1.8248 | 80.2155 | 72.9165 | 1.9257 | FALSE | none | -0.13551 | -7.1635 | -0.16893 | -9.8243 | Confirmed/Materialized Shift | 12 | 2025-08-10 19:15 |  | 2.4708 | 0.56 | 0.56 | 0.266 | 0.24837 | 1.1837 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.557 | Night
2025-08-10 22:15 | 79.8 | 76.818 | 1.9083 | 80.6346 | 73.0014 | 1.5626 | FALSE | none | -0.83464 | -6.7986 | -1.0351 | -9.313 | Confirmed/Materialized Shift | 13 | 2025-08-10 19:15 |  | 2.4009 | -0.28 | -0.28 | 0.252 | 0.27101 | -1.963 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.5042 | Night
2025-08-10 22:30 | 80.08 | 77.084 | 1.9759 | 81.0359 | 73.1321 | 1.5162 | FALSE | none | -0.95587 | -6.9479 | -1.1796 | -9.5004 | Confirmed/Materialized Shift | 14 | 2025-08-10 19:15 |  | 2.3378 | 0.28 | 0.28 | 0.266 | 0.26446 | 0.052937 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.5011 | Night
2025-08-10 22:45 | 80.08 | 77.35 | 2.0045 | 81.359 | 73.341 | 1.3619 | FALSE | none | -1.279 | -6.739 | -1.572 | -9.1886 | Confirmed/Materialized Shift | 15 | 2025-08-10 19:15 |  | 2.2727 | 0 | 0 | 0.266 | 0.26446 | -1.0058 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4908 | Night
2025-08-10 23:00 | 80.08 | 77.602 | 2.0156 | 81.6332 | 73.5708 | 1.2294 | FALSE | none | -1.5532 | -6.5092 | -1.9026 | -8.8475 | Confirmed/Materialized Shift | 16 | 2025-08-10 19:15 |  | 2.2075 | 0 | 0 | 0.252 | 0.27101 | -0.92984 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.482 | Night
2025-08-10 23:15 | 80.36 | 77.868 | 2.0107 | 81.8894 | 73.8466 | 1.2394 | FALSE | none | -1.5294 | -6.5134 | -1.8677 | -8.8202 | Confirmed/Materialized Shift | 17 | 2025-08-10 19:15 |  | 2.1505 | 0.28 | 0.28 | 0.266 | 0.26446 | 0.052937 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4826 | Night
2025-08-10 23:30 | 79.8 | 78.106 | 1.9388 | 81.9836 | 74.2284 | 0.87375 | FALSE | none | -2.1836 | -5.5716 | -2.6634 | -7.506 | Persistence ends | 0 |  |  |  | -0.56 | -0.56 | 0.238 | 0.31828 | -2.5072 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0868 | Night
2025-08-10 23:45 | 80.08 | 78.372 | 1.8167 | 82.0053 | 74.7387 | 0.94019 | FALSE | none | -1.9253 | -5.3413 | -2.3478 | -7.1466 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.266 | 0.29402 | 0.047616 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0913 | Night
2025-08-11 | 79.8 | 78.61 | 1.6624 | 81.9348 | 75.2852 | 0.71583 | FALSE | none | -2.1348 | -4.5148 | -2.6055 | -5.997 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.238 | 0.31828 | -1.6275 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0763 | Night
2025-08-11 00:15 | 79.8 | 78.834 | 1.4885 | 81.811 | 75.857 | 0.64898 | FALSE | none | -2.011 | -3.943 | -2.4581 | -5.1979 | Normal | 0 |  |  |  | 0 | 0 | 0.224 | 0.32246 | -0.69465 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Night
2025-08-11 00:30 | 80.08 | 79.058 | 1.3016 | 81.6611 | 76.4549 | 0.78521 | FALSE | none | -1.5811 | -3.6251 | -1.9362 | -4.7415 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.224 | 0.32246 | 0.17366 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0809 | Night
2025-08-11 00:45 | 79.8 | 79.24 | 1.1163 | 81.4726 | 77.0074 | 0.50165 | FALSE | none | -1.6726 | -2.7926 | -2.053 | -3.6264 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.182 | 0.33099 | -1.3958 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.062 | Night
2025-08-11 01:00 | 80.08 | 79.408 | 0.95882 | 81.3256 | 77.4904 | 0.70086 | FALSE | none | -1.2456 | -2.5896 | -1.5317 | -3.3419 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.168 | 0.31989 | 0.35012 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0753 | Night
2025-08-11 01:15 | 79.8 | 79.548 | 0.77564 | 81.0993 | 77.9967 | 0.32489 | FALSE | none | -1.2993 | -1.8033 | -1.6021 | -2.312 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.14 | 0.33378 | -1.2583 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0502 | Night
2025-08-11 01:30 | 80.08 | 79.674 | 0.62593 | 80.9259 | 78.4221 | 0.64863 | FALSE | none | -0.84587 | -1.6579 | -1.0452 | -2.114 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.126 | 0.32086 | 0.47996 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0718 | Night
2025-08-11 01:45 | 79.8 | 79.758 | 0.50804 | 80.7741 | 78.7419 | 0.082671 | FALSE | none | -0.97407 | -1.0581 | -1.2059 | -1.3437 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.084 | 0.316 | -1.1519 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0341 | Night
2025-08-11 02:00 | 80.08 | 79.842 | 0.39884 | 80.6397 | 79.0443 | 0.59674 | FALSE | none | -0.55967 | -1.0357 | -0.69404 | -1.3102 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.084 | 0.316 | 0.62025 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0398 | Night
2025-08-11 02:15 | 80.08 | 79.912 | 0.29296 | 80.4979 | 79.3261 | 0.57345 | FALSE | none | -0.41793 | -0.75393 | -0.51918 | -0.95041 | Normal | 0 |  |  |  | 0 | 0 | 0.07 | 0.31305 | -0.22361 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0382 | Night
2025-08-11 02:30 | 79.8 | 79.954 | 0.19217 | 80.3383 | 79.5697 | -0.80136 | FALSE | none | -0.53835 | -0.23035 | -0.6701 | -0.28949 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.042 | 0.31828 | -1.0117 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0534 | Night
2025-08-11 02:45 | 80.08 | 79.982 | 0.1644 | 80.3108 | 79.6532 | 0.59611 | FALSE | none | -0.2308 | -0.4268 | -0.28738 | -0.53582 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.028 | 0.29992 | 0.84022 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0397 | Night
2025-08-11 03:00 | 79.8 | 79.968 | 0.16751 | 80.303 | 79.633 | -1.0029 | FALSE | none | -0.50302 | -0.16702 | -0.6264 | -0.20973 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.27963 | -0.95125 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0669 | Night
2025-08-11 03:15 | 79.8 | 79.968 | 0.16751 | 80.303 | 79.633 | -1.0029 | FALSE | none | -0.50302 | -0.16702 | -0.6264 | -0.20973 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.27253 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0669 | Night
2025-08-11 03:30 | 80.08 | 79.968 | 0.16751 | 80.303 | 79.633 | 0.66862 | FALSE | none | -0.22302 | -0.44702 | -0.27772 | -0.56135 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.27253 | 1.0274 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0446 | Night
2025-08-11 03:45 | 80.08 | 79.968 | 0.16751 | 80.303 | 79.633 | 0.66862 | FALSE | none | -0.22302 | -0.44702 | -0.27772 | -0.56135 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.27253 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0446 | Night
2025-08-11 04:00 | 80.08 | 79.968 | 0.16751 | 80.303 | 79.633 | 0.66862 | FALSE | none | -0.22302 | -0.44702 | -0.27772 | -0.56135 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.27253 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0446 | Night
2025-08-11 04:15 | 80.08 | 79.954 | 0.14292 | 80.2398 | 79.6682 | 0.88163 | FALSE | none | -0.15983 | -0.41183 | -0.1992 | -0.51694 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.26446 | 0.052937 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Night
2025-08-11 04:30 | 80.36 | 79.982 | 0.1644 | 80.3108 | 79.6532 | 2.2993 | TRUE | upper | 0.0492 | -0.7068 | 0.061262 | -0.88735 | Extreme triggered | 1 | 2025-08-11 04:30 | 2025-08-11 05:30 | 2.2993 | 0.28 | 0.28 | 0.028 | 0.23863 | 1.056 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.2104 | Night
2025-08-11 04:45 | 79.8 | 79.968 | 0.16751 | 80.303 | 79.633 | -1.0029 | FALSE | none | -0.50302 | -0.16702 | -0.6264 | -0.20973 | Extreme/elevated | 2 | 2025-08-11 04:30 |  | 1.6511 | -0.56 | -0.56 | -0.014 | 0.26446 | -2.0646 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.2097 | Night
2025-08-11 05:00 | 79.8 | 79.968 | 0.16751 | 80.303 | 79.633 | -1.0029 | FALSE | none | -0.50302 | -0.16702 | -0.6264 | -0.20973 | Persistent | 3 | 2025-08-11 04:30 |  | 1.435 | 0 | 0 | 0 | 0.25695 | 0 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.2669 | Night
2025-08-11 05:15 | 79.8 | 79.968 | 0.16751 | 80.303 | 79.633 | -1.0029 | FALSE | none | -0.50302 | -0.16702 | -0.6264 | -0.20973 | Persistent | 4 | 2025-08-11 04:30 |  | 1.327 | 0 | 0 | 0 | 0.25695 | 0 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.324 | Night
2025-08-11 05:30 | 80.08 | 79.968 | 0.16751 | 80.303 | 79.633 | 0.66862 | FALSE | none | -0.22302 | -0.44702 | -0.27772 | -0.56135 | Persistence ends | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.25695 | 1.0897 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0731 | Night
2025-08-11 05:45 | 80.08 | 79.982 | 0.1644 | 80.3108 | 79.6532 | 0.59611 | FALSE | none | -0.2308 | -0.4268 | -0.28738 | -0.53582 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.24837 | -0.056367 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0683 | Night
2025-08-11 06:00 | 80.08 | 79.982 | 0.1644 | 80.3108 | 79.6532 | 0.59611 | FALSE | none | -0.2308 | -0.4268 | -0.28738 | -0.53582 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.24035 | 0 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0683 | Night
2025-08-11 06:15 | 80.08 | 79.996 | 0.15995 | 80.3159 | 79.6761 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.29371 | -0.50692 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.23116 | -0.060564 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0636 | Night
2025-08-11 06:30 | 80.08 | 79.996 | 0.15995 | 80.3159 | 79.6761 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.29371 | -0.50692 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.22252 | 0 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0636 | Night
2025-08-11 06:45 | 79.8 | 79.996 | 0.15995 | 80.3159 | 79.6761 | -1.2254 | FALSE | none | -0.51589 | -0.12389 | -0.64233 | -0.1555 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.22252 | -1.2583 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1103 | Night
2025-08-11 07:00 | 79.8 | 79.982 | 0.1644 | 80.3108 | 79.6532 | -1.1071 | FALSE | none | -0.5108 | -0.1468 | -0.63603 | -0.1843 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.21256 | 0.065863 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1024 | Day
2025-08-11 07:15 | 80.36 | 79.996 | 0.18395 | 80.3639 | 79.6281 | 1.9789 | FALSE | none | -0.0038901 | -0.73189 | -0.0048407 | -0.91914 | Normal | 0 |  |  |  | 0.56 | 0.56 | 0.014 | 0.24837 | 2.1983 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1605 | Day
2025-08-11 07:30 | 80.08 | 80.01 | 0.17883 | 80.3677 | 79.6523 | 0.39144 | FALSE | none | -0.28765 | -0.42765 | -0.35792 | -0.5369 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.014 | 0.24837 | -1.1837 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0547 | Day
2025-08-11 07:45 | 80.08 | 80.01 | 0.17883 | 80.3677 | 79.6523 | 0.39144 | FALSE | none | -0.28765 | -0.42765 | -0.35792 | -0.5369 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.24035 | 0 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0547 | Day
2025-08-11 08:00 | 80.08 | 80.024 | 0.17236 | 80.3687 | 79.6793 | 0.32489 | FALSE | none | -0.28873 | -0.40073 | -0.35926 | -0.50293 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.23116 | -0.060564 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0502 | Day
2025-08-11 08:15 | 79.24 | 79.996 | 0.24206 | 80.4801 | 79.5119 | -3.1232 | TRUE | lower | -1.2401 | 0.27188 | -1.5409 | 0.34193 | Extreme triggered | 1 | 2025-08-11 08:15 | 2025-08-11 11:30 | 3.1232 | -0.84 | -0.84 | -0.028 | 0.29992 | -2.7074 | TRUE | 2 | TRUE | FALSE | FALSE | TRUE | 0.3225 | Day
2025-08-11 08:30 | 78.68 | 79.926 | 0.37976 | 80.6855 | 79.1665 | -3.2811 | TRUE | lower | -2.0055 | 0.48649 | -2.4856 | 0.61451 | Extreme/elevated | 2 | 2025-08-11 08:15 |  | 3.2021 | -0.56 | -0.56 | -0.07 | 0.31305 | -1.5652 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.3902 | Day
2025-08-11 08:45 | 78.12 | 79.828 | 0.55184 | 80.9317 | 78.7243 | -3.0951 | TRUE | lower | -2.8117 | 0.60433 | -3.4741 | 0.76765 | Persistent | 3 | 2025-08-11 08:15 |  | 3.1665 | -0.56 | -0.56 | -0.098 | 0.33099 | -1.3958 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.4349 | Day
2025-08-11 09:00 | 77 | 79.674 | 0.83495 | 81.3439 | 78.0041 | -3.2026 | TRUE | lower | -4.3439 | 1.0041 | -5.3402 | 1.2872 | Persistent | 4 | 2025-08-11 08:15 |  | 3.1755 | -1.12 | -1.12 | -0.154 | 0.4009 | -2.4096 | TRUE | 3 | TRUE | TRUE | FALSE | TRUE | 0.5278 | Day
2025-08-11 09:15 | 76.72 | 79.506 | 1.0574 | 81.6207 | 77.3913 | -2.6348 | TRUE | lower | -4.9007 | 0.67127 | -6.0043 | 0.86737 | Persistent | 5 | 2025-08-11 08:15 |  | 3.0674 | -0.28 | -0.28 | -0.168 | 0.40013 | -0.27991 | FALSE | 3 | FALSE | TRUE | FALSE | FALSE | 0.5471 | Day
2025-08-11 09:30 | 76.16 | 79.296 | 1.2738 | 81.8435 | 76.7485 | -2.462 | TRUE | lower | -5.6835 | 0.58848 | -6.9444 | 0.76676 | Persistent | 6 | 2025-08-11 08:15 |  | 2.9665 | -0.56 | -0.56 | -0.21 | 0.39468 | -0.88681 | FALSE | 3 | FALSE | TRUE | FALSE | FALSE | 0.5927 | Day
2025-08-11 09:45 | 75.6 | 79.086 | 1.5105 | 82.107 | 76.065 | -2.3078 | TRUE | lower | -6.507 | 0.46498 | -7.9251 | 0.61129 | Confirmed/Materialized Shift | 7 | 2025-08-11 08:15 |  | 2.8724 | -0.56 | -0.56 | -0.21 | 0.39468 | -0.88681 | FALSE | 2 | FALSE | TRUE | TRUE | FALSE | 0.611 | Day
2025-08-11 10:00 | 75.04 | 78.848 | 1.7484 | 82.3447 | 75.3513 | -2.178 | TRUE | lower | -7.3047 | 0.31127 | -8.8709 | 0.4131 | Confirmed/Materialized Shift | 8 | 2025-08-11 08:15 |  | 2.7856 | -0.56 | -0.56 | -0.238 | 0.39884 | -0.80735 | FALSE | 2 | FALSE | TRUE | TRUE | FALSE | 0.6023 | Day
2025-08-11 10:15 | 75.04 | 78.61 | 1.9268 | 82.4636 | 74.7564 | -1.8528 | FALSE | none | -7.4236 | -0.28365 | -9.0023 | -0.37943 | Confirmed/Materialized Shift | 9 | 2025-08-11 08:15 |  | 2.6819 | 0 | 0 | -0.238 | 0.39884 | 0.59674 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5807 | Day
2025-08-11 10:30 | 74.76 | 78.344 | 2.0747 | 82.4935 | 74.1945 | -1.7274 | FALSE | none | -7.7335 | -0.56549 | -9.3747 | -0.76218 | Confirmed/Materialized Shift | 10 | 2025-08-11 08:15 |  | 2.5865 | -0.28 | -0.28 | -0.266 | 0.37976 | -0.036866 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5723 | Day
2025-08-11 10:45 | 75.04 | 78.092 | 2.1572 | 82.4065 | 73.7775 | -1.4148 | FALSE | none | -7.3665 | -1.2625 | -8.9392 | -1.7112 | Confirmed/Materialized Shift | 11 | 2025-08-11 08:15 |  | 2.48 | 0.28 | 0.28 | -0.252 | 0.39494 | 1.3471 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5229 | Day
2025-08-11 11:00 | 74.48 | 77.812 | 2.2472 | 82.3063 | 73.3177 | -1.4828 | FALSE | none | -7.8263 | -1.1623 | -9.5088 | -1.5854 | Confirmed/Materialized Shift | 12 | 2025-08-11 08:15 |  | 2.3969 | -0.56 | -0.56 | -0.28 | 0.39598 | -0.70711 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5274 | Day
2025-08-11 11:15 | 74.76 | 77.546 | 2.2792 | 82.1044 | 72.9876 | -1.2224 | FALSE | none | -7.3444 | -1.7724 | -8.9452 | -2.4284 | Confirmed/Materialized Shift | 13 | 2025-08-11 08:15 |  | 2.3065 | 0.28 | 0.28 | -0.266 | 0.41106 | 1.3283 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5101 | Day
2025-08-11 11:30 | 75.04 | 77.294 | 2.2629 | 81.8197 | 72.7683 | -0.99608 | FALSE | none | -6.7797 | -2.2717 | -8.2862 | -3.1219 | Persistence ends | 0 |  |  |  | 0.28 | 0.28 | -0.252 | 0.42513 | 1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0664 | Day
2025-08-11 11:45 | 74.76 | 77.042 | 2.2497 | 81.5414 | 72.5426 | -1.0144 | FALSE | none | -6.7814 | -2.2174 | -8.3165 | -3.0567 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.252 | 0.42513 | -0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0676 | Day
2025-08-11 12:00 | 74.76 | 76.79 | 2.2064 | 81.2027 | 72.3773 | -0.92007 | FALSE | none | -6.4427 | -2.3827 | -7.9341 | -3.2921 | Normal | 0 |  |  |  | 0 | 0 | -0.252 | 0.42513 | 0.59276 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0613 | Day
2025-08-11 12:15 | 75.04 | 76.524 | 2.0698 | 80.6635 | 72.3845 | -0.71699 | FALSE | none | -5.6235 | -2.6555 | -6.9716 | -3.6687 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.266 | 0.4009 | 1.3619 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0478 | Day
2025-08-11 12:30 | 74.76 | 76.258 | 1.9255 | 80.1091 | 72.4069 | -0.77796 | FALSE | none | -5.3491 | -2.3531 | -6.6772 | -3.2498 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.266 | 0.4009 | -0.034922 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0519 | Day
2025-08-11 12:45 | 75.04 | 76.006 | 1.7176 | 79.4412 | 72.5708 | -0.56242 | FALSE | none | -4.4012 | -2.4692 | -5.5402 | -3.4024 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.252 | 0.41531 | 1.281 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0375 | Day
2025-08-11 13:00 | 74.76 | 75.74 | 1.4435 | 78.6271 | 72.8529 | -0.67889 | FALSE | none | -3.8671 | -1.9071 | -4.9182 | -2.6177 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.266 | 0.41106 | -0.034058 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0453 | Day
2025-08-11 13:15 | 74.48 | 75.502 | 1.2095 | 77.9211 | 73.0829 | -0.84495 | FALSE | none | -3.4411 | -1.3971 | -4.4161 | -1.9116 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.238 | 0.38835 | -0.10815 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0563 | Day
2025-08-11 13:30 | 74.76 | 75.306 | 0.95915 | 77.2243 | 73.3877 | -0.56926 | FALSE | none | -2.4643 | -1.3723 | -3.1911 | -1.8699 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.196 | 0.39702 | 1.1989 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.038 | Day
2025-08-11 13:45 | 74.76 | 75.138 | 0.69941 | 76.5368 | 73.7392 | -0.54046 | FALSE | none | -1.7768 | -1.0208 | -2.3215 | -1.3844 | Normal | 0 |  |  |  | 0 | 0 | -0.168 | 0.38968 | 0.43113 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.036 | Day
2025-08-11 14:00 | 74.76 | 75.026 | 0.54865 | 76.1233 | 73.9287 | -0.48483 | FALSE | none | -1.3633 | -0.8313 | -1.7909 | -1.1245 | Normal | 0 |  |  |  | 0 | 0 | -0.112 | 0.31989 | 0.35012 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0323 | Day
2025-08-11 14:15 | 74.76 | 74.928 | 0.37894 | 75.6859 | 74.1701 | -0.44334 | FALSE | none | -0.92588 | -0.58988 | -1.2233 | -0.79531 | Normal | 0 |  |  |  | 0 | 0 | -0.098 | 0.31828 | 0.30791 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0296 | Day
2025-08-11 14:30 | 75.04 | 74.872 | 0.24712 | 75.3662 | 74.3778 | 0.67983 | FALSE | none | -0.32624 | -0.66224 | -0.43288 | -0.89038 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.056 | 0.3094 | 1.086 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0453 | Day
2025-08-11 14:45 | 74.76 | 74.83 | 0.17883 | 75.1877 | 74.4723 | -0.39144 | FALSE | none | -0.42765 | -0.28765 | -0.56878 | -0.38626 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.042 | 0.2912 | -0.81732 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0261 | Day
2025-08-11 15:00 | 75.32 | 74.844 | 0.20515 | 75.2543 | 74.4337 | 2.3202 | TRUE | upper | 0.065691 | -0.88631 | 0.087292 | -1.1907 | Extreme triggered | 1 | 2025-08-11 15:00 | 2025-08-11 15:15 | 2.3202 | 0.56 | 0.56 | 0.014 | 0.29402 | 1.857 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.2118 | Day
2025-08-11 15:15 | 74.76 | 74.83 | 0.20058 | 75.2312 | 74.4288 | -0.34899 | FALSE | none | -0.47116 | -0.33116 | -0.62628 | -0.44493 | Persistence ends | 0 |  |  |  | -0.56 | -0.56 | -0.014 | 0.32086 | -1.7017 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0233 | Day
2025-08-11 15:30 | 74.76 | 74.83 | 0.20058 | 75.2312 | 74.4288 | -0.34899 | FALSE | none | -0.47116 | -0.33116 | -0.62628 | -0.44493 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.31469 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0233 | Day
2025-08-11 15:45 | 75.04 | 74.83 | 0.20058 | 75.2312 | 74.4288 | 1.047 | FALSE | none | -0.19116 | -0.61116 | -0.25409 | -0.82113 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.31469 | 0.88976 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0698 | Day
2025-08-11 16:00 | 74.76 | 74.844 | 0.18395 | 75.2119 | 74.4761 | -0.45666 | FALSE | none | -0.45189 | -0.28389 | -0.60082 | -0.38118 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.014 | 0.29402 | -0.99994 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0304 | Day
2025-08-11 16:15 | 74.76 | 74.844 | 0.18395 | 75.2119 | 74.4761 | -0.45666 | FALSE | none | -0.45189 | -0.28389 | -0.60082 | -0.38118 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.28727 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0304 | Day
2025-08-11 16:30 | 75.04 | 74.844 | 0.18395 | 75.2119 | 74.4761 | 1.0655 | FALSE | none | -0.17189 | -0.56389 | -0.22854 | -0.75714 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.28727 | 0.97468 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.071 | Day
2025-08-11 16:45 | 75.04 | 74.858 | 0.18783 | 75.2337 | 74.4823 | 0.96896 | FALSE | none | -0.19366 | -0.55766 | -0.25741 | -0.74871 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.27963 | -0.050066 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0646 | Day
2025-08-11 17:00 | 75.04 | 74.872 | 0.19056 | 75.2531 | 74.4909 | 0.88163 | FALSE | none | -0.21311 | -0.54911 | -0.28319 | -0.73715 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.27963 | -0.050066 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-11 17:15 | 75.04 | 74.872 | 0.19056 | 75.2531 | 74.4909 | 0.88163 | FALSE | none | -0.21311 | -0.54911 | -0.28319 | -0.73715 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.27253 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Day
2025-08-11 17:30 | 74.76 | 74.872 | 0.19056 | 75.2531 | 74.4909 | -0.58775 | FALSE | none | -0.49311 | -0.26911 | -0.65527 | -0.36127 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.27253 | -1.0274 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0392 | Day
2025-08-11 17:45 | 74.76 | 74.858 | 0.18783 | 75.2337 | 74.4823 | -0.52175 | FALSE | none | -0.47366 | -0.27766 | -0.62958 | -0.37279 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.26446 | 0.052937 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0348 | Day
2025-08-11 18:00 | 75.32 | 74.886 | 0.21256 | 75.3111 | 74.4609 | 2.0417 | TRUE | upper | 0.0088734 | -0.85913 | 0.011782 | -1.1538 | Extreme triggered | 1 | 2025-08-11 18:00 | 2025-08-11 18:15 | 2.0417 | 0.56 | 0.56 | 0.028 | 0.28583 | 1.8612 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1933 | Day
2025-08-11 18:15 | 74.76 | 74.9 | 0.19271 | 75.2854 | 74.5146 | -0.72648 | FALSE | none | -0.52542 | -0.24542 | -0.6979 | -0.32936 | Persistence ends | 0 |  |  |  | -0.56 | -0.56 | 0.014 | 0.30773 | -1.8653 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0484 | Day
2025-08-11 18:30 | 75.04 | 74.914 | 0.19217 | 75.2983 | 74.5297 | 0.65566 | FALSE | none | -0.25835 | -0.51035 | -0.3431 | -0.68476 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.30773 | 0.86439 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0437 | Day
2025-08-11 18:45 | 75.04 | 74.928 | 0.19056 | 75.3091 | 74.5469 | 0.58775 | FALSE | none | -0.26911 | -0.49311 | -0.35734 | -0.66148 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.30773 | -0.045494 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0392 | Day
2025-08-11 19:00 | 75.04 | 74.942 | 0.18783 | 75.3177 | 74.5663 | 0.52175 | FALSE | none | -0.27766 | -0.47366 | -0.36865 | -0.63522 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.30773 | -0.045494 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0348 | Night
2025-08-11 19:15 | 75.04 | 74.956 | 0.18395 | 75.3239 | 74.5881 | 0.45666 | FALSE | none | -0.28389 | -0.45189 | -0.37689 | -0.60585 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.30773 | -0.045494 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0304 | Night
2025-08-11 19:30 | 75.6 | 74.984 | 0.23338 | 75.4508 | 74.5172 | 2.6394 | TRUE | upper | 0.14924 | -1.0828 | 0.19779 | -1.453 | Extreme triggered | 1 | 2025-08-11 19:30 | 2025-08-11 23:45 | 2.6394 | 0.56 | 0.56 | 0.028 | 0.32628 | 1.6305 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.2331 | Night
2025-08-11 19:45 | 76.16 | 75.054 | 0.34563 | 75.7453 | 74.3627 | 3.2 | TRUE | upper | 0.41475 | -1.7973 | 0.54756 | -2.4169 | Extreme/elevated | 2 | 2025-08-11 19:30 |  | 2.9197 | 0.56 | 0.56 | 0.07 | 0.33839 | 1.448 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.3276 | Night
2025-08-11 20:00 | 76.44 | 75.11 | 0.4621 | 76.0342 | 74.1858 | 2.8782 | TRUE | upper | 0.4058 | -2.2542 | 0.53371 | -3.0386 | Persistent | 3 | 2025-08-11 19:30 |  | 2.9059 | 0.28 | 0.28 | 0.056 | 0.32246 | 0.69465 | FALSE | 0 | FALSE | TRUE | FALSE | FALSE | 0.3633 | Night
2025-08-11 20:15 | 76.72 | 75.208 | 0.57741 | 76.3628 | 74.0532 | 2.6186 | TRUE | upper | 0.35717 | -2.6668 | 0.46773 | -3.6012 | Persistent | 4 | 2025-08-11 19:30 |  | 2.834 | 0.28 | 0.28 | 0.098 | 0.2912 | 0.62501 | FALSE | 0 | FALSE | TRUE | FALSE | FALSE | 0.4031 | Night
2025-08-11 20:30 | 77.56 | 75.348 | 0.7703 | 76.8886 | 73.8074 | 2.8716 | TRUE | upper | 0.6714 | -3.7526 | 0.87321 | -5.0843 | Persistent | 5 | 2025-08-11 19:30 |  | 2.8416 | 0.84 | 0.84 | 0.14 | 0.33378 | 2.0972 | TRUE | 1 | FALSE | TRUE | FALSE | FALSE | 0.5057 | Night
2025-08-11 20:45 | 77.56 | 75.474 | 0.91059 | 77.2952 | 73.6528 | 2.2908 | TRUE | upper | 0.26481 | -3.9072 | 0.3426 | -5.3049 | Persistent | 6 | 2025-08-11 19:30 |  | 2.7498 | 0 | 0 | 0.126 | 0.33347 | -0.37784 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.5241 | Night
2025-08-11 21:00 | 78.4 | 75.656 | 1.1037 | 77.8633 | 73.4487 | 2.4862 | TRUE | upper | 0.53666 | -4.9513 | 0.68923 | -6.7412 | Confirmed/Materialized Shift | 7 | 2025-08-11 19:30 |  | 2.7121 | 0.84 | 0.84 | 0.182 | 0.35505 | 1.8533 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5943 | Night
2025-08-11 21:15 | 78.68 | 75.852 | 1.2715 | 78.395 | 73.309 | 2.2242 | TRUE | upper | 0.28502 | -5.371 | 0.36357 | -7.3265 | Confirmed/Materialized Shift | 8 | 2025-08-11 19:30 |  | 2.6511 | 0.28 | 0.28 | 0.196 | 0.35301 | 0.23795 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5768 | Night
2025-08-11 21:30 | 79.24 | 76.062 | 1.4628 | 78.9875 | 73.1365 | 2.1726 | TRUE | upper | 0.25246 | -6.1035 | 0.31962 | -8.3454 | Confirmed/Materialized Shift | 9 | 2025-08-11 19:30 |  | 2.598 | 0.56 | 0.56 | 0.21 | 0.36195 | 0.96697 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5734 | Night
2025-08-11 21:45 | 79.52 | 76.286 | 1.6313 | 79.5487 | 73.0233 | 1.9824 | FALSE | none | -0.028678 | -6.4967 | -0.036051 | -8.8967 | Confirmed/Materialized Shift | 10 | 2025-08-11 19:30 |  | 2.5364 | 0.28 | 0.28 | 0.224 | 0.35881 | 0.15607 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5607 | Night
2025-08-11 22:00 | 80.08 | 76.538 | 1.8084 | 80.1548 | 72.9212 | 1.9586 | FALSE | none | -0.074801 | -7.1588 | -0.09332 | -9.8172 | Confirmed/Materialized Shift | 11 | 2025-08-11 19:30 |  | 2.4839 | 0.56 | 0.56 | 0.252 | 0.36224 | 0.85027 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5591 | Night
2025-08-11 22:15 | 79.8 | 76.776 | 1.9112 | 80.5984 | 72.9536 | 1.5823 | FALSE | none | -0.79836 | -6.8464 | -0.99054 | -9.3845 | Confirmed/Materialized Shift | 12 | 2025-08-11 19:30 |  | 2.4087 | -0.28 | -0.28 | 0.238 | 0.37758 | -1.3719 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5341 | Night
2025-08-11 22:30 | 79.8 | 77.028 | 1.9629 | 80.9539 | 73.1021 | 1.4122 | FALSE | none | -1.1539 | -6.6979 | -1.4254 | -9.1624 | Confirmed/Materialized Shift | 13 | 2025-08-11 19:30 |  | 2.3321 | 0 | 0 | 0.252 | 0.36224 | -0.69567 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5227 | Night
2025-08-11 22:45 | 79.8 | 77.28 | 1.9799 | 81.2398 | 73.3202 | 1.2728 | FALSE | none | -1.4398 | -6.4798 | -1.7723 | -8.8377 | Confirmed/Materialized Shift | 14 | 2025-08-11 19:30 |  | 2.2564 | 0 | 0 | 0.252 | 0.36224 | -0.69567 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5134 | Night
2025-08-11 23:00 | 79.8 | 77.504 | 1.9998 | 81.5036 | 73.5044 | 1.1481 | FALSE | none | -1.7036 | -6.2956 | -2.0902 | -8.5649 | Confirmed/Materialized Shift | 15 | 2025-08-11 19:30 |  | 2.1825 | 0 | 0 | 0.224 | 0.35881 | -0.62429 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4765 | Night
2025-08-11 23:15 | 80.08 | 77.77 | 1.9692 | 81.7084 | 73.8316 | 1.1731 | FALSE | none | -1.6284 | -6.2484 | -1.9929 | -8.463 | Confirmed/Materialized Shift | 16 | 2025-08-11 19:30 |  | 2.1194 | 0.28 | 0.28 | 0.266 | 0.30773 | 0.045494 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4782 | Night
2025-08-11 23:30 | 80.08 | 78.022 | 1.9234 | 81.8688 | 74.1752 | 1.07 | FALSE | none | -1.7888 | -5.9048 | -2.1849 | -7.9606 | Confirmed/Materialized Shift | 17 | 2025-08-11 19:30 |  | 2.0577 | 0 | 0 | 0.252 | 0.31338 | -0.80414 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4713 | Night
2025-08-11 23:45 | 79.8 | 78.26 | 1.8271 | 81.9141 | 74.6059 | 0.84288 | FALSE | none | -2.1141 | -5.1941 | -2.5809 | -6.9621 | Persistence ends | 0 |  |  |  | -0.28 | -0.28 | 0.238 | 0.33099 | -1.565 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0562 | Night
2025-08-12 | 79.8 | 78.498 | 1.6905 | 81.8789 | 75.1171 | 0.7702 | FALSE | none | -2.0789 | -4.6829 | -2.539 | -6.2342 | Normal | 0 |  |  |  | 0 | 0 | 0.238 | 0.33099 | -0.71906 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0513 | Night
2025-08-12 00:15 | 80.08 | 78.75 | 1.5143 | 81.7787 | 75.7213 | 0.87828 | FALSE | none | -1.6987 | -4.3587 | -2.0771 | -5.7562 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.252 | 0.32628 | 0.085816 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0586 | Night
2025-08-12 00:30 | 80.08 | 78.974 | 1.3458 | 81.6657 | 76.2823 | 0.8218 | FALSE | none | -1.5857 | -3.7977 | -1.9416 | -4.9784 | Normal | 0 |  |  |  | 0 | 0 | 0.224 | 0.32246 | -0.69465 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0548 | Night
2025-08-12 00:45 | 80.08 | 79.17 | 1.191 | 81.5519 | 76.7881 | 0.76408 | FALSE | none | -1.4719 | -3.2919 | -1.8049 | -4.2871 | Normal | 0 |  |  |  | 0 | 0 | 0.196 | 0.316 | -0.62025 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0509 | Night
2025-08-12 01:00 | 79.8 | 79.338 | 1.0086 | 81.3553 | 77.3207 | 0.45805 | FALSE | none | -1.5553 | -2.4793 | -1.9117 | -3.2065 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.168 | 0.33254 | -1.3472 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0305 | Night
2025-08-12 01:15 | 80.08 | 79.506 | 0.80986 | 81.1257 | 77.8863 | 0.70876 | FALSE | none | -1.0457 | -2.1937 | -1.289 | -2.8166 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.168 | 0.33254 | 0.3368 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0473 | Night
2025-08-12 01:30 | 79.8 | 79.618 | 0.66926 | 80.9565 | 78.2795 | 0.27194 | FALSE | none | -1.1565 | -1.5205 | -1.4286 | -1.9424 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.112 | 0.30672 | -1.278 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0181 | Night
2025-08-12 01:45 | 80.08 | 79.744 | 0.46853 | 80.6811 | 78.8069 | 0.71714 | FALSE | none | -0.60106 | -1.2731 | -0.74498 | -1.6154 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.126 | 0.30773 | 0.50044 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0478 | Night
2025-08-12 02:00 | 80.08 | 79.828 | 0.35066 | 80.5293 | 79.1267 | 0.71864 | FALSE | none | -0.44933 | -0.95333 | -0.55796 | -1.2048 | Normal | 0 |  |  |  | 0 | 0 | 0.084 | 0.25855 | -0.32489 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0479 | Night
2025-08-12 02:15 | 80.36 | 79.912 | 0.24712 | 80.4062 | 79.4178 | 1.8129 | FALSE | none | -0.046245 | -0.94224 | -0.057514 | -1.1864 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.084 | 0.25855 | 0.75808 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1209 | Night
2025-08-12 02:30 | 80.08 | 79.954 | 0.19217 | 80.3383 | 79.5697 | 0.65566 | FALSE | none | -0.25835 | -0.51035 | -0.32157 | -0.64138 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.042 | 0.24503 | -1.3141 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0437 | Night
2025-08-12 02:45 | 80.08 | 79.982 | 0.1644 | 80.3108 | 79.6532 | 0.59611 | FALSE | none | -0.2308 | -0.4268 | -0.28738 | -0.53582 | Normal | 0 |  |  |  | 0 | 0 | 0.028 | 0.23863 | -0.11734 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0397 | Night
2025-08-12 03:00 | 79.8 | 79.968 | 0.16751 | 80.303 | 79.633 | -1.0029 | FALSE | none | -0.50302 | -0.16702 | -0.6264 | -0.20973 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.21256 | -1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0669 | Night
2025-08-12 03:15 | 79.8 | 79.968 | 0.16751 | 80.303 | 79.633 | -1.0029 | FALSE | none | -0.50302 | -0.16702 | -0.6264 | -0.20973 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.20313 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0669 | Night
2025-08-12 03:30 | 80.08 | 79.982 | 0.1644 | 80.3108 | 79.6532 | 0.59611 | FALSE | none | -0.2308 | -0.4268 | -0.28738 | -0.53582 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.21256 | 1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0397 | Night
2025-08-12 03:45 | 80.08 | 79.996 | 0.15995 | 80.3159 | 79.6761 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.29371 | -0.50692 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.21256 | -0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.035 | Night
2025-08-12 04:00 | 80.08 | 80.01 | 0.15403 | 80.3181 | 79.7019 | 0.45445 | FALSE | none | -0.23807 | -0.37807 | -0.29641 | -0.47435 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.21256 | -0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0303 | Night
2025-08-12 04:15 | 79.8 | 79.996 | 0.15995 | 80.3159 | 79.6761 | -1.2254 | FALSE | none | -0.51589 | -0.12389 | -0.64233 | -0.1555 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.21256 | -1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0817 | Night
2025-08-12 04:30 | 80.08 | 79.996 | 0.15995 | 80.3159 | 79.6761 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.29371 | -0.50692 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.22252 | 1.2583 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.035 | Night
2025-08-12 04:45 | 80.08 | 80.01 | 0.15403 | 80.3181 | 79.7019 | 0.45445 | FALSE | none | -0.23807 | -0.37807 | -0.29641 | -0.47435 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.21256 | -0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0303 | Night
2025-08-12 05:00 | 79.8 | 80.01 | 0.15403 | 80.3181 | 79.7019 | -1.3633 | FALSE | none | -0.51807 | -0.098067 | -0.64502 | -0.12304 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.22252 | -1.2583 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0909 | Night
2025-08-12 05:15 | 79.8 | 79.996 | 0.15995 | 80.3159 | 79.6761 | -1.2254 | FALSE | none | -0.51589 | -0.12389 | -0.64233 | -0.1555 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.21256 | 0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0817 | Night
2025-08-12 05:30 | 80.36 | 80.01 | 0.17883 | 80.3677 | 79.6523 | 1.9572 | FALSE | none | -0.0076532 | -0.70765 | -0.0095227 | -0.88843 | Normal | 0 |  |  |  | 0.56 | 0.56 | 0.014 | 0.24837 | 2.1983 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1591 | Night
2025-08-12 05:45 | 80.08 | 80.01 | 0.17883 | 80.3677 | 79.6523 | 0.39144 | FALSE | none | -0.28765 | -0.42765 | -0.35792 | -0.5369 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.25695 | -1.0897 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0547 | Night
2025-08-12 06:00 | 80.08 | 80.024 | 0.17236 | 80.3687 | 79.6793 | 0.32489 | FALSE | none | -0.28873 | -0.40073 | -0.35926 | -0.50293 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.24837 | -0.056367 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0502 | Night
2025-08-12 06:15 | 79.8 | 80.01 | 0.17883 | 80.3677 | 79.6523 | -1.1743 | FALSE | none | -0.56765 | -0.14765 | -0.70632 | -0.18537 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.24837 | -1.071 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1069 | Night
2025-08-12 06:30 | 79.8 | 80.01 | 0.17883 | 80.3677 | 79.6523 | -1.1743 | FALSE | none | -0.56765 | -0.14765 | -0.70632 | -0.18537 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.24035 | 0 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1069 | Night
2025-08-12 06:45 | 80.08 | 80.01 | 0.17883 | 80.3677 | 79.6523 | 0.39144 | FALSE | none | -0.28765 | -0.42765 | -0.35792 | -0.5369 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.24035 | 1.165 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0547 | Night
2025-08-12 07:00 | 80.08 | 80.01 | 0.17883 | 80.3677 | 79.6523 | 0.39144 | FALSE | none | -0.28765 | -0.42765 | -0.35792 | -0.5369 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.24035 | 0 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0547 | Day
2025-08-12 07:15 | 79.8 | 79.982 | 0.1644 | 80.3108 | 79.6532 | -1.1071 | FALSE | none | -0.5108 | -0.1468 | -0.63603 | -0.1843 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.028 | 0.23863 | -1.056 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1024 | Day
2025-08-12 07:30 | 80.36 | 79.996 | 0.18395 | 80.3639 | 79.6281 | 1.9789 | FALSE | none | -0.0038901 | -0.73189 | -0.0048407 | -0.91914 | Normal | 0 |  |  |  | 0.56 | 0.56 | 0.014 | 0.26446 | 2.0646 | TRUE | 2 | TRUE | FALSE | FALSE | TRUE | 0.1891 | Day
2025-08-12 07:45 | 79.8 | 79.982 | 0.18783 | 80.3577 | 79.6063 | -0.96896 | FALSE | none | -0.55766 | -0.19366 | -0.69397 | -0.24327 | Normal | 0 |  |  |  | -0.56 | -0.56 | -0.014 | 0.29402 | -1.857 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.1217 | Day
2025-08-12 08:00 | 80.08 | 79.996 | 0.18395 | 80.3639 | 79.6281 | 0.45666 | FALSE | none | -0.28389 | -0.45189 | -0.35326 | -0.5675 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.29402 | 0.90471 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.059 | Day
2025-08-12 08:15 | 79.52 | 79.982 | 0.20864 | 80.3993 | 79.5647 | -2.2143 | TRUE | lower | -0.87929 | 0.044711 | -1.0937 | 0.056194 | Extreme triggered | 1 | 2025-08-12 08:15 | 2025-08-12 12:00 | 2.2143 | -0.56 | -0.56 | -0.014 | 0.32086 | -1.7017 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.2333 | Day
2025-08-12 08:30 | 78.68 | 79.912 | 0.3565 | 80.625 | 79.199 | -3.4558 | TRUE | lower | -1.945 | 0.519 | -2.4124 | 0.65532 | Extreme/elevated | 2 | 2025-08-12 08:15 |  | 2.8351 | -0.84 | -0.84 | -0.07 | 0.36195 | -2.1273 | TRUE | 2 | TRUE | FALSE | FALSE | TRUE | 0.4018 | Day
2025-08-12 08:45 | 77.84 | 79.8 | 0.58169 | 80.9634 | 78.6366 | -3.3695 | TRUE | lower | -3.1234 | 0.79663 | -3.8578 | 1.0131 | Persistent | 3 | 2025-08-12 08:15 |  | 3.0132 | -0.84 | -0.84 | -0.112 | 0.40013 | -1.8194 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.4532 | Day
2025-08-12 09:00 | 77.56 | 79.674 | 0.76263 | 81.1993 | 78.1487 | -2.772 | TRUE | lower | -3.6393 | 0.58874 | -4.4819 | 0.75336 | Persistent | 4 | 2025-08-12 08:15 |  | 2.9529 | -0.28 | -0.28 | -0.126 | 0.4009 | -0.38414 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.4705 | Day
2025-08-12 09:15 | 77 | 79.534 | 0.96771 | 81.4694 | 77.5986 | -2.6185 | TRUE | lower | -4.4694 | 0.59858 | -5.486 | 0.77137 | Persistent | 5 | 2025-08-12 08:15 |  | 2.886 | -0.56 | -0.56 | -0.14 | 0.41131 | -1.0211 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.5174 | Day
2025-08-12 09:30 | 75.88 | 79.324 | 1.2558 | 81.8356 | 76.8124 | -2.7424 | TRUE | lower | -5.9556 | 0.93236 | -7.2776 | 1.2138 | Persistent | 6 | 2025-08-12 08:15 |  | 2.8621 | -1.12 | -1.12 | -0.21 | 0.45308 | -2.0085 | TRUE | 3 | TRUE | TRUE | FALSE | TRUE | 0.6114 | Day
2025-08-12 09:45 | 75.6 | 79.1 | 1.4913 | 82.0827 | 76.1173 | -2.3469 | TRUE | lower | -6.4827 | 0.51733 | -7.8977 | 0.67964 | Confirmed/Materialized Shift | 7 | 2025-08-12 08:15 |  | 2.7885 | -0.28 | -0.28 | -0.224 | 0.45057 | -0.12429 | FALSE | 3 | FALSE | TRUE | TRUE | FALSE | 0.6422 | Day
2025-08-12 10:00 | 74.76 | 78.848 | 1.7671 | 82.3823 | 75.3137 | -2.3133 | TRUE | lower | -7.6223 | 0.55371 | -9.2523 | 0.73521 | Confirmed/Materialized Shift | 8 | 2025-08-12 08:15 |  | 2.7291 | -0.84 | -0.84 | -0.252 | 0.47116 | -1.248 | FALSE | 2 | FALSE | TRUE | TRUE | FALSE | 0.6114 | Day
2025-08-12 10:15 | 74.76 | 78.596 | 1.9718 | 82.5395 | 74.6525 | -1.9455 | FALSE | none | -7.7795 | -0.10751 | -9.4252 | -0.14401 | Confirmed/Materialized Shift | 9 | 2025-08-12 08:15 |  | 2.642 | 0 | 0 | -0.252 | 0.47116 | 0.53485 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5868 | Day
2025-08-12 10:30 | 75.04 | 78.33 | 2.0773 | 82.4846 | 74.1754 | -1.5838 | FALSE | none | -7.4446 | -0.86456 | -9.0254 | -1.1656 | Confirmed/Materialized Shift | 10 | 2025-08-12 08:15 |  | 2.5362 | 0.28 | 0.28 | -0.266 | 0.44943 | 1.2149 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5627 | Day
2025-08-12 10:45 | 74.76 | 78.064 | 2.1795 | 82.423 | 73.705 | -1.5159 | FALSE | none | -7.663 | -1.055 | -9.2972 | -1.4314 | Confirmed/Materialized Shift | 11 | 2025-08-12 08:15 |  | 2.4435 | -0.28 | -0.28 | -0.266 | 0.44943 | -0.031151 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5582 | Day
2025-08-12 11:00 | 74.76 | 77.798 | 2.2442 | 82.2864 | 73.3096 | -1.3537 | FALSE | none | -7.5264 | -1.4504 | -9.1466 | -1.9784 | Confirmed/Materialized Shift | 12 | 2025-08-12 08:15 |  | 2.3526 | 0 | 0 | -0.266 | 0.44943 | 0.59187 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5188 | Day
2025-08-12 11:15 | 75.04 | 77.56 | 2.2729 | 82.1058 | 73.0142 | -1.1087 | FALSE | none | -7.0658 | -2.0258 | -8.6058 | -2.7746 | Confirmed/Materialized Shift | 13 | 2025-08-12 08:15 |  | 2.257 | 0.28 | 0.28 | -0.238 | 0.46566 | 1.1124 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5025 | Day
2025-08-12 11:30 | 75.04 | 77.322 | 2.2752 | 81.8725 | 72.7715 | -1.003 | FALSE | none | -6.8325 | -2.2685 | -8.3452 | -3.1172 | Confirmed/Materialized Shift | 14 | 2025-08-12 08:15 |  | 2.1674 | 0 | 0 | -0.238 | 0.46566 | 0.5111 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.4954 | Day
2025-08-12 11:45 | 74.76 | 77.056 | 2.2466 | 81.5492 | 72.5628 | -1.022 | FALSE | none | -6.7892 | -2.1972 | -8.3253 | -3.0281 | Confirmed/Materialized Shift | 15 | 2025-08-12 08:15 |  | 2.091 | -0.28 | -0.28 | -0.266 | 0.44943 | -0.031151 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.4967 | Day
2025-08-12 12:00 | 75.04 | 76.804 | 2.171 | 81.1459 | 72.4621 | -0.81254 | FALSE | none | -6.1059 | -2.5779 | -7.5246 | -3.5576 | Persistence ends | 0 |  |  |  | 0.28 | 0.28 | -0.252 | 0.46232 | 1.1507 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0542 | Day
2025-08-12 12:15 | 74.76 | 76.552 | 2.0961 | 80.7442 | 72.3598 | -0.85491 | FALSE | none | -5.9842 | -2.4002 | -7.4113 | -3.3171 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.252 | 0.46232 | -0.060564 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.057 | Day
2025-08-12 12:30 | 75.04 | 76.286 | 1.9174 | 80.1208 | 72.4512 | -0.64985 | FALSE | none | -5.0808 | -2.5888 | -6.3414 | -3.5731 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.266 | 0.44015 | 1.2405 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0433 | Day
2025-08-12 12:45 | 74.76 | 76.034 | 1.7556 | 79.5452 | 72.5228 | -0.72568 | FALSE | none | -4.7852 | -2.2372 | -6.0157 | -3.0848 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.252 | 0.43472 | -0.064409 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0484 | Day
2025-08-12 13:00 | 74.76 | 75.768 | 1.4938 | 78.7556 | 72.7804 | -0.67478 | FALSE | none | -3.9956 | -1.9796 | -5.0735 | -2.72 | Normal | 0 |  |  |  | 0 | 0 | -0.266 | 0.42098 | 0.63186 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.045 | Day
2025-08-12 13:15 | 75.04 | 75.544 | 1.2106 | 77.9653 | 73.1227 | -0.41631 | FALSE | none | -2.9253 | -1.9173 | -3.752 | -2.622 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.224 | 0.43187 | 1.167 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0278 | Day
2025-08-12 13:30 | 75.32 | 75.376 | 0.95968 | 77.2954 | 73.4566 | -0.058353 | FALSE | none | -1.9754 | -1.8634 | -2.5556 | -2.5367 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.168 | 0.42025 | 1.066 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0039 | Day
2025-08-12 13:45 | 75.04 | 75.236 | 0.766 | 76.768 | 73.704 | -0.25587 | FALSE | none | -1.728 | -1.336 | -2.2509 | -1.8127 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.14 | 0.39073 | -0.3583 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0171 | Day
2025-08-12 14:00 | 74.76 | 75.096 | 0.54203 | 76.1801 | 74.0119 | -0.61989 | FALSE | none | -1.4201 | -0.74805 | -1.8641 | -1.0107 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.14 | 0.39073 | -0.3583 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0413 | Day
2025-08-12 14:15 | 75.04 | 74.998 | 0.30504 | 75.6081 | 74.3879 | 0.13769 | FALSE | none | -0.56808 | -0.65208 | -0.75134 | -0.87659 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.098 | 0.38835 | 0.97335 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0092 | Day
2025-08-12 14:30 | 74.76 | 74.942 | 0.22756 | 75.3971 | 74.4869 | -0.79978 | FALSE | none | -0.63713 | -0.27313 | -0.84503 | -0.36668 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.056 | 0.3094 | -0.72397 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0533 | Day
2025-08-12 14:45 | 74.76 | 74.9 | 0.16995 | 75.2399 | 74.5601 | -0.82375 | FALSE | none | -0.47991 | -0.19991 | -0.63784 | -0.26812 | Normal | 0 |  |  |  | 0 | 0 | -0.042 | 0.30504 | 0.13769 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0549 | Day
2025-08-12 15:00 | 75.04 | 74.914 | 0.16935 | 75.2527 | 74.5753 | 0.74404 | FALSE | none | -0.21269 | -0.46469 | -0.28264 | -0.62312 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.24837 | 1.071 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0496 | Day
2025-08-12 15:15 | 75.04 | 74.928 | 0.16751 | 75.263 | 74.593 | 0.66862 | FALSE | none | -0.22302 | -0.44702 | -0.29632 | -0.59927 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.24837 | -0.056367 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0446 | Day
2025-08-12 15:30 | 75.04 | 74.928 | 0.16751 | 75.263 | 74.593 | 0.66862 | FALSE | none | -0.22302 | -0.44702 | -0.29632 | -0.59927 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.24035 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0446 | Day
2025-08-12 15:45 | 74.76 | 74.928 | 0.16751 | 75.263 | 74.593 | -1.0029 | FALSE | none | -0.50302 | -0.16702 | -0.66834 | -0.2239 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.24035 | -1.165 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0669 | Day
2025-08-12 16:00 | 75.04 | 74.942 | 0.1644 | 75.2708 | 74.6132 | 0.59611 | FALSE | none | -0.2308 | -0.4268 | -0.30663 | -0.57202 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.24837 | 1.071 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0397 | Day
2025-08-12 16:15 | 75.04 | 74.942 | 0.1644 | 75.2708 | 74.6132 | 0.59611 | FALSE | none | -0.2308 | -0.4268 | -0.30663 | -0.57202 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.24035 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0397 | Day
2025-08-12 16:30 | 75.04 | 74.942 | 0.1644 | 75.2708 | 74.6132 | 0.59611 | FALSE | none | -0.2308 | -0.4268 | -0.30663 | -0.57202 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.24035 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0397 | Day
2025-08-12 16:45 | 74.76 | 74.942 | 0.1644 | 75.2708 | 74.6132 | -1.1071 | FALSE | none | -0.5108 | -0.1468 | -0.67862 | -0.19675 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.24035 | -1.165 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0738 | Day
2025-08-12 17:00 | 74.76 | 74.928 | 0.16751 | 75.263 | 74.593 | -1.0029 | FALSE | none | -0.50302 | -0.16702 | -0.66834 | -0.2239 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.23116 | 0.060564 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0669 | Day
2025-08-12 17:15 | 75.04 | 74.942 | 0.1644 | 75.2708 | 74.6132 | 0.59611 | FALSE | none | -0.2308 | -0.4268 | -0.30663 | -0.57202 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.23116 | 1.1507 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0397 | Day
2025-08-12 17:30 | 75.04 | 74.942 | 0.1644 | 75.2708 | 74.6132 | 0.59611 | FALSE | none | -0.2308 | -0.4268 | -0.30663 | -0.57202 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.22252 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0397 | Day
2025-08-12 17:45 | 75.04 | 74.956 | 0.15995 | 75.2759 | 74.6361 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.31337 | -0.54115 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.21256 | -0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.035 | Day
2025-08-12 18:00 | 74.76 | 74.956 | 0.15995 | 75.2759 | 74.6361 | -1.2254 | FALSE | none | -0.51589 | -0.12389 | -0.68534 | -0.166 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.22252 | -1.2583 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0817 | Day
2025-08-12 18:15 | 75.04 | 74.956 | 0.15995 | 75.2759 | 74.6361 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.31337 | -0.54115 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.22252 | 1.2583 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.035 | Day
2025-08-12 18:30 | 74.76 | 74.928 | 0.14073 | 75.2095 | 74.6465 | -1.1937 | FALSE | none | -0.44947 | -0.11347 | -0.59762 | -0.15201 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.028 | 0.22066 | -1.142 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0796 | Day
2025-08-12 18:45 | 75.04 | 74.928 | 0.14073 | 75.2095 | 74.6465 | 0.79582 | FALSE | none | -0.16947 | -0.39347 | -0.22533 | -0.52711 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.22252 | 1.2583 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0531 | Day
2025-08-12 19:00 | 75.04 | 74.942 | 0.13702 | 75.216 | 74.668 | 0.71522 | FALSE | none | -0.17604 | -0.37204 | -0.23405 | -0.49826 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.21256 | -0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0477 | Night
2025-08-12 19:15 | 75.32 | 74.956 | 0.15995 | 75.2759 | 74.6361 | 2.2757 | TRUE | upper | 0.044105 | -0.68389 | 0.058592 | -0.91631 | Extreme triggered | 1 | 2025-08-12 19:15 | 2025-08-12 23:15 | 2.2757 | 0.28 | 0.28 | 0.014 | 0.21256 | 1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.2089 | Night
2025-08-12 19:30 | 75.88 | 75.012 | 0.25533 | 75.5227 | 74.5013 | 3.3995 | TRUE | upper | 0.35733 | -1.3787 | 0.47314 | -1.8505 | Extreme/elevated | 2 | 2025-08-12 19:15 |  | 2.8376 | 0.56 | 0.56 | 0.056 | 0.23338 | 2.1595 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.3695 | Night
2025-08-12 19:45 | 76.16 | 75.082 | 0.35505 | 75.7921 | 74.3719 | 3.0362 | TRUE | upper | 0.3679 | -1.7881 | 0.48541 | -2.4043 | Persistent | 3 | 2025-08-12 19:15 |  | 2.9038 | 0.28 | 0.28 | 0.07 | 0.23819 | 0.88163 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4024 | Night
2025-08-12 20:00 | 76.72 | 75.166 | 0.50966 | 76.1853 | 74.1467 | 3.0491 | TRUE | upper | 0.53468 | -2.5733 | 0.70182 | -3.4706 | Persistent | 4 | 2025-08-12 19:15 |  | 2.9401 | 0.56 | 0.56 | 0.084 | 0.25855 | 1.8411 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4604 | Night
2025-08-12 20:15 | 77 | 75.264 | 0.65256 | 76.5691 | 73.9589 | 2.6603 | TRUE | upper | 0.43088 | -3.0411 | 0.56273 | -4.1119 | Persistent | 5 | 2025-08-12 19:15 |  | 2.8842 | 0.28 | 0.28 | 0.098 | 0.26132 | 0.69645 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4916 | Night
2025-08-12 20:30 | 77.28 | 75.376 | 0.78987 | 76.9557 | 73.7963 | 2.4105 | TRUE | upper | 0.32425 | -3.4837 | 0.42135 | -4.7208 | Persistent | 6 | 2025-08-12 19:15 |  | 2.8052 | 0.28 | 0.28 | 0.112 | 0.26329 | 0.63808 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.5321 | Night
2025-08-12 20:45 | 77.84 | 75.53 | 0.9479 | 77.4258 | 73.6342 | 2.437 | TRUE | upper | 0.41421 | -4.2058 | 0.53498 | -5.7117 | Confirmed/Materialized Shift | 7 | 2025-08-12 19:15 |  | 2.7526 | 0.56 | 0.56 | 0.154 | 0.26446 | 1.5352 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.591 | Night
2025-08-12 21:00 | 78.4 | 75.698 | 1.1356 | 77.9693 | 73.4267 | 2.3793 | TRUE | upper | 0.43072 | -4.9733 | 0.55242 | -6.7731 | Confirmed/Materialized Shift | 8 | 2025-08-12 19:15 |  | 2.7059 | 0.56 | 0.56 | 0.168 | 0.27852 | 1.4074 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5872 | Night
2025-08-12 21:15 | 78.68 | 75.88 | 1.3039 | 78.4877 | 73.2723 | 2.1475 | TRUE | upper | 0.19229 | -5.4077 | 0.24499 | -7.3803 | Confirmed/Materialized Shift | 9 | 2025-08-12 19:15 |  | 2.6439 | 0.28 | 0.28 | 0.182 | 0.27666 | 0.35422 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5717 | Night
2025-08-12 21:30 | 79.24 | 76.09 | 1.4868 | 79.0637 | 73.1163 | 2.1186 | TRUE | upper | 0.17633 | -6.1237 | 0.22303 | -8.3752 | Confirmed/Materialized Shift | 10 | 2025-08-12 19:15 |  | 2.5914 | 0.56 | 0.56 | 0.21 | 0.28547 | 1.226 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5698 | Night
2025-08-12 21:45 | 79.52 | 76.328 | 1.6362 | 79.6004 | 73.0556 | 1.9509 | FALSE | none | -0.080402 | -6.4644 | -0.10101 | -8.8486 | Confirmed/Materialized Shift | 11 | 2025-08-12 19:15 |  | 2.5331 | 0.28 | 0.28 | 0.238 | 0.26132 | 0.16072 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5586 | Night
2025-08-12 22:00 | 80.08 | 76.594 | 1.7928 | 80.1796 | 73.0084 | 1.9444 | FALSE | none | -0.099634 | -7.0716 | -0.12426 | -9.6861 | Confirmed/Materialized Shift | 12 | 2025-08-12 19:15 |  | 2.4841 | 0.56 | 0.56 | 0.266 | 0.26446 | 1.1117 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.5296 | Night
2025-08-12 22:15 | 80.08 | 76.846 | 1.9131 | 80.6721 | 73.0199 | 1.6905 | FALSE | none | -0.59214 | -7.0601 | -0.73401 | -9.6688 | Confirmed/Materialized Shift | 13 | 2025-08-12 19:15 |  | 2.423 | 0 | 0 | 0.252 | 0.27101 | -0.92984 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.5127 | Night
2025-08-12 22:30 | 80.08 | 77.098 | 1.9929 | 81.0839 | 73.1121 | 1.4963 | FALSE | none | -1.0039 | -6.9679 | -1.2381 | -9.5304 | Confirmed/Materialized Shift | 14 | 2025-08-12 19:15 |  | 2.3568 | 0 | 0 | 0.252 | 0.27101 | -0.92984 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4998 | Night
2025-08-12 22:45 | 80.08 | 77.35 | 2.0372 | 81.4243 | 73.2757 | 1.3401 | FALSE | none | -1.3443 | -6.8043 | -1.651 | -9.2859 | Confirmed/Materialized Shift | 15 | 2025-08-12 19:15 |  | 2.2891 | 0 | 0 | 0.252 | 0.27101 | -0.92984 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4893 | Night
2025-08-12 23:00 | 80.36 | 77.63 | 2.0473 | 81.7245 | 73.5355 | 1.3335 | FALSE | none | -1.3645 | -6.8245 | -1.6697 | -9.2806 | Confirmed/Materialized Shift | 16 | 2025-08-12 19:15 |  | 2.2293 | 0.28 | 0.28 | 0.28 | 0.24035 | 3.0025e-15 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4889 | Night
2025-08-12 23:15 | 79.8 | 77.868 | 2.0066 | 81.8812 | 73.8548 | 0.96282 | FALSE | none | -2.0812 | -5.9452 | -2.5417 | -8.0499 | Persistence ends | 0 |  |  |  | -0.56 | -0.56 | 0.238 | 0.30504 | -2.6161 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0928 | Night
2025-08-12 23:30 | 80.08 | 78.134 | 1.9238 | 81.9816 | 74.2864 | 1.0115 | FALSE | none | -1.9016 | -5.7936 | -2.3196 | -7.7991 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.266 | 0.27963 | 0.050066 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.096 | Night
2025-08-12 23:45 | 80.08 | 78.386 | 1.8248 | 82.0355 | 74.7365 | 0.92834 | FALSE | none | -1.9555 | -5.3435 | -2.3837 | -7.1498 | Normal | 0 |  |  |  | 0 | 0 | 0.252 | 0.28583 | -0.88163 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0905 | Night
2025-08-13 | 79.8 | 78.624 | 1.6692 | 81.9623 | 75.2857 | 0.70455 | FALSE | none | -2.1623 | -4.5143 | -2.6382 | -5.9962 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.238 | 0.30504 | -1.6981 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0755 | Night
2025-08-13 00:15 | 79.8 | 78.848 | 1.4938 | 81.8356 | 75.8604 | 0.63729 | FALSE | none | -2.0356 | -3.9396 | -2.4875 | -5.1933 | Normal | 0 |  |  |  | 0 | 0 | 0.224 | 0.3094 | -0.72397 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0711 | Night
2025-08-13 00:30 | 80.36 | 79.072 | 1.3548 | 81.7815 | 76.3625 | 0.95072 | FALSE | none | -1.4215 | -3.9975 | -1.7382 | -5.2349 | Normal | 0 |  |  |  | 0.56 | 0.56 | 0.224 | 0.3094 | 1.086 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.092 | Night
2025-08-13 00:45 | 79.8 | 79.254 | 1.1756 | 81.6053 | 76.9027 | 0.46443 | FALSE | none | -1.8053 | -2.8973 | -2.2122 | -3.7674 | Normal | 0 |  |  |  | -0.56 | -0.56 | 0.182 | 0.35505 | -2.0899 | TRUE | 2 | TRUE | FALSE | FALSE | TRUE | 0.0881 | Night
2025-08-13 01:00 | 80.08 | 79.422 | 1.0249 | 81.4717 | 77.3723 | 0.64203 | FALSE | none | -1.3917 | -2.7077 | -1.7082 | -3.4996 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.168 | 0.34473 | 0.32489 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.0999 | Night
2025-08-13 01:15 | 79.8 | 79.562 | 0.85352 | 81.269 | 77.855 | 0.27884 | FALSE | none | -1.469 | -1.945 | -1.8076 | -2.4983 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.14 | 0.35765 | -1.1743 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.0757 | Night
2025-08-13 01:30 | 79.8 | 79.688 | 0.66385 | 81.0157 | 78.3603 | 0.16871 | FALSE | none | -1.2157 | -1.4397 | -1.5006 | -1.8373 | Normal | 0 |  |  |  | 0 | 0 | 0.126 | 0.35736 | -0.35258 | FALSE | 2 | FALSE | FALSE | FALSE | FALSE | 0.0684 | Night
2025-08-13 01:45 | 79.8 | 79.786 | 0.5015 | 80.789 | 78.783 | 0.027916 | FALSE | none | -0.98899 | -1.017 | -1.2242 | -1.2909 | Normal | 0 |  |  |  | 0 | 0 | 0.098 | 0.34323 | -0.28552 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0304 | Night
2025-08-13 02:00 | 79.8 | 79.856 | 0.38111 | 80.6182 | 79.0938 | -0.14694 | FALSE | none | -0.81822 | -0.70622 | -1.0149 | -0.89289 | Normal | 0 |  |  |  | 0 | 0 | 0.07 | 0.32596 | -0.21475 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0384 | Night
2025-08-13 02:15 | 80.08 | 79.926 | 0.26446 | 80.4549 | 79.3971 | 0.58231 | FALSE | none | -0.37493 | -0.68293 | -0.46601 | -0.86014 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.07 | 0.32596 | 0.64424 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0674 | Night
2025-08-13 02:30 | 79.8 | 79.954 | 0.21256 | 80.3791 | 79.5289 | -0.72449 | FALSE | none | -0.57913 | -0.27113 | -0.72049 | -0.34092 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.028 | 0.31338 | -0.98284 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0769 | Night
2025-08-13 02:45 | 80.08 | 79.982 | 0.18783 | 80.3577 | 79.6063 | 0.52175 | FALSE | none | -0.27766 | -0.47366 | -0.34553 | -0.595 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.028 | 0.31338 | 0.80414 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0634 | Night
2025-08-13 03:00 | 80.08 | 79.982 | 0.18783 | 80.3577 | 79.6063 | 0.52175 | FALSE | none | -0.27766 | -0.47366 | -0.34553 | -0.595 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.28727 | 0 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0634 | Night
2025-08-13 03:15 | 80.36 | 79.996 | 0.20515 | 80.4063 | 79.5857 | 1.7743 | FALSE | none | -0.046309 | -0.77431 | -0.057594 | -0.97293 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.29402 | 0.90471 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1183 | Night
2025-08-13 03:30 | 79.8 | 79.982 | 0.20864 | 80.3993 | 79.5647 | -0.8723 | FALSE | none | -0.59929 | -0.23529 | -0.74539 | -0.29572 | Normal | 0 |  |  |  | -0.56 | -0.56 | -0.014 | 0.32086 | -1.7017 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0582 | Night
2025-08-13 03:45 | 80.08 | 79.982 | 0.20864 | 80.3993 | 79.5647 | 0.4697 | FALSE | none | -0.31929 | -0.51529 | -0.39713 | -0.64764 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.32754 | 0.85485 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0313 | Night
2025-08-13 04:00 | 80.08 | 79.968 | 0.19056 | 80.3491 | 79.5869 | 0.58775 | FALSE | none | -0.26911 | -0.49311 | -0.33493 | -0.61959 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.32086 | 0.043633 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0392 | Night
2025-08-13 04:15 | 80.08 | 79.982 | 0.18783 | 80.3577 | 79.6063 | 0.52175 | FALSE | none | -0.27766 | -0.47366 | -0.34553 | -0.595 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.29402 | -0.047616 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0348 | Night
2025-08-13 04:30 | 79.8 | 79.968 | 0.19056 | 80.3491 | 79.5869 | -0.88163 | FALSE | none | -0.54911 | -0.21311 | -0.68341 | -0.26777 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.29402 | -0.90471 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Night
2025-08-13 04:45 | 80.36 | 79.982 | 0.20864 | 80.3993 | 79.5647 | 1.8117 | FALSE | none | -0.039289 | -0.79529 | -0.048868 | -0.99955 | Normal | 0 |  |  |  | 0.56 | 0.56 | 0.014 | 0.32086 | 1.7017 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1208 | Night
2025-08-13 05:00 | 79.8 | 79.982 | 0.20864 | 80.3993 | 79.5647 | -0.8723 | FALSE | none | -0.59929 | -0.23529 | -0.74539 | -0.29572 | Normal | 0 |  |  |  | -0.56 | -0.56 | 0 | 0.33991 | -1.6475 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0582 | Night
2025-08-13 05:15 | 79.8 | 79.982 | 0.20864 | 80.3993 | 79.5647 | -0.8723 | FALSE | none | -0.59929 | -0.23529 | -0.74539 | -0.29572 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.33991 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0582 | Night
2025-08-13 05:30 | 80.08 | 79.968 | 0.19056 | 80.3491 | 79.5869 | 0.58775 | FALSE | none | -0.26911 | -0.49311 | -0.33493 | -0.61959 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.014 | 0.32086 | 0.91629 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0392 | Night
2025-08-13 05:45 | 80.08 | 79.982 | 0.18783 | 80.3577 | 79.6063 | 0.52175 | FALSE | none | -0.27766 | -0.47366 | -0.34553 | -0.595 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.29402 | -0.047616 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0348 | Night
2025-08-13 06:00 | 79.8 | 79.968 | 0.19056 | 80.3491 | 79.5869 | -0.88163 | FALSE | none | -0.54911 | -0.21311 | -0.68341 | -0.26777 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.29402 | -0.90471 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0588 | Night
2025-08-13 06:15 | 80.08 | 79.982 | 0.18783 | 80.3577 | 79.6063 | 0.52175 | FALSE | none | -0.27766 | -0.47366 | -0.34553 | -0.595 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.29402 | 0.90471 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0348 | Night
2025-08-13 06:30 | 80.08 | 79.996 | 0.18395 | 80.3639 | 79.6281 | 0.45666 | FALSE | none | -0.28389 | -0.45189 | -0.35326 | -0.5675 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.29402 | -0.047616 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0304 | Night
2025-08-13 06:45 | 80.08 | 80.01 | 0.17883 | 80.3677 | 79.6523 | 0.39144 | FALSE | none | -0.28765 | -0.42765 | -0.35792 | -0.5369 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.29402 | -0.047616 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0261 | Night
2025-08-13 07:00 | 80.36 | 80.038 | 0.18783 | 80.4137 | 79.6623 | 1.7143 | FALSE | none | -0.053659 | -0.69766 | -0.066729 | -0.87577 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.028 | 0.29992 | 0.84022 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1143 | Day
2025-08-13 07:15 | 79.8 | 80.024 | 0.19484 | 80.4137 | 79.6343 | -1.1497 | FALSE | none | -0.61368 | -0.16568 | -0.76315 | -0.20805 | Normal | 0 |  |  |  | -0.56 | -0.56 | -0.014 | 0.32086 | -1.7017 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0766 | Day
2025-08-13 07:30 | 80.08 | 80.038 | 0.18783 | 80.4137 | 79.6623 | 0.22361 | FALSE | none | -0.33366 | -0.41766 | -0.41493 | -0.52429 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.32086 | 0.82902 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0149 | Day
2025-08-13 07:45 | 79.52 | 80.01 | 0.22019 | 80.4504 | 79.5696 | -2.2253 | TRUE | lower | -0.93038 | 0.049617 | -1.1565 | 0.062357 | Extreme triggered | 1 | 2025-08-13 07:45 | 2025-08-13 08:00 | 2.2253 | -0.56 | -0.56 | -0.028 | 0.33869 | -1.5708 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.2055 | Day
2025-08-13 08:00 | 80.08 | 80.01 | 0.22019 | 80.4504 | 79.5696 | 0.31791 | FALSE | none | -0.37038 | -0.51038 | -0.46039 | -0.64143 | Persistence ends | 0 |  |  |  | 0.56 | 0.56 | 0 | 0.36338 | 1.5411 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0212 | Day
2025-08-13 08:15 | 79.24 | 79.954 | 0.26446 | 80.4829 | 79.4251 | -2.6998 | TRUE | lower | -1.2429 | 0.18507 | -1.5443 | 0.23302 | Extreme triggered | 1 | 2025-08-13 08:15 | 2025-08-13 11:45 | 2.6998 | -0.84 | -0.84 | -0.056 | 0.40218 | -1.9494 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.2371 | Day
2025-08-13 08:30 | 78.96 | 79.912 | 0.34473 | 80.6015 | 79.2225 | -2.7616 | TRUE | lower | -1.6415 | 0.26254 | -2.0365 | 0.3314 | Extreme/elevated | 2 | 2025-08-13 08:15 |  | 2.7307 | -0.28 | -0.28 | -0.042 | 0.38835 | -0.61285 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.2984 | Day
2025-08-13 08:45 | 78.12 | 79.814 | 0.5256 | 80.8652 | 78.7628 | -3.223 | TRUE | lower | -2.7452 | 0.6428 | -3.3948 | 0.81612 | Persistent | 3 | 2025-08-13 08:15 |  | 2.8948 | -0.84 | -0.84 | -0.098 | 0.41902 | -1.7708 | FALSE | 0 | FALSE | TRUE | FALSE | FALSE | 0.3863 | Day
2025-08-13 09:00 | 77.28 | 79.674 | 0.76802 | 81.21 | 78.138 | -3.1171 | TRUE | lower | -3.93 | 0.85796 | -4.8394 | 1.098 | Persistent | 4 | 2025-08-13 08:15 |  | 2.9504 | -0.84 | -0.84 | -0.14 | 0.44965 | -1.5567 | FALSE | 0 | FALSE | TRUE | FALSE | FALSE | 0.4364 | Day
2025-08-13 09:15 | 76.72 | 79.506 | 1.0054 | 81.5167 | 77.4953 | -2.7712 | TRUE | lower | -4.7967 | 0.77529 | -5.8843 | 1.0004 | Persistent | 5 | 2025-08-13 08:15 |  | 2.9145 | -0.56 | -0.56 | -0.168 | 0.45784 | -0.8562 | FALSE | 0 | FALSE | TRUE | FALSE | FALSE | 0.4705 | Day
2025-08-13 09:30 | 76.16 | 79.324 | 1.2492 | 81.8225 | 76.8255 | -2.5328 | TRUE | lower | -5.6625 | 0.66554 | -6.9204 | 0.8663 | Persistent | 6 | 2025-08-13 08:15 |  | 2.8509 | -0.56 | -0.56 | -0.182 | 0.46566 | -0.81175 | FALSE | 0 | FALSE | TRUE | FALSE | FALSE | 0.5117 | Day
2025-08-13 09:45 | 75.6 | 79.086 | 1.4746 | 82.0351 | 76.1369 | -2.3641 | TRUE | lower | -6.4351 | 0.53686 | -7.8444 | 0.70512 | Confirmed/Materialized Shift | 7 | 2025-08-13 08:15 |  | 2.7814 | -0.56 | -0.56 | -0.238 | 0.43827 | -0.73471 | FALSE | 0 | FALSE | TRUE | TRUE | FALSE | 0.5576 | Day
2025-08-13 10:00 | 74.76 | 78.834 | 1.7509 | 82.3358 | 75.3322 | -2.3268 | TRUE | lower | -7.5758 | 0.5722 | -9.2011 | 0.75957 | Confirmed/Materialized Shift | 8 | 2025-08-13 08:15 |  | 2.7245 | -0.84 | -0.84 | -0.252 | 0.45331 | -1.2971 | FALSE | 0 | FALSE | TRUE | TRUE | FALSE | 0.5551 | Day
2025-08-13 10:15 | 75.04 | 78.596 | 1.9273 | 82.4506 | 74.7414 | -1.8451 | FALSE | none | -7.4106 | -0.29861 | -8.9879 | -0.39953 | Confirmed/Materialized Shift | 9 | 2025-08-13 08:15 |  | 2.6268 | 0.28 | 0.28 | -0.238 | 0.46566 | 1.1124 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.523 | Day
2025-08-13 10:30 | 75.04 | 78.344 | 2.0487 | 82.4415 | 74.2465 | -1.6127 | FALSE | none | -7.4015 | -0.79346 | -8.9778 | -1.0687 | Confirmed/Materialized Shift | 10 | 2025-08-13 08:15 |  | 2.5254 | 0 | 0 | -0.252 | 0.45331 | 0.55591 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.5075 | Day
2025-08-13 10:45 | 75.04 | 78.092 | 2.1322 | 82.3564 | 73.8276 | -1.4314 | FALSE | none | -7.3164 | -1.2124 | -8.8839 | -1.6423 | Confirmed/Materialized Shift | 11 | 2025-08-13 08:15 |  | 2.4259 | 0 | 0 | -0.252 | 0.45331 | 0.55591 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4954 | Day
2025-08-13 11:00 | 74.76 | 77.84 | 2.2159 | 82.2718 | 73.4082 | -1.3899 | FALSE | none | -7.5118 | -1.3518 | -9.1305 | -1.8415 | Confirmed/Materialized Shift | 12 | 2025-08-13 08:15 |  | 2.3396 | -0.28 | -0.28 | -0.252 | 0.45331 | -0.061768 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4927 | Day
2025-08-13 11:15 | 74.76 | 77.574 | 2.2519 | 82.0778 | 73.0702 | -1.2496 | FALSE | none | -7.3178 | -1.6898 | -8.9157 | -2.3126 | Confirmed/Materialized Shift | 13 | 2025-08-13 08:15 |  | 2.2558 | 0 | 0 | -0.266 | 0.44015 | 0.60434 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4833 | Day
2025-08-13 11:30 | 74.76 | 77.308 | 2.2545 | 81.817 | 72.799 | -1.1302 | FALSE | none | -7.057 | -1.961 | -8.6254 | -2.6937 | Confirmed/Materialized Shift | 14 | 2025-08-13 08:15 |  | 2.1754 | 0 | 0 | -0.266 | 0.44015 | 0.60434 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4753 | Day
2025-08-13 11:45 | 75.04 | 77.056 | 2.2096 | 81.4752 | 72.6368 | -0.91239 | FALSE | none | -6.4352 | -2.4032 | -7.8983 | -3.3085 | Persistence ends | 0 |  |  |  | 0.28 | 0.28 | -0.252 | 0.45331 | 1.1736 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0608 | Day
2025-08-13 12:00 | 74.76 | 76.776 | 2.1219 | 81.0199 | 72.5321 | -0.95007 | FALSE | none | -6.2599 | -2.2279 | -7.7264 | -3.0716 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.28 | 0.43567 | -1.6564e-15 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0633 | Day
2025-08-13 12:15 | 74.76 | 76.524 | 2.0417 | 80.6073 | 72.4407 | -0.864 | FALSE | none | -5.8473 | -2.3193 | -7.2541 | -3.2017 | Normal | 0 |  |  |  | 0 | 0 | -0.252 | 0.43472 | 0.57968 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0576 | Day
2025-08-13 12:30 | 75.04 | 76.272 | 1.8847 | 80.0413 | 72.5027 | -0.6537 | FALSE | none | -5.0013 | -2.5373 | -6.2484 | -3.4996 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.252 | 0.43472 | 1.2238 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0436 | Day
2025-08-13 12:45 | 74.76 | 76.034 | 1.7485 | 79.5311 | 72.5369 | -0.72861 | FALSE | none | -4.7711 | -2.2231 | -5.999 | -3.0648 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.238 | 0.42875 | -0.097959 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0486 | Day
2025-08-13 13:00 | 74.76 | 75.768 | 1.4855 | 78.739 | 72.797 | -0.67855 | FALSE | none | -3.979 | -1.963 | -5.0534 | -2.6966 | Normal | 0 |  |  |  | 0 | 0 | -0.266 | 0.39047 | 0.68123 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0452 | Day
2025-08-13 13:15 | 75.04 | 75.558 | 1.2465 | 78.051 | 73.065 | -0.41556 | FALSE | none | -3.011 | -1.975 | -3.8577 | -2.7031 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.21 | 0.38408 | 1.2758 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0277 | Day
2025-08-13 13:30 | 74.76 | 75.348 | 0.96526 | 77.2785 | 73.4175 | -0.60916 | FALSE | none | -2.5185 | -1.3425 | -3.259 | -1.8286 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.21 | 0.38408 | -0.18225 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0406 | Day
2025-08-13 13:45 | 74.76 | 75.18 | 0.71818 | 76.6164 | 73.7436 | -0.58481 | FALSE | none | -1.8564 | -1.0164 | -2.4229 | -1.3782 | Normal | 0 |  |  |  | 0 | 0 | -0.168 | 0.3565 | 0.47125 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.039 | Day
2025-08-13 14:00 | 75.04 | 75.068 | 0.52107 | 76.1101 | 74.0259 | -0.053736 | FALSE | none | -1.0701 | -1.0141 | -1.406 | -1.37 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.112 | 0.33254 | 1.1788 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0036 | Day
2025-08-13 14:15 | 74.76 | 74.97 | 0.35037 | 75.6707 | 74.2693 | -0.59937 | FALSE | none | -0.91074 | -0.49074 | -1.2036 | -0.66075 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.098 | 0.31828 | -0.57183 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.04 | Day
2025-08-13 14:30 | 74.76 | 74.9 | 0.21305 | 75.3261 | 74.4739 | -0.65713 | FALSE | none | -0.5661 | -0.2861 | -0.75153 | -0.38416 | Normal | 0 |  |  |  | 0 | 0 | -0.07 | 0.29958 | 0.23366 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0438 | Day
2025-08-13 14:45 | 74.76 | 74.858 | 0.13702 | 75.132 | 74.584 | -0.71522 | FALSE | none | -0.37204 | -0.17604 | -0.49518 | -0.23603 | Normal | 0 |  |  |  | 0 | 0 | -0.042 | 0.27666 | 0.15181 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0477 | Day
2025-08-13 15:00 | 75.04 | 74.872 | 0.14073 | 75.1535 | 74.5905 | 1.1937 | FALSE | none | -0.11347 | -0.44947 | -0.15098 | -0.60258 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.21256 | 1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0796 | Day
2025-08-13 15:15 | 75.04 | 74.872 | 0.14073 | 75.1535 | 74.5905 | 1.1937 | FALSE | none | -0.11347 | -0.44947 | -0.15098 | -0.60258 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.20313 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0796 | Day
2025-08-13 15:30 | 74.76 | 74.858 | 0.13702 | 75.132 | 74.584 | -0.71522 | FALSE | none | -0.37204 | -0.17604 | -0.49518 | -0.23603 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.21256 | -1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0477 | Day
2025-08-13 15:45 | 74.76 | 74.844 | 0.13165 | 75.1073 | 74.5807 | -0.63808 | FALSE | none | -0.34729 | -0.17929 | -0.46239 | -0.2404 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.21256 | 0.065863 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0425 | Day
2025-08-13 16:00 | 75.04 | 74.858 | 0.13702 | 75.132 | 74.584 | 1.3283 | FALSE | none | -0.092042 | -0.45604 | -0.12251 | -0.61145 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.21256 | 1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0886 | Day
2025-08-13 16:15 | 75.32 | 74.886 | 0.16935 | 75.2247 | 74.5473 | 2.5628 | TRUE | upper | 0.095309 | -0.77269 | 0.1267 | -1.0365 | Extreme triggered | 1 | 2025-08-13 16:15 | 2025-08-13 16:30 | 2.5628 | 0.28 | 0.28 | 0.028 | 0.22066 | 1.142 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.228 | Day
2025-08-13 16:30 | 74.76 | 74.886 | 0.16935 | 75.2247 | 74.5473 | -0.74404 | FALSE | none | -0.46469 | -0.21269 | -0.61774 | -0.28531 | Persistence ends | 0 |  |  |  | -0.56 | -0.56 | 0 | 0.25695 | -2.1794 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0782 | Day
2025-08-13 16:45 | 75.04 | 74.886 | 0.16935 | 75.2247 | 74.5473 | 0.90938 | FALSE | none | -0.18469 | -0.49269 | -0.24552 | -0.66091 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.25695 | 1.0897 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0892 | Day
2025-08-13 17:00 | 74.76 | 74.886 | 0.16935 | 75.2247 | 74.5473 | -0.74404 | FALSE | none | -0.46469 | -0.21269 | -0.61774 | -0.28531 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.25695 | -1.0897 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0782 | Day
2025-08-13 17:15 | 75.04 | 74.9 | 0.16995 | 75.2399 | 74.5601 | 0.82375 | FALSE | none | -0.19991 | -0.47991 | -0.26569 | -0.64365 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.26446 | 1.0058 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0835 | Day
2025-08-13 17:30 | 75.04 | 74.9 | 0.16995 | 75.2399 | 74.5601 | 0.82375 | FALSE | none | -0.19991 | -0.47991 | -0.26569 | -0.64365 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.25695 | 0 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0835 | Day
2025-08-13 17:45 | 75.04 | 74.914 | 0.16935 | 75.2527 | 74.5753 | 0.74404 | FALSE | none | -0.21269 | -0.46469 | -0.28264 | -0.62312 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.24837 | -0.056367 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0782 | Day
2025-08-13 18:00 | 75.04 | 74.928 | 0.16751 | 75.263 | 74.593 | 0.66862 | FALSE | none | -0.22302 | -0.44702 | -0.29632 | -0.59927 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.24837 | -0.056367 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0731 | Day
2025-08-13 18:15 | 74.76 | 74.914 | 0.16935 | 75.2527 | 74.5753 | -0.90938 | FALSE | none | -0.49269 | -0.18469 | -0.65472 | -0.24766 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.24837 | -1.071 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0892 | Day
2025-08-13 18:30 | 74.76 | 74.914 | 0.16935 | 75.2527 | 74.5753 | -0.90938 | FALSE | none | -0.49269 | -0.18469 | -0.65472 | -0.24766 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.24035 | 0 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0892 | Day
2025-08-13 18:45 | 75.04 | 74.928 | 0.16751 | 75.263 | 74.593 | 0.66862 | FALSE | none | -0.22302 | -0.44702 | -0.29632 | -0.59927 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.24837 | 1.071 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0731 | Day
2025-08-13 19:00 | 75.04 | 74.928 | 0.16751 | 75.263 | 74.593 | 0.66862 | FALSE | none | -0.22302 | -0.44702 | -0.29632 | -0.59927 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.24035 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0446 | Night
2025-08-13 19:15 | 75.6 | 74.97 | 0.22019 | 75.4104 | 74.5296 | 2.8611 | TRUE | upper | 0.18962 | -1.0704 | 0.25145 | -1.4362 | Extreme triggered | 1 | 2025-08-13 19:15 | 2025-08-13 23:45 | 2.8611 | 0.56 | 0.56 | 0.042 | 0.26132 | 1.9822 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.2479 | Night
2025-08-13 19:30 | 75.88 | 75.026 | 0.29402 | 75.614 | 74.438 | 2.9046 | TRUE | upper | 0.26596 | -1.442 | 0.35174 | -1.9372 | Extreme/elevated | 2 | 2025-08-13 19:15 |  | 2.8829 | 0.28 | 0.28 | 0.056 | 0.26641 | 0.84082 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.3079 | Night
2025-08-13 19:45 | 75.88 | 75.082 | 0.34323 | 75.7685 | 74.3955 | 2.325 | TRUE | upper | 0.11154 | -1.4845 | 0.14721 | -1.9954 | Persistent | 3 | 2025-08-13 19:15 |  | 2.6969 | 0 | 0 | 0.056 | 0.26641 | -0.2102 | FALSE | 0 | FALSE | TRUE | FALSE | FALSE | 0.3264 | Night
2025-08-13 20:00 | 76.72 | 75.166 | 0.5015 | 76.169 | 74.163 | 3.0987 | TRUE | upper | 0.55101 | -2.557 | 0.7234 | -3.4478 | Persistent | 4 | 2025-08-13 19:15 |  | 2.7974 | 0.84 | 0.84 | 0.084 | 0.316 | 2.3924 | TRUE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4637 | Night
2025-08-13 20:15 | 76.72 | 75.25 | 0.60855 | 76.4671 | 74.0329 | 2.4156 | TRUE | upper | 0.25289 | -2.6871 | 0.33072 | -3.6296 | Persistent | 5 | 2025-08-13 19:15 |  | 2.721 | 0 | 0 | 0.084 | 0.316 | -0.26582 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.4753 | Night
2025-08-13 20:30 | 77.28 | 75.376 | 0.74691 | 76.8698 | 73.8822 | 2.5492 | TRUE | upper | 0.41018 | -3.3978 | 0.5336 | -4.599 | Persistent | 6 | 2025-08-13 19:15 |  | 2.6924 | 0.56 | 0.56 | 0.126 | 0.32086 | 1.3526 | FALSE | 1 | FALSE | TRUE | FALSE | FALSE | 0.5414 | Night
2025-08-13 20:45 | 78.12 | 75.544 | 0.95105 | 77.4461 | 73.6419 | 2.7086 | TRUE | upper | 0.67391 | -4.4781 | 0.87016 | -6.0809 | Confirmed/Materialized Shift | 7 | 2025-08-13 19:15 |  | 2.6947 | 0.84 | 0.84 | 0.168 | 0.3565 | 1.885 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.6091 | Night
2025-08-13 21:00 | 78.4 | 75.712 | 1.1361 | 77.9842 | 73.4398 | 2.366 | TRUE | upper | 0.41581 | -4.9602 | 0.5332 | -6.7541 | Confirmed/Materialized Shift | 8 | 2025-08-13 19:15 |  | 2.6536 | 0.28 | 0.28 | 0.168 | 0.3565 | 0.31417 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5863 | Night
2025-08-13 21:15 | 78.68 | 75.88 | 1.3102 | 78.5003 | 73.2597 | 2.1371 | TRUE | upper | 0.17966 | -5.4203 | 0.22886 | -7.3988 | Confirmed/Materialized Shift | 9 | 2025-08-13 19:15 |  | 2.5962 | 0.28 | 0.28 | 0.168 | 0.3565 | 0.31417 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.571 | Night
2025-08-13 21:30 | 79.52 | 76.118 | 1.5127 | 79.1434 | 73.0926 | 2.249 | TRUE | upper | 0.37661 | -6.4274 | 0.47586 | -8.7935 | Confirmed/Materialized Shift | 10 | 2025-08-13 19:15 |  | 2.5615 | 0.84 | 0.84 | 0.238 | 0.34323 | 1.7539 | FALSE | 1 | FALSE | TRUE | TRUE | FALSE | 0.5785 | Night
2025-08-13 21:45 | 79.52 | 76.342 | 1.6684 | 79.6787 | 73.0053 | 1.9049 | FALSE | none | -0.15871 | -6.5147 | -0.19919 | -8.9236 | Confirmed/Materialized Shift | 11 | 2025-08-13 19:15 |  | 2.5018 | 0 | 0 | 0.224 | 0.34711 | -0.64532 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5556 | Night
2025-08-13 22:00 | 79.8 | 76.594 | 1.7928 | 80.1796 | 73.0084 | 1.7882 | FALSE | none | -0.37963 | -6.7916 | -0.47348 | -9.3025 | Confirmed/Materialized Shift | 12 | 2025-08-13 19:15 |  | 2.4423 | 0.28 | 0.28 | 0.252 | 0.32628 | 0.085816 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5478 | Night
2025-08-13 22:15 | 80.08 | 76.846 | 1.9131 | 80.6721 | 73.0199 | 1.6905 | FALSE | none | -0.59214 | -7.0601 | -0.73401 | -9.6688 | Confirmed/Materialized Shift | 13 | 2025-08-13 19:15 |  | 2.3845 | 0.28 | 0.28 | 0.252 | 0.32628 | 0.085816 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5413 | Night
2025-08-13 22:30 | 80.08 | 77.098 | 1.9929 | 81.0839 | 73.1121 | 1.4963 | FALSE | none | -1.0039 | -6.9679 | -1.2381 | -9.5304 | Confirmed/Materialized Shift | 14 | 2025-08-13 19:15 |  | 2.3211 | 0 | 0 | 0.252 | 0.32628 | -0.77234 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4998 | Night
2025-08-13 22:45 | 80.08 | 77.35 | 2.0372 | 81.4243 | 73.2757 | 1.3401 | FALSE | none | -1.3443 | -6.8043 | -1.651 | -9.2859 | Confirmed/Materialized Shift | 15 | 2025-08-13 19:15 |  | 2.2557 | 0 | 0 | 0.252 | 0.32628 | -0.77234 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4893 | Night
2025-08-13 23:00 | 80.08 | 77.602 | 2.0481 | 81.6981 | 73.5059 | 1.2099 | FALSE | none | -1.6181 | -6.5741 | -1.9806 | -8.9437 | Confirmed/Materialized Shift | 16 | 2025-08-13 19:15 |  | 2.1903 | 0 | 0 | 0.252 | 0.32628 | -0.77234 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4807 | Night
2025-08-13 23:15 | 80.08 | 77.868 | 2.0045 | 81.8771 | 73.8589 | 1.1035 | FALSE | none | -1.7971 | -6.2211 | -2.1949 | -8.4229 | Confirmed/Materialized Shift | 17 | 2025-08-13 19:15 |  | 2.1264 | 0 | 0 | 0.266 | 0.30773 | -0.86439 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4736 | Night
2025-08-13 23:30 | 80.08 | 78.134 | 1.9217 | 81.9774 | 74.2906 | 1.0127 | FALSE | none | -1.8974 | -5.7894 | -2.3145 | -7.7928 | Confirmed/Materialized Shift | 18 | 2025-08-13 19:15 |  | 2.0645 | 0 | 0 | 0.266 | 0.30773 | -0.86439 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4675 | Night
2025-08-13 23:45 | 80.08 | 78.386 | 1.8225 | 82.031 | 74.741 | 0.9295 | FALSE | none | -1.951 | -5.339 | -2.3784 | -7.1433 | Persistence ends | 0 |  |  |  | 0 | 0 | 0.252 | 0.31338 | -0.80414 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.062 | Night
2025-08-14 | 79.8 | 78.624 | 1.6667 | 81.9574 | 75.2906 | 0.70559 | FALSE | none | -2.1574 | -4.5094 | -2.6323 | -5.9893 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.238 | 0.33099 | -1.565 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.047 | Night
2025-08-14 00:15 | 79.8 | 78.834 | 1.5241 | 81.8822 | 75.7858 | 0.63381 | FALSE | none | -2.0822 | -4.0142 | -2.5429 | -5.2968 | Normal | 0 |  |  |  | 0 | 0 | 0.21 | 0.32596 | -0.64424 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0423 | Night
2025-08-14 00:30 | 80.08 | 79.044 | 1.378 | 81.8 | 76.288 | 0.75181 | FALSE | none | -1.72 | -3.792 | -2.1027 | -4.9707 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.21 | 0.32596 | 0.21475 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0501 | Night
2025-08-14 00:45 | 79.8 | 79.24 | 1.1669 | 81.5738 | 76.9062 | 0.4799 | FALSE | none | -1.7738 | -2.8938 | -2.1745 | -3.7628 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.196 | 0.34112 | -1.3954 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.032 | Night
2025-08-14 01:00 | 80.08 | 79.408 | 1.0173 | 81.4426 | 77.3734 | 0.66058 | FALSE | none | -1.3626 | -2.7066 | -1.6731 | -3.4981 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.168 | 0.30672 | 0.36515 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.044 | Night
2025-08-14 01:15 | 80.08 | 79.576 | 0.80539 | 81.1868 | 77.9652 | 0.62578 | FALSE | none | -1.1068 | -2.1148 | -1.3633 | -2.7125 | Normal | 0 |  |  |  | 0 | 0 | 0.168 | 0.30672 | -0.54772 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0417 | Night
2025-08-14 01:30 | 80.08 | 79.716 | 0.60328 | 80.9226 | 78.5094 | 0.60337 | FALSE | none | -0.84255 | -1.5706 | -1.0412 | -2.0005 | Normal | 0 |  |  |  | 0 | 0 | 0.14 | 0.29437 | -0.47559 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0402 | Night
2025-08-14 01:45 | 80.08 | 79.814 | 0.47617 | 80.7663 | 78.8617 | 0.55862 | FALSE | none | -0.68635 | -1.2183 | -0.84979 | -1.5449 | Normal | 0 |  |  |  | 0 | 0 | 0.098 | 0.24503 | -0.39996 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0372 | Night
2025-08-14 02:00 | 80.36 | 79.912 | 0.3565 | 80.625 | 79.199 | 1.2567 | FALSE | none | -0.265 | -1.161 | -0.32868 | -1.4659 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.098 | 0.24503 | 0.74278 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0838 | Night
2025-08-14 02:15 | 80.08 | 79.982 | 0.20864 | 80.3993 | 79.5647 | 0.4697 | FALSE | none | -0.31929 | -0.51529 | -0.39713 | -0.64764 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.07 | 0.25493 | -1.3729 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0313 | Night
2025-08-14 02:30 | 80.36 | 80.024 | 0.19484 | 80.4137 | 79.6343 | 1.7245 | FALSE | none | -0.053677 | -0.72568 | -0.066751 | -0.91126 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.042 | 0.18783 | 1.2671 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.115 | Night
2025-08-14 02:45 | 80.36 | 80.066 | 0.16935 | 80.4047 | 79.7273 | 1.7361 | FALSE | none | -0.044691 | -0.63269 | -0.055583 | -0.79357 | Normal | 0 |  |  |  | 0 | 0 | 0.042 | 0.18783 | -0.22361 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1157 | Night
2025-08-14 03:00 | 80.08 | 80.08 | 0.15735 | 80.3947 | 79.7653 | 0 | FALSE | none | -0.31469 | -0.31469 | -0.39143 | -0.39452 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0.014 | 0.19217 | -1.5299 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-14 03:15 | 80.08 | 80.08 | 0.15735 | 80.3947 | 79.7653 | 0 | FALSE | none | -0.31469 | -0.31469 | -0.39143 | -0.39452 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.18169 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-14 03:30 | 79.8 | 80.066 | 0.16935 | 80.4047 | 79.7273 | -1.5708 | FALSE | none | -0.60469 | -0.072691 | -0.75206 | -0.091175 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.19217 | -1.3842 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1047 | Night
2025-08-14 03:45 | 79.8 | 80.052 | 0.1794 | 80.4108 | 79.6932 | -1.4047 | FALSE | none | -0.61081 | -0.10681 | -0.75961 | -0.13402 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.19217 | 0.072851 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0936 | Night
2025-08-14 04:00 | 80.08 | 80.052 | 0.1794 | 80.4108 | 79.6932 | 0.15607 | FALSE | none | -0.33081 | -0.38681 | -0.41139 | -0.48537 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.20313 | 1.3784 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0104 | Night
2025-08-14 04:15 | 80.08 | 80.052 | 0.1794 | 80.4108 | 79.6932 | 0.15607 | FALSE | none | -0.33081 | -0.38681 | -0.41139 | -0.48537 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.20313 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0104 | Night
2025-08-14 04:30 | 80.08 | 80.052 | 0.1794 | 80.4108 | 79.6932 | 0.15607 | FALSE | none | -0.33081 | -0.38681 | -0.41139 | -0.48537 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.20313 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0104 | Night
2025-08-14 04:45 | 80.08 | 80.052 | 0.1794 | 80.4108 | 79.6932 | 0.15607 | FALSE | none | -0.33081 | -0.38681 | -0.41139 | -0.48537 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.20313 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0104 | Night
2025-08-14 05:00 | 79.8 | 80.052 | 0.1794 | 80.4108 | 79.6932 | -1.4047 | FALSE | none | -0.61081 | -0.10681 | -0.75961 | -0.13402 | Normal | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.20313 | -1.3784 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0936 | Night
2025-08-14 05:15 | 80.08 | 80.066 | 0.16935 | 80.4047 | 79.7273 | 0.082671 | FALSE | none | -0.32469 | -0.35269 | -0.40382 | -0.44237 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.21256 | 1.2514 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0055 | Night
2025-08-14 05:30 | 80.08 | 80.066 | 0.16935 | 80.4047 | 79.7273 | 0.082671 | FALSE | none | -0.32469 | -0.35269 | -0.40382 | -0.44237 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.20313 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0055 | Night
2025-08-14 05:45 | 80.08 | 80.08 | 0.15735 | 80.3947 | 79.7653 | 0 | FALSE | none | -0.31469 | -0.31469 | -0.39143 | -0.39452 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.19217 | -0.072851 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-14 06:00 | 80.08 | 80.08 | 0.15735 | 80.3947 | 79.7653 | 0 | FALSE | none | -0.31469 | -0.31469 | -0.39143 | -0.39452 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.18169 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-14 06:15 | 80.08 | 80.08 | 0.15735 | 80.3947 | 79.7653 | 0 | FALSE | none | -0.31469 | -0.31469 | -0.39143 | -0.39452 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.18169 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0 | Night
2025-08-14 06:30 | 80.36 | 80.094 | 0.16935 | 80.4327 | 79.7553 | 1.5708 | FALSE | none | -0.072691 | -0.60469 | -0.090375 | -0.75818 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.19217 | 1.3842 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1047 | Night
2025-08-14 06:45 | 79.8 | 80.08 | 0.18169 | 80.4434 | 79.7166 | -1.5411 | FALSE | none | -0.64338 | -0.083376 | -0.79979 | -0.10459 | Normal | 0 |  |  |  | -0.56 | -0.56 | -0.014 | 0.23116 | -2.362 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1313 | Night
2025-08-14 07:00 | 80.08 | 80.066 | 0.16935 | 80.4047 | 79.7273 | 0.082671 | FALSE | none | -0.32469 | -0.35269 | -0.40382 | -0.44237 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.014 | 0.23116 | 1.2718 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0341 | Day
2025-08-14 07:15 | 80.08 | 80.066 | 0.16935 | 80.4047 | 79.7273 | 0.082671 | FALSE | none | -0.32469 | -0.35269 | -0.40382 | -0.44237 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.22252 | 0 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0341 | Day
2025-08-14 07:30 | 80.08 | 80.052 | 0.1547 | 80.3614 | 79.7426 | 0.18099 | FALSE | none | -0.2814 | -0.3374 | -0.35017 | -0.42312 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.21256 | 0.065863 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0406 | Day
2025-08-14 07:45 | 80.08 | 80.038 | 0.13702 | 80.312 | 79.764 | 0.30652 | FALSE | none | -0.23204 | -0.31604 | -0.28893 | -0.39622 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.21256 | 0.065863 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.049 | Day
2025-08-14 08:00 | 80.36 | 80.052 | 0.1547 | 80.3614 | 79.7426 | 1.9909 | FALSE | none | -0.0014035 | -0.6174 | -0.0017465 | -0.77425 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.21256 | 1.2514 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1613 | Day
2025-08-14 08:15 | 79.24 | 80.01 | 0.23819 | 80.4864 | 79.5336 | -3.2326 | TRUE | lower | -1.2464 | 0.29361 | -1.5486 | 0.36916 | Extreme triggered | 1 | 2025-08-14 08:15 | 2025-08-14 12:00 | 3.2326 | -1.12 | -1.12 | -0.042 | 0.33099 | -3.2569 | TRUE | 2 | TRUE | FALSE | FALSE | TRUE | 0.3298 | Day
2025-08-14 08:30 | 78.4 | 79.94 | 0.43091 | 80.8018 | 79.0782 | -3.5738 | TRUE | lower | -2.4018 | 0.67818 | -2.9725 | 0.8576 | Extreme/elevated | 2 | 2025-08-14 08:15 |  | 3.4032 | -0.84 | -0.84 | -0.07 | 0.37318 | -2.0633 | TRUE | 3 | TRUE | FALSE | FALSE | TRUE | 0.4383 | Day
2025-08-14 08:45 | 78.12 | 79.856 | 0.59293 | 81.0419 | 78.6701 | -2.9278 | TRUE | lower | -2.9219 | 0.55015 | -3.6054 | 0.69931 | Persistent | 3 | 2025-08-14 08:15 |  | 3.2448 | -0.28 | -0.28 | -0.084 | 0.37566 | -0.52175 | FALSE | 3 | FALSE | TRUE | FALSE | FALSE | 0.4523 | Day
2025-08-14 09:00 | 77.28 | 79.716 | 0.82313 | 81.3623 | 78.0697 | -2.9594 | TRUE | lower | -4.0823 | 0.78974 | -5.0174 | 1.0116 | Persistent | 4 | 2025-08-14 08:15 |  | 3.1734 | -0.84 | -0.84 | -0.14 | 0.40116 | -1.745 | FALSE | 3 | FALSE | TRUE | FALSE | FALSE | 0.5116 | Day
2025-08-14 09:15 | 76.44 | 79.534 | 1.0957 | 81.7254 | 77.3426 | -2.8238 | TRUE | lower | -5.2854 | 0.90261 | -6.4673 | 1.167 | Persistent | 5 | 2025-08-14 08:15 |  | 3.1035 | -0.84 | -0.84 | -0.182 | 0.42875 | -1.5347 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.5311 | Day
2025-08-14 09:30 | 76.44 | 79.352 | 1.286 | 81.924 | 76.78 | -2.2644 | TRUE | lower | -5.484 | 0.33998 | -6.694 | 0.44279 | Persistent | 6 | 2025-08-14 08:15 |  | 2.9636 | 0 | 0 | -0.182 | 0.42875 | 0.42449 | FALSE | 2 | FALSE | TRUE | FALSE | FALSE | 0.551 | Day
2025-08-14 09:45 | 75.6 | 79.128 | 1.5212 | 82.1704 | 76.0856 | -2.3192 | TRUE | lower | -6.5704 | 0.48561 | -7.9961 | 0.63824 | Confirmed/Materialized Shift | 7 | 2025-08-14 08:15 |  | 2.8716 | -0.84 | -0.84 | -0.224 | 0.45057 | -1.3672 | FALSE | 2 | FALSE | TRUE | TRUE | FALSE | 0.6118 | Day
2025-08-14 10:00 | 75.04 | 78.89 | 1.7636 | 82.4172 | 75.3628 | -2.1831 | TRUE | lower | -7.3772 | 0.32284 | -8.951 | 0.42838 | Confirmed/Materialized Shift | 8 | 2025-08-14 08:15 |  | 2.7855 | -0.56 | -0.56 | -0.238 | 0.45671 | -0.70504 | FALSE | 2 | FALSE | TRUE | TRUE | FALSE | 0.6027 | Day
2025-08-14 10:15 | 74.76 | 78.624 | 1.9644 | 82.5528 | 74.6952 | -1.967 | FALSE | none | -7.7928 | -0.064832 | -9.4398 | -0.086796 | Confirmed/Materialized Shift | 9 | 2025-08-14 08:15 |  | 2.6946 | -0.28 | -0.28 | -0.266 | 0.44015 | -0.031807 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5883 | Day
2025-08-14 10:30 | 75.04 | 78.372 | 2.0872 | 82.5465 | 74.1975 | -1.5964 | FALSE | none | -7.5065 | -0.84248 | -9.0936 | -1.1355 | Confirmed/Materialized Shift | 10 | 2025-08-14 08:15 |  | 2.5848 | 0.28 | 0.28 | -0.252 | 0.45331 | 1.1736 | FALSE | 2 | FALSE | FALSE | TRUE | FALSE | 0.5636 | Day
2025-08-14 10:45 | 74.76 | 78.106 | 2.1944 | 82.4947 | 73.7173 | -1.5248 | FALSE | none | -7.7347 | -1.0427 | -9.376 | -1.4145 | Confirmed/Materialized Shift | 11 | 2025-08-14 08:15 |  | 2.4884 | -0.28 | -0.28 | -0.266 | 0.44943 | -0.031151 | FALSE | 1 | FALSE | FALSE | TRUE | FALSE | 0.5302 | Day
2025-08-14 11:00 | 75.04 | 77.854 | 2.2446 | 82.3431 | 73.3649 | -1.2537 | FALSE | none | -7.3031 | -1.6751 | -8.8691 | -2.2833 | Confirmed/Materialized Shift | 12 | 2025-08-14 08:15 |  | 2.3855 | 0.28 | 0.28 | -0.252 | 0.46232 | 1.1507 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4836 | Day
2025-08-14 11:15 | 75.04 | 77.602 | 2.2643 | 82.1306 | 73.0734 | -1.1315 | FALSE | none | -7.0906 | -1.9666 | -8.6334 | -2.6913 | Confirmed/Materialized Shift | 13 | 2025-08-14 08:15 |  | 2.289 | 0 | 0 | -0.252 | 0.46232 | 0.54507 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4754 | Day
2025-08-14 11:30 | 75.04 | 77.336 | 2.2356 | 81.8071 | 72.8649 | -1.027 | FALSE | none | -6.7671 | -2.1751 | -8.2721 | -2.9852 | Confirmed/Materialized Shift | 14 | 2025-08-14 08:15 |  | 2.1989 | 0 | 0 | -0.266 | 0.44943 | 0.59187 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4685 | Day
2025-08-14 11:45 | 74.48 | 77.07 | 2.2435 | 81.5569 | 72.5831 | -1.1545 | FALSE | none | -7.0769 | -1.8969 | -8.6773 | -2.6134 | Confirmed/Materialized Shift | 15 | 2025-08-14 08:15 |  | 2.1293 | -0.56 | -0.56 | -0.266 | 0.44943 | -0.65417 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.477 | Day
2025-08-14 12:00 | 75.04 | 76.818 | 2.1694 | 81.1568 | 72.4792 | -0.81958 | FALSE | none | -6.1168 | -2.5608 | -7.537 | -3.5331 | Persistence ends | 0 |  |  |  | 0.56 | 0.56 | -0.252 | 0.47116 | 1.7234 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0546 | Day
2025-08-14 12:15 | 75.04 | 76.566 | 2.0605 | 80.6871 | 72.4449 | -0.74059 | FALSE | none | -5.6471 | -2.5951 | -6.9987 | -3.5821 | Normal | 0 |  |  |  | 0 | 0 | -0.252 | 0.47116 | 0.53485 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0494 | Day
2025-08-14 12:30 | 75.04 | 76.314 | 1.9109 | 80.1358 | 72.4922 | -0.6667 | FALSE | none | -5.0958 | -2.5478 | -6.359 | -3.5146 | Normal | 0 |  |  |  | 0 | 0 | -0.252 | 0.47116 | 0.53485 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0444 | Day
2025-08-14 12:45 | 75.04 | 76.062 | 1.7099 | 79.4818 | 72.6422 | -0.5977 | FALSE | none | -4.4418 | -2.3978 | -5.5884 | -3.3008 | Normal | 0 |  |  |  | 0 | 0 | -0.252 | 0.47116 | 0.53485 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0398 | Day
2025-08-14 13:00 | 74.76 | 75.782 | 1.3993 | 78.5807 | 72.9833 | -0.73035 | FALSE | none | -3.8207 | -1.7767 | -4.8621 | -2.4344 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.28 | 0.45422 | -1.5888e-15 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0487 | Day
2025-08-14 13:15 | 74.76 | 75.558 | 1.1537 | 77.8653 | 73.2507 | -0.69171 | FALSE | none | -3.1053 | -1.5093 | -3.9881 | -2.0605 | Normal | 0 |  |  |  | 0 | 0 | -0.224 | 0.41232 | 0.54327 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0461 | Day
2025-08-14 13:30 | 75.04 | 75.39 | 0.94353 | 77.2771 | 73.5029 | -0.37095 | FALSE | none | -2.2371 | -1.5371 | -2.8949 | -2.0912 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.168 | 0.40013 | 1.1196 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0247 | Day
2025-08-14 13:45 | 75.04 | 75.236 | 0.69244 | 76.6209 | 73.8511 | -0.28306 | FALSE | none | -1.5809 | -1.1889 | -2.0633 | -1.6098 | Normal | 0 |  |  |  | 0 | 0 | -0.154 | 0.4009 | 0.38414 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0189 | Day
2025-08-14 14:00 | 75.04 | 75.124 | 0.4984 | 76.1208 | 74.1272 | -0.16854 | FALSE | none | -1.0808 | -0.9128 | -1.4199 | -1.2314 | Normal | 0 |  |  |  | 0 | 0 | -0.112 | 0.36789 | 0.30444 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0112 | Day
2025-08-14 14:15 | 74.76 | 75.04 | 0.39598 | 75.832 | 74.248 | -0.70711 | FALSE | none | -1.072 | -0.51196 | -1.4136 | -0.68953 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.084 | 0.3288 | -0.59611 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0471 | Day
2025-08-14 14:30 | 75.04 | 74.97 | 0.22019 | 75.4104 | 74.5296 | 0.31791 | FALSE | none | -0.37038 | -0.51038 | -0.49116 | -0.68481 | Normal | 0 |  |  |  | 0.28 | 0.28 | -0.07 | 0.33839 | 1.0343 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0212 | Day
2025-08-14 14:45 | 74.76 | 74.928 | 0.16751 | 75.263 | 74.593 | -1.0029 | FALSE | none | -0.50302 | -0.16702 | -0.66834 | -0.2239 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.042 | 0.2912 | -0.81732 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0669 | Day
2025-08-14 15:00 | 74.76 | 74.914 | 0.16935 | 75.2527 | 74.5753 | -0.90938 | FALSE | none | -0.49269 | -0.18469 | -0.65472 | -0.24766 | Normal | 0 |  |  |  | 0 | 0 | -0.014 | 0.26446 | 0.052937 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0606 | Day
2025-08-14 15:15 | 74.76 | 74.914 | 0.16935 | 75.2527 | 74.5753 | -0.90938 | FALSE | none | -0.49269 | -0.18469 | -0.65472 | -0.24766 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.25695 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0606 | Day
2025-08-14 15:30 | 75.04 | 74.914 | 0.16935 | 75.2527 | 74.5753 | 0.74404 | FALSE | none | -0.21269 | -0.46469 | -0.28264 | -0.62312 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.25695 | 1.0897 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0496 | Day
2025-08-14 15:45 | 75.04 | 74.928 | 0.16751 | 75.263 | 74.593 | 0.66862 | FALSE | none | -0.22302 | -0.44702 | -0.29632 | -0.59927 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.24837 | -0.056367 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0446 | Day
2025-08-14 16:00 | 75.04 | 74.928 | 0.16751 | 75.263 | 74.593 | 0.66862 | FALSE | none | -0.22302 | -0.44702 | -0.29632 | -0.59927 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.24035 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0446 | Day
2025-08-14 16:15 | 75.04 | 74.928 | 0.16751 | 75.263 | 74.593 | 0.66862 | FALSE | none | -0.22302 | -0.44702 | -0.29632 | -0.59927 | Normal | 0 |  |  |  | 0 | 0 | 0 | 0.24035 | 0 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0446 | Day
2025-08-14 16:30 | 74.76 | 74.914 | 0.16935 | 75.2527 | 74.5753 | -0.90938 | FALSE | none | -0.49269 | -0.18469 | -0.65472 | -0.24766 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.24837 | -1.071 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0606 | Day
2025-08-14 16:45 | 75.32 | 74.956 | 0.15995 | 75.2759 | 74.6361 | 2.2757 | TRUE | upper | 0.044105 | -0.68389 | 0.058592 | -0.91631 | Extreme triggered | 1 | 2025-08-14 16:45 | 2025-08-14 17:00 | 2.2757 | 0.56 | 0.56 | 0.042 | 0.24503 | 2.1141 | TRUE | 1 | FALSE | FALSE | FALSE | FALSE | 0.2374 | Day
2025-08-14 17:00 | 75.04 | 74.956 | 0.15995 | 75.2759 | 74.6361 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.31337 | -0.54115 | Persistence ends | 0 |  |  |  | -0.28 | -0.28 | 0 | 0.22252 | -1.2583 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0636 | Day
2025-08-14 17:15 | 74.76 | 74.942 | 0.1644 | 75.2708 | 74.6132 | -1.1071 | FALSE | none | -0.5108 | -0.1468 | -0.67862 | -0.19675 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.23116 | -1.1507 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1024 | Day
2025-08-14 17:30 | 75.04 | 74.942 | 0.1644 | 75.2708 | 74.6132 | 0.59611 | FALSE | none | -0.2308 | -0.4268 | -0.30663 | -0.57202 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0 | 0.24035 | 1.165 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0683 | Day
2025-08-14 17:45 | 74.76 | 74.928 | 0.16751 | 75.263 | 74.593 | -1.0029 | FALSE | none | -0.50302 | -0.16702 | -0.66834 | -0.2239 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.24837 | -1.071 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0954 | Day
2025-08-14 18:00 | 75.04 | 74.942 | 0.1644 | 75.2708 | 74.6132 | 0.59611 | FALSE | none | -0.2308 | -0.4268 | -0.30663 | -0.57202 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.014 | 0.24837 | 1.071 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0683 | Day
2025-08-14 18:15 | 75.04 | 74.956 | 0.15995 | 75.2759 | 74.6361 | 0.52517 | FALSE | none | -0.23589 | -0.40389 | -0.31337 | -0.54115 | Normal | 0 |  |  |  | 0 | 0 | 0.014 | 0.24837 | -0.056367 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.0636 | Day
2025-08-14 18:30 | 74.76 | 74.942 | 0.1644 | 75.2708 | 74.6132 | -1.1071 | FALSE | none | -0.5108 | -0.1468 | -0.67862 | -0.19675 | Normal | 0 |  |  |  | -0.28 | -0.28 | -0.014 | 0.24837 | -1.071 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.1024 | Day
2025-08-14 18:45 | 74.48 | 74.914 | 0.19217 | 75.2983 | 74.5297 | -2.2584 | TRUE | lower | -0.81835 | 0.049654 | -1.0868 | 0.066623 | Extreme triggered | 1 | 2025-08-14 18:45 | 2025-08-14 19:00 | 2.2584 | -0.28 | -0.28 | -0.028 | 0.25533 | -0.98694 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.2363 | Day
2025-08-14 19:00 | 74.76 | 74.9 | 0.19271 | 75.2854 | 74.5146 | -0.72648 | FALSE | none | -0.52542 | -0.24542 | -0.6979 | -0.32936 | Persistence ends | 0 |  |  |  | 0.28 | 0.28 | -0.014 | 0.26446 | 1.1117 | FALSE | 1 | FALSE | FALSE | FALSE | FALSE | 0.077 | Night
2025-08-14 19:15 | 75.32 | 74.928 | 0.2111 | 75.3502 | 74.5058 | 1.8569 | FALSE | none | -0.030205 | -0.8142 | -0.040086 | -1.0928 | Normal | 0 |  |  |  | 0.56 | 0.56 | 0.028 | 0.28583 | 1.8612 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.1238 | Night
2025-08-14 19:30 | 75.88 | 74.97 | 0.29958 | 75.5692 | 74.3708 | 3.0376 | TRUE | upper | 0.31084 | -1.5092 | 0.41134 | -2.0292 | Extreme triggered | 1 | 2025-08-14 19:30 | 2025-08-14 23:30 | 3.0376 | 0.56 | 0.56 | 0.042 | 0.30504 | 1.6981 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.2596 | Night
2025-08-14 19:45 | 76.16 | 75.04 | 0.39598 | 75.832 | 74.248 | 2.8284 | TRUE | upper | 0.32804 | -1.912 | 0.43259 | -2.5751 | Extreme/elevated | 2 | 2025-08-14 19:30 |  | 2.933 | 0.28 | 0.28 | 0.07 | 0.29958 | 0.70098 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.3028 | Night
2025-08-14 20:00 | 76.72 | 75.138 | 0.53955 | 76.2171 | 74.0589 | 2.9321 | TRUE | upper | 0.5029 | -2.6611 | 0.65983 | -3.5932 | Persistent | 3 | 2025-08-14 19:30 |  | 2.9327 | 0.56 | 0.56 | 0.098 | 0.31828 | 1.4516 | FALSE | 0 | FALSE | TRUE | FALSE | FALSE | 0.3669 | Night
2025-08-14 20:15 | 77.28 | 75.264 | 0.713 | 76.69 | 73.838 | 2.8275 | TRUE | upper | 0.59001 | -3.442 | 0.76934 | -4.6615 | Persistent | 4 | 2025-08-14 19:30 |  | 2.9064 | 0.56 | 0.56 | 0.126 | 0.33347 | 1.3015 | FALSE | 0 | FALSE | TRUE | FALSE | FALSE | 0.4171 | Night
2025-08-14 20:30 | 77.28 | 75.376 | 0.84049 | 77.057 | 73.695 | 2.2653 | TRUE | upper | 0.22302 | -3.585 | 0.28942 | -4.8646 | Persistent | 5 | 2025-08-14 19:30 |  | 2.7782 | 0 | 0 | 0.112 | 0.33254 | -0.3368 | FALSE | 0 | FALSE | TRUE | FALSE | FALSE | 0.4367 | Night
2025-08-14 20:45 | 78.12 | 75.53 | 1.0353 | 77.6006 | 73.4594 | 2.5017 | TRUE | upper | 0.51943 | -4.6606 | 0.66937 | -6.3444 | Persistent | 6 | 2025-08-14 19:30 |  | 2.7321 | 0.84 | 0.84 | 0.154 | 0.36873 | 1.8604 | FALSE | 0 | FALSE | TRUE | FALSE | FALSE | 0.5096 | Night
2025-08-14 21:00 | 78.12 | 75.684 | 1.1778 | 78.0396 | 73.3284 | 2.0682 | TRUE | upper | 0.080354 | -4.7916 | 0.10297 | -6.5345 | Confirmed/Materialized Shift | 7 | 2025-08-14 19:30 |  | 2.6373 | 0 | 0 | 0.154 | 0.36873 | -0.41765 | FALSE | 0 | FALSE | TRUE | TRUE | FALSE | 0.5379 | Night
2025-08-14 21:15 | 78.4 | 75.852 | 1.313 | 78.478 | 73.226 | 1.9406 | FALSE | none | -0.078004 | -5.174 | -0.099396 | -7.0658 | Confirmed/Materialized Shift | 8 | 2025-08-14 19:30 |  | 2.5502 | 0.28 | 0.28 | 0.168 | 0.36789 | 0.30444 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.5294 | Night
2025-08-14 21:30 | 78.96 | 76.062 | 1.4571 | 78.9762 | 73.1478 | 1.9889 | FALSE | none | -0.016238 | -5.8122 | -0.020561 | -7.9459 | Confirmed/Materialized Shift | 9 | 2025-08-14 19:30 |  | 2.4878 | 0.56 | 0.56 | 0.21 | 0.36195 | 0.96697 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.5326 | Night
2025-08-14 21:45 | 79.24 | 76.258 | 1.6079 | 79.4738 | 73.0422 | 1.8546 | FALSE | none | -0.2338 | -6.1978 | -0.29419 | -8.4852 | Confirmed/Materialized Shift | 10 | 2025-08-14 19:30 |  | 2.4245 | 0.28 | 0.28 | 0.196 | 0.35301 | 0.23795 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.5236 | Night
2025-08-14 22:00 | 79.8 | 76.496 | 1.7629 | 80.0219 | 72.9701 | 1.8741 | FALSE | none | -0.22187 | -6.8299 | -0.27726 | -9.3598 | Confirmed/Materialized Shift | 11 | 2025-08-14 19:30 |  | 2.3745 | 0.56 | 0.56 | 0.238 | 0.34323 | 0.93815 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.5249 | Night
2025-08-14 22:15 | 80.08 | 76.762 | 1.8844 | 80.5308 | 72.9932 | 1.7608 | FALSE | none | -0.45077 | -7.0868 | -0.55974 | -9.7088 | Confirmed/Materialized Shift | 12 | 2025-08-14 19:30 |  | 2.3233 | 0.28 | 0.28 | 0.266 | 0.32086 | 0.043633 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.5174 | Night
2025-08-14 22:30 | 80.08 | 77.014 | 1.9767 | 80.9674 | 73.0606 | 1.5511 | FALSE | none | -0.88744 | -7.0194 | -1.096 | -9.6077 | Confirmed/Materialized Shift | 13 | 2025-08-14 19:30 |  | 2.2639 | 0 | 0 | 0.252 | 0.32628 | -0.77234 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.5034 | Night
2025-08-14 22:45 | 80.08 | 77.28 | 2.015 | 81.31 | 73.25 | 1.3896 | FALSE | none | -1.23 | -6.83 | -1.5128 | -9.3243 | Confirmed/Materialized Shift | 14 | 2025-08-14 19:30 |  | 2.2015 | 0 | 0 | 0.266 | 0.30773 | -0.86439 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4926 | Night
2025-08-14 23:00 | 80.36 | 77.546 | 2.0545 | 81.655 | 73.437 | 1.3697 | FALSE | none | -1.295 | -6.923 | -1.586 | -9.4272 | Confirmed/Materialized Shift | 15 | 2025-08-14 19:30 |  | 2.146 | 0.28 | 0.28 | 0.266 | 0.30773 | 0.045494 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4913 | Night
2025-08-14 23:15 | 80.08 | 77.798 | 2.04 | 81.878 | 73.718 | 1.1186 | FALSE | none | -1.798 | -6.362 | -2.1959 | -8.6302 | Confirmed/Materialized Shift | 16 | 2025-08-14 19:30 |  | 2.0818 | -0.28 | -0.28 | 0.252 | 0.32628 | -1.6305 | FALSE | 0 | FALSE | FALSE | TRUE | FALSE | 0.4746 | Night
2025-08-14 23:30 | 79.8 | 78.05 | 1.9545 | 81.9589 | 74.1411 | 0.89539 | FALSE | none | -2.1589 | -5.6589 | -2.6342 | -7.6327 | Persistence ends | 0 |  |  |  | -0.28 | -0.28 | 0.252 | 0.32628 | -1.6305 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0597 | Night
2025-08-14 23:45 | 80.08 | 78.33 | 1.812 | 81.9541 | 74.7059 | 0.96576 | FALSE | none | -1.8741 | -5.3741 | -2.2868 | -7.1937 | Normal | 0 |  |  |  | 0.28 | 0.28 | 0.28 | 0.3013 | 2.3951e-15 | FALSE | 0 | FALSE | FALSE | FALSE | FALSE | 0.0644 | Night