## Summary
Results analysis summary: Monthly overview |  |  | Report generated: 10/08/2026 12:28
Hello,
Below is a summary of the 3 months of readings for Jensen Beach AHU 1 (8,111 readings, 12/01/2025 – 02/25/2026), and our recommendations.
Use the tabs at the bottom to find more detail about each month, including event-level actions.
Read the Guide | See the charts (go to 'Dashboard')
December 2025 / Sensor: Jensen Beach AHU 1 (°F) |  | Rank by mean materiality: 3 out of 3 months · extremes 12% of readings | Status: | 4 recommendations
Improve | Recommendations | Why have we recommended this? |  | Learn more
Operating level | ● Review what changed when the level shifted | Confirmed shift share: 19% of readings (143 h). The value stayed away from its baseline for 7+ readings with mean ¦Z¦ ≥ 1.2 - check setpoint or schedule changes, sensor drift or an equipment fault. |  | Confirmed/Materialized Shift
Daily cycle | ● Check the day/night pattern before acting on single extremes | Upper extremes happen mostly by day and lower extremes mostly at night (137 upper, 235 lower). With a 20-reading (5 h) baseline, the normal daily swing itself is flagged. If the swing is intended (setback), consider Window = 96 (24 h). |  | Window (W)
Stability | ● Check for hunting or short-cycling | Material changes: 4.3 per day - fast changes that repeat within 10 readings. Check valve/damper control loops and compressor or fan staging. |  | MaterialChangeFlag
Data quality | ● Fix the data gaps | Missing data: 54.8 h in gaps longer than three intervals. Events inside a gap cannot be detected. |  | Data gaps
Show events and benchmarks for this month (go to 'Dec 2025')
January 2026 / Sensor: Jensen Beach AHU 1 (°F) |  | Rank by mean materiality: 2 out of 3 months · extremes 12% of readings | Status: | 4 recommendations
Improve | Recommendations | Why have we recommended this? |  | Learn more
Operating level | ● Review what changed when the level shifted | Confirmed shift share: 25% of readings (175 h). The value stayed away from its baseline for 7+ readings with mean ¦Z¦ ≥ 1.2 - check setpoint or schedule changes, sensor drift or an equipment fault. |  | Confirmed/Materialized Shift
Daily cycle | ● Check the day/night pattern before acting on single extremes | Upper extremes happen mostly by day and lower extremes mostly at night (171 upper, 171 lower). With a 20-reading (5 h) baseline, the normal daily swing itself is flagged. If the swing is intended (setback), consider Window = 96 (24 h). |  | Window (W)
Stability | ● Check for hunting or short-cycling | Material changes: 4.1 per day - fast changes that repeat within 10 readings. Check valve/damper control loops and compressor or fan staging. |  | MaterialChangeFlag
Data quality | ● Fix the data gaps | Missing data: 60.7 h in gaps longer than three intervals. Events inside a gap cannot be detected. |  | Data gaps
Show events and benchmarks for this month (go to 'Jan 2026')
February 2026 / Sensor: Jensen Beach AHU 1 (°F) |  | Rank by mean materiality: 1 out of 3 months · extremes 13% of readings | Status: | 4 recommendations
Improve | Recommendations | Why have we recommended this? |  | Learn more
Operating level | ● Review what changed when the level shifted | Confirmed shift share: 33% of readings (190 h). The value stayed away from its baseline for 7+ readings with mean ¦Z¦ ≥ 1.2 - check setpoint or schedule changes, sensor drift or an equipment fault. |  | Confirmed/Materialized Shift
Daily cycle | ● Check the day/night pattern before acting on single extremes | Upper extremes happen mostly by day and lower extremes mostly at night (170 upper, 123 lower). With a 20-reading (5 h) baseline, the normal daily swing itself is flagged. If the swing is intended (setback), consider Window = 96 (24 h). |  | Window (W)
Stability | ● Check for hunting or short-cycling | Material changes: 3.2 per day - fast changes that repeat within 10 readings. Check valve/damper control loops and compressor or fan staging. |  | MaterialChangeFlag
Data quality | ● Fix the data gaps | Missing data: 40.4 h in gaps longer than three intervals. Events inside a gap cannot be detected. |  | Data gaps
Show events and benchmarks for this month (go to 'Feb 2026')
Data quality / Gaps in the readings |  | 12 gaps, 155.9 hours of missing data | Status: | Gaps to review
Show the gaps (go to 'Data gaps')

## Dashboard
Dashboard | [11 empty] | Report generated: 10/08/2026 12:28
< Back to summary worksheet
Charts for the whole period, drawn from the Data tab. The monthly figures behind them are in the table below (live formulas).
Monthly figures
Month | Extreme share | Confirmed share | Sustained (h) | Material changes/day | Investigate | Review | Monitor | Upper – Day | Upper – Night | Lower – Day | Lower – Night
Dec 2025 | 12.27% | 18.8% | 235.7833 | 4.2903 | 81 | 19 | 22 | 94 | 43 | 113 | 122
Jan 2026 | 12.15% | 24.8% | 251.335 | 4.1 | 59 | 29 | 14 | 141 | 30 | 61 | 110
Feb 2026 | 12.94% | 33.39% | 246.3183 | 3.24 | 49 | 11 | 5 | 164 | 6 | 29 | 94
By month
Events and extremes
Time of day
By day

## Guide
Guide
This report summarises the Extreme & Change analysis of Jensen Beach AHU 1 and gives recommendations and benchmarks for each month.
It shows when the readings left their normal range, how long deviations lasted, how often the value changed abnormally fast, and how much data is missing.
How to use this report
Use the tabs at the bottom of the screen to move through the workbook.
Tab (at the bottom of the screen) | What is on the tab?
Summary | Overview of each month with recommendations, and links to the month tabs.
Month tabs | ● Analysis funnel: extreme share, sustained deviation hours and material changes per day, with the month's rank.
● Recommendations with this month vs the best and worst month.
● More benchmarks, including the same figures for day and night.
● Every event in the month, sorted by materiality; click the Action to jump to the readings.
Data gaps | Every break in the data longer than three reading intervals, with the hours missing.
Events | All events in the whole period in one filterable list.
Daily overview | One row per day: readings, value range, extremes, persistent and confirmed periods, changes, peak materiality.
Monthly metrics | The calculation table behind the Summary and month tabs (all formulas). The reading interval can be changed here.
Column descriptor | What every column of the results file means, which parameters drive it, and the settings used for this run.
Data | The results file Jensen_Beach_Results_Analysis.csv as exported by the app, plus three helper columns. Rows are in time order (UTC), so the local time repeats once when daylight saving ends.
How are the results calculated?
Each reading is compared with a rolling baseline of the previous 20 readings (about 5 hours). ¦Z¦ ≥ 2 flags an Extreme reading.
An event continues while ¦Z¦ ≥ 1; after 3 readings it is Persistent, after 7 readings with mean ¦Z¦ ≥ 1.2 it is a Confirmed/Materialized Shift.
The rate of change has its own baseline; ¦Z_ROC¦ ≥ 2 is an Abnormal Change, and 2 or more within 10 readings make a Material Change.
The Materiality score (0–1) combines size (¦Z¦), duration and recurrence. Rank 1 = the month with the most issues.
Recommendations are rules applied to these figures; they point to what to check, they are not a diagnosis of the equipment.
Learn more: info_main\Statistical_calc_parameters\Statistical calc parameters manual.docx

## Data gaps
Data gaps | [7 empty] | Report generated: 10/08/2026 12:28
The analysis expects one reading about every 15 minutes.
A gap is any break of more than three reading intervals. No readings, and so no extremes or events, exist inside a gap.
This tab lists every gap and the time it covers, so missing data is not mistaken for normal operation.
Summary of gaps
Number of gaps |  | 12
Missing time (hours) |  | 155.8906
From (last reading) | To (next reading) | Hours missing | Readings missing (approx.) | Day/Night at start | Severity | Action | Month key
2025-12-31 06:24 | 2026-01-02 13:13 | 54.8228 | 218 | Night | High | Check the logger / network for this period | 202512
2026-01-16 03:27 | 2026-01-16 09:48 | 6.3411 | 24 | Night | Medium | Check the logger / network for this period | 202601
2026-01-19 06:24 | 2026-01-20 11:30 | 29.1064 | 115 | Night | High | Check the logger / network for this period | 202601
2026-01-28 04:27 | 2026-01-28 09:51 | 5.4036 | 21 | Night | Low | Monitor | 202601
2026-01-29 02:43 | 2026-01-29 09:43 | 7.0117 | 27 | Night | Medium | Check the logger / network for this period | 202601
2026-01-31 22:26 | 2026-02-01 11:17 | 12.8511 | 50 | Night | Medium | Check the logger / network for this period | 202601
2026-02-01 18:02 | 2026-02-02 11:31 | 17.4756 | 69 | Day | Medium | Check the logger / network for this period | 202602
2026-02-02 18:30 | 2026-02-03 11:44 | 17.2256 | 68 | Night | Medium | Check the logger / network for this period | 202602
2026-02-03 14:13 | 2026-02-03 15:35 | 1.3633 | 4 | Day | Low | Monitor | 202602
2026-02-03 17:10 | 2026-02-03 18:46 | 1.6144 | 5 | Day | Low | Monitor | 202602
2026-02-06 20:29 | 2026-02-06 21:46 | 1.2742 | 4 | Night | Low | Monitor | 202602
2026-02-07 14:39 | 2026-02-07 16:03 | 1.4008 | 5 | Day | Low | Monitor | 202602

## Dec 2025
We compared each reading with its own rolling baseline using the settings below | [5 empty] | Rank by mean materiality: 3 of 3 months (1 = most issues)
Sensor: Jensen Beach AHU 1 (°F), Period: December 2025, Value range: 67.9 – 75.5 °F | [5 empty] | Report generated: 10/08/2026 12:28
< Back to summary worksheet
Analysis funnel
Readings in this month: 3,032 |  | vs other months (3) | Recommendations to improve |  |  |  | Why have we recommended this?
| Extreme readings |  |  | This month | Best month | Worst month
| Share of readings | Rank vs other months | ● Review what changed when the level shifted | 18.8% | 18.8% | 33.39% | Confirmed shift share: 19% of readings (143 h). The value stayed away from its baseline for 7+ readings with mean ¦Z¦ ≥ 1.2 - check setpoint or schedule changes, sensor drift or an equipment fault.
| 12.27% | 2
| Sustained deviations |  | ● Check the day/night pattern before acting on single extremes | 12.27% | 12.15% | 12.94% | Upper extremes happen mostly by day and lower extremes mostly at night (137 upper, 235 lower). With a 20-reading (5 h) baseline, the normal daily swing itself is flagged. If the swing is intended (setback), consider Window = 96 (24 h).
| Hours (Persistent + Confirmed) | Rank vs other months
| 235.7833 | 3
|  |  | ● Check for hunting or short-cycling | 4.2903 | 3.24 | 4.2903 | Material changes: 4.3 per day - fast changes that repeat within 10 readings. Check valve/damper control loops and compressor or fan staging.
Material changes
| Per day | Rank vs other months
| 4.2903 | 1 | ● Fix the data gaps | 54.8228 | 40.3539 | 60.7139 | Missing data: 54.8 h in gaps longer than three intervals. Events inside a gap cannot be detected.
More benchmarks
|  |  | Measure | This month | Best month | Worst month | Whole period | This month – Day | This month – Night
|  |  | Mean value | 73.1788 | 71.6342 | 73.1788 | 72.5343 | 73.0248 | 73.304
|  |  | Min value | 67.8596 | 65.0354 | 67.8596 | 65.0354 | 69.836 | 67.8596
|  |  | Max value | 75.4826 | 74.9174 | 75.4826 | 75.4826 | 75.4826 | 75.2
|  |  | Extreme share | 12.27% | 12.15% | 12.94% | 12.42% | 15.23% | 9.863%
|  |  | Upper extremes | 137 | 137 | 171 | 478 | 94 | 43
|  |  | Lower extremes | 235 | 123 | 235 | 529 | 113 | 122
|  |  | Sustained deviation (h) | 235.7833 | 235.7833 | 251.335 | 733.4367 | 88.2933 | 147.49
|  |  | Confirmed share | 18.8% | 18.8% | 33.39% | 24.95% | 13.83% | 22.83%
|  |  | Material changes per day | 4.2903 | 3.24 | 4.2903 | 3.9186 | Not relevant | Not relevant
|  |  | Mean materiality score | 0.21424 | 0.21424 | 0.26953 | 0.2369 | 0.19869 | 0.22687
|  |  | Max ¦Z¦ | 4.2485 | 4.2485 | 4.2485 | 4.2485 | 4.2485 | 4.2485
|  |  | Data gap hours | 54.8228 | 40.3539 | 60.7139 | 155.8906 | Not relevant | Not relevant
* Best = lowest month, Worst = highest month for each measure (for Mean/Min/Max value: simply the lowest and highest month).
* Max ¦Z¦ is capped at 4.25 with a 20-reading rolling window ((W−1)/√W), so it is the same in every month; use Extreme share and the events instead.
* Settings: Rolling Mean/Std, Window 20, K_E 2.0, K_P 1.0, N_P 3, N_M 7, K_M 1.2, N_EXIT 1, ROC h 1, ROC window 20, ROC_K 2.0, frequency 10 / min 2.
Readings against the normal range
Grey band = normal range (moving average ± 2σ). Dots outside it are Extreme readings: orange = upper, blue = lower.
Events in this month
View all events
* Sorted by materiality score (highest first). Action: Investigate = Confirmed shift, Review = Persistent, Monitor = shorter events. Click the Action to see the readings.
Start | End | Duration (h) | Highest state | Direction | Peak value | Max ¦Z¦ | Mean ¦Z¦ | Max materiality | Day/Night | Action
2025-12-02 08:16 | 2025-12-02 11:29 | 3.4794 | Confirmed/Materialized Shift | upper | 74.9174 | 3.783 | 2.0473 | 0.7019 | Day | Investigate
2025-12-15 10:00 | 2025-12-15 11:05 | 1.3328 | Confirmed/Materialized Shift | upper | 74.0714 | 3.7804 | 2.7601 | 0.7004 | Day | Investigate
2025-12-15 02:13 | 2025-12-15 05:12 | 3.2364 | Confirmed/Materialized Shift | lower | 73.5062 | 4.2485 | 2.0302 | 0.6648 | Night | Investigate
2025-12-14 17:13 | 2025-12-14 20:14 | 3.2761 | Confirmed/Materialized Shift | upper | 74.0714 | 2.9539 | 1.8358 | 0.6541 | Day | Investigate
2025-12-18 08:49 | 2025-12-18 10:29 | 1.9286 | Confirmed/Materialized Shift | lower | 72.095 | 3.5884 | 2.5668 | 0.6508 | Day | Investigate
2025-12-06 03:13 | 2025-12-06 04:58 | 1.9897 | Confirmed/Materialized Shift | lower | 73.5062 | 2.5628 | 1.9608 | 0.628 | Night | Investigate
2025-12-30 04:12 | 2025-12-30 07:45 | 3.8022 | Confirmed/Materialized Shift | lower | 72.095 | 2.5628 | 1.6459 | 0.628 | Night | Investigate
2025-12-07 05:18 | 2025-12-07 08:02 | 2.9847 | Confirmed/Materialized Shift | lower | 74.0714 | 2.4865 | 1.8722 | 0.6229 | Night | Investigate
2025-12-21 01:28 | 2025-12-21 05:12 | 3.9875 | Confirmed/Materialized Shift | lower | 72.941 | 2.4713 | 1.5711 | 0.6219 | Night | Investigate
2025-12-17 04:42 | 2025-12-17 06:12 | 1.7472 | Confirmed/Materialized Shift | lower | 72.6584 | 2.4597 | 1.8067 | 0.6211 | Night | Investigate
2025-12-06 15:29 | 2025-12-06 17:21 | 2.1181 | Confirmed/Materialized Shift | lower | 71.8124 | 3.0822 | 2.3897 | 0.6204 | Day | Investigate
2025-12-08 09:03 | 2025-12-08 10:23 | 1.5911 | Confirmed/Materialized Shift | lower | 71.8124 | 3.4159 | 2.7761 | 0.6195 | Day | Investigate
2025-12-30 20:41 | 2026-01-02 15:58 | 67.5222 | Confirmed/Materialized Shift | lower | 67.8596 | 2.8497 | 1.6803 | 0.6185 | Night | Investigate
2025-12-24 09:00 | 2025-12-24 12:02 | 3.2872 | Confirmed/Materialized Shift | upper | 74.0714 | 2.7761 | 1.9538 | 0.6182 | Day | Investigate
2025-12-16 07:30 | 2025-12-16 11:57 | 4.6919 | Confirmed/Materialized Shift | upper | 73.7888 | 2.703 | 1.7134 | 0.6088 | Day | Investigate
2025-12-10 01:55 | 2025-12-10 04:54 | 3.2356 | Confirmed/Materialized Shift | lower | 73.2236 | 4.2485 | 2.0622 | 0.6077 | Night | Investigate
2025-12-05 00:29 | 2025-12-05 04:57 | 4.7317 | Confirmed/Materialized Shift | lower | 73.2236 | 2.8102 | 1.7562 | 0.6077 | Night | Investigate
2025-12-22 08:33 | 2025-12-22 10:44 | 2.4392 | Confirmed/Materialized Shift | lower | 72.6584 | 3.5896 | 2.3818 | 0.6062 | Day | Investigate
2025-12-21 05:56 | 2025-12-21 07:26 | 1.7389 | Confirmed/Materialized Shift | lower | 72.3758 | 2.2253 | 1.7435 | 0.6055 | Night | Investigate
2025-12-12 09:15 | 2025-12-12 12:59 | 3.9772 | Confirmed/Materialized Shift | upper | 73.7888 | 2.7117 | 1.8381 | 0.6048 | Day | Investigate
2025-12-11 00:14 | 2025-12-11 08:00 | 8.0331 | Confirmed/Materialized Shift | lower | 70.9646 | 2.2757 | 1.7051 | 0.6024 | Night | Investigate
2025-12-28 09:00 | 2025-12-28 12:44 | 3.9775 | Confirmed/Materialized Shift | upper | 74.0714 | 2.9202 | 1.8121 | 0.5986 | Day | Investigate
2025-12-25 00:14 | 2025-12-25 06:41 | 6.7131 | Confirmed/Materialized Shift | lower | 72.095 | 2.4713 | 1.6207 | 0.596 | Night | Investigate
2025-12-28 23:28 | 2025-12-29 06:11 | 6.9719 | Confirmed/Materialized Shift | lower | 71.8124 | 2.8102 | 1.6373 | 0.5941 | Night | Investigate
2025-12-16 02:58 | 2025-12-16 04:57 | 2.2406 | Confirmed/Materialized Shift | lower | 71.8124 | 2.4779 | 1.6214 | 0.5938 | Night | Investigate
2025-12-25 23:59 | 2025-12-26 08:15 | 8.5331 | Confirmed/Materialized Shift | lower | 71.5298 | 2.4713 | 1.6097 | 0.5913 | Night | Investigate
2025-12-24 00:40 | 2025-12-24 05:54 | 5.4758 | Confirmed/Materialized Shift | lower | 72.095 | 2.6745 | 1.5527 | 0.591 | Night | Investigate
2025-12-17 06:56 | 2025-12-17 08:30 | 1.8131 | Confirmed/Materialized Shift | lower | 72.3758 | 2.3111 | 1.7284 | 0.5877 | Night | Investigate
2025-12-26 09:15 | 2025-12-26 11:44 | 2.7319 | Confirmed/Materialized Shift | upper | 74.0714 | 3.0644 | 1.9009 | 0.5813 | Day | Investigate
2025-12-21 08:45 | 2025-12-21 09:51 | 1.3467 | Confirmed/Materialized Shift | upper | 74.0714 | 3.0775 | 2.1572 | 0.5798 | Day | Investigate
2025-12-19 08:48 | 2025-12-19 10:29 | 1.9375 | Confirmed/Materialized Shift | lower | 72.095 | 3.8577 | 2.3488 | 0.5796 | Day | Investigate
2025-12-22 01:13 | 2025-12-22 03:42 | 2.7406 | Confirmed/Materialized Shift | lower | 74.3522 | 4.2485 | 2.0997 | 0.5742 | Night | Investigate
2025-12-10 16:28 | 2025-12-10 18:27 | 2.2403 | Confirmed/Materialized Shift | lower | 72.095 | 3.1509 | 2.3684 | 0.5688 | Day | Investigate
2025-12-20 03:57 | 2025-12-20 08:16 | 4.5558 | Confirmed/Materialized Shift | lower | 72.941 | 2.0867 | 1.5562 | 0.5656 | Night | Investigate
2025-12-18 02:39 | 2025-12-18 04:24 | 1.9981 | Confirmed/Materialized Shift | lower | 73.7888 | 2.924 | 1.7463 | 0.5653 | Night | Investigate
2025-12-14 09:45 | 2025-12-14 11:15 | 1.7453 | Confirmed/Materialized Shift | lower | 72.3758 | 3.5547 | 2.2088 | 0.5647 | Day | Investigate
2025-12-27 09:30 | 2025-12-27 12:03 | 2.8111 | Confirmed/Materialized Shift | upper | 74.0714 | 3.1806 | 1.9413 | 0.5627 | Day | Investigate
2025-12-25 09:00 | 2025-12-25 11:44 | 2.9831 | Confirmed/Materialized Shift | upper | 74.0714 | 3.0222 | 1.9148 | 0.5614 | Day | Investigate
2025-12-29 09:00 | 2025-12-29 11:44 | 2.9825 | Confirmed/Materialized Shift | upper | 74.0714 | 2.7707 | 2.0477 | 0.5608 | Day | Investigate
2025-12-21 18:16 | 2025-12-21 21:14 | 3.2256 | Confirmed/Materialized Shift | upper | 74.9174 | 2.3123 | 1.5763 | 0.5607 | Night | Investigate
2025-12-04 16:14 | 2025-12-04 18:13 | 2.2408 | Confirmed/Materialized Shift | lower | 72.095 | 2.7404 | 2.2193 | 0.5588 | Day | Investigate
2025-12-13 09:30 | 2025-12-13 13:31 | 4.2694 | Confirmed/Materialized Shift | upper | 74.0714 | 2.743 | 1.7371 | 0.557 | Day | Investigate
2025-12-06 05:42 | 2025-12-06 07:12 | 1.7472 | Confirmed/Materialized Shift | lower | 73.5062 | 2.0125 | 1.4461 | 0.5555 | Night | Investigate
2025-12-02 18:57 | 2025-12-02 22:40 | 3.9689 | Confirmed/Materialized Shift | upper | 74.0714 | 2.6876 | 1.7013 | 0.5529 | Night | Investigate
2025-12-20 15:43 | 2025-12-20 17:31 | 2.0472 | Confirmed/Materialized Shift | lower | 72.095 | 2.351 | 1.7708 | 0.5527 | Day | Investigate
2025-12-09 19:27 | 2025-12-09 20:56 | 1.7367 | Confirmed/Materialized Shift | upper | 74.0714 | 2.976 | 1.6231 | 0.5526 | Night | Investigate
2025-12-04 08:46 | 2025-12-04 11:04 | 2.5597 | Confirmed/Materialized Shift | upper | 74.0714 | 2.6216 | 1.7921 | 0.5504 | Day | Investigate
2025-12-26 23:28 | 2025-12-27 04:27 | 5.2256 | Confirmed/Materialized Shift | lower | 72.095 | 2.2418 | 1.5875 | 0.5495 | Night | Investigate
2025-12-06 18:06 | 2025-12-06 21:05 | 3.2331 | Confirmed/Materialized Shift | upper | 74.9174 | 2.297 | 1.7075 | 0.5494 | Night | Investigate
2025-12-23 08:48 | 2025-12-23 10:29 | 1.9375 | Confirmed/Materialized Shift | lower | 72.095 | 3.7773 | 2.2726 | 0.5437 | Day | Investigate
2025-12-13 05:18 | 2025-12-13 07:30 | 2.4544 | Confirmed/Materialized Shift | lower | 70.3994 | 2.1273 | 1.4632 | 0.5426 | Night | Investigate
2025-12-19 15:58 | 2025-12-19 17:27 | 1.7389 | Confirmed/Materialized Shift | lower | 72.095 | 2.6584 | 2.1332 | 0.5417 | Day | Investigate
2025-12-03 23:55 | 2025-12-04 04:54 | 5.2247 | Confirmed/Materialized Shift | lower | 72.6584 | 2.4713 | 1.5676 | 0.5389 | Night | Investigate
2025-12-11 23:28 | 2025-12-12 07:45 | 8.5331 | Confirmed/Materialized Shift | lower | 69.836 | 2.1657 | 1.62 | 0.5377 | Night | Investigate
2025-12-27 22:59 | 2025-12-28 05:41 | 6.965 | Confirmed/Materialized Shift | lower | 71.8124 | 2.1759 | 1.4905 | 0.5361 | Night | Investigate
2025-12-11 10:00 | 2025-12-11 12:29 | 2.7342 | Confirmed/Materialized Shift | upper | 73.5062 | 2.4799 | 1.882 | 0.536 | Day | Investigate
2025-12-07 15:28 | 2025-12-07 17:35 | 2.3586 | Confirmed/Materialized Shift | lower | 71.8124 | 2.6456 | 2.0826 | 0.534 | Day | Investigate
2025-12-25 18:46 | 2025-12-25 21:15 | 2.7325 | Confirmed/Materialized Shift | upper | 73.7888 | 2.897 | 1.8679 | 0.5307 | Night | Investigate
2025-12-10 09:00 | 2025-12-10 11:16 | 2.5156 | Confirmed/Materialized Shift | upper | 74.0714 | 2.477 | 1.5651 | 0.5279 | Day | Investigate
2025-12-05 19:31 | 2025-12-05 21:45 | 2.4911 | Confirmed/Materialized Shift | upper | 74.0714 | 2.1636 | 1.5364 | 0.5238 | Night | Investigate
2025-12-20 18:45 | 2025-12-20 20:59 | 2.4914 | Confirmed/Materialized Shift | upper | 73.7888 | 2.0317 | 1.4916 | 0.5208 | Night | Investigate
2025-12-08 19:41 | 2025-12-08 22:26 | 2.9928 | Confirmed/Materialized Shift | upper | 74.3522 | 2.0578 | 1.4195 | 0.5205 | Night | Investigate
2025-12-03 18:57 | 2025-12-03 21:11 | 2.4808 | Confirmed/Materialized Shift | upper | 73.7888 | 2.2292 | 1.6162 | 0.519 | Night | Investigate
2025-12-09 02:25 | 2025-12-09 04:24 | 2.2406 | Confirmed/Materialized Shift | lower | 73.7888 | 3.0911 | 1.782 | 0.5171 | Night | Investigate
2025-12-17 01:43 | 2025-12-17 03:42 | 2.2403 | Confirmed/Materialized Shift | lower | 73.2236 | 4.2485 | 2.0243 | 0.5171 | Night | Investigate
2025-12-07 02:33 | 2025-12-07 04:33 | 2.2403 | Confirmed/Materialized Shift | lower | 74.9174 | 2.924 | 1.8771 | 0.5171 | Night | Investigate
2025-12-09 05:38 | 2025-12-09 07:30 | 2.1208 | Confirmed/Materialized Shift | lower | 73.5062 | 2.2722 | 1.5498 | 0.5171 | Night | Investigate
2025-12-27 17:46 | 2025-12-27 19:44 | 2.23 | Confirmed/Materialized Shift | upper | 73.7888 | 2.5141 | 1.7124 | 0.5148 | Night | Investigate
2025-12-19 18:46 | 2025-12-19 20:44 | 2.2297 | Confirmed/Materialized Shift | upper | 74.0714 | 2.2702 | 1.6192 | 0.5134 | Night | Investigate
2025-12-17 19:57 | 2025-12-17 22:41 | 2.9844 | Confirmed/Materialized Shift | upper | 74.0714 | 2.0094 | 1.4217 | 0.5066 | Night | Investigate
2025-12-06 10:01 | 2025-12-06 11:45 | 1.9897 | Confirmed/Materialized Shift | lower | 72.941 | 2.4908 | 1.6141 | 0.5065 | Day | Investigate
2025-12-22 16:58 | 2025-12-22 18:30 | 1.7914 | Confirmed/Materialized Shift | lower | 72.095 | 2.7751 | 2.0656 | 0.5062 | Day | Investigate
2025-12-27 06:41 | 2025-12-27 08:16 | 1.8211 | Confirmed/Materialized Shift | lower | 71.5298 | 2.163 | 1.5294 | 0.5062 | Night | Investigate
2025-12-30 01:13 | 2025-12-30 02:58 | 1.9897 | Confirmed/Materialized Shift | lower | 72.941 | 2.1794 | 1.5183 | 0.5046 | Night | Investigate
2025-12-15 17:00 | 2025-12-15 18:46 | 2.0042 | Confirmed/Materialized Shift | lower | 72.3758 | 2.4597 | 1.7666 | 0.5043 | Day | Investigate
2025-12-17 10:00 | 2025-12-17 11:29 | 1.7389 | Confirmed/Materialized Shift | upper | 73.7888 | 2.4597 | 1.8704 | 0.4995 | Day | Investigate
2025-12-29 19:01 | 2025-12-29 20:44 | 1.9789 | Confirmed/Materialized Shift | upper | 73.7888 | 2.3702 | 1.5318 | 0.4974 | Night | Investigate
2025-12-10 06:38 | 2025-12-10 08:00 | 1.6256 | Confirmed/Materialized Shift | lower | 72.3758 | 2.2294 | 1.7133 | 0.4971 | Night | Investigate
2025-12-05 16:44 | 2025-12-05 18:13 | 1.7472 | Confirmed/Materialized Shift | lower | 72.095 | 2.1419 | 1.613 | 0.4958 | Day | Investigate
2025-12-23 16:58 | 2025-12-23 18:27 | 1.7392 | Confirmed/Materialized Shift | lower | 71.8124 | 2.4287 | 1.9651 | 0.4851 | Day | Investigate
2025-12-15 23:58 | 2025-12-16 01:43 | 1.9906 | Confirmed/Materialized Shift | lower | 72.3758 | 2.1141 | 1.4708 | 0.4777 | Night | Investigate
2025-12-18 17:42 | 2025-12-18 18:31 | 1.0556 | Persistent | lower | 72.3758 | 2.5868 | 2.069 | 0.4687 | Night | Review
2025-12-11 15:43 | 2025-12-11 16:35 | 1.1142 | Persistent | lower | 72.3758 | 2.5192 | 1.9186 | 0.4679 | Day | Review
2025-12-26 18:46 | 2025-12-26 20:00 | 1.4858 | Persistent | upper | 73.7888 | 2.536 | 1.9687 | 0.4665 | Night | Review
2025-12-28 16:43 | 2025-12-28 17:31 | 1.0464 | Persistent | lower | 72.095 | 2.4753 | 2.1551 | 0.4614 | Day | Review
2025-12-01 18:12 | 2025-12-01 18:42 | 0.75528 | Persistent | lower | 72.095 | 2.571 | 2.2268 | 0.4351 | Night | Review
2025-12-03 09:00 | 2025-12-03 09:59 | 1.2383 | Persistent | lower | 72.095 | 4.1266 | 2.7441 | 0.4324 | Day | Review
2025-12-05 08:46 | 2025-12-05 09:16 | 0.75472 | Persistent | upper | 73.7888 | 2.5534 | 2.2604 | 0.4282 | Day | Review
2025-12-08 07:45 | 2025-12-08 08:30 | 0.98806 | Persistent | lower | 74.9174 | 2.3202 | 1.8617 | 0.4135 | Day | Review
2025-12-13 18:05 | 2025-12-13 19:04 | 1.2356 | Persistent | upper | 73.5062 | 2.1127 | 1.6401 | 0.3991 | Night | Review
2025-12-19 08:00 | 2025-12-19 08:30 | 0.7375 | Persistent | lower | 74.3522 | 2.924 | 2.3979 | 0.3871 | Day | Review
2025-12-18 14:14 | 2025-12-18 15:13 | 1.2461 | Persistent | upper | 73.5062 | 2.106 | 1.4201 | 0.3855 | Day | Review
2025-12-30 09:15 | 2025-12-30 10:15 | 1.2436 | Persistent | upper | 73.2236 | 2.8416 | 1.9475 | 0.3766 | Day | Review
2025-12-08 07:01 | 2025-12-08 07:16 | 0.50139 | Extreme/elevated | lower | 74.9174 | 4.2485 | 3.5863 | 0.3689 | Day | Monitor
2025-12-19 07:11 | 2025-12-19 07:11 | 0.25083 | Extreme triggered | lower | 74.3522 | 4.2485 | 4.2485 | 0.3689 | Day | Monitor
2025-12-18 08:31 | 2025-12-18 08:31 | 0.25083 | Extreme triggered | upper | 74.0714 | 4.2485 | 4.2485 | 0.3689 | Day | Monitor
2025-12-18 02:10 | 2025-12-18 02:10 | 0.25083 | Extreme triggered | lower | 73.7888 | 4.2485 | 4.2485 | 0.3689 | Night | Monitor
2025-12-14 06:31 | 2025-12-14 06:45 | 0.49333 | Extreme/elevated | lower | 73.2236 | 4.2485 | 3.5863 | 0.3689 | Night | Monitor
2025-12-07 09:30 | 2025-12-07 09:48 | 0.56083 | Persistent | upper | 75.4826 | 2.3376 | 1.9391 | 0.3629 | Day | Review
2025-12-20 09:11 | 2025-12-20 09:14 | 0.30083 | Extreme/elevated | upper | 74.0714 | 2.9046 | 2.6472 | 0.3593 | Day | Monitor
2025-12-26 16:28 | 2025-12-26 16:58 | 0.75222 | Persistent | lower | 72.095 | 2.3865 | 2.1385 | 0.3591 | Day | Review
2025-12-03 03:54 | 2025-12-03 04:09 | 0.50167 | Extreme/elevated | upper | 74.3522 | 2.3202 | 2.1348 | 0.3585 | Night | Monitor
2025-12-03 02:39 | 2025-12-03 02:39 | 0.25083 | Extreme triggered | upper | 74.3522 | 2.924 | 2.924 | 0.3378 | Night | Monitor
2025-12-21 17:13 | 2025-12-21 17:31 | 0.54472 | Persistent | lower | 72.6584 | 2.1794 | 1.8483 | 0.3328 | Day | Review
2025-12-09 10:59 | 2025-12-09 11:14 | 0.50167 | Extreme/elevated | lower | 73.2236 | 2.3202 | 2.1348 | 0.33 | Day | Monitor
2025-12-16 18:30 | 2025-12-16 18:46 | 0.51 | Persistent | lower | 72.6584 | 2.1127 | 2.0274 | 0.3238 | Night | Review
2025-12-06 09:17 | 2025-12-06 09:20 | 0.30083 | Extreme/elevated | upper | 74.0714 | 2.6745 | 2.4664 | 0.322 | Day | Monitor
2025-12-12 14:52 | 2025-12-12 15:37 | 1.0033 | Persistent | lower | 72.3758 | 2.2946 | 1.9221 | 0.3177 | Day | Review
2025-12-09 09:30 | 2025-12-09 09:44 | 0.49083 | Extreme/elevated | lower | 73.2236 | 2.6647 | 2.5378 | 0.3036 | Day | Monitor
2025-12-05 07:26 | 2025-12-05 07:31 | 0.33306 | Extreme/elevated | lower | 72.6584 | 2.1222 | 2.0161 | 0.2988 | Day | Monitor
2025-12-16 13:24 | 2025-12-16 13:27 | 0.30722 | Extreme/elevated | lower | 71.8124 | 2.1526 | 2.024 | 0.2978 | Day | Monitor
2025-12-16 19:45 | 2025-12-16 20:00 | 0.50139 | Extreme/elevated | upper | 73.7888 | 2.2069 | 2.0491 | 0.2975 | Night | Monitor
2025-12-14 07:15 | 2025-12-14 07:15 | 0.25083 | Extreme triggered | lower | 73.2236 | 2.3202 | 2.3202 | 0.2975 | Day | Monitor
2025-12-04 07:08 | 2025-12-04 07:23 | 0.50139 | Extreme/elevated | lower | 72.095 | 2.1158 | 1.9946 | 0.2963 | Day | Monitor
2025-12-03 02:10 | 2025-12-03 02:10 | 0.25083 | Extreme triggered | upper | 74.3522 | 3.0733 | 3.0733 | 0.2906 | Night | Monitor
2025-12-29 16:58 | 2025-12-29 17:27 | 0.74389 | Persistent | lower | 72.095 | 2.5666 | 2.1471 | 0.2854 | Day | Review
2025-12-30 16:43 | 2025-12-30 16:58 | 0.50167 | Extreme/elevated | lower | 72.6584 | 2.411 | 1.7284 | 0.275 | Day | Monitor
2025-12-09 15:58 | 2025-12-09 16:13 | 0.50139 | Extreme/elevated | upper | 73.7888 | 2.2757 | 2.1126 | 0.2442 | Day | Monitor
2025-12-05 12:11 | 2025-12-05 12:29 | 0.55194 | Persistent | upper | 74.0714 | 2.1794 | 1.4844 | 0.2438 | Day | Review
2025-12-13 21:18 | 2025-12-13 21:18 | 0.25083 | Extreme triggered | upper | 73.7888 | 2.2993 | 2.2993 | 0.239 | Night | Monitor
2025-12-23 06:26 | 2025-12-23 06:26 | 0.25083 | Extreme triggered | lower | 74.0714 | 2.2856 | 2.2856 | 0.2095 | Night | Monitor
2025-12-13 22:48 | 2025-12-13 22:48 | 0.25083 | Extreme triggered | upper | 73.7888 | 2.1794 | 2.1794 | 0.2024 | Night | Monitor

## Jan 2026
We compared each reading with its own rolling baseline using the settings below | [5 empty] | Rank by mean materiality: 2 of 3 months (1 = most issues)
Sensor: Jensen Beach AHU 1 (°F), Period: January 2026, Value range: 66.2 – 75.5 °F | [5 empty] | Report generated: 10/08/2026 12:28
< Back to summary worksheet
Analysis funnel
Readings in this month: 2,815 |  | vs other months (3) | Recommendations to improve |  |  |  | Why have we recommended this?
| Extreme readings |  |  | This month | Best month | Worst month
| Share of readings | Rank vs other months | ● Review what changed when the level shifted | 24.8% | 18.8% | 33.39% | Confirmed shift share: 25% of readings (175 h). The value stayed away from its baseline for 7+ readings with mean ¦Z¦ ≥ 1.2 - check setpoint or schedule changes, sensor drift or an equipment fault.
| 12.15% | 3
| Sustained deviations |  | ● Check the day/night pattern before acting on single extremes | 12.15% | 12.15% | 12.94% | Upper extremes happen mostly by day and lower extremes mostly at night (171 upper, 171 lower). With a 20-reading (5 h) baseline, the normal daily swing itself is flagged. If the swing is intended (setback), consider Window = 96 (24 h).
| Hours (Persistent + Confirmed) | Rank vs other months
| 251.335 | 1
|  |  | ● Check for hunting or short-cycling | 4.1 | 3.24 | 4.2903 | Material changes: 4.1 per day - fast changes that repeat within 10 readings. Check valve/damper control loops and compressor or fan staging.
Material changes
| Per day | Rank vs other months
| 4.1 | 2 | ● Fix the data gaps | 60.7139 | 40.3539 | 60.7139 | Missing data: 60.7 h in gaps longer than three intervals. Events inside a gap cannot be detected.
More benchmarks
|  |  | Measure | This month | Best month | Worst month | Whole period | This month – Day | This month – Night
|  |  | Mean value | 72.564 | 71.6342 | 73.1788 | 72.5343 | 72.6168 | 72.5191
|  |  | Min value | 66.164 | 65.0354 | 67.8596 | 65.0354 | 66.164 | 67.2944
|  |  | Max value | 75.4826 | 74.9174 | 75.4826 | 75.4826 | 75.4826 | 75.4826
|  |  | Extreme share | 12.15% | 12.15% | 12.94% | 12.42% | 15.61% | 9.204%
|  |  | Upper extremes | 171 | 137 | 171 | 478 | 141 | 30
|  |  | Lower extremes | 171 | 123 | 235 | 529 | 61 | 110
|  |  | Sustained deviation (h) | 251.335 | 235.7833 | 251.335 | 733.4367 | 96.8217 | 154.5133
|  |  | Confirmed share | 24.8% | 18.8% | 33.39% | 24.95% | 19.32% | 29.45%
|  |  | Material changes per day | 4.1 | 3.24 | 4.2903 | 3.9186 | Not relevant | Not relevant
|  |  | Mean materiality score | 0.23506 | 0.21424 | 0.26953 | 0.2369 | 0.21525 | 0.25191
|  |  | Max ¦Z¦ | 4.2485 | 4.2485 | 4.2485 | 4.2485 | 4.2485 | 4.2485
|  |  | Data gap hours | 60.7139 | 40.3539 | 60.7139 | 155.8906 | Not relevant | Not relevant
* Best = lowest month, Worst = highest month for each measure (for Mean/Min/Max value: simply the lowest and highest month).
* Max ¦Z¦ is capped at 4.25 with a 20-reading rolling window ((W−1)/√W), so it is the same in every month; use Extreme share and the events instead.
* Settings: Rolling Mean/Std, Window 20, K_E 2.0, K_P 1.0, N_P 3, N_M 7, K_M 1.2, N_EXIT 1, ROC h 1, ROC window 20, ROC_K 2.0, frequency 10 / min 2.
Readings against the normal range
Grey band = normal range (moving average ± 2σ). Dots outside it are Extreme readings: orange = upper, blue = lower.
Events in this month
View all events
* Sorted by materiality score (highest first). Action: Investigate = Confirmed shift, Review = Persistent, Monitor = shorter events. Click the Action to see the readings.
Start | End | Duration (h) | Highest state | Direction | Peak value | Max ¦Z¦ | Mean ¦Z¦ | Max materiality | Day/Night | Action
2026-01-13 12:43 | 2026-01-13 14:25 | 1.95 | Confirmed/Materialized Shift | upper | 74.0714 | 3.4626 | 1.7762 | 0.688 | Day | Investigate
2026-01-03 09:00 | 2026-01-03 11:42 | 2.9611 | Confirmed/Materialized Shift | upper | 72.941 | 2.9016 | 2.1484 | 0.6791 | Day | Investigate
2026-01-07 09:00 | 2026-01-07 11:18 | 2.5497 | Confirmed/Materialized Shift | upper | 74.0714 | 2.9226 | 2.1587 | 0.6694 | Day | Investigate
2026-01-25 02:57 | 2026-01-25 07:41 | 4.9742 | Confirmed/Materialized Shift | lower | 73.7888 | 2.924 | 1.8036 | 0.6596 | Night | Investigate
2026-01-21 09:00 | 2026-01-21 14:17 | 5.5286 | Confirmed/Materialized Shift | upper | 74.0714 | 2.924 | 1.674 | 0.6492 | Day | Investigate
2026-01-18 09:16 | 2026-01-18 12:59 | 3.9772 | Confirmed/Materialized Shift | upper | 73.7888 | 3.0822 | 2.0959 | 0.6394 | Day | Investigate
2026-01-31 18:28 | 2026-02-01 12:32 | 18.325 | Confirmed/Materialized Shift | lower | 65.0354 | 3.0822 | 2.0116 | 0.6331 | Night | Investigate
2026-01-30 09:30 | 2026-01-30 17:42 | 8.4614 | Confirmed/Materialized Shift | upper | 73.7888 | 2.8092 | 1.7617 | 0.6268 | Day | Investigate
2026-01-22 00:58 | 2026-01-22 05:12 | 4.4806 | Confirmed/Materialized Shift | lower | 72.6584 | 4.2485 | 1.8716 | 0.6219 | Night | Investigate
2026-01-28 19:30 | 2026-01-29 09:58 | 14.7308 | Confirmed/Materialized Shift | lower | 66.4466 | 3.2606 | 1.8378 | 0.6199 | Night | Investigate
2026-01-29 19:30 | 2026-01-30 03:42 | 8.4603 | Confirmed/Materialized Shift | lower | 69.5534 | 2.8102 | 1.6714 | 0.6187 | Night | Investigate
2026-01-18 03:57 | 2026-01-18 06:11 | 2.4917 | Confirmed/Materialized Shift | lower | 71.5298 | 2.3975 | 1.5618 | 0.617 | Night | Investigate
2026-01-10 23:28 | 2026-01-11 07:11 | 7.9669 | Confirmed/Materialized Shift | lower | 72.6584 | 2.0543 | 1.5626 | 0.5941 | Night | Investigate
2026-01-04 10:00 | 2026-01-04 13:08 | 3.38 | Confirmed/Materialized Shift | upper | 74.0714 | 2.8931 | 1.9575 | 0.5933 | Day | Investigate
2026-01-15 19:16 | 2026-01-16 09:48 | 14.7914 | Confirmed/Materialized Shift | lower | 66.164 | 2.9676 | 1.8145 | 0.5919 | Night | Investigate
2026-01-12 02:13 | 2026-01-12 05:56 | 3.9792 | Confirmed/Materialized Shift | lower | 73.7888 | 2.6647 | 1.7432 | 0.5917 | Night | Investigate
2026-01-09 00:43 | 2026-01-09 02:28 | 1.9894 | Confirmed/Materialized Shift | lower | 72.941 | 2.3975 | 1.7208 | 0.5893 | Night | Investigate
2026-01-14 23:09 | 2026-01-15 04:08 | 5.2253 | Confirmed/Materialized Shift | lower | 72.095 | 2.2993 | 1.5405 | 0.5853 | Night | Investigate
2026-01-18 21:27 | 2026-01-20 14:58 | 41.7719 | Confirmed/Materialized Shift | upper | 74.0714 | 2.3231 | 1.6571 | 0.5834 | Night | Investigate
2026-01-21 02:43 | 2026-01-21 06:26 | 3.9797 | Confirmed/Materialized Shift | lower | 71.2472 | 2.3662 | 1.4771 | 0.582 | Night | Investigate
2026-01-09 16:58 | 2026-01-09 18:27 | 1.7389 | Confirmed/Materialized Shift | lower | 72.3758 | 2.9654 | 2.4098 | 0.5807 | Day | Investigate
2026-01-24 18:01 | 2026-01-24 21:14 | 3.4758 | Confirmed/Materialized Shift | upper | 74.9174 | 2.7087 | 1.7816 | 0.5795 | Night | Investigate
2026-01-26 08:48 | 2026-01-26 10:15 | 1.695 | Confirmed/Materialized Shift | lower | 71.8124 | 3.6206 | 2.405 | 0.5786 | Day | Investigate
2026-01-17 09:00 | 2026-01-17 13:14 | 4.4792 | Confirmed/Materialized Shift | upper | 73.5062 | 3.3859 | 2.0479 | 0.5781 | Day | Investigate
2026-01-05 09:59 | 2026-01-05 12:46 | 3.0286 | Confirmed/Materialized Shift | upper | 74.0714 | 3.1769 | 2.0526 | 0.5767 | Day | Investigate
2026-01-15 10:14 | 2026-01-15 12:44 | 2.735 | Confirmed/Materialized Shift | upper | 73.7888 | 3.2199 | 2.3409 | 0.5757 | Day | Investigate
2026-01-23 06:41 | 2026-01-23 08:16 | 1.8192 | Confirmed/Materialized Shift | lower | 72.941 | 2.924 | 1.7463 | 0.5653 | Night | Investigate
2026-01-22 10:00 | 2026-01-22 11:40 | 1.9222 | Confirmed/Materialized Shift | upper | 74.0714 | 3.3751 | 2.154 | 0.5636 | Day | Investigate
2026-01-04 23:27 | 2026-01-05 04:39 | 5.4672 | Confirmed/Materialized Shift | lower | 71.5298 | 2.1983 | 1.5201 | 0.5599 | Night | Investigate
2026-01-04 00:54 | 2026-01-04 03:54 | 3.2358 | Confirmed/Materialized Shift | lower | 72.095 | 2.3402 | 1.653 | 0.5594 | Night | Investigate
2026-01-08 00:43 | 2026-01-08 06:56 | 6.4706 | Confirmed/Materialized Shift | lower | 72.095 | 2.362 | 1.5753 | 0.5593 | Night | Investigate
2026-01-31 10:00 | 2026-01-31 15:43 | 5.9692 | Confirmed/Materialized Shift | upper | 71.5298 | 2.7681 | 1.6106 | 0.5591 | Day | Investigate
2026-01-09 09:30 | 2026-01-09 11:21 | 2.1125 | Confirmed/Materialized Shift | upper | 74.0714 | 2.4887 | 1.9526 | 0.5587 | Day | Investigate
2026-01-05 23:43 | 2026-01-06 05:57 | 6.4706 | Confirmed/Materialized Shift | lower | 71.5298 | 2.2757 | 1.6056 | 0.5517 | Night | Investigate
2026-01-30 20:15 | 2026-01-31 08:30 | 12.5056 | Confirmed/Materialized Shift | lower | 68.9882 | 2.936 | 1.5533 | 0.5488 | Night | Investigate
2026-01-11 18:16 | 2026-01-11 21:29 | 3.4675 | Confirmed/Materialized Shift | upper | 75.2 | 2.5153 | 1.6674 | 0.5454 | Night | Investigate
2026-01-06 08:27 | 2026-01-06 11:29 | 3.2828 | Confirmed/Materialized Shift | upper | 74.0714 | 2.9785 | 1.8514 | 0.545 | Day | Investigate
2026-01-25 08:45 | 2026-01-25 09:48 | 1.2953 | Confirmed/Materialized Shift | upper | 75.4826 | 2.6211 | 2.1447 | 0.5439 | Day | Investigate
2026-01-28 11:06 | 2026-01-28 16:34 | 5.7269 | Confirmed/Materialized Shift | upper | 73.2236 | 2.1298 | 1.513 | 0.5423 | Day | Investigate
2026-01-10 18:16 | 2026-01-10 20:59 | 2.9744 | Confirmed/Materialized Shift | upper | 74.6348 | 2.4325 | 1.66 | 0.5413 | Night | Investigate
2026-01-25 18:16 | 2026-01-25 21:44 | 3.7183 | Confirmed/Materialized Shift | upper | 75.4826 | 2.3801 | 1.6001 | 0.5389 | Night | Investigate
2026-01-07 01:58 | 2026-01-07 07:30 | 5.7911 | Confirmed/Materialized Shift | lower | 71.8124 | 2.1696 | 1.5112 | 0.5378 | Night | Investigate
2026-01-14 01:50 | 2026-01-14 03:34 | 1.9903 | Confirmed/Materialized Shift | lower | 73.5062 | 2.924 | 1.7463 | 0.5367 | Night | Investigate
2026-01-09 05:27 | 2026-01-09 08:00 | 2.8158 | Confirmed/Materialized Shift | lower | 72.3758 | 2.3444 | 1.7189 | 0.5353 | Night | Investigate
2026-01-27 09:45 | 2026-01-27 15:32 | 6.0403 | Confirmed/Materialized Shift | upper | 74.0714 | 2.3202 | 1.5861 | 0.5314 | Day | Investigate
2026-01-27 00:58 | 2026-01-27 08:16 | 7.5397 | Confirmed/Materialized Shift | lower | 68.7056 | 2.1595 | 1.6459 | 0.5303 | Night | Investigate
2026-01-27 20:29 | 2026-01-28 09:51 | 13.6136 | Confirmed/Materialized Shift | lower | 67.577 | 2.2722 | 1.6645 | 0.5271 | Night | Investigate
2026-01-16 20:15 | 2026-01-16 23:59 | 3.9794 | Confirmed/Materialized Shift | lower | 70.3994 | 2.3413 | 1.6755 | 0.5235 | Night | Investigate
2026-01-08 09:00 | 2026-01-08 11:15 | 2.4892 | Confirmed/Materialized Shift | upper | 73.5062 | 2.9263 | 1.9754 | 0.5204 | Day | Investigate
2026-01-10 03:54 | 2026-01-10 05:09 | 1.4967 | Persistent | lower | 73.2236 | 2.3975 | 1.8851 | 0.5201 | Night | Review
2026-01-23 10:00 | 2026-01-23 10:57 | 1.2081 | Persistent | upper | 74.0714 | 3.0887 | 2.4019 | 0.5093 | Day | Review
2026-01-17 23:28 | 2026-01-18 02:42 | 3.4864 | Confirmed/Materialized Shift | lower | 72.095 | 2.0548 | 1.4239 | 0.5092 | Night | Investigate
2026-01-17 04:12 | 2026-01-17 05:57 | 1.9894 | Confirmed/Materialized Shift | lower | 69.5534 | 2.0144 | 1.4543 | 0.5054 | Night | Investigate
2026-01-24 02:27 | 2026-01-24 04:12 | 1.9983 | Confirmed/Materialized Shift | lower | 73.5062 | 2.5628 | 1.62 | 0.5053 | Night | Investigate
2026-01-23 19:01 | 2026-01-23 20:44 | 1.9789 | Confirmed/Materialized Shift | upper | 73.7888 | 2.0899 | 1.5121 | 0.5049 | Night | Investigate
2026-01-24 06:41 | 2026-01-24 08:00 | 1.5706 | Confirmed/Materialized Shift | lower | 72.941 | 2.1222 | 1.5951 | 0.5047 | Night | Investigate
2026-01-04 06:53 | 2026-01-04 08:37 | 1.9903 | Confirmed/Materialized Shift | lower | 71.5298 | 2.3975 | 1.565 | 0.5046 | Night | Investigate
2026-01-08 18:46 | 2026-01-08 22:14 | 3.7269 | Confirmed/Materialized Shift | upper | 73.7888 | 2.485 | 1.4996 | 0.5038 | Night | Investigate
2026-01-05 19:16 | 2026-01-05 20:44 | 1.7283 | Confirmed/Materialized Shift | upper | 73.7888 | 2.158 | 1.7288 | 0.4835 | Night | Investigate
2026-01-26 01:58 | 2026-01-26 03:57 | 2.2403 | Confirmed/Materialized Shift | lower | 74.9174 | 2.2993 | 1.4883 | 0.4783 | Night | Investigate
2026-01-26 19:16 | 2026-01-26 20:29 | 1.4775 | Persistent | upper | 74.0714 | 2.8408 | 2.1469 | 0.4698 | Night | Review
2026-01-22 16:27 | 2026-01-22 17:42 | 1.4964 | Persistent | lower | 72.095 | 2.9654 | 2.3719 | 0.4686 | Day | Review
2026-01-25 15:14 | 2026-01-25 16:43 | 1.7392 | Confirmed/Materialized Shift | upper | 74.0714 | 2.8853 | 1.9116 | 0.4675 | Day | Investigate
2026-01-14 09:00 | 2026-01-14 10:14 | 1.4947 | Persistent | upper | 73.5062 | 2.924 | 1.9498 | 0.46 | Day | Review
2026-01-14 04:19 | 2026-01-14 05:33 | 1.4881 | Persistent | lower | 73.2236 | 2.2993 | 1.692 | 0.4559 | Night | Review
2026-01-12 12:59 | 2026-01-12 13:29 | 0.7525 | Persistent | lower | 71.8124 | 3.396 | 2.8588 | 0.455 | Day | Review
2026-01-04 14:29 | 2026-01-04 15:44 | 1.4964 | Persistent | lower | 72.095 | 2.4259 | 1.9357 | 0.4534 | Day | Review
2026-01-13 09:15 | 2026-01-13 09:44 | 0.74194 | Persistent | upper | 73.7888 | 3.2242 | 2.4312 | 0.4435 | Day | Review
2026-01-17 18:16 | 2026-01-17 19:15 | 1.235 | Persistent | upper | 73.7888 | 2.4713 | 1.8523 | 0.4359 | Night | Review
2026-01-07 16:58 | 2026-01-07 18:12 | 1.4964 | Persistent | lower | 72.095 | 2.3897 | 2.0009 | 0.4248 | Day | Review
2026-01-11 09:26 | 2026-01-11 09:44 | 0.54694 | Persistent | upper | 74.0714 | 2.7587 | 2.3806 | 0.4224 | Day | Review
2026-01-21 07:26 | 2026-01-21 08:15 | 1.0769 | Persistent | lower | 70.9646 | 2.2993 | 1.777 | 0.4066 | Day | Review
2026-01-14 10:44 | 2026-01-14 10:59 | 0.50167 | Extreme/elevated | lower | 72.3758 | 3.1616 | 3.1078 | 0.4036 | Day | Monitor
2026-01-12 09:15 | 2026-01-12 09:59 | 0.9925 | Persistent | lower | 73.2236 | 3.2242 | 2.598 | 0.3986 | Day | Review
2026-01-26 07:30 | 2026-01-26 08:00 | 0.7525 | Persistent | lower | 74.6348 | 2.924 | 2.3979 | 0.3871 | Day | Review
2026-01-12 19:12 | 2026-01-12 19:56 | 0.99278 | Persistent | upper | 73.7888 | 2.142 | 2.003 | 0.3789 | Night | Review
2026-01-24 09:00 | 2026-01-24 09:08 | 0.39333 | Persistent | upper | 74.0714 | 2.788 | 2.5603 | 0.3784 | Day | Review
2026-01-08 13:59 | 2026-01-08 14:58 | 1.2456 | Persistent | lower | 72.6584 | 2.0633 | 1.5701 | 0.3765 | Day | Review
2026-01-26 07:11 | 2026-01-26 07:11 | 0.25083 | Extreme triggered | lower | 74.6348 | 4.2485 | 4.2485 | 0.3689 | Day | Monitor
2026-01-14 00:50 | 2026-01-14 00:50 | 0.25083 | Extreme triggered | lower | 73.5062 | 4.2485 | 4.2485 | 0.3689 | Night | Monitor
2026-01-23 06:12 | 2026-01-23 06:12 | 0.25083 | Extreme triggered | lower | 72.941 | 4.2485 | 4.2485 | 0.3689 | Night | Monitor
2026-01-25 02:27 | 2026-01-25 02:27 | 0.25083 | Extreme triggered | lower | 74.6348 | 4.2485 | 4.2485 | 0.3689 | Night | Monitor
2026-01-13 07:30 | 2026-01-13 07:30 | 0.25083 | Extreme triggered | lower | 72.941 | 4.2485 | 4.2485 | 0.3689 | Day | Monitor
2026-01-18 15:16 | 2026-01-18 15:56 | 0.90972 | Persistent | lower | 71.8124 | 2.981 | 2.2404 | 0.3538 | Day | Review
2026-01-13 08:15 | 2026-01-13 08:15 | 0.25083 | Extreme triggered | lower | 72.941 | 2.924 | 2.924 | 0.3378 | Day | Monitor
2026-01-06 17:13 | 2026-01-06 17:57 | 0.995 | Persistent | lower | 72.095 | 2.6862 | 2.0897 | 0.3293 | Day | Review
2026-01-04 18:29 | 2026-01-04 19:13 | 0.98417 | Persistent | upper | 73.5062 | 2.057 | 1.374 | 0.3259 | Night | Review
2026-01-21 15:13 | 2026-01-21 15:43 | 0.74417 | Persistent | lower | 72.095 | 2.0813 | 1.777 | 0.3196 | Day | Review
2026-01-23 17:27 | 2026-01-23 18:12 | 1.0033 | Persistent | lower | 72.3758 | 2.6973 | 2.1287 | 0.3174 | Day | Review
2026-01-17 07:11 | 2026-01-17 07:30 | 0.56694 | Persistent | lower | 69.2708 | 2.2757 | 1.9806 | 0.3145 | Night | Review
2026-01-27 16:17 | 2026-01-27 16:28 | 0.42222 | Persistent | lower | 71.8124 | 2.3312 | 1.8695 | 0.3114 | Day | Review
2026-01-10 11:59 | 2026-01-10 12:06 | 0.3625 | Persistent | upper | 74.0714 | 2.8747 | 2.3013 | 0.3059 | Day | Review
2026-01-07 14:58 | 2026-01-07 15:43 | 0.995 | Persistent | lower | 72.941 | 2.378 | 1.4625 | 0.298 | Day | Review
2026-01-24 17:27 | 2026-01-24 17:31 | 0.305 | Persistent | lower | 72.6584 | 2.3975 | 2.0614 | 0.2897 | Day | Review
2026-01-14 15:41 | 2026-01-14 16:11 | 0.74417 | Persistent | lower | 72.3758 | 2.2938 | 1.9678 | 0.2832 | Day | Review
2026-01-22 07:26 | 2026-01-22 07:30 | 0.32444 | Extreme/elevated | lower | 72.3758 | 2.1794 | 2.096 | 0.277 | Day | Monitor
2026-01-10 13:28 | 2026-01-10 13:43 | 0.50167 | Extreme/elevated | lower | 72.6584 | 2.0674 | 1.921 | 0.2612 | Day | Monitor
2026-01-16 17:18 | 2026-01-16 17:33 | 0.50167 | Extreme/elevated | lower | 71.8124 | 2.1171 | 1.6956 | 0.2554 | Day | Monitor
2026-01-07 00:43 | 2026-01-07 00:43 | 0.25083 | Extreme triggered | lower | 72.941 | 2.351 | 2.351 | 0.2424 | Night | Monitor
2026-01-15 08:30 | 2026-01-15 08:30 | 0.25083 | Extreme triggered | lower | 71.5298 | 2.2757 | 2.2757 | 0.2374 | Day | Monitor
2026-01-15 04:52 | 2026-01-15 04:52 | 0.25083 | Extreme triggered | lower | 71.8124 | 2.1175 | 2.1175 | 0.2269 | Night | Monitor
2026-01-10 06:53 | 2026-01-10 06:53 | 0.25083 | Extreme triggered | lower | 72.941 | 2.0646 | 2.0646 | 0.1948 | Night | Monitor

## Feb 2026
We compared each reading with its own rolling baseline using the settings below | [5 empty] | Rank by mean materiality: 1 of 3 months (1 = most issues)
Sensor: Jensen Beach AHU 1 (°F), Period: February 2026, Value range: 65.0 – 74.9 °F | [5 empty] | Report generated: 10/08/2026 12:28
< Back to summary worksheet
Analysis funnel
Readings in this month: 2,264 |  | vs other months (3) | Recommendations to improve |  |  |  | Why have we recommended this?
| Extreme readings |  |  | This month | Best month | Worst month
| Share of readings | Rank vs other months | ● Review what changed when the level shifted | 33.39% | 18.8% | 33.39% | Confirmed shift share: 33% of readings (190 h). The value stayed away from its baseline for 7+ readings with mean ¦Z¦ ≥ 1.2 - check setpoint or schedule changes, sensor drift or an equipment fault.
| 12.94% | 1
| Sustained deviations |  | ● Check the day/night pattern before acting on single extremes | 12.94% | 12.15% | 12.94% | Upper extremes happen mostly by day and lower extremes mostly at night (170 upper, 123 lower). With a 20-reading (5 h) baseline, the normal daily swing itself is flagged. If the swing is intended (setback), consider Window = 96 (24 h).
| Hours (Persistent + Confirmed) | Rank vs other months
| 246.3183 | 2
|  |  | ● Check for hunting or short-cycling | 3.24 | 3.24 | 4.2903 | Material changes: 3.2 per day - fast changes that repeat within 10 readings. Check valve/damper control loops and compressor or fan staging.
Material changes
| Per day | Rank vs other months
| 3.24 | 3 | ● Fix the data gaps | 40.3539 | 40.3539 | 60.7139 | Missing data: 40.4 h in gaps longer than three intervals. Events inside a gap cannot be detected.
More benchmarks
|  |  | Measure | This month | Best month | Worst month | Whole period | This month – Day | This month – Night
|  |  | Mean value | 71.6342 | 71.6342 | 73.1788 | 72.5343 | 71.7471 | 71.525
|  |  | Min value | 65.0354 | 65.0354 | 67.8596 | 65.0354 | 65.0354 | 67.2944
|  |  | Max value | 74.9174 | 74.9174 | 75.4826 | 75.4826 | 74.0714 | 74.9174
|  |  | Extreme share | 12.94% | 12.15% | 12.94% | 12.42% | 17.34% | 8.688%
|  |  | Upper extremes | 170 | 137 | 171 | 478 | 164 | 6
|  |  | Lower extremes | 123 | 123 | 235 | 529 | 29 | 94
|  |  | Sustained deviation (h) | 246.3183 | 235.7833 | 251.335 | 733.4367 | 106.3533 | 139.965
|  |  | Confirmed share | 33.39% | 18.8% | 33.39% | 24.95% | 27.58% | 39.01%
|  |  | Material changes per day | 3.24 | 3.24 | 4.2903 | 3.9186 | Not relevant | Not relevant
|  |  | Mean materiality score | 0.26953 | 0.21424 | 0.26953 | 0.2369 | 0.25102 | 0.28744
|  |  | Max ¦Z¦ | 4.2485 | 4.2485 | 4.2485 | 4.2485 | 3.2557 | 4.2485
|  |  | Data gap hours | 40.3539 | 40.3539 | 60.7139 | 155.8906 | Not relevant | Not relevant
* Best = lowest month, Worst = highest month for each measure (for Mean/Min/Max value: simply the lowest and highest month).
* Max ¦Z¦ is capped at 4.25 with a 20-reading rolling window ((W−1)/√W), so it is the same in every month; use Extreme share and the events instead.
* Settings: Rolling Mean/Std, Window 20, K_E 2.0, K_P 1.0, N_P 3, N_M 7, K_M 1.2, N_EXIT 1, ROC h 1, ROC window 20, ROC_K 2.0, frequency 10 / min 2.
Readings against the normal range
Grey band = normal range (moving average ± 2σ). Dots outside it are Extreme readings: orange = upper, blue = lower.
Events in this month
View all events
* Sorted by materiality score (highest first). Action: Investigate = Confirmed shift, Review = Persistent, Monitor = shorter events. Click the Action to see the readings.
Start | End | Duration (h) | Highest state | Direction | Peak value | Max ¦Z¦ | Mean ¦Z¦ | Max materiality | Day/Night | Action
2026-02-16 09:00 | 2026-02-16 11:15 | 2.5042 | Confirmed/Materialized Shift | upper | 74.0714 | 2.924 | 1.8503 | 0.6851 | Day | Investigate
2026-02-06 08:15 | 2026-02-06 13:44 | 5.7239 | Confirmed/Materialized Shift | upper | 72.6584 | 2.9639 | 2.0694 | 0.6833 | Day | Investigate
2026-02-19 16:57 | 2026-02-19 18:42 | 2.0003 | Confirmed/Materialized Shift | lower | 72.3758 | 2.9459 | 2.2399 | 0.6698 | Day | Investigate
2026-02-11 09:11 | 2026-02-11 12:25 | 3.4839 | Confirmed/Materialized Shift | upper | 73.2236 | 2.9881 | 2.0245 | 0.6665 | Day | Investigate
2026-02-22 00:43 | 2026-02-22 07:26 | 6.9642 | Confirmed/Materialized Shift | lower | 72.941 | 4.2485 | 1.8999 | 0.6533 | Night | Investigate
2026-02-05 19:01 | 2026-02-06 00:43 | 5.9586 | Confirmed/Materialized Shift | lower | 67.2944 | 2.788 | 1.8904 | 0.6392 | Night | Investigate
2026-02-12 09:19 | 2026-02-12 12:47 | 3.7264 | Confirmed/Materialized Shift | upper | 73.5062 | 2.9369 | 2.0188 | 0.6388 | Day | Investigate
2026-02-04 08:30 | 2026-02-04 12:43 | 4.4817 | Confirmed/Materialized Shift | upper | 72.095 | 2.9247 | 2.0632 | 0.6384 | Day | Investigate
2026-02-14 09:00 | 2026-02-14 11:44 | 2.9825 | Confirmed/Materialized Shift | upper | 73.5062 | 2.7262 | 2.0686 | 0.636 | Day | Investigate
2026-02-15 22:56 | 2026-02-16 02:25 | 3.7372 | Confirmed/Materialized Shift | lower | 72.941 | 2.924 | 1.9001 | 0.6354 | Night | Investigate
2026-02-25 08:00 | 2026-02-25 11:14 | 3.4794 | Confirmed/Materialized Shift | upper | 72.3758 | 2.5785 | 2.2424 | 0.629 | Day | Investigate
2026-02-24 19:27 | 2026-02-25 05:24 | 10.1981 | Confirmed/Materialized Shift | lower | 67.2944 | 3.1509 | 1.7285 | 0.6279 | Night | Investigate
2026-02-07 08:15 | 2026-02-07 13:14 | 5.2233 | Confirmed/Materialized Shift | upper | 73.2236 | 2.7817 | 1.9294 | 0.614 | Day | Investigate
2026-02-20 08:30 | 2026-02-20 09:19 | 1.0678 | Confirmed/Materialized Shift | upper | 74.0714 | 2.6647 | 2.2339 | 0.6098 | Day | Investigate
2026-02-08 08:30 | 2026-02-08 13:59 | 5.7233 | Confirmed/Materialized Shift | upper | 73.2236 | 3.1811 | 2.0074 | 0.6042 | Day | Investigate
2026-02-20 01:55 | 2026-02-20 05:09 | 3.4861 | Confirmed/Materialized Shift | lower | 73.2236 | 2.4878 | 1.781 | 0.6033 | Night | Investigate
2026-02-10 09:15 | 2026-02-10 12:44 | 3.7264 | Confirmed/Materialized Shift | upper | 73.2236 | 2.6307 | 2.0435 | 0.5986 | Day | Investigate
2026-02-17 00:28 | 2026-02-17 08:00 | 7.7906 | Confirmed/Materialized Shift | lower | 71.5298 | 2.4597 | 1.6004 | 0.5983 | Night | Investigate
2026-02-18 00:40 | 2026-02-18 07:45 | 7.34 | Confirmed/Materialized Shift | lower | 71.5298 | 2.351 | 1.5983 | 0.596 | Night | Investigate
2026-02-09 08:45 | 2026-02-09 12:44 | 4.2286 | Confirmed/Materialized Shift | upper | 73.2236 | 2.5458 | 1.972 | 0.5904 | Day | Investigate
2026-02-23 19:27 | 2026-02-24 05:38 | 10.4394 | Confirmed/Materialized Shift | lower | 67.577 | 3.188 | 1.6669 | 0.5739 | Night | Investigate
2026-02-13 09:00 | 2026-02-13 13:07 | 4.3619 | Confirmed/Materialized Shift | upper | 74.0714 | 2.5805 | 1.7481 | 0.5698 | Day | Investigate
2026-02-12 17:16 | 2026-02-12 18:46 | 1.7453 | Confirmed/Materialized Shift | lower | 72.6584 | 2.5868 | 1.9928 | 0.56 | Day | Investigate
2026-02-06 19:16 | 2026-02-07 07:13 | 12.2081 | Confirmed/Materialized Shift | lower | 67.8596 | 3.2606 | 1.6059 | 0.5579 | Night | Investigate
2026-02-24 08:30 | 2026-02-24 13:43 | 5.4808 | Confirmed/Materialized Shift | upper | 72.941 | 2.752 | 1.9221 | 0.5551 | Day | Investigate
2026-02-14 22:41 | 2026-02-15 00:40 | 2.2403 | Confirmed/Materialized Shift | lower | 72.941 | 2.1222 | 1.5461 | 0.5547 | Night | Investigate
2026-02-05 09:59 | 2026-02-05 17:25 | 7.6739 | Confirmed/Materialized Shift | upper | 72.095 | 2.9145 | 1.5608 | 0.5514 | Day | Investigate
2026-02-09 21:44 | 2026-02-10 07:45 | 10.2725 | Confirmed/Materialized Shift | lower | 68.423 | 2.3629 | 1.5506 | 0.5479 | Night | Investigate
2026-02-13 23:56 | 2026-02-14 08:16 | 8.5844 | Confirmed/Materialized Shift | lower | 70.3994 | 2.1714 | 1.5557 | 0.5469 | Night | Investigate
2026-02-17 09:30 | 2026-02-17 12:14 | 2.9933 | Confirmed/Materialized Shift | upper | 73.7888 | 2.9583 | 1.8692 | 0.5435 | Day | Investigate
2026-02-09 17:27 | 2026-02-09 19:30 | 2.2908 | Confirmed/Materialized Shift | upper | 73.5062 | 3.2341 | 1.9126 | 0.5414 | Day | Investigate
2026-02-15 03:10 | 2026-02-15 04:39 | 1.7389 | Confirmed/Materialized Shift | lower | 72.3758 | 2.2584 | 1.7744 | 0.5409 | Night | Investigate
2026-02-04 19:56 | 2026-02-05 08:15 | 12.57 | Confirmed/Materialized Shift | lower | 67.577 | 2.3877 | 1.5954 | 0.5397 | Night | Investigate
2026-02-19 01:55 | 2026-02-19 07:30 | 5.8472 | Confirmed/Materialized Shift | lower | 72.095 | 2.5686 | 1.7258 | 0.5377 | Night | Investigate
2026-02-23 09:44 | 2026-02-23 17:42 | 8.2111 | Confirmed/Materialized Shift | upper | 73.5062 | 2.1227 | 1.4934 | 0.5339 | Day | Investigate
2026-02-19 09:15 | 2026-02-19 11:35 | 2.5867 | Confirmed/Materialized Shift | upper | 74.0714 | 2.1585 | 1.6863 | 0.5334 | Day | Investigate
2026-02-23 00:28 | 2026-02-23 07:45 | 7.5442 | Confirmed/Materialized Shift | lower | 68.7056 | 2.1141 | 1.6471 | 0.5314 | Night | Investigate
2026-02-10 21:44 | 2026-02-11 08:27 | 10.9586 | Confirmed/Materialized Shift | lower | 69.5534 | 2.1141 | 1.5362 | 0.5278 | Night | Investigate
2026-02-21 01:55 | 2026-02-21 07:45 | 6.0981 | Confirmed/Materialized Shift | lower | 72.941 | 2.3629 | 1.5012 | 0.5237 | Night | Investigate
2026-02-13 05:12 | 2026-02-13 07:30 | 2.5567 | Confirmed/Materialized Shift | lower | 70.3994 | 2.1007 | 1.7056 | 0.5228 | Night | Investigate
2026-02-12 02:35 | 2026-02-12 07:49 | 5.4828 | Confirmed/Materialized Shift | lower | 69.5534 | 2.0682 | 1.5271 | 0.5168 | Night | Investigate
2026-02-15 08:30 | 2026-02-15 10:00 | 1.7425 | Confirmed/Materialized Shift | upper | 73.5062 | 2.5552 | 2.0848 | 0.5157 | Day | Investigate
2026-02-08 20:44 | 2026-02-09 07:45 | 11.2728 | Confirmed/Materialized Shift | lower | 67.577 | 2.0503 | 1.5212 | 0.5148 | Night | Investigate
2026-02-16 05:54 | 2026-02-16 07:45 | 2.1142 | Confirmed/Materialized Shift | lower | 72.6584 | 2.2722 | 1.5384 | 0.5103 | Night | Investigate
2026-02-18 09:00 | 2026-02-18 12:59 | 4.2289 | Confirmed/Materialized Shift | upper | 73.7888 | 2.443 | 1.5571 | 0.5048 | Day | Investigate
2026-02-22 18:30 | 2026-02-22 20:14 | 1.9981 | Confirmed/Materialized Shift | upper | 74.0714 | 2.0966 | 1.4984 | 0.5031 | Night | Investigate
2026-02-18 14:13 | 2026-02-18 15:43 | 1.7392 | Confirmed/Materialized Shift | lower | 72.3758 | 2.2584 | 1.7495 | 0.4953 | Day | Investigate
2026-02-22 15:14 | 2026-02-22 16:13 | 1.2467 | Persistent | lower | 72.095 | 2.66 | 2.3281 | 0.4769 | Day | Review
2026-02-03 14:13 | 2026-02-03 17:07 | 3.1442 | Confirmed/Materialized Shift | upper | 70.682 | 2.5623 | 1.7811 | 0.4765 | Day | Investigate
2026-02-02 11:31 | 2026-02-02 12:31 | 1.2456 | Persistent | lower | 65.0354 | 3.2557 | 1.8971 | 0.4707 | Day | Review
2026-02-15 18:28 | 2026-02-15 19:57 | 1.7281 | Confirmed/Materialized Shift | upper | 73.7888 | 2.09 | 1.4832 | 0.4701 | Night | Investigate
2026-02-21 08:45 | 2026-02-21 09:12 | 0.71167 | Persistent | upper | 74.0714 | 2.6394 | 2.2866 | 0.4636 | Day | Review
2026-02-20 17:57 | 2026-02-20 18:42 | 1.0053 | Persistent | lower | 72.941 | 2.6647 | 2.1339 | 0.4475 | Day | Review
2026-02-21 17:12 | 2026-02-21 17:46 | 0.80639 | Persistent | lower | 72.941 | 2.9429 | 2.216 | 0.4189 | Day | Review
2026-02-13 14:43 | 2026-02-13 15:43 | 1.2456 | Persistent | lower | 72.3758 | 2.0085 | 1.6502 | 0.4035 | Day | Review
2026-02-10 18:27 | 2026-02-10 18:46 | 0.56333 | Persistent | lower | 72.6584 | 2.4597 | 2.0235 | 0.3661 | Night | Review
2026-02-22 11:00 | 2026-02-22 11:29 | 0.74417 | Persistent | upper | 74.0714 | 2.7587 | 1.962 | 0.3602 | Day | Review
2026-02-11 19:23 | 2026-02-11 19:52 | 0.74222 | Persistent | upper | 73.5062 | 2.0673 | 1.812 | 0.3053 | Night | Review
2026-02-14 19:12 | 2026-02-14 19:57 | 0.99472 | Persistent | upper | 74.0714 | 2.0286 | 1.4814 | 0.2955 | Night | Review
2026-02-11 17:23 | 2026-02-11 17:23 | 0.25083 | Extreme triggered | lower | 72.3758 | 2.6745 | 2.6745 | 0.2926 | Day | Monitor
2026-02-16 16:13 | 2026-02-16 16:42 | 0.74444 | Persistent | lower | 72.3758 | 2.1909 | 1.937 | 0.2854 | Day | Review
2026-02-11 18:08 | 2026-02-11 18:08 | 0.25083 | Extreme triggered | lower | 72.3758 | 2.0571 | 2.0571 | 0.2514 | Day | Monitor
2026-02-14 14:54 | 2026-02-14 14:57 | 0.30111 | Extreme/elevated | upper | 74.0714 | 2.2586 | 1.7799 | 0.2077 | Day | Monitor
2026-02-14 16:43 | 2026-02-14 16:58 | 0.50194 | Extreme/elevated | lower | 72.3758 | 2.0571 | 1.6906 | 0.2026 | Day | Monitor
2026-02-15 07:08 | 2026-02-15 07:08 | 0.25083 | Extreme triggered | lower | 72.095 | 2.0244 | 2.0244 | 0.1921 | Day | Monitor

## Events
All events
One row per event (from Extreme triggered until Persistence ends), sorted by start time. Derived from the Data tab.
Start | End | Duration (h) | Direction | Peak value | Max ¦Z¦ | Mean ¦Z¦ (event) | Highest state | Max materiality score | Day/Night at start | Month key | Action | Readings
2025-12-01 18:12 | 2025-12-01 18:42 | 0.75528 | lower | 72.095 | 2.571 | 2.2268 | Persistent | 0.4351 | Night | 202512 | Review | View readings
2025-12-02 08:16 | 2025-12-02 11:29 | 3.4794 | upper | 74.9174 | 3.783 | 2.0473 | Confirmed/Materialized Shift | 0.7019 | Day | 202512 | Investigate | View readings
2025-12-02 18:57 | 2025-12-02 22:40 | 3.9689 | upper | 74.0714 | 2.6876 | 1.7013 | Confirmed/Materialized Shift | 0.5529 | Night | 202512 | Investigate | View readings
2025-12-03 02:10 | 2025-12-03 02:10 | 0.25083 | upper | 74.3522 | 3.0733 | 3.0733 | Extreme triggered | 0.2906 | Night | 202512 | Monitor | View readings
2025-12-03 02:39 | 2025-12-03 02:39 | 0.25083 | upper | 74.3522 | 2.924 | 2.924 | Extreme triggered | 0.3378 | Night | 202512 | Monitor | View readings
2025-12-03 03:54 | 2025-12-03 04:09 | 0.50167 | upper | 74.3522 | 2.3202 | 2.1348 | Extreme/elevated | 0.3585 | Night | 202512 | Monitor | View readings
2025-12-03 09:00 | 2025-12-03 09:59 | 1.2383 | lower | 72.095 | 4.1266 | 2.7441 | Persistent | 0.4324 | Day | 202512 | Review | View readings
2025-12-03 18:57 | 2025-12-03 21:11 | 2.4808 | upper | 73.7888 | 2.2292 | 1.6162 | Confirmed/Materialized Shift | 0.519 | Night | 202512 | Investigate | View readings
2025-12-03 23:55 | 2025-12-04 04:54 | 5.2247 | lower | 72.6584 | 2.4713 | 1.5676 | Confirmed/Materialized Shift | 0.5389 | Night | 202512 | Investigate | View readings
2025-12-04 07:08 | 2025-12-04 07:23 | 0.50139 | lower | 72.095 | 2.1158 | 1.9946 | Extreme/elevated | 0.2963 | Day | 202512 | Monitor | View readings
2025-12-04 08:46 | 2025-12-04 11:04 | 2.5597 | upper | 74.0714 | 2.6216 | 1.7921 | Confirmed/Materialized Shift | 0.5504 | Day | 202512 | Investigate | View readings
2025-12-04 16:14 | 2025-12-04 18:13 | 2.2408 | lower | 72.095 | 2.7404 | 2.2193 | Confirmed/Materialized Shift | 0.5588 | Day | 202512 | Investigate | View readings
2025-12-05 00:29 | 2025-12-05 04:57 | 4.7317 | lower | 73.2236 | 2.8102 | 1.7562 | Confirmed/Materialized Shift | 0.6077 | Night | 202512 | Investigate | View readings
2025-12-05 07:26 | 2025-12-05 07:31 | 0.33306 | lower | 72.6584 | 2.1222 | 2.0161 | Extreme/elevated | 0.2988 | Day | 202512 | Monitor | View readings
2025-12-05 08:46 | 2025-12-05 09:16 | 0.75472 | upper | 73.7888 | 2.5534 | 2.2604 | Persistent | 0.4282 | Day | 202512 | Review | View readings
2025-12-05 12:11 | 2025-12-05 12:29 | 0.55194 | upper | 74.0714 | 2.1794 | 1.4844 | Persistent | 0.2438 | Day | 202512 | Review | View readings
2025-12-05 16:44 | 2025-12-05 18:13 | 1.7472 | lower | 72.095 | 2.1419 | 1.613 | Confirmed/Materialized Shift | 0.4958 | Day | 202512 | Investigate | View readings
2025-12-05 19:31 | 2025-12-05 21:45 | 2.4911 | upper | 74.0714 | 2.1636 | 1.5364 | Confirmed/Materialized Shift | 0.5238 | Night | 202512 | Investigate | View readings
2025-12-06 03:13 | 2025-12-06 04:58 | 1.9897 | lower | 73.5062 | 2.5628 | 1.9608 | Confirmed/Materialized Shift | 0.628 | Night | 202512 | Investigate | View readings
2025-12-06 05:42 | 2025-12-06 07:12 | 1.7472 | lower | 73.5062 | 2.0125 | 1.4461 | Confirmed/Materialized Shift | 0.5555 | Night | 202512 | Investigate | View readings
2025-12-06 09:17 | 2025-12-06 09:20 | 0.30083 | upper | 74.0714 | 2.6745 | 2.4664 | Extreme/elevated | 0.322 | Day | 202512 | Monitor | View readings
2025-12-06 10:01 | 2025-12-06 11:45 | 1.9897 | lower | 72.941 | 2.4908 | 1.6141 | Confirmed/Materialized Shift | 0.5065 | Day | 202512 | Investigate | View readings
2025-12-06 15:29 | 2025-12-06 17:21 | 2.1181 | lower | 71.8124 | 3.0822 | 2.3897 | Confirmed/Materialized Shift | 0.6204 | Day | 202512 | Investigate | View readings
2025-12-06 18:06 | 2025-12-06 21:05 | 3.2331 | upper | 74.9174 | 2.297 | 1.7075 | Confirmed/Materialized Shift | 0.5494 | Night | 202512 | Investigate | View readings
2025-12-07 02:33 | 2025-12-07 04:33 | 2.2403 | lower | 74.9174 | 2.924 | 1.8771 | Confirmed/Materialized Shift | 0.5171 | Night | 202512 | Investigate | View readings
2025-12-07 05:18 | 2025-12-07 08:02 | 2.9847 | lower | 74.0714 | 2.4865 | 1.8722 | Confirmed/Materialized Shift | 0.6229 | Night | 202512 | Investigate | View readings
2025-12-07 09:30 | 2025-12-07 09:48 | 0.56083 | upper | 75.4826 | 2.3376 | 1.9391 | Persistent | 0.3629 | Day | 202512 | Review | View readings
2025-12-07 15:28 | 2025-12-07 17:35 | 2.3586 | lower | 71.8124 | 2.6456 | 2.0826 | Confirmed/Materialized Shift | 0.534 | Day | 202512 | Investigate | View readings
2025-12-08 07:01 | 2025-12-08 07:16 | 0.50139 | lower | 74.9174 | 4.2485 | 3.5863 | Extreme/elevated | 0.3689 | Day | 202512 | Monitor | View readings
2025-12-08 07:45 | 2025-12-08 08:30 | 0.98806 | lower | 74.9174 | 2.3202 | 1.8617 | Persistent | 0.4135 | Day | 202512 | Review | View readings
2025-12-08 09:03 | 2025-12-08 10:23 | 1.5911 | lower | 71.8124 | 3.4159 | 2.7761 | Confirmed/Materialized Shift | 0.6195 | Day | 202512 | Investigate | View readings
2025-12-08 19:41 | 2025-12-08 22:26 | 2.9928 | upper | 74.3522 | 2.0578 | 1.4195 | Confirmed/Materialized Shift | 0.5205 | Night | 202512 | Investigate | View readings
2025-12-09 02:25 | 2025-12-09 04:24 | 2.2406 | lower | 73.7888 | 3.0911 | 1.782 | Confirmed/Materialized Shift | 0.5171 | Night | 202512 | Investigate | View readings
2025-12-09 05:38 | 2025-12-09 07:30 | 2.1208 | lower | 73.5062 | 2.2722 | 1.5498 | Confirmed/Materialized Shift | 0.5171 | Night | 202512 | Investigate | View readings
2025-12-09 09:30 | 2025-12-09 09:44 | 0.49083 | lower | 73.2236 | 2.6647 | 2.5378 | Extreme/elevated | 0.3036 | Day | 202512 | Monitor | View readings
2025-12-09 10:59 | 2025-12-09 11:14 | 0.50167 | lower | 73.2236 | 2.3202 | 2.1348 | Extreme/elevated | 0.33 | Day | 202512 | Monitor | View readings
2025-12-09 15:58 | 2025-12-09 16:13 | 0.50139 | upper | 73.7888 | 2.2757 | 2.1126 | Extreme/elevated | 0.2442 | Day | 202512 | Monitor | View readings
2025-12-09 19:27 | 2025-12-09 20:56 | 1.7367 | upper | 74.0714 | 2.976 | 1.6231 | Confirmed/Materialized Shift | 0.5526 | Night | 202512 | Investigate | View readings
2025-12-10 01:55 | 2025-12-10 04:54 | 3.2356 | lower | 73.2236 | 4.2485 | 2.0622 | Confirmed/Materialized Shift | 0.6077 | Night | 202512 | Investigate | View readings
2025-12-10 06:38 | 2025-12-10 08:00 | 1.6256 | lower | 72.3758 | 2.2294 | 1.7133 | Confirmed/Materialized Shift | 0.4971 | Night | 202512 | Investigate | View readings
2025-12-10 09:00 | 2025-12-10 11:16 | 2.5156 | upper | 74.0714 | 2.477 | 1.5651 | Confirmed/Materialized Shift | 0.5279 | Day | 202512 | Investigate | View readings
2025-12-10 16:28 | 2025-12-10 18:27 | 2.2403 | lower | 72.095 | 3.1509 | 2.3684 | Confirmed/Materialized Shift | 0.5688 | Day | 202512 | Investigate | View readings
2025-12-11 00:14 | 2025-12-11 08:00 | 8.0331 | lower | 70.9646 | 2.2757 | 1.7051 | Confirmed/Materialized Shift | 0.6024 | Night | 202512 | Investigate | View readings
2025-12-11 10:00 | 2025-12-11 12:29 | 2.7342 | upper | 73.5062 | 2.4799 | 1.882 | Confirmed/Materialized Shift | 0.536 | Day | 202512 | Investigate | View readings
2025-12-11 15:43 | 2025-12-11 16:35 | 1.1142 | lower | 72.3758 | 2.5192 | 1.9186 | Persistent | 0.4679 | Day | 202512 | Review | View readings
2025-12-11 23:28 | 2025-12-12 07:45 | 8.5331 | lower | 69.836 | 2.1657 | 1.62 | Confirmed/Materialized Shift | 0.5377 | Night | 202512 | Investigate | View readings
2025-12-12 09:15 | 2025-12-12 12:59 | 3.9772 | upper | 73.7888 | 2.7117 | 1.8381 | Confirmed/Materialized Shift | 0.6048 | Day | 202512 | Investigate | View readings
2025-12-12 14:52 | 2025-12-12 15:37 | 1.0033 | lower | 72.3758 | 2.2946 | 1.9221 | Persistent | 0.3177 | Day | 202512 | Review | View readings
2025-12-13 05:18 | 2025-12-13 07:30 | 2.4544 | lower | 70.3994 | 2.1273 | 1.4632 | Confirmed/Materialized Shift | 0.5426 | Night | 202512 | Investigate | View readings
2025-12-13 09:30 | 2025-12-13 13:31 | 4.2694 | upper | 74.0714 | 2.743 | 1.7371 | Confirmed/Materialized Shift | 0.557 | Day | 202512 | Investigate | View readings
2025-12-13 18:05 | 2025-12-13 19:04 | 1.2356 | upper | 73.5062 | 2.1127 | 1.6401 | Persistent | 0.3991 | Night | 202512 | Review | View readings
2025-12-13 21:18 | 2025-12-13 21:18 | 0.25083 | upper | 73.7888 | 2.2993 | 2.2993 | Extreme triggered | 0.239 | Night | 202512 | Monitor | View readings
2025-12-13 22:48 | 2025-12-13 22:48 | 0.25083 | upper | 73.7888 | 2.1794 | 2.1794 | Extreme triggered | 0.2024 | Night | 202512 | Monitor | View readings
2025-12-14 06:31 | 2025-12-14 06:45 | 0.49333 | lower | 73.2236 | 4.2485 | 3.5863 | Extreme/elevated | 0.3689 | Night | 202512 | Monitor | View readings
2025-12-14 07:15 | 2025-12-14 07:15 | 0.25083 | lower | 73.2236 | 2.3202 | 2.3202 | Extreme triggered | 0.2975 | Day | 202512 | Monitor | View readings
2025-12-14 09:45 | 2025-12-14 11:15 | 1.7453 | lower | 72.3758 | 3.5547 | 2.2088 | Confirmed/Materialized Shift | 0.5647 | Day | 202512 | Investigate | View readings
2025-12-14 17:13 | 2025-12-14 20:14 | 3.2761 | upper | 74.0714 | 2.9539 | 1.8358 | Confirmed/Materialized Shift | 0.6541 | Day | 202512 | Investigate | View readings
2025-12-15 02:13 | 2025-12-15 05:12 | 3.2364 | lower | 73.5062 | 4.2485 | 2.0302 | Confirmed/Materialized Shift | 0.6648 | Night | 202512 | Investigate | View readings
2025-12-15 10:00 | 2025-12-15 11:05 | 1.3328 | upper | 74.0714 | 3.7804 | 2.7601 | Confirmed/Materialized Shift | 0.7004 | Day | 202512 | Investigate | View readings
2025-12-15 17:00 | 2025-12-15 18:46 | 2.0042 | lower | 72.3758 | 2.4597 | 1.7666 | Confirmed/Materialized Shift | 0.5043 | Day | 202512 | Investigate | View readings
2025-12-15 23:58 | 2025-12-16 01:43 | 1.9906 | lower | 72.3758 | 2.1141 | 1.4708 | Confirmed/Materialized Shift | 0.4777 | Night | 202512 | Investigate | View readings
2025-12-16 02:58 | 2025-12-16 04:57 | 2.2406 | lower | 71.8124 | 2.4779 | 1.6214 | Confirmed/Materialized Shift | 0.5938 | Night | 202512 | Investigate | View readings
2025-12-16 07:30 | 2025-12-16 11:57 | 4.6919 | upper | 73.7888 | 2.703 | 1.7134 | Confirmed/Materialized Shift | 0.6088 | Day | 202512 | Investigate | View readings
2025-12-16 13:24 | 2025-12-16 13:27 | 0.30722 | lower | 71.8124 | 2.1526 | 2.024 | Extreme/elevated | 0.2978 | Day | 202512 | Monitor | View readings
2025-12-16 18:30 | 2025-12-16 18:46 | 0.51 | lower | 72.6584 | 2.1127 | 2.0274 | Persistent | 0.3238 | Night | 202512 | Review | View readings
2025-12-16 19:45 | 2025-12-16 20:00 | 0.50139 | upper | 73.7888 | 2.2069 | 2.0491 | Extreme/elevated | 0.2975 | Night | 202512 | Monitor | View readings
2025-12-17 01:43 | 2025-12-17 03:42 | 2.2403 | lower | 73.2236 | 4.2485 | 2.0243 | Confirmed/Materialized Shift | 0.5171 | Night | 202512 | Investigate | View readings
2025-12-17 04:42 | 2025-12-17 06:12 | 1.7472 | lower | 72.6584 | 2.4597 | 1.8067 | Confirmed/Materialized Shift | 0.6211 | Night | 202512 | Investigate | View readings
2025-12-17 06:56 | 2025-12-17 08:30 | 1.8131 | lower | 72.3758 | 2.3111 | 1.7284 | Confirmed/Materialized Shift | 0.5877 | Night | 202512 | Investigate | View readings
2025-12-17 10:00 | 2025-12-17 11:29 | 1.7389 | upper | 73.7888 | 2.4597 | 1.8704 | Confirmed/Materialized Shift | 0.4995 | Day | 202512 | Investigate | View readings
2025-12-17 19:57 | 2025-12-17 22:41 | 2.9844 | upper | 74.0714 | 2.0094 | 1.4217 | Confirmed/Materialized Shift | 0.5066 | Night | 202512 | Investigate | View readings
2025-12-18 02:10 | 2025-12-18 02:10 | 0.25083 | lower | 73.7888 | 4.2485 | 4.2485 | Extreme triggered | 0.3689 | Night | 202512 | Monitor | View readings
2025-12-18 02:39 | 2025-12-18 04:24 | 1.9981 | lower | 73.7888 | 2.924 | 1.7463 | Confirmed/Materialized Shift | 0.5653 | Night | 202512 | Investigate | View readings
2025-12-18 08:31 | 2025-12-18 08:31 | 0.25083 | upper | 74.0714 | 4.2485 | 4.2485 | Extreme triggered | 0.3689 | Day | 202512 | Monitor | View readings
2025-12-18 08:49 | 2025-12-18 10:29 | 1.9286 | lower | 72.095 | 3.5884 | 2.5668 | Confirmed/Materialized Shift | 0.6508 | Day | 202512 | Investigate | View readings
2025-12-18 14:14 | 2025-12-18 15:13 | 1.2461 | upper | 73.5062 | 2.106 | 1.4201 | Persistent | 0.3855 | Day | 202512 | Review | View readings
2025-12-18 17:42 | 2025-12-18 18:31 | 1.0556 | lower | 72.3758 | 2.5868 | 2.069 | Persistent | 0.4687 | Night | 202512 | Review | View readings
2025-12-19 07:11 | 2025-12-19 07:11 | 0.25083 | lower | 74.3522 | 4.2485 | 4.2485 | Extreme triggered | 0.3689 | Day | 202512 | Monitor | View readings
2025-12-19 08:00 | 2025-12-19 08:30 | 0.7375 | lower | 74.3522 | 2.924 | 2.3979 | Persistent | 0.3871 | Day | 202512 | Review | View readings
2025-12-19 08:48 | 2025-12-19 10:29 | 1.9375 | lower | 72.095 | 3.8577 | 2.3488 | Confirmed/Materialized Shift | 0.5796 | Day | 202512 | Investigate | View readings
2025-12-19 15:58 | 2025-12-19 17:27 | 1.7389 | lower | 72.095 | 2.6584 | 2.1332 | Confirmed/Materialized Shift | 0.5417 | Day | 202512 | Investigate | View readings
2025-12-19 18:46 | 2025-12-19 20:44 | 2.2297 | upper | 74.0714 | 2.2702 | 1.6192 | Confirmed/Materialized Shift | 0.5134 | Night | 202512 | Investigate | View readings
2025-12-20 03:57 | 2025-12-20 08:16 | 4.5558 | lower | 72.941 | 2.0867 | 1.5562 | Confirmed/Materialized Shift | 0.5656 | Night | 202512 | Investigate | View readings
2025-12-20 09:11 | 2025-12-20 09:14 | 0.30083 | upper | 74.0714 | 2.9046 | 2.6472 | Extreme/elevated | 0.3593 | Day | 202512 | Monitor | View readings
2025-12-20 15:43 | 2025-12-20 17:31 | 2.0472 | lower | 72.095 | 2.351 | 1.7708 | Confirmed/Materialized Shift | 0.5527 | Day | 202512 | Investigate | View readings
2025-12-20 18:45 | 2025-12-20 20:59 | 2.4914 | upper | 73.7888 | 2.0317 | 1.4916 | Confirmed/Materialized Shift | 0.5208 | Night | 202512 | Investigate | View readings
2025-12-21 01:28 | 2025-12-21 05:12 | 3.9875 | lower | 72.941 | 2.4713 | 1.5711 | Confirmed/Materialized Shift | 0.6219 | Night | 202512 | Investigate | View readings
2025-12-21 05:56 | 2025-12-21 07:26 | 1.7389 | lower | 72.3758 | 2.2253 | 1.7435 | Confirmed/Materialized Shift | 0.6055 | Night | 202512 | Investigate | View readings
2025-12-21 08:45 | 2025-12-21 09:51 | 1.3467 | upper | 74.0714 | 3.0775 | 2.1572 | Confirmed/Materialized Shift | 0.5798 | Day | 202512 | Investigate | View readings
2025-12-21 17:13 | 2025-12-21 17:31 | 0.54472 | lower | 72.6584 | 2.1794 | 1.8483 | Persistent | 0.3328 | Day | 202512 | Review | View readings
2025-12-21 18:16 | 2025-12-21 21:14 | 3.2256 | upper | 74.9174 | 2.3123 | 1.5763 | Confirmed/Materialized Shift | 0.5607 | Night | 202512 | Investigate | View readings
2025-12-22 01:13 | 2025-12-22 03:42 | 2.7406 | lower | 74.3522 | 4.2485 | 2.0997 | Confirmed/Materialized Shift | 0.5742 | Night | 202512 | Investigate | View readings
2025-12-22 08:33 | 2025-12-22 10:44 | 2.4392 | lower | 72.6584 | 3.5896 | 2.3818 | Confirmed/Materialized Shift | 0.6062 | Day | 202512 | Investigate | View readings
2025-12-22 16:58 | 2025-12-22 18:30 | 1.7914 | lower | 72.095 | 2.7751 | 2.0656 | Confirmed/Materialized Shift | 0.5062 | Day | 202512 | Investigate | View readings
2025-12-23 06:26 | 2025-12-23 06:26 | 0.25083 | lower | 74.0714 | 2.2856 | 2.2856 | Extreme triggered | 0.2095 | Night | 202512 | Monitor | View readings
2025-12-23 08:48 | 2025-12-23 10:29 | 1.9375 | lower | 72.095 | 3.7773 | 2.2726 | Confirmed/Materialized Shift | 0.5437 | Day | 202512 | Investigate | View readings
2025-12-23 16:58 | 2025-12-23 18:27 | 1.7392 | lower | 71.8124 | 2.4287 | 1.9651 | Confirmed/Materialized Shift | 0.4851 | Day | 202512 | Investigate | View readings
2025-12-24 00:40 | 2025-12-24 05:54 | 5.4758 | lower | 72.095 | 2.6745 | 1.5527 | Confirmed/Materialized Shift | 0.591 | Night | 202512 | Investigate | View readings
2025-12-24 09:00 | 2025-12-24 12:02 | 3.2872 | upper | 74.0714 | 2.7761 | 1.9538 | Confirmed/Materialized Shift | 0.6182 | Day | 202512 | Investigate | View readings
2025-12-25 00:14 | 2025-12-25 06:41 | 6.7131 | lower | 72.095 | 2.4713 | 1.6207 | Confirmed/Materialized Shift | 0.596 | Night | 202512 | Investigate | View readings
2025-12-25 09:00 | 2025-12-25 11:44 | 2.9831 | upper | 74.0714 | 3.0222 | 1.9148 | Confirmed/Materialized Shift | 0.5614 | Day | 202512 | Investigate | View readings
2025-12-25 18:46 | 2025-12-25 21:15 | 2.7325 | upper | 73.7888 | 2.897 | 1.8679 | Confirmed/Materialized Shift | 0.5307 | Night | 202512 | Investigate | View readings
2025-12-25 23:59 | 2025-12-26 08:15 | 8.5331 | lower | 71.5298 | 2.4713 | 1.6097 | Confirmed/Materialized Shift | 0.5913 | Night | 202512 | Investigate | View readings
2025-12-26 09:15 | 2025-12-26 11:44 | 2.7319 | upper | 74.0714 | 3.0644 | 1.9009 | Confirmed/Materialized Shift | 0.5813 | Day | 202512 | Investigate | View readings
2025-12-26 16:28 | 2025-12-26 16:58 | 0.75222 | lower | 72.095 | 2.3865 | 2.1385 | Persistent | 0.3591 | Day | 202512 | Review | View readings
2025-12-26 18:46 | 2025-12-26 20:00 | 1.4858 | upper | 73.7888 | 2.536 | 1.9687 | Persistent | 0.4665 | Night | 202512 | Review | View readings
2025-12-26 23:28 | 2025-12-27 04:27 | 5.2256 | lower | 72.095 | 2.2418 | 1.5875 | Confirmed/Materialized Shift | 0.5495 | Night | 202512 | Investigate | View readings
2025-12-27 06:41 | 2025-12-27 08:16 | 1.8211 | lower | 71.5298 | 2.163 | 1.5294 | Confirmed/Materialized Shift | 0.5062 | Night | 202512 | Investigate | View readings
2025-12-27 09:30 | 2025-12-27 12:03 | 2.8111 | upper | 74.0714 | 3.1806 | 1.9413 | Confirmed/Materialized Shift | 0.5627 | Day | 202512 | Investigate | View readings
2025-12-27 17:46 | 2025-12-27 19:44 | 2.23 | upper | 73.7888 | 2.5141 | 1.7124 | Confirmed/Materialized Shift | 0.5148 | Night | 202512 | Investigate | View readings
2025-12-27 22:59 | 2025-12-28 05:41 | 6.965 | lower | 71.8124 | 2.1759 | 1.4905 | Confirmed/Materialized Shift | 0.5361 | Night | 202512 | Investigate | View readings
2025-12-28 09:00 | 2025-12-28 12:44 | 3.9775 | upper | 74.0714 | 2.9202 | 1.8121 | Confirmed/Materialized Shift | 0.5986 | Day | 202512 | Investigate | View readings
2025-12-28 16:43 | 2025-12-28 17:31 | 1.0464 | lower | 72.095 | 2.4753 | 2.1551 | Persistent | 0.4614 | Day | 202512 | Review | View readings
2025-12-28 23:28 | 2025-12-29 06:11 | 6.9719 | lower | 71.8124 | 2.8102 | 1.6373 | Confirmed/Materialized Shift | 0.5941 | Night | 202512 | Investigate | View readings
2025-12-29 09:00 | 2025-12-29 11:44 | 2.9825 | upper | 74.0714 | 2.7707 | 2.0477 | Confirmed/Materialized Shift | 0.5608 | Day | 202512 | Investigate | View readings
2025-12-29 16:58 | 2025-12-29 17:27 | 0.74389 | lower | 72.095 | 2.5666 | 2.1471 | Persistent | 0.2854 | Day | 202512 | Review | View readings
2025-12-29 19:01 | 2025-12-29 20:44 | 1.9789 | upper | 73.7888 | 2.3702 | 1.5318 | Confirmed/Materialized Shift | 0.4974 | Night | 202512 | Investigate | View readings
2025-12-30 01:13 | 2025-12-30 02:58 | 1.9897 | lower | 72.941 | 2.1794 | 1.5183 | Confirmed/Materialized Shift | 0.5046 | Night | 202512 | Investigate | View readings
2025-12-30 04:12 | 2025-12-30 07:45 | 3.8022 | lower | 72.095 | 2.5628 | 1.6459 | Confirmed/Materialized Shift | 0.628 | Night | 202512 | Investigate | View readings
2025-12-30 09:15 | 2025-12-30 10:15 | 1.2436 | upper | 73.2236 | 2.8416 | 1.9475 | Persistent | 0.3766 | Day | 202512 | Review | View readings
2025-12-30 16:43 | 2025-12-30 16:58 | 0.50167 | lower | 72.6584 | 2.411 | 1.7284 | Extreme/elevated | 0.275 | Day | 202512 | Monitor | View readings
2025-12-30 20:41 | 2026-01-02 15:58 | 67.5222 | lower | 67.8596 | 2.8497 | 1.6803 | Confirmed/Materialized Shift | 0.6185 | Night | 202512 | Investigate | View readings
2026-01-03 09:00 | 2026-01-03 11:42 | 2.9611 | upper | 72.941 | 2.9016 | 2.1484 | Confirmed/Materialized Shift | 0.6791 | Day | 202601 | Investigate | View readings
2026-01-04 00:54 | 2026-01-04 03:54 | 3.2358 | lower | 72.095 | 2.3402 | 1.653 | Confirmed/Materialized Shift | 0.5594 | Night | 202601 | Investigate | View readings
2026-01-04 06:53 | 2026-01-04 08:37 | 1.9903 | lower | 71.5298 | 2.3975 | 1.565 | Confirmed/Materialized Shift | 0.5046 | Night | 202601 | Investigate | View readings
2026-01-04 10:00 | 2026-01-04 13:08 | 3.38 | upper | 74.0714 | 2.8931 | 1.9575 | Confirmed/Materialized Shift | 0.5933 | Day | 202601 | Investigate | View readings
2026-01-04 14:29 | 2026-01-04 15:44 | 1.4964 | lower | 72.095 | 2.4259 | 1.9357 | Persistent | 0.4534 | Day | 202601 | Review | View readings
2026-01-04 18:29 | 2026-01-04 19:13 | 0.98417 | upper | 73.5062 | 2.057 | 1.374 | Persistent | 0.3259 | Night | 202601 | Review | View readings
2026-01-04 23:27 | 2026-01-05 04:39 | 5.4672 | lower | 71.5298 | 2.1983 | 1.5201 | Confirmed/Materialized Shift | 0.5599 | Night | 202601 | Investigate | View readings
2026-01-05 09:59 | 2026-01-05 12:46 | 3.0286 | upper | 74.0714 | 3.1769 | 2.0526 | Confirmed/Materialized Shift | 0.5767 | Day | 202601 | Investigate | View readings
2026-01-05 19:16 | 2026-01-05 20:44 | 1.7283 | upper | 73.7888 | 2.158 | 1.7288 | Confirmed/Materialized Shift | 0.4835 | Night | 202601 | Investigate | View readings
2026-01-05 23:43 | 2026-01-06 05:57 | 6.4706 | lower | 71.5298 | 2.2757 | 1.6056 | Confirmed/Materialized Shift | 0.5517 | Night | 202601 | Investigate | View readings
2026-01-06 08:27 | 2026-01-06 11:29 | 3.2828 | upper | 74.0714 | 2.9785 | 1.8514 | Confirmed/Materialized Shift | 0.545 | Day | 202601 | Investigate | View readings
2026-01-06 17:13 | 2026-01-06 17:57 | 0.995 | lower | 72.095 | 2.6862 | 2.0897 | Persistent | 0.3293 | Day | 202601 | Review | View readings
2026-01-07 00:43 | 2026-01-07 00:43 | 0.25083 | lower | 72.941 | 2.351 | 2.351 | Extreme triggered | 0.2424 | Night | 202601 | Monitor | View readings
2026-01-07 01:58 | 2026-01-07 07:30 | 5.7911 | lower | 71.8124 | 2.1696 | 1.5112 | Confirmed/Materialized Shift | 0.5378 | Night | 202601 | Investigate | View readings
2026-01-07 09:00 | 2026-01-07 11:18 | 2.5497 | upper | 74.0714 | 2.9226 | 2.1587 | Confirmed/Materialized Shift | 0.6694 | Day | 202601 | Investigate | View readings
2026-01-07 14:58 | 2026-01-07 15:43 | 0.995 | lower | 72.941 | 2.378 | 1.4625 | Persistent | 0.298 | Day | 202601 | Review | View readings
2026-01-07 16:58 | 2026-01-07 18:12 | 1.4964 | lower | 72.095 | 2.3897 | 2.0009 | Persistent | 0.4248 | Day | 202601 | Review | View readings
2026-01-08 00:43 | 2026-01-08 06:56 | 6.4706 | lower | 72.095 | 2.362 | 1.5753 | Confirmed/Materialized Shift | 0.5593 | Night | 202601 | Investigate | View readings
2026-01-08 09:00 | 2026-01-08 11:15 | 2.4892 | upper | 73.5062 | 2.9263 | 1.9754 | Confirmed/Materialized Shift | 0.5204 | Day | 202601 | Investigate | View readings
2026-01-08 13:59 | 2026-01-08 14:58 | 1.2456 | lower | 72.6584 | 2.0633 | 1.5701 | Persistent | 0.3765 | Day | 202601 | Review | View readings
2026-01-08 18:46 | 2026-01-08 22:14 | 3.7269 | upper | 73.7888 | 2.485 | 1.4996 | Confirmed/Materialized Shift | 0.5038 | Night | 202601 | Investigate | View readings
2026-01-09 00:43 | 2026-01-09 02:28 | 1.9894 | lower | 72.941 | 2.3975 | 1.7208 | Confirmed/Materialized Shift | 0.5893 | Night | 202601 | Investigate | View readings
2026-01-09 05:27 | 2026-01-09 08:00 | 2.8158 | lower | 72.3758 | 2.3444 | 1.7189 | Confirmed/Materialized Shift | 0.5353 | Night | 202601 | Investigate | View readings
2026-01-09 09:30 | 2026-01-09 11:21 | 2.1125 | upper | 74.0714 | 2.4887 | 1.9526 | Confirmed/Materialized Shift | 0.5587 | Day | 202601 | Investigate | View readings
2026-01-09 16:58 | 2026-01-09 18:27 | 1.7389 | lower | 72.3758 | 2.9654 | 2.4098 | Confirmed/Materialized Shift | 0.5807 | Day | 202601 | Investigate | View readings
2026-01-10 03:54 | 2026-01-10 05:09 | 1.4967 | lower | 73.2236 | 2.3975 | 1.8851 | Persistent | 0.5201 | Night | 202601 | Review | View readings
2026-01-10 06:53 | 2026-01-10 06:53 | 0.25083 | lower | 72.941 | 2.0646 | 2.0646 | Extreme triggered | 0.1948 | Night | 202601 | Monitor | View readings
2026-01-10 11:59 | 2026-01-10 12:06 | 0.3625 | upper | 74.0714 | 2.8747 | 2.3013 | Persistent | 0.3059 | Day | 202601 | Review | View readings
2026-01-10 13:28 | 2026-01-10 13:43 | 0.50167 | lower | 72.6584 | 2.0674 | 1.921 | Extreme/elevated | 0.2612 | Day | 202601 | Monitor | View readings
2026-01-10 18:16 | 2026-01-10 20:59 | 2.9744 | upper | 74.6348 | 2.4325 | 1.66 | Confirmed/Materialized Shift | 0.5413 | Night | 202601 | Investigate | View readings
2026-01-10 23:28 | 2026-01-11 07:11 | 7.9669 | lower | 72.6584 | 2.0543 | 1.5626 | Confirmed/Materialized Shift | 0.5941 | Night | 202601 | Investigate | View readings
2026-01-11 09:26 | 2026-01-11 09:44 | 0.54694 | upper | 74.0714 | 2.7587 | 2.3806 | Persistent | 0.4224 | Day | 202601 | Review | View readings
2026-01-11 18:16 | 2026-01-11 21:29 | 3.4675 | upper | 75.2 | 2.5153 | 1.6674 | Confirmed/Materialized Shift | 0.5454 | Night | 202601 | Investigate | View readings
2026-01-12 02:13 | 2026-01-12 05:56 | 3.9792 | lower | 73.7888 | 2.6647 | 1.7432 | Confirmed/Materialized Shift | 0.5917 | Night | 202601 | Investigate | View readings
2026-01-12 09:15 | 2026-01-12 09:59 | 0.9925 | lower | 73.2236 | 3.2242 | 2.598 | Persistent | 0.3986 | Day | 202601 | Review | View readings
2026-01-12 12:59 | 2026-01-12 13:29 | 0.7525 | lower | 71.8124 | 3.396 | 2.8588 | Persistent | 0.455 | Day | 202601 | Review | View readings
2026-01-12 19:12 | 2026-01-12 19:56 | 0.99278 | upper | 73.7888 | 2.142 | 2.003 | Persistent | 0.3789 | Night | 202601 | Review | View readings
2026-01-13 07:30 | 2026-01-13 07:30 | 0.25083 | lower | 72.941 | 4.2485 | 4.2485 | Extreme triggered | 0.3689 | Day | 202601 | Monitor | View readings
2026-01-13 08:15 | 2026-01-13 08:15 | 0.25083 | lower | 72.941 | 2.924 | 2.924 | Extreme triggered | 0.3378 | Day | 202601 | Monitor | View readings
2026-01-13 09:15 | 2026-01-13 09:44 | 0.74194 | upper | 73.7888 | 3.2242 | 2.4312 | Persistent | 0.4435 | Day | 202601 | Review | View readings
2026-01-13 12:43 | 2026-01-13 14:25 | 1.95 | upper | 74.0714 | 3.4626 | 1.7762 | Confirmed/Materialized Shift | 0.688 | Day | 202601 | Investigate | View readings
2026-01-14 00:50 | 2026-01-14 00:50 | 0.25083 | lower | 73.5062 | 4.2485 | 4.2485 | Extreme triggered | 0.3689 | Night | 202601 | Monitor | View readings
2026-01-14 01:50 | 2026-01-14 03:34 | 1.9903 | lower | 73.5062 | 2.924 | 1.7463 | Confirmed/Materialized Shift | 0.5367 | Night | 202601 | Investigate | View readings
2026-01-14 04:19 | 2026-01-14 05:33 | 1.4881 | lower | 73.2236 | 2.2993 | 1.692 | Persistent | 0.4559 | Night | 202601 | Review | View readings
2026-01-14 09:00 | 2026-01-14 10:14 | 1.4947 | upper | 73.5062 | 2.924 | 1.9498 | Persistent | 0.46 | Day | 202601 | Review | View readings
2026-01-14 10:44 | 2026-01-14 10:59 | 0.50167 | lower | 72.3758 | 3.1616 | 3.1078 | Extreme/elevated | 0.4036 | Day | 202601 | Monitor | View readings
2026-01-14 15:41 | 2026-01-14 16:11 | 0.74417 | lower | 72.3758 | 2.2938 | 1.9678 | Persistent | 0.2832 | Day | 202601 | Review | View readings
2026-01-14 23:09 | 2026-01-15 04:08 | 5.2253 | lower | 72.095 | 2.2993 | 1.5405 | Confirmed/Materialized Shift | 0.5853 | Night | 202601 | Investigate | View readings
2026-01-15 04:52 | 2026-01-15 04:52 | 0.25083 | lower | 71.8124 | 2.1175 | 2.1175 | Extreme triggered | 0.2269 | Night | 202601 | Monitor | View readings
2026-01-15 08:30 | 2026-01-15 08:30 | 0.25083 | lower | 71.5298 | 2.2757 | 2.2757 | Extreme triggered | 0.2374 | Day | 202601 | Monitor | View readings
2026-01-15 10:14 | 2026-01-15 12:44 | 2.735 | upper | 73.7888 | 3.2199 | 2.3409 | Confirmed/Materialized Shift | 0.5757 | Day | 202601 | Investigate | View readings
2026-01-15 19:16 | 2026-01-16 09:48 | 14.7914 | lower | 66.164 | 2.9676 | 1.8145 | Confirmed/Materialized Shift | 0.5919 | Night | 202601 | Investigate | View readings
2026-01-16 17:18 | 2026-01-16 17:33 | 0.50167 | lower | 71.8124 | 2.1171 | 1.6956 | Extreme/elevated | 0.2554 | Day | 202601 | Monitor | View readings
2026-01-16 20:15 | 2026-01-16 23:59 | 3.9794 | lower | 70.3994 | 2.3413 | 1.6755 | Confirmed/Materialized Shift | 0.5235 | Night | 202601 | Investigate | View readings
2026-01-17 04:12 | 2026-01-17 05:57 | 1.9894 | lower | 69.5534 | 2.0144 | 1.4543 | Confirmed/Materialized Shift | 0.5054 | Night | 202601 | Investigate | View readings
2026-01-17 07:11 | 2026-01-17 07:30 | 0.56694 | lower | 69.2708 | 2.2757 | 1.9806 | Persistent | 0.3145 | Night | 202601 | Review | View readings
2026-01-17 09:00 | 2026-01-17 13:14 | 4.4792 | upper | 73.5062 | 3.3859 | 2.0479 | Confirmed/Materialized Shift | 0.5781 | Day | 202601 | Investigate | View readings
2026-01-17 18:16 | 2026-01-17 19:15 | 1.235 | upper | 73.7888 | 2.4713 | 1.8523 | Persistent | 0.4359 | Night | 202601 | Review | View readings
2026-01-17 23:28 | 2026-01-18 02:42 | 3.4864 | lower | 72.095 | 2.0548 | 1.4239 | Confirmed/Materialized Shift | 0.5092 | Night | 202601 | Investigate | View readings
2026-01-18 03:57 | 2026-01-18 06:11 | 2.4917 | lower | 71.5298 | 2.3975 | 1.5618 | Confirmed/Materialized Shift | 0.617 | Night | 202601 | Investigate | View readings
2026-01-18 09:16 | 2026-01-18 12:59 | 3.9772 | upper | 73.7888 | 3.0822 | 2.0959 | Confirmed/Materialized Shift | 0.6394 | Day | 202601 | Investigate | View readings
2026-01-18 15:16 | 2026-01-18 15:56 | 0.90972 | lower | 71.8124 | 2.981 | 2.2404 | Persistent | 0.3538 | Day | 202601 | Review | View readings
2026-01-18 21:27 | 2026-01-20 14:58 | 41.7719 | upper | 74.0714 | 2.3231 | 1.6571 | Confirmed/Materialized Shift | 0.5834 | Night | 202601 | Investigate | View readings
2026-01-21 02:43 | 2026-01-21 06:26 | 3.9797 | lower | 71.2472 | 2.3662 | 1.4771 | Confirmed/Materialized Shift | 0.582 | Night | 202601 | Investigate | View readings
2026-01-21 07:26 | 2026-01-21 08:15 | 1.0769 | lower | 70.9646 | 2.2993 | 1.777 | Persistent | 0.4066 | Day | 202601 | Review | View readings
2026-01-21 09:00 | 2026-01-21 14:17 | 5.5286 | upper | 74.0714 | 2.924 | 1.674 | Confirmed/Materialized Shift | 0.6492 | Day | 202601 | Investigate | View readings
2026-01-21 15:13 | 2026-01-21 15:43 | 0.74417 | lower | 72.095 | 2.0813 | 1.777 | Persistent | 0.3196 | Day | 202601 | Review | View readings
2026-01-22 00:58 | 2026-01-22 05:12 | 4.4806 | lower | 72.6584 | 4.2485 | 1.8716 | Confirmed/Materialized Shift | 0.6219 | Night | 202601 | Investigate | View readings
2026-01-22 07:26 | 2026-01-22 07:30 | 0.32444 | lower | 72.3758 | 2.1794 | 2.096 | Extreme/elevated | 0.277 | Day | 202601 | Monitor | View readings
2026-01-22 10:00 | 2026-01-22 11:40 | 1.9222 | upper | 74.0714 | 3.3751 | 2.154 | Confirmed/Materialized Shift | 0.5636 | Day | 202601 | Investigate | View readings
2026-01-22 16:27 | 2026-01-22 17:42 | 1.4964 | lower | 72.095 | 2.9654 | 2.3719 | Persistent | 0.4686 | Day | 202601 | Review | View readings
2026-01-23 06:12 | 2026-01-23 06:12 | 0.25083 | lower | 72.941 | 4.2485 | 4.2485 | Extreme triggered | 0.3689 | Night | 202601 | Monitor | View readings
2026-01-23 06:41 | 2026-01-23 08:16 | 1.8192 | lower | 72.941 | 2.924 | 1.7463 | Confirmed/Materialized Shift | 0.5653 | Night | 202601 | Investigate | View readings
2026-01-23 10:00 | 2026-01-23 10:57 | 1.2081 | upper | 74.0714 | 3.0887 | 2.4019 | Persistent | 0.5093 | Day | 202601 | Review | View readings
2026-01-23 17:27 | 2026-01-23 18:12 | 1.0033 | lower | 72.3758 | 2.6973 | 2.1287 | Persistent | 0.3174 | Day | 202601 | Review | View readings
2026-01-23 19:01 | 2026-01-23 20:44 | 1.9789 | upper | 73.7888 | 2.0899 | 1.5121 | Confirmed/Materialized Shift | 0.5049 | Night | 202601 | Investigate | View readings
2026-01-24 02:27 | 2026-01-24 04:12 | 1.9983 | lower | 73.5062 | 2.5628 | 1.62 | Confirmed/Materialized Shift | 0.5053 | Night | 202601 | Investigate | View readings
2026-01-24 06:41 | 2026-01-24 08:00 | 1.5706 | lower | 72.941 | 2.1222 | 1.5951 | Confirmed/Materialized Shift | 0.5047 | Night | 202601 | Investigate | View readings
2026-01-24 09:00 | 2026-01-24 09:08 | 0.39333 | upper | 74.0714 | 2.788 | 2.5603 | Persistent | 0.3784 | Day | 202601 | Review | View readings
2026-01-24 17:27 | 2026-01-24 17:31 | 0.305 | lower | 72.6584 | 2.3975 | 2.0614 | Persistent | 0.2897 | Day | 202601 | Review | View readings
2026-01-24 18:01 | 2026-01-24 21:14 | 3.4758 | upper | 74.9174 | 2.7087 | 1.7816 | Confirmed/Materialized Shift | 0.5795 | Night | 202601 | Investigate | View readings
2026-01-25 02:27 | 2026-01-25 02:27 | 0.25083 | lower | 74.6348 | 4.2485 | 4.2485 | Extreme triggered | 0.3689 | Night | 202601 | Monitor | View readings
2026-01-25 02:57 | 2026-01-25 07:41 | 4.9742 | lower | 73.7888 | 2.924 | 1.8036 | Confirmed/Materialized Shift | 0.6596 | Night | 202601 | Investigate | View readings
2026-01-25 08:45 | 2026-01-25 09:48 | 1.2953 | upper | 75.4826 | 2.6211 | 2.1447 | Confirmed/Materialized Shift | 0.5439 | Day | 202601 | Investigate | View readings
2026-01-25 15:14 | 2026-01-25 16:43 | 1.7392 | upper | 74.0714 | 2.8853 | 1.9116 | Confirmed/Materialized Shift | 0.4675 | Day | 202601 | Investigate | View readings
2026-01-25 18:16 | 2026-01-25 21:44 | 3.7183 | upper | 75.4826 | 2.3801 | 1.6001 | Confirmed/Materialized Shift | 0.5389 | Night | 202601 | Investigate | View readings
2026-01-26 01:58 | 2026-01-26 03:57 | 2.2403 | lower | 74.9174 | 2.2993 | 1.4883 | Confirmed/Materialized Shift | 0.4783 | Night | 202601 | Investigate | View readings
2026-01-26 07:11 | 2026-01-26 07:11 | 0.25083 | lower | 74.6348 | 4.2485 | 4.2485 | Extreme triggered | 0.3689 | Day | 202601 | Monitor | View readings
2026-01-26 07:30 | 2026-01-26 08:00 | 0.7525 | lower | 74.6348 | 2.924 | 2.3979 | Persistent | 0.3871 | Day | 202601 | Review | View readings
2026-01-26 08:48 | 2026-01-26 10:15 | 1.695 | lower | 71.8124 | 3.6206 | 2.405 | Confirmed/Materialized Shift | 0.5786 | Day | 202601 | Investigate | View readings
2026-01-26 19:16 | 2026-01-26 20:29 | 1.4775 | upper | 74.0714 | 2.8408 | 2.1469 | Persistent | 0.4698 | Night | 202601 | Review | View readings
2026-01-27 00:58 | 2026-01-27 08:16 | 7.5397 | lower | 68.7056 | 2.1595 | 1.6459 | Confirmed/Materialized Shift | 0.5303 | Night | 202601 | Investigate | View readings
2026-01-27 09:45 | 2026-01-27 15:32 | 6.0403 | upper | 74.0714 | 2.3202 | 1.5861 | Confirmed/Materialized Shift | 0.5314 | Day | 202601 | Investigate | View readings
2026-01-27 16:17 | 2026-01-27 16:28 | 0.42222 | lower | 71.8124 | 2.3312 | 1.8695 | Persistent | 0.3114 | Day | 202601 | Review | View readings
2026-01-27 20:29 | 2026-01-28 09:51 | 13.6136 | lower | 67.577 | 2.2722 | 1.6645 | Confirmed/Materialized Shift | 0.5271 | Night | 202601 | Investigate | View readings
2026-01-28 11:06 | 2026-01-28 16:34 | 5.7269 | upper | 73.2236 | 2.1298 | 1.513 | Confirmed/Materialized Shift | 0.5423 | Day | 202601 | Investigate | View readings
2026-01-28 19:30 | 2026-01-29 09:58 | 14.7308 | lower | 66.4466 | 3.2606 | 1.8378 | Confirmed/Materialized Shift | 0.6199 | Night | 202601 | Investigate | View readings
2026-01-29 19:30 | 2026-01-30 03:42 | 8.4603 | lower | 69.5534 | 2.8102 | 1.6714 | Confirmed/Materialized Shift | 0.6187 | Night | 202601 | Investigate | View readings
2026-01-30 09:30 | 2026-01-30 17:42 | 8.4614 | upper | 73.7888 | 2.8092 | 1.7617 | Confirmed/Materialized Shift | 0.6268 | Day | 202601 | Investigate | View readings
2026-01-30 20:15 | 2026-01-31 08:30 | 12.5056 | lower | 68.9882 | 2.936 | 1.5533 | Confirmed/Materialized Shift | 0.5488 | Night | 202601 | Investigate | View readings
2026-01-31 10:00 | 2026-01-31 15:43 | 5.9692 | upper | 71.5298 | 2.7681 | 1.6106 | Confirmed/Materialized Shift | 0.5591 | Day | 202601 | Investigate | View readings
2026-01-31 18:28 | 2026-02-01 12:32 | 18.325 | lower | 65.0354 | 3.0822 | 2.0116 | Confirmed/Materialized Shift | 0.6331 | Night | 202601 | Investigate | View readings
2026-02-02 11:31 | 2026-02-02 12:31 | 1.2456 | lower | 65.0354 | 3.2557 | 1.8971 | Persistent | 0.4707 | Day | 202602 | Review | View readings
2026-02-03 14:13 | 2026-02-03 17:07 | 3.1442 | upper | 70.682 | 2.5623 | 1.7811 | Confirmed/Materialized Shift | 0.4765 | Day | 202602 | Investigate | View readings
2026-02-04 08:30 | 2026-02-04 12:43 | 4.4817 | upper | 72.095 | 2.9247 | 2.0632 | Confirmed/Materialized Shift | 0.6384 | Day | 202602 | Investigate | View readings
2026-02-04 19:56 | 2026-02-05 08:15 | 12.57 | lower | 67.577 | 2.3877 | 1.5954 | Confirmed/Materialized Shift | 0.5397 | Night | 202602 | Investigate | View readings
2026-02-05 09:59 | 2026-02-05 17:25 | 7.6739 | upper | 72.095 | 2.9145 | 1.5608 | Confirmed/Materialized Shift | 0.5514 | Day | 202602 | Investigate | View readings
2026-02-05 19:01 | 2026-02-06 00:43 | 5.9586 | lower | 67.2944 | 2.788 | 1.8904 | Confirmed/Materialized Shift | 0.6392 | Night | 202602 | Investigate | View readings
2026-02-06 08:15 | 2026-02-06 13:44 | 5.7239 | upper | 72.6584 | 2.9639 | 2.0694 | Confirmed/Materialized Shift | 0.6833 | Day | 202602 | Investigate | View readings
2026-02-06 19:16 | 2026-02-07 07:13 | 12.2081 | lower | 67.8596 | 3.2606 | 1.6059 | Confirmed/Materialized Shift | 0.5579 | Night | 202602 | Investigate | View readings
2026-02-07 08:15 | 2026-02-07 13:14 | 5.2233 | upper | 73.2236 | 2.7817 | 1.9294 | Confirmed/Materialized Shift | 0.614 | Day | 202602 | Investigate | View readings
2026-02-08 08:30 | 2026-02-08 13:59 | 5.7233 | upper | 73.2236 | 3.1811 | 2.0074 | Confirmed/Materialized Shift | 0.6042 | Day | 202602 | Investigate | View readings
2026-02-08 20:44 | 2026-02-09 07:45 | 11.2728 | lower | 67.577 | 2.0503 | 1.5212 | Confirmed/Materialized Shift | 0.5148 | Night | 202602 | Investigate | View readings
2026-02-09 08:45 | 2026-02-09 12:44 | 4.2286 | upper | 73.2236 | 2.5458 | 1.972 | Confirmed/Materialized Shift | 0.5904 | Day | 202602 | Investigate | View readings
2026-02-09 17:27 | 2026-02-09 19:30 | 2.2908 | upper | 73.5062 | 3.2341 | 1.9126 | Confirmed/Materialized Shift | 0.5414 | Day | 202602 | Investigate | View readings
2026-02-09 21:44 | 2026-02-10 07:45 | 10.2725 | lower | 68.423 | 2.3629 | 1.5506 | Confirmed/Materialized Shift | 0.5479 | Night | 202602 | Investigate | View readings
2026-02-10 09:15 | 2026-02-10 12:44 | 3.7264 | upper | 73.2236 | 2.6307 | 2.0435 | Confirmed/Materialized Shift | 0.5986 | Day | 202602 | Investigate | View readings
2026-02-10 18:27 | 2026-02-10 18:46 | 0.56333 | lower | 72.6584 | 2.4597 | 2.0235 | Persistent | 0.3661 | Night | 202602 | Review | View readings
2026-02-10 21:44 | 2026-02-11 08:27 | 10.9586 | lower | 69.5534 | 2.1141 | 1.5362 | Confirmed/Materialized Shift | 0.5278 | Night | 202602 | Investigate | View readings
2026-02-11 09:11 | 2026-02-11 12:25 | 3.4839 | upper | 73.2236 | 2.9881 | 2.0245 | Confirmed/Materialized Shift | 0.6665 | Day | 202602 | Investigate | View readings
2026-02-11 17:23 | 2026-02-11 17:23 | 0.25083 | lower | 72.3758 | 2.6745 | 2.6745 | Extreme triggered | 0.2926 | Day | 202602 | Monitor | View readings
2026-02-11 18:08 | 2026-02-11 18:08 | 0.25083 | lower | 72.3758 | 2.0571 | 2.0571 | Extreme triggered | 0.2514 | Day | 202602 | Monitor | View readings
2026-02-11 19:23 | 2026-02-11 19:52 | 0.74222 | upper | 73.5062 | 2.0673 | 1.812 | Persistent | 0.3053 | Night | 202602 | Review | View readings
2026-02-12 02:35 | 2026-02-12 07:49 | 5.4828 | lower | 69.5534 | 2.0682 | 1.5271 | Confirmed/Materialized Shift | 0.5168 | Night | 202602 | Investigate | View readings
2026-02-12 09:19 | 2026-02-12 12:47 | 3.7264 | upper | 73.5062 | 2.9369 | 2.0188 | Confirmed/Materialized Shift | 0.6388 | Day | 202602 | Investigate | View readings
2026-02-12 17:16 | 2026-02-12 18:46 | 1.7453 | lower | 72.6584 | 2.5868 | 1.9928 | Confirmed/Materialized Shift | 0.56 | Day | 202602 | Investigate | View readings
2026-02-13 05:12 | 2026-02-13 07:30 | 2.5567 | lower | 70.3994 | 2.1007 | 1.7056 | Confirmed/Materialized Shift | 0.5228 | Night | 202602 | Investigate | View readings
2026-02-13 09:00 | 2026-02-13 13:07 | 4.3619 | upper | 74.0714 | 2.5805 | 1.7481 | Confirmed/Materialized Shift | 0.5698 | Day | 202602 | Investigate | View readings
2026-02-13 14:43 | 2026-02-13 15:43 | 1.2456 | lower | 72.3758 | 2.0085 | 1.6502 | Persistent | 0.4035 | Day | 202602 | Review | View readings
2026-02-13 23:56 | 2026-02-14 08:16 | 8.5844 | lower | 70.3994 | 2.1714 | 1.5557 | Confirmed/Materialized Shift | 0.5469 | Night | 202602 | Investigate | View readings
2026-02-14 09:00 | 2026-02-14 11:44 | 2.9825 | upper | 73.5062 | 2.7262 | 2.0686 | Confirmed/Materialized Shift | 0.636 | Day | 202602 | Investigate | View readings
2026-02-14 14:54 | 2026-02-14 14:57 | 0.30111 | upper | 74.0714 | 2.2586 | 1.7799 | Extreme/elevated | 0.2077 | Day | 202602 | Monitor | View readings
2026-02-14 16:43 | 2026-02-14 16:58 | 0.50194 | lower | 72.3758 | 2.0571 | 1.6906 | Extreme/elevated | 0.2026 | Day | 202602 | Monitor | View readings
2026-02-14 19:12 | 2026-02-14 19:57 | 0.99472 | upper | 74.0714 | 2.0286 | 1.4814 | Persistent | 0.2955 | Night | 202602 | Review | View readings
2026-02-14 22:41 | 2026-02-15 00:40 | 2.2403 | lower | 72.941 | 2.1222 | 1.5461 | Confirmed/Materialized Shift | 0.5547 | Night | 202602 | Investigate | View readings
2026-02-15 03:10 | 2026-02-15 04:39 | 1.7389 | lower | 72.3758 | 2.2584 | 1.7744 | Confirmed/Materialized Shift | 0.5409 | Night | 202602 | Investigate | View readings
2026-02-15 07:08 | 2026-02-15 07:08 | 0.25083 | lower | 72.095 | 2.0244 | 2.0244 | Extreme triggered | 0.1921 | Day | 202602 | Monitor | View readings
2026-02-15 08:30 | 2026-02-15 10:00 | 1.7425 | upper | 73.5062 | 2.5552 | 2.0848 | Confirmed/Materialized Shift | 0.5157 | Day | 202602 | Investigate | View readings
2026-02-15 18:28 | 2026-02-15 19:57 | 1.7281 | upper | 73.7888 | 2.09 | 1.4832 | Confirmed/Materialized Shift | 0.4701 | Night | 202602 | Investigate | View readings
2026-02-15 22:56 | 2026-02-16 02:25 | 3.7372 | lower | 72.941 | 2.924 | 1.9001 | Confirmed/Materialized Shift | 0.6354 | Night | 202602 | Investigate | View readings
2026-02-16 05:54 | 2026-02-16 07:45 | 2.1142 | lower | 72.6584 | 2.2722 | 1.5384 | Confirmed/Materialized Shift | 0.5103 | Night | 202602 | Investigate | View readings
2026-02-16 09:00 | 2026-02-16 11:15 | 2.5042 | upper | 74.0714 | 2.924 | 1.8503 | Confirmed/Materialized Shift | 0.6851 | Day | 202602 | Investigate | View readings
2026-02-16 16:13 | 2026-02-16 16:42 | 0.74444 | lower | 72.3758 | 2.1909 | 1.937 | Persistent | 0.2854 | Day | 202602 | Review | View readings
2026-02-17 00:28 | 2026-02-17 08:00 | 7.7906 | lower | 71.5298 | 2.4597 | 1.6004 | Confirmed/Materialized Shift | 0.5983 | Night | 202602 | Investigate | View readings
2026-02-17 09:30 | 2026-02-17 12:14 | 2.9933 | upper | 73.7888 | 2.9583 | 1.8692 | Confirmed/Materialized Shift | 0.5435 | Day | 202602 | Investigate | View readings
2026-02-18 00:40 | 2026-02-18 07:45 | 7.34 | lower | 71.5298 | 2.351 | 1.5983 | Confirmed/Materialized Shift | 0.596 | Night | 202602 | Investigate | View readings
2026-02-18 09:00 | 2026-02-18 12:59 | 4.2289 | upper | 73.7888 | 2.443 | 1.5571 | Confirmed/Materialized Shift | 0.5048 | Day | 202602 | Investigate | View readings
2026-02-18 14:13 | 2026-02-18 15:43 | 1.7392 | lower | 72.3758 | 2.2584 | 1.7495 | Confirmed/Materialized Shift | 0.4953 | Day | 202602 | Investigate | View readings
2026-02-19 01:55 | 2026-02-19 07:30 | 5.8472 | lower | 72.095 | 2.5686 | 1.7258 | Confirmed/Materialized Shift | 0.5377 | Night | 202602 | Investigate | View readings
2026-02-19 09:15 | 2026-02-19 11:35 | 2.5867 | upper | 74.0714 | 2.1585 | 1.6863 | Confirmed/Materialized Shift | 0.5334 | Day | 202602 | Investigate | View readings
2026-02-19 16:57 | 2026-02-19 18:42 | 2.0003 | lower | 72.3758 | 2.9459 | 2.2399 | Confirmed/Materialized Shift | 0.6698 | Day | 202602 | Investigate | View readings
2026-02-20 01:55 | 2026-02-20 05:09 | 3.4861 | lower | 73.2236 | 2.4878 | 1.781 | Confirmed/Materialized Shift | 0.6033 | Night | 202602 | Investigate | View readings
2026-02-20 08:30 | 2026-02-20 09:19 | 1.0678 | upper | 74.0714 | 2.6647 | 2.2339 | Confirmed/Materialized Shift | 0.6098 | Day | 202602 | Investigate | View readings
2026-02-20 17:57 | 2026-02-20 18:42 | 1.0053 | lower | 72.941 | 2.6647 | 2.1339 | Persistent | 0.4475 | Day | 202602 | Review | View readings
2026-02-21 01:55 | 2026-02-21 07:45 | 6.0981 | lower | 72.941 | 2.3629 | 1.5012 | Confirmed/Materialized Shift | 0.5237 | Night | 202602 | Investigate | View readings
2026-02-21 08:45 | 2026-02-21 09:12 | 0.71167 | upper | 74.0714 | 2.6394 | 2.2866 | Persistent | 0.4636 | Day | 202602 | Review | View readings
2026-02-21 17:12 | 2026-02-21 17:46 | 0.80639 | lower | 72.941 | 2.9429 | 2.216 | Persistent | 0.4189 | Day | 202602 | Review | View readings
2026-02-22 00:43 | 2026-02-22 07:26 | 6.9642 | lower | 72.941 | 4.2485 | 1.8999 | Confirmed/Materialized Shift | 0.6533 | Night | 202602 | Investigate | View readings
2026-02-22 11:00 | 2026-02-22 11:29 | 0.74417 | upper | 74.0714 | 2.7587 | 1.962 | Persistent | 0.3602 | Day | 202602 | Review | View readings
2026-02-22 15:14 | 2026-02-22 16:13 | 1.2467 | lower | 72.095 | 2.66 | 2.3281 | Persistent | 0.4769 | Day | 202602 | Review | View readings
2026-02-22 18:30 | 2026-02-22 20:14 | 1.9981 | upper | 74.0714 | 2.0966 | 1.4984 | Confirmed/Materialized Shift | 0.5031 | Night | 202602 | Investigate | View readings
2026-02-23 00:28 | 2026-02-23 07:45 | 7.5442 | lower | 68.7056 | 2.1141 | 1.6471 | Confirmed/Materialized Shift | 0.5314 | Night | 202602 | Investigate | View readings
2026-02-23 09:44 | 2026-02-23 17:42 | 8.2111 | upper | 73.5062 | 2.1227 | 1.4934 | Confirmed/Materialized Shift | 0.5339 | Day | 202602 | Investigate | View readings
2026-02-23 19:27 | 2026-02-24 05:38 | 10.4394 | lower | 67.577 | 3.188 | 1.6669 | Confirmed/Materialized Shift | 0.5739 | Night | 202602 | Investigate | View readings
2026-02-24 08:30 | 2026-02-24 13:43 | 5.4808 | upper | 72.941 | 2.752 | 1.9221 | Confirmed/Materialized Shift | 0.5551 | Day | 202602 | Investigate | View readings
2026-02-24 19:27 | 2026-02-25 05:24 | 10.1981 | lower | 67.2944 | 3.1509 | 1.7285 | Confirmed/Materialized Shift | 0.6279 | Night | 202602 | Investigate | View readings
2026-02-25 08:00 | 2026-02-25 11:14 | 3.4794 | upper | 72.3758 | 2.5785 | 2.2424 | Confirmed/Materialized Shift | 0.629 | Day | 202602 | Investigate | View readings

## Daily overview
Daily overview
One row per day with data. All figures are formulas over the Data tab.
Date | Readings | Mean value | Min value | Max value | Extreme readings | Extreme share | Persistent periods | Confirmed shift periods | Abnormal changes | Material changes | Max materiality score
2025-12-01 | 51 | 73.2678 | 72.095 | 74.6348 | 4 | 7.843% | 3 | 0 | 2 | 1 | 0.4351
2025-12-02 | 101 | 73.4808 | 72.095 | 74.9174 | 11 | 10.89% | 8 | 20 | 8 | 5 | 0.7019
2025-12-03 | 101 | 73.4642 | 72.095 | 74.3522 | 9 | 8.911% | 7 | 4 | 8 | 5 | 0.519
2025-12-04 | 103 | 73.2429 | 72.095 | 74.0714 | 15 | 14.56% | 12 | 25 | 6 | 4 | 0.5588
2025-12-05 | 103 | 73.3389 | 72.095 | 74.3522 | 15 | 14.56% | 15 | 18 | 10 | 8 | 0.6077
2025-12-06 | 102 | 73.6749 | 71.8124 | 75.2 | 21 | 20.59% | 20 | 15 | 10 | 7 | 0.628
2025-12-07 | 100 | 74.2343 | 71.8124 | 75.4826 | 15 | 15% | 14 | 13 | 8 | 5 | 0.6229
2025-12-08 | 106 | 73.9642 | 71.8124 | 75.2 | 10 | 9.434% | 10 | 7 | 8 | 6 | 0.6195
2025-12-09 | 99 | 73.6289 | 73.2236 | 74.0714 | 10 | 10.1% | 12 | 7 | 9 | 5 | 0.5526
2025-12-10 | 102 | 73.3345 | 72.095 | 74.0714 | 16 | 15.69% | 16 | 17 | 7 | 4 | 0.6077
2025-12-11 | 102 | 72.5343 | 70.9646 | 74.0714 | 15 | 14.71% | 13 | 32 | 8 | 3 | 0.6024
2025-12-12 | 103 | 72.0666 | 69.836 | 73.7888 | 12 | 11.65% | 9 | 39 | 4 | 2 | 0.6048
2025-12-13 | 104 | 72.4771 | 70.3994 | 74.0714 | 10 | 9.615% | 11 | 16 | 5 | 1 | 0.557
2025-12-14 | 101 | 73.4978 | 72.3758 | 74.0714 | 11 | 10.89% | 8 | 10 | 8 | 5 | 0.6541
2025-12-15 | 102 | 73.1932 | 71.8124 | 74.0714 | 15 | 14.71% | 12 | 12 | 10 | 7 | 0.7004
2025-12-16 | 102 | 72.7836 | 71.5298 | 73.7888 | 13 | 12.75% | 13 | 20 | 9 | 5 | 0.6088
2025-12-17 | 102 | 73.243 | 72.3758 | 74.0714 | 10 | 9.804% | 20 | 14 | 7 | 4 | 0.6211
2025-12-18 | 102 | 73.459 | 72.095 | 74.6348 | 14 | 13.73% | 15 | 4 | 9 | 6 | 0.6508
2025-12-19 | 101 | 73.8132 | 72.095 | 74.6348 | 15 | 14.85% | 13 | 6 | 10 | 8 | 0.5796
2025-12-20 | 102 | 73.2625 | 72.095 | 74.0714 | 7 | 6.863% | 12 | 21 | 10 | 4 | 0.5656
2025-12-21 | 102 | 73.5058 | 72.3758 | 74.9174 | 12 | 11.76% | 18 | 20 | 10 | 7 | 0.6219
2025-12-22 | 102 | 73.6776 | 72.095 | 74.9174 | 16 | 15.69% | 12 | 12 | 7 | 3 | 0.6062
2025-12-23 | 101 | 73.3855 | 71.8124 | 74.6348 | 9 | 8.911% | 8 | 3 | 4 | 1 | 0.5437
2025-12-24 | 103 | 72.818 | 71.8124 | 74.0714 | 8 | 7.767% | 8 | 25 | 10 | 6 | 0.6182
2025-12-25 | 102 | 72.9274 | 71.8124 | 74.0714 | 15 | 14.71% | 12 | 34 | 6 | 2 | 0.596
2025-12-26 | 102 | 72.8638 | 71.5298 | 74.0714 | 15 | 14.71% | 14 | 36 | 8 | 6 | 0.5913
2025-12-27 | 102 | 72.8002 | 71.5298 | 74.0714 | 12 | 11.76% | 18 | 27 | 6 | 4 | 0.5627
2025-12-28 | 102 | 72.8086 | 71.5298 | 74.0714 | 13 | 12.75% | 10 | 35 | 7 | 2 | 0.5986
2025-12-29 | 102 | 72.8943 | 71.8124 | 74.0714 | 12 | 11.76% | 12 | 32 | 4 | 2 | 0.5941
2025-12-30 | 99 | 72.7643 | 71.2472 | 73.5062 | 11 | 11.11% | 15 | 20 | 8 | 5 | 0.628
2025-12-31 | 26 | 69.4007 | 67.8596 | 70.9646 | 1 | 3.846% | 0 | 26 | 0 | 0 | 0.5334
2026-01-02 | 49 | 72.3247 | 70.3994 | 73.5062 | 3 | 6.122% | 0 | 13 | 1 | 0 | 0.6185
2026-01-03 | 109 | 71.4155 | 68.423 | 74.0714 | 9 | 8.257% | 4 | 8 | 9 | 7 | 0.6791
2026-01-04 | 103 | 72.5712 | 71.5298 | 74.0714 | 16 | 15.53% | 19 | 18 | 10 | 6 | 0.5933
2026-01-05 | 102 | 72.5789 | 71.5298 | 74.0714 | 11 | 10.78% | 11 | 25 | 9 | 7 | 0.5767
2026-01-06 | 110 | 72.7643 | 71.5298 | 74.0714 | 10 | 9.091% | 10 | 29 | 5 | 2 | 0.5517
2026-01-07 | 101 | 72.9974 | 71.8124 | 74.0714 | 14 | 13.86% | 14 | 24 | 9 | 5 | 0.6694
2026-01-08 | 102 | 72.9884 | 71.8124 | 74.0714 | 12 | 11.76% | 15 | 33 | 4 | 2 | 0.5593
2026-01-09 | 102 | 73.2181 | 72.3758 | 74.0714 | 16 | 15.69% | 16 | 13 | 10 | 7 | 0.5893
2026-01-10 | 103 | 73.6266 | 72.6584 | 74.6348 | 12 | 11.65% | 10 | 6 | 7 | 3 | 0.5413
2026-01-11 | 102 | 73.6609 | 72.3758 | 75.2 | 11 | 10.78% | 10 | 34 | 5 | 1 | 0.5941
2026-01-12 | 102 | 73.5642 | 71.8124 | 74.9174 | 15 | 14.71% | 9 | 10 | 12 | 8 | 0.5917
2026-01-13 | 104 | 73.3975 | 71.8124 | 74.0714 | 7 | 6.731% | 5 | 4 | 7 | 4 | 0.688
2026-01-14 | 103 | 73.1715 | 72.3758 | 73.7888 | 10 | 9.709% | 15 | 2 | 13 | 8 | 0.5367
2026-01-15 | 103 | 72.1573 | 69.2708 | 73.7888 | 18 | 17.48% | 10 | 34 | 10 | 7 | 0.5853
2026-01-16 | 83 | 70.7741 | 66.164 | 72.941 | 6 | 7.229% | 4 | 26 | 4 | 2 | 0.5919
2026-01-17 | 100 | 71.7441 | 69.2708 | 73.7888 | 13 | 13% | 13 | 14 | 9 | 5 | 0.5781
2026-01-18 | 102 | 72.3684 | 70.9646 | 74.0714 | 16 | 15.69% | 17 | 28 | 8 | 5 | 0.6394
2026-01-19 | 26 | 69.3139 | 67.577 | 70.9646 | 0 | 0% | 0 | 26 | 0 | 0 | 0.5253
2026-01-20 | 55 | 72.7564 | 70.9646 | 74.0714 | 4 | 7.273% | 0 | 16 | 1 | 0 | 0.5834
2026-01-21 | 102 | 72.4874 | 70.9646 | 74.0714 | 10 | 9.804% | 12 | 28 | 9 | 6 | 0.6492
2026-01-22 | 102 | 72.9965 | 72.095 | 74.0714 | 18 | 17.65% | 12 | 15 | 9 | 4 | 0.6219
2026-01-23 | 102 | 73.3372 | 72.3758 | 74.0714 | 12 | 11.76% | 14 | 4 | 6 | 3 | 0.5653
2026-01-24 | 102 | 73.5889 | 72.3758 | 74.9174 | 13 | 12.75% | 14 | 11 | 10 | 7 | 0.5795
2026-01-25 | 100 | 74.3135 | 72.941 | 75.4826 | 18 | 18% | 16 | 24 | 8 | 5 | 0.6596
2026-01-26 | 101 | 73.8498 | 71.8124 | 75.2 | 12 | 11.88% | 13 | 5 | 9 | 7 | 0.5786
2026-01-27 | 103 | 71.5705 | 68.7056 | 74.0714 | 14 | 13.59% | 13 | 54 | 3 | 1 | 0.5314
2026-01-28 | 77 | 71.0381 | 67.577 | 73.2236 | 10 | 12.99% | 8 | 49 | 5 | 3 | 0.6199
2026-01-29 | 72 | 71.2471 | 66.4466 | 73.5062 | 8 | 11.11% | 4 | 27 | 5 | 3 | 0.6187
2026-01-30 | 100 | 71.1455 | 69.2708 | 73.7888 | 9 | 9% | 8 | 53 | 7 | 4 | 0.6268
2026-01-31 | 93 | 70.2482 | 68.1404 | 71.8124 | 15 | 16.13% | 8 | 65 | 3 | 1 | 0.5591
2026-02-01 | 29 | 66.7979 | 65.0354 | 67.8596 | 2 | 6.897% | 0 | 7 | 2 | 0 | 0.6331
2026-02-02 | 32 | 67.1881 | 65.0354 | 68.423 | 2 | 6.25% | 4 | 0 | 2 | 1 | 0.4707
2026-02-03 | 43 | 69.1325 | 67.0118 | 70.682 | 3 | 6.977% | 4 | 2 | 1 | 1 | 0.4765
2026-02-04 | 99 | 70.1491 | 67.2944 | 72.941 | 14 | 14.14% | 8 | 24 | 6 | 2 | 0.6384
2026-02-05 | 102 | 69.7496 | 67.577 | 72.095 | 14 | 13.73% | 8 | 76 | 7 | 3 | 0.6392
2026-02-06 | 98 | 69.6253 | 67.2944 | 72.6584 | 20 | 20.41% | 8 | 33 | 8 | 5 | 0.6833
2026-02-07 | 97 | 70.3504 | 67.8596 | 73.2236 | 9 | 9.278% | 4 | 46 | 6 | 4 | 0.614
2026-02-08 | 100 | 70.6934 | 68.1404 | 73.5062 | 13 | 13% | 8 | 26 | 6 | 1 | 0.6042
2026-02-09 | 100 | 70.9054 | 67.577 | 73.5062 | 16 | 16% | 12 | 52 | 5 | 3 | 0.5904
2026-02-10 | 100 | 71.4079 | 68.423 | 73.5062 | 12 | 12% | 10 | 45 | 5 | 1 | 0.5986
2026-02-11 | 99 | 71.8003 | 69.5534 | 73.5062 | 11 | 11.11% | 5 | 43 | 7 | 5 | 0.6665
2026-02-12 | 100 | 71.9077 | 69.5534 | 73.5062 | 13 | 13% | 12 | 28 | 8 | 6 | 0.6388
2026-02-13 | 102 | 72.2629 | 70.3994 | 74.0714 | 11 | 10.78% | 11 | 18 | 6 | 1 | 0.5698
2026-02-14 | 102 | 72.4846 | 70.3994 | 74.0714 | 13 | 12.75% | 14 | 35 | 3 | 2 | 0.636
2026-02-15 | 102 | 73.099 | 72.095 | 74.0714 | 13 | 12.75% | 15 | 7 | 6 | 1 | 0.5547
2026-02-16 | 101 | 73.0277 | 72.3758 | 74.0714 | 8 | 7.921% | 10 | 17 | 12 | 9 | 0.6851
2026-02-17 | 102 | 72.7254 | 71.5298 | 74.0714 | 9 | 8.824% | 8 | 32 | 9 | 6 | 0.5983
2026-02-18 | 102 | 72.8583 | 71.5298 | 74.0714 | 10 | 9.804% | 12 | 36 | 8 | 5 | 0.596
2026-02-19 | 102 | 73.3842 | 72.095 | 74.3522 | 13 | 12.75% | 12 | 28 | 7 | 5 | 0.6698
2026-02-20 | 102 | 73.6417 | 72.941 | 74.6348 | 13 | 12.75% | 12 | 9 | 8 | 5 | 0.6098
2026-02-21 | 102 | 73.7883 | 72.6584 | 74.9174 | 8 | 7.843% | 10 | 19 | 6 | 4 | 0.5237
2026-02-22 | 103 | 73.5253 | 72.095 | 74.9174 | 17 | 16.5% | 15 | 24 | 6 | 3 | 0.6533
2026-02-23 | 99 | 71.4753 | 68.7056 | 73.5062 | 14 | 14.14% | 12 | 65 | 4 | 2 | 0.5739
2026-02-24 | 99 | 70.4485 | 67.2944 | 73.5062 | 22 | 22.22% | 8 | 53 | 7 | 3 | 0.6279
2026-02-25 | 47 | 68.5438 | 67.2944 | 72.3758 | 13 | 27.66% | 4 | 31 | 4 | 3 | 0.629

## Monthly metrics
Monthly metrics
All figures are formulas over the Data tab. The month tabs and the Summary read from this table.
Reading interval (minutes) |  | 15.05 | Median spacing of the timestamps in the data (15.05 min). Used to turn readings into hours.
Month | Month key | Readings | Days with data | Mean value | Min value | Max value | Extreme readings | Extreme share | Upper extremes | Lower extremes | Persistent periods | Confirmed shift periods | Sustained deviation (h) | Confirmed share | Abnormal changes | Material changes | Material changes per day | Mean materiality score | Max materiality score | Max ¦Z¦ | Events | Data gap hours | Rank: extreme share | Rank: sustained (h) | Rank: material changes/day | Rank: mean materiality
Dec 2025 | 202512 | 3032 | 31 | 73.1788 | 67.8596 | 75.4826 | 372 | 12.27% | 137 | 235 | 370 | 570 | 235.7833 | 18.8% | 226 | 133 | 4.2903 | 0.21424 | 0.7019 | 4.2485 | 122 | 54.8228 | 2 | 3 | 1 | 3
Jan 2026 | 202601 | 2815 | 30 | 72.564 | 66.164 | 75.4826 | 342 | 12.15% | 171 | 171 | 304 | 698 | 251.335 | 24.8% | 207 | 123 | 4.1 | 0.23506 | 0.688 | 4.2485 | 102 | 60.7139 | 3 | 1 | 2 | 2
Feb 2026 | 202602 | 2264 | 25 | 71.6342 | 65.0354 | 74.9174 | 293 | 12.94% | 170 | 123 | 226 | 756 | 246.3183 | 33.39% | 149 | 81 | 3.24 | 0.26953 | 0.6851 | 4.2485 | 65 | 40.3539 | 1 | 2 | 3 | 1
All |  | 8111 | 86 | 72.5343 | 65.0354 | 75.4826 | 1007 | 12.42% | 478 | 529 | 900 | 2024 | 733.4367 | 24.95% | 582 | 337 | 3.9186 | 0.2369 | 0.7019 | 4.2485 | 289 | 155.8906
Rank 1 = the month with the most issues for that measure. Gap hours are assigned to the month in which the gap starts.

## Column descriptor
Column descriptor: Jensen_Beach_Results_Analysis
Meaning of every column in the results file (Data tab) and the parameters that drive it. Full detail: Statistical calc parameters manual.
Column | Data tab column | Meaning | Driven by | Step
Timestamp | A | Time of the reading | — | Input
Value | B | The reading (°F) | — | Input
AbnormalChangeFlag | C | Unusually fast change: ¦ROC_ZScore¦ ≥ ROC_K | ROC_K | Change
ConfirmedShiftFlag | D | Reading is in a Confirmed/Materialized Shift | N_M, K_M | Materiality
DeltaLower | E | LowerLimit − Value (positive = below the band) | limits | Extreme
DeltaLower_pct | F | DeltaLower as % of LowerLimit | limits | Extreme
DeltaUpper | G | Value − UpperLimit (positive = above the band) | limits | Extreme
DeltaUpper_pct | H | DeltaUpper as % of UpperLimit | limits | Extreme
DeltaX | I | Change from the previous reading | — | Change
EventEndTime | J | End of the event this reading belongs to | K_P, N_EXIT | Persistence
EventStartTime | K | Start of the event this reading belongs to | K_E | Persistence
ExtremeDirection | L | upper / lower / none | Method, K_E | Extreme
ExtremeFlag | M | Reading outside the normal range | Method, Window, K_E, p, K_IQR | Extreme
FrequencyCount | N | Abnormal changes in the last frequency window | Frequency window | Change
LowerLimit | O | Lower edge of the normal range: MA − K_E·σ | Method, Window, K_E | Extreme
MaterialChangeFlag | P | Abnormal change that recurs (FrequencyCount ≥ min) | Min recurrences | Change
MaterialExtremeFlag | Q | Extreme that also lasted N_P readings | N_P | Materiality
MaterialityScore | R | 0–1 ranking: Wm·magnitude + Wd·duration + Wf·frequency | Weights, K_E, N_M | Materiality
MeanZ_event | S | Average ¦Z¦ over the event so far | — | Persistence
MovingAverage | T | Baseline (rolling mean over Window) | Method, Window, α | Extreme
PersistenceCount | U | Readings in the current event | K_P, N_EXIT | Persistence
ROC | V | Rate of change: (x(t) − x(t−h)) / h | ROC horizon | Change
ROC_MeanBaseline | W | Rolling mean of ROC | ROC baseline window | Change
ROC_StdDev | X | Rolling std of ROC | ROC baseline window | Change
ROC_ZScore | Y | (ROC − mean) / std | ROC baseline window | Change
RollingStdDev | Z | σ used for the limits | Method, Window | Extreme
State | AA | Normal, Extreme triggered, Extreme/elevated, Persistent, Confirmed/Materialized Shift, Persistence ends | K_E, K_P, N_P, N_M, K_M, N_EXIT | Persistence
UpperLimit | AB | Upper edge of the normal range: MA + K_E·σ | Method, Window, K_E | Extreme
ZScore | AC | (Value − MA) / σ | Method, Window | Extreme
Day/Night | AD | Day or night category of the reading | time of day | Input
MonthKey | AE | Helper added in this report: YYYYMM | — | Report
Date | AF | Helper added in this report: date of the reading | — | Report
AbsZ | AG | Helper added in this report: ¦ZScore¦ (the three helper columns are stored as values) | — | Report
Settings used for this run (inferred from the results)
Parameter | Value | How we know
Method | Rolling Mean/Std (Bollinger) | MovingAverage equals the 20-reading rolling mean
Window (W) | 20 | as above
K_E | 2 | smallest flagged ¦Z¦ = 2.001
ROC_K | 2 | smallest flagged ¦ROC_ZScore¦ = 2.002
K_P / N_P / N_M / K_M / N_EXIT | 1.0 / 3 / 7 / 1.2 / 1 | app defaults
ROC h / Frequency window / Min recurrences | 1 / 10 / 2 | app defaults
Weights (magnitude / duration / frequency) | 0.4 / 0.4 / 0.2 | app defaults

## Data
Timestamp | Value | AbnormalChangeFlag | ConfirmedShiftFlag | DeltaLower | DeltaLower_pct | DeltaUpper | DeltaUpper_pct | DeltaX | EventEndTime | EventStartTime | ExtremeDirection | ExtremeFlag | FrequencyCount | LowerLimit | MaterialChangeFlag | MaterialExtremeFlag | MaterialityScore | MeanZ_event | MovingAverage | PersistenceCount | ROC | ROC_MeanBaseline | ROC_StdDev | ROC_ZScore | RollingStdDev | State | UpperLimit | ZScore | Day/Night | MonthKey | Date | AbsZ
2025-12-01 11:44 | 72.3758 | FALSE | FALSE | [7 empty] | none | FALSE | 0 |  | FALSE | FALSE | 0 |  |  | 0 | [5 empty] | Normal |  |  | Day | 202512 | 2025-12-01
2025-12-01 11:59 | 72.095 | FALSE | FALSE | -0.25671 | -0.35735 | -0.53751 | -0.74004 | -0.2808 |  |  | none | FALSE | 0 | 71.8383 | FALSE | FALSE | 0.0471 |  | 72.2354 | 0 | -0.2808 |  |  |  | 0.19856 | Normal | 72.6325 | -0.70711 | Day | 202512 | 2025-12-01 | 0.70711
2025-12-01 12:14 | 72.095 | FALSE | FALSE | -0.23064 | -0.32094 | -0.41784 | -0.57623 | 0 |  |  | none | FALSE | 0 | 71.8644 | FALSE | FALSE | 0.0385 |  | 72.1886 | 0 | 0 | -0.1404 | 0.19856 | 0.70711 | 0.16212 | Normal | 72.5128 | -0.57735 | Day | 202512 | 2025-12-01 | 0.57735
2025-12-01 12:29 | 72.3758 | FALSE | FALSE | -0.46464 | -0.64613 | -0.18384 | -0.25336 | 0.2808 |  |  | none | FALSE | 0 | 71.9112 | FALSE | FALSE | 0.0577 |  | 72.2354 | 0 | 0.2808 | 0 | 0.2808 | 1 | 0.16212 | Normal | 72.5596 | 0.86603 | Day | 202512 | 2025-12-01 | 0.86603
2025-12-01 12:43 | 72.6584 | FALSE | FALSE | -0.80956 | -1.1268 | -0.13276 | -0.18238 | 0.2826 |  |  | none | FALSE | 0 | 71.8488 | FALSE | FALSE | 0.0958 |  | 72.32 | 0 | 0.2826 | 0.07065 | 0.26932 | 0.78699 | 0.23558 | Normal | 72.7912 | 1.4365 | Day | 202512 | 2025-12-01 | 1.4365
2025-12-01 12:58 | 72.3758 | FALSE | FALSE | -0.47037 | -0.65416 | -0.37737 | -0.5187 | -0.2826 |  |  | none | FALSE | 0 | 71.9054 | FALSE | FALSE | 0.0146 |  | 72.3293 | 0 | -0.2826 | 0 | 0.2817 | -1.0032 | 0.21194 | Normal | 72.7532 | 0.2194 | Day | 202512 | 2025-12-01 | 0.2194
2025-12-01 13:14 | 72.6584 | FALSE | FALSE | -0.7421 | -1.0319 | -0.17793 | -0.24429 | 0.2826 |  |  | none | FALSE | 0 | 71.9163 | FALSE | FALSE | 0.0818 |  | 72.3763 | 0 | 0.2826 | 0.0471 | 0.27712 | 0.84981 | 0.23001 | Normal | 72.8363 | 1.2264 | Day | 202512 | 2025-12-01 | 1.2264
2025-12-01 13:29 | 72.6584 | FALSE | FALSE | -0.71711 | -0.9968 | -0.22346 | -0.30661 | 0 |  |  | none | FALSE | 0 | 71.9413 | FALSE | FALSE | 0.07 |  | 72.4116 | 0 | 0 | 0.040371 | 0.2536 | -0.15919 | 0.23514 | Normal | 72.8819 | 1.0497 | Day | 202512 | 2025-12-01 | 1.0497
2025-12-01 13:43 | 72.6584 | FALSE | FALSE | -0.68908 | -0.95746 | -0.25028 | -0.34328 | 0 |  |  | none | FALSE | 0 | 71.9693 | FALSE | FALSE | 0.0623 |  | 72.439 | 0 | 0 | 0.035325 | 0.23522 | -0.15018 | 0.23484 | Normal | 72.9087 | 0.93425 | Day | 202512 | 2025-12-01 | 0.93425
2025-12-01 13:58 | 72.941 | FALSE | FALSE | -0.99668 | -1.3853 | -0.093077 | -0.12744 | 0.2826 |  |  | none | FALSE | 0 | 71.9443 | FALSE | FALSE | 0.1106 |  | 72.4892 | 0 | 0.2826 | 0.0628 | 0.23496 | 0.93547 | 0.27244 | Normal | 73.0341 | 1.6584 | Day | 202512 | 2025-12-01 | 1.6584
2025-12-01 14:13 | 72.941 | FALSE | FALSE | -0.99505 | -1.383 | -0.17359 | -0.23742 | 0 |  |  | none | FALSE | 0 | 71.946 | FALSE | FALSE | 0.0937 |  | 72.5303 | 0 | 0 | 0.05652 | 0.22241 | -0.25412 | 0.29216 | Normal | 73.1146 | 1.4058 | Day | 202512 | 2025-12-01 | 1.4058
2025-12-01 14:28 | 72.941 | FALSE | FALSE | -0.98199 | -1.3647 | -0.22899 | -0.31296 | 0 |  |  | none | FALSE | 0 | 71.959 | FALSE | FALSE | 0.0829 |  | 72.5645 | 0 | 0 | 0.051382 | 0.21169 | -0.24273 | 0.30275 | Normal | 73.17 | 1.2436 | Day | 202512 | 2025-12-01 | 1.2436
2025-12-01 14:43 | 72.941 | FALSE | FALSE | -0.96372 | -1.3389 | -0.26865 | -0.36696 | 0 |  |  | none | FALSE | 0 | 71.9773 | FALSE | FALSE | 0.0752 |  | 72.5935 | 0 | 0 | 0.0471 | 0.20238 | -0.23273 | 0.30809 | Normal | 73.2096 | 1.128 | Day | 202512 | 2025-12-01 | 1.128
2025-12-01 14:58 | 73.2236 | FALSE | FALSE | -1.2663 | -1.7597 | -0.095995 | -0.13093 | 0.2826 |  |  | none | FALSE | 0 | 71.9573 | FALSE | FALSE | 0.1145 |  | 72.6385 | 0 | 0.2826 | 0.065215 | 0.20448 | 1.0631 | 0.34056 | Normal | 73.3196 | 1.7181 | Day | 202512 | 2025-12-01 | 1.7181
2025-12-01 15:13 | 73.2236 | FALSE | FALSE | -1.2687 | -1.7632 | -0.17644 | -0.24038 | 0 |  |  | none | FALSE | 0 | 71.9549 | FALSE | FALSE | 0.1008 |  | 72.6775 | 0 | 0 | 0.060557 | 0.19723 | -0.30705 | 0.36128 | Normal | 73.4 | 1.5116 | Day | 202512 | 2025-12-01 | 1.5116
2025-12-01 15:28 | 73.2236 | FALSE | FALSE | -1.2616 | -1.7531 | -0.23758 | -0.3234 | 0 |  |  | none | FALSE | 0 | 71.962 | FALSE | FALSE | 0.0911 |  | 72.7116 | 0 | 0 | 0.05652 | 0.19069 | -0.29639 | 0.37478 | Normal | 73.4612 | 1.3661 | Day | 202512 | 2025-12-01 | 1.3661
2025-12-01 15:43 | 73.2236 | FALSE | FALSE | -1.2489 | -1.7353 | -0.28521 | -0.38799 | 0 |  |  | none | FALSE | 0 | 71.9747 | FALSE | FALSE | 0.0838 |  | 72.7417 | 0 | 0 | 0.052988 | 0.18477 | -0.28678 | 0.38354 | Normal | 73.5088 | 1.2564 | Day | 202512 | 2025-12-01 | 1.2564
2025-12-01 15:58 | 73.2236 | FALSE | FALSE | -1.2332 | -1.713 | -0.32297 | -0.43914 | 0 |  |  | none | FALSE | 0 | 71.9904 | FALSE | FALSE | 0.078 |  | 72.7685 | 0 | 0 | 0.049871 | 0.17936 | -0.27804 | 0.38904 | Normal | 73.5466 | 1.1698 | Day | 202512 | 2025-12-01 | 1.1698
2025-12-01 16:13 | 73.2236 | FALSE | FALSE | -1.2156 | -1.6881 | -0.35331 | -0.48019 | 0 |  |  | none | FALSE | 0 | 72.008 | FALSE | FALSE | 0.0733 |  | 72.7925 | 0 | 0 | 0.0471 | 0.1744 | -0.27006 | 0.39223 | Normal | 73.5769 | 1.0992 | Day | 202512 | 2025-12-01 | 1.0992
2025-12-01 16:28 | 73.2236 | FALSE | FALSE | -1.1971 | -1.662 | -0.37791 | -0.51345 | 0 |  |  | none | FALSE | 0 | 72.0265 | FALSE | FALSE | 0.0693 |  | 72.814 | 0 | 0 | 0.044621 | 0.16983 | -0.26273 | 0.39375 | Normal | 73.6015 | 1.0402 | Day | 202512 | 2025-12-01 | 1.0402
2025-12-01 16:42 | 72.941 | FALSE | FALSE | -0.86015 | -1.1933 | -0.66269 | -0.90035 | -0.2826 |  |  | none | FALSE | 0 | 72.0808 | FALSE | FALSE | 0.0173 |  | 72.8423 | 0 | -0.2826 | 0.02826 | 0.18077 | -1.7196 | 0.38071 | Normal | 73.6037 | 0.25933 | Day | 202512 | 2025-12-01 | 0.25933
2025-12-01 16:57 | 72.941 | FALSE | FALSE | -0.73224 | -1.0141 | -0.61938 | -0.842 | 0 |  |  | none | FALSE | 0 | 72.2088 | FALSE | FALSE | 0.0111 |  | 72.8846 | 0 | 0 | 0.0423 | 0.16579 | -0.25514 | 0.33791 | Normal | 73.5604 | 0.167 | Day | 202512 | 2025-12-01 | 0.167
2025-12-01 17:12 | 72.941 | FALSE | FALSE | -0.57859 | -0.79957 | -0.55033 | -0.74883 | 0 |  |  | none | FALSE | 0 | 72.3624 | FALSE | FALSE | 0.0033 |  | 72.9269 | 0 | 0 | 0.0423 | 0.16579 | -0.25514 | 0.28223 | Normal | 73.4913 | 0.050066 | Day | 202512 | 2025-12-01 | 0.050066
2025-12-01 17:27 | 72.941 | FALSE | FALSE | -0.48723 | -0.67246 | -0.51549 | -0.70176 | 0 |  |  | none | FALSE | 0 | 72.4538 | FALSE | FALSE | 0.0038 |  | 72.9551 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.25068 | Normal | 73.4565 | -0.056367 | Day | 202512 | 2025-12-01 | 0.056367
2025-12-01 17:42 | 72.941 | FALSE | FALSE | -0.45343 | -0.62552 | -0.50995 | -0.69427 | 0 |  |  | none | FALSE | 0 | 72.4876 | FALSE | FALSE | 0.0078 |  | 72.9693 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.24084 | Normal | 73.4509 | -0.11734 | Night | 202512 | 2025-12-01 | 0.11734
2025-12-01 17:57 | 72.6584 | TRUE | FALSE | -0.096174 | -0.13254 | -0.74615 | -1.0165 | -0.2826 |  |  | none | FALSE | 1 | 72.5622 | FALSE | FALSE | 0.1315 |  | 72.9834 | 0 | -0.2826 | 0.01413 | 0.14424 | -2.0571 | 0.21058 | Normal | 73.4046 | -1.5433 | Night | 202512 | 2025-12-01 | 1.5433
2025-12-01 18:12 | 72.3758 | FALSE | FALSE | 0.11177 | 0.1542 | -1.0751 | -1.4638 | -0.2826 | 2025-12-01 18:57 | 2025-12-01 18:12 | lower | TRUE | 1 | 72.4876 | FALSE | FALSE | 0.25 | 2.4641 | 72.9693 | 1 | -0.2826 | -0.01413 | 0.14424 | -1.8612 | 0.24084 | Extreme triggered | 73.4509 | -2.4641 | Night | 202512 | 2025-12-01 | 2.4641
2025-12-01 18:27 | 72.3758 | FALSE | FALSE | 0.045491 | 0.062815 | -1.1132 | -1.5147 | 0 |  | 2025-12-01 18:12 | lower | TRUE | 1 | 72.4213 | FALSE | FALSE | 0.2876 | 2.3173 | 72.9551 | 2 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.26692 | Extreme/elevated | 73.489 | -2.1704 | Night | 202512 | 2025-12-01 | 2.1704
2025-12-01 18:42 | 72.095 | FALSE | FALSE | 0.18477 | 0.25563 | -1.4792 | -2.0104 | -0.2808 |  | 2025-12-01 18:12 | lower | TRUE | 1 | 72.2798 | FALSE | TRUE | 0.3714 | 2.4018 | 72.927 | 3 | -0.2808 | -0.02817 | 0.15598 | -1.6196 | 0.3236 | Persistent | 73.5742 | -2.571 | Night | 202512 | 2025-12-01 | 2.571
2025-12-01 18:42 | 72.095 | FALSE | FALSE | 0.043335 | 0.060073 | -1.536 | -2.0861 | 0 |  | 2025-12-01 18:12 | lower | TRUE | 1 | 72.1383 | FALSE | TRUE | 0.3982 | 2.3304 | 72.8847 | 4 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.37316 | Persistent | 73.631 | -2.1161 | Night | 202512 | 2025-12-01 | 2.1161
2025-12-01 18:42 | 72.095 | FALSE | FALSE | -0.077306 | -0.10734 | -1.572 | -2.134 | 0 |  | 2025-12-01 18:12 | none | FALSE | 1 | 72.0177 | FALSE | FALSE | 0.4351 | 2.2268 | 72.8424 | 5 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.41233 | Persistent | 73.667 | -1.8125 | Night | 202512 | 2025-12-01 | 1.8125
2025-12-01 18:57 | 73.2236 | TRUE | FALSE | -1.2084 | -1.678 | -0.47419 | -0.64342 | 1.1286 |  |  | none | FALSE | 2 | 72.0152 | TRUE | FALSE | 0.1153 |  | 72.8565 | 0 | 1.1286 | 0.01413 | 0.2963 | 3.7613 | 0.42065 | Persistence ends | 73.6978 | 0.87272 | Night | 202512 | 2025-12-01 | 0.87272
2025-12-01 19:12 | 73.5062 | FALSE | FALSE | -1.5113 | -2.0991 | -0.26837 | -0.36378 | 0.2826 |  |  | none | FALSE | 2 | 71.9949 | FALSE | FALSE | 0.1503 |  | 72.8847 | 0 | 0.2826 | 0.02826 | 0.30227 | 0.84144 | 0.44491 | Normal | 73.7746 | 1.3968 | Night | 202512 | 2025-12-01 | 1.3968
2025-12-01 19:27 | 73.7888 | FALSE | FALSE | -1.8434 | -2.5623 | -0.091844 | -0.12431 | 0.2826 |  |  | none | FALSE | 2 | 71.9454 | FALSE | FALSE | 0.1778 |  | 72.913 | 0 | 0.2826 | 0.02826 | 0.30227 | 0.84144 | 0.48382 | Normal | 73.8806 | 1.8102 | Night | 202512 | 2025-12-01 | 1.8102
2025-12-01 19:41 | 73.7888 | FALSE | FALSE | -1.8839 | -2.62 | -0.18887 | -0.2553 | 0 |  |  | none | FALSE | 2 | 71.9049 | FALSE | FALSE | 0.1662 |  | 72.9413 | 0 | 0 | 0.02826 | 0.30227 | -0.093494 | 0.5182 | Normal | 73.9777 | 1.6355 | Night | 202512 | 2025-12-01 | 1.6355
2025-12-01 19:56 | 73.7888 | FALSE | FALSE | -1.9171 | -2.6674 | -0.27855 | -0.37607 | 0 |  |  | none | FALSE | 1 | 71.8717 | FALSE | FALSE | 0.1281 |  | 72.9695 | 0 | 0 | 0.02826 | 0.30227 | -0.093494 | 0.54891 | Normal | 74.0673 | 1.4925 | Night | 202512 | 2025-12-01 | 1.4925
2025-12-01 20:11 | 73.7888 | FALSE | FALSE | -1.9441 | -2.7059 | -0.36205 | -0.48826 | 0 |  |  | none | FALSE | 1 | 71.8447 | FALSE | FALSE | 0.12 |  | 72.9978 | 0 | 0 | 0.02826 | 0.30227 | -0.093494 | 0.57653 | Normal | 74.1509 | 1.372 | Night | 202512 | 2025-12-01 | 1.372
2025-12-01 20:26 | 74.0714 | FALSE | FALSE | -2.2778 | -3.1727 | -0.21534 | -0.28988 | 0.2826 |  |  | none | FALSE | 1 | 71.7936 | FALSE | FALSE | 0.1389 |  | 73.0402 | 0 | 0.2826 | 0.04239 | 0.30744 | 0.78133 | 0.62328 | Normal | 74.2867 | 1.6545 | Night | 202512 | 2025-12-01 | 1.6545
2025-12-01 20:41 | 74.0714 | FALSE | FALSE | -2.3167 | -3.2286 | -0.339 | -0.45559 | 0 |  |  | none | FALSE | 1 | 71.7547 | FALSE | FALSE | 0.1279 |  | 73.0826 | 0 | 0 | 0.04239 | 0.30744 | -0.13788 | 0.66392 | Normal | 74.4104 | 1.4894 | Night | 202512 | 2025-12-01 | 1.4894
2025-12-01 20:56 | 74.0714 | FALSE | FALSE | -2.3455 | -3.27 | -0.45257 | -0.60728 | 0 |  |  | none | FALSE | 1 | 71.7259 | FALSE | FALSE | 0.1188 |  | 73.125 | 0 | 0 | 0.04239 | 0.30744 | -0.13788 | 0.69951 | Normal | 74.524 | 1.353 | Night | 202512 | 2025-12-01 | 1.353
2025-12-01 21:11 | 74.0714 | FALSE | FALSE | -2.3477 | -3.2733 | -0.5679 | -0.76086 | 0 |  |  | none | FALSE | 1 | 71.7237 | FALSE | FALSE | 0.11 |  | 73.1815 | 0 | 0 | 0.05652 | 0.29806 | -0.18962 | 0.72891 | Normal | 74.6393 | 1.2209 | Night | 202512 | 2025-12-01 | 1.2209
2025-12-01 21:26 | 74.0714 | FALSE | FALSE | -2.3388 | -3.2605 | -0.67204 | -0.89913 | 0 |  |  | none | FALSE | 0 | 71.7326 | FALSE | FALSE | 0.0738 |  | 73.238 | 0 | 0 | 0.05652 | 0.29806 | -0.18962 | 0.75272 | Normal | 74.7434 | 1.1072 | Night | 202512 | 2025-12-01 | 1.1072
2025-12-01 21:41 | 74.3522 | FALSE | FALSE | -2.621 | -3.654 | -0.53375 | -0.71275 | 0.2808 |  |  | none | FALSE | 0 | 71.7312 | FALSE | FALSE | 0.0882 |  | 73.3086 | 0 | 0.2808 | 0.07056 | 0.30185 | 0.6965 | 0.7887 | Normal | 74.886 | 1.3232 | Night | 202512 | 2025-12-01 | 1.3232
2025-12-01 21:56 | 74.3522 | FALSE | FALSE | -2.6065 | -3.633 | -0.66034 | -0.88031 | 0 |  |  | none | FALSE | 0 | 71.7457 | FALSE | FALSE | 0.0794 |  | 73.3791 | 0 | 0 | 0.07056 | 0.30185 | -0.23376 | 0.81671 | Normal | 75.0125 | 1.1915 | Night | 202512 | 2025-12-01 | 1.1915
2025-12-01 22:11 | 74.3522 | FALSE | FALSE | -2.5776 | -3.5913 | -0.7726 | -1.0284 | 0 |  |  | none | FALSE | 0 | 71.7746 | FALSE | FALSE | 0.0718 |  | 73.4497 | 0 | 0 | 0.07056 | 0.30185 | -0.23376 | 0.83756 | Normal | 75.1248 | 1.0776 | Night | 202512 | 2025-12-01 | 1.0776
2025-12-01 22:40 | 74.3522 | FALSE | FALSE | -2.4958 | -3.4733 | -0.86012 | -1.1436 | 0 |  |  | none | FALSE | 0 | 71.8564 | FALSE | FALSE | 0.065 |  | 73.5344 | 0 | 0 | 0.08469 | 0.29086 | -0.29117 | 0.83897 | Normal | 75.2123 | 0.9748 | Night | 202512 | 2025-12-01 | 0.9748
2025-12-01 22:55 | 74.3522 | FALSE | FALSE | -2.3415 | -3.2517 | -0.90352 | -1.2006 | 0 |  |  | none | FALSE | 0 | 72.0107 | FALSE | FALSE | 0.0591 |  | 73.6332 | 0 | 0 | 0.09882 | 0.27869 | -0.35458 | 0.81127 | Normal | 75.2557 | 0.88628 | Night | 202512 | 2025-12-01 | 0.88628
2025-12-01 23:10 | 74.3522 | FALSE | FALSE | -2.1589 | -2.9904 | -0.91847 | -1.2202 | 0 |  |  | none | FALSE | 0 | 72.1933 | FALSE | FALSE | 0.0537 |  | 73.732 | 0 | 0 | 0.09882 | 0.27869 | -0.35458 | 0.76933 | Normal | 75.2707 | 0.80614 | Night | 202512 | 2025-12-01 | 0.80614
2025-12-01 23:26 | 74.6348 | FALSE | FALSE | -2.1567 | -2.9757 | -0.60514 | -0.80428 | 0.2826 |  |  | none | FALSE | 0 | 72.4781 | FALSE | FALSE | 0.0749 |  | 73.859 | 0 | 0.2826 | 0.12699 | 0.26651 | 0.58388 | 0.69047 | Normal | 75.2399 | 1.1236 | Night | 202512 | 2025-12-01 | 1.1236
2025-12-01 23:40 | 74.3522 | FALSE | FALSE | -1.4981 | -2.0564 | -0.73746 | -0.98211 | -0.2826 |  |  | none | FALSE | 0 | 72.8541 | FALSE | FALSE | 0.0454 |  | 73.9719 | 0 | -0.2826 | 0.11286 | 0.28071 | -1.4088 | 0.5589 | Normal | 75.0897 | 0.68052 | Night | 202512 | 2025-12-01 | 0.68052
2025-12-01 23:55 | 74.6348 | FALSE | FALSE | -1.2657 | -1.7251 | -0.19378 | -0.25896 | 0.2826 |  |  | none | FALSE | 0 | 73.3691 | FALSE | FALSE | 0.0979 |  | 74.0988 | 0 | 0.2826 | 0.12699 | 0.28184 | 0.55212 | 0.36486 | Normal | 74.8286 | 1.4689 | Night | 202512 | 2025-12-01 | 1.4689
2025-12-02 00:10 | 74.6348 | FALSE | FALSE | -1.1063 | -1.5046 | -0.17549 | -0.23459 | 0 |  |  | none | FALSE | 0 | 73.5285 | FALSE | FALSE | 0.0968 |  | 74.1694 | 0 | 0 | 0.07056 | 0.15534 | -0.45424 | 0.32044 | Normal | 74.8103 | 1.4523 | Night | 202512 | 2025-12-02 | 1.4523
2025-12-02 00:25 | 74.3522 | FALSE | FALSE | -0.70408 | -0.95601 | -0.4231 | -0.56583 | -0.2826 |  |  | none | FALSE | 0 | 73.6481 | FALSE | FALSE | 0.0332 |  | 74.2117 | 0 | -0.2826 | 0.0423 | 0.16579 | -1.9597 | 0.2818 | Normal | 74.7753 | 0.49855 | Night | 202512 | 2025-12-02 | 0.49855
2025-12-02 00:40 | 74.6348 | FALSE | FALSE | -0.93769 | -1.2723 | -0.17611 | -0.2354 | 0.2826 |  |  | none | FALSE | 0 | 73.6971 | FALSE | FALSE | 0.0912 |  | 74.254 | 0 | 0.2826 | 0.0423 | 0.16579 | 1.4494 | 0.27845 | Normal | 74.8109 | 1.3675 | Night | 202512 | 2025-12-02 | 1.3675
2025-12-02 00:55 | 74.3522 | FALSE | FALSE | -0.58311 | -0.79045 | -0.44307 | -0.59237 | -0.2826 |  |  | none | FALSE | 0 | 73.7691 | FALSE | FALSE | 0.0182 |  | 74.2822 | 0 | -0.2826 | 0.02817 | 0.18094 | -1.7176 | 0.25654 | Normal | 74.7953 | 0.27294 | Night | 202512 | 2025-12-02 | 0.27294
2025-12-02 01:10 | 74.3522 | FALSE | FALSE | -0.49978 | -0.67673 | -0.41608 | -0.5565 | 0 |  |  | none | FALSE | 0 | 73.8524 | FALSE | FALSE | 0.0122 |  | 74.3103 | 0 | 0 | 0.02817 | 0.18094 | -0.15569 | 0.22897 | Normal | 74.7683 | 0.18278 | Night | 202512 | 2025-12-02 | 0.18278
2025-12-02 01:25 | 74.3522 | FALSE | FALSE | -0.40029 | -0.54128 | -0.37293 | -0.49906 | 0 |  |  | none | FALSE | 0 | 73.9519 | FALSE | FALSE | 0.0047 |  | 74.3385 | 0 | 0 | 0.02817 | 0.18094 | -0.15569 | 0.1933 | Normal | 74.7251 | 0.07077 | Night | 202512 | 2025-12-02 | 0.07077
2025-12-02 01:40 | 74.3522 | FALSE | FALSE | -0.36522 | -0.49363 | -0.36594 | -0.48976 | 0 |  |  | none | FALSE | 0 | 73.987 | FALSE | FALSE | 0.0001 |  | 74.3526 | 0 | 0 | 0.01404 | 0.17077 | -0.082216 | 0.18279 | Normal | 74.7181 | -0.0019695 | Night | 202512 | 2025-12-02 | 0.0019695
2025-12-02 01:55 | 74.3522 | FALSE | FALSE | -0.32645 | -0.441 | -0.35525 | -0.47552 | 0 |  |  | none | FALSE | 0 | 74.0257 | FALSE | FALSE | 0.0056 |  | 74.3666 | 0 | 0 | 0.01404 | 0.17077 | -0.082216 | 0.17043 | Normal | 74.7075 | -0.084495 | Night | 202512 | 2025-12-02 | 0.084495
2025-12-02 02:10 | 74.3522 | FALSE | FALSE | -0.28308 | -0.38219 | -0.33996 | -0.45515 | 0 |  |  | none | FALSE | 0 | 74.0691 | FALSE | FALSE | 0.0122 |  | 74.3806 | 0 | 0 | 0.01404 | 0.17077 | -0.082216 | 0.15576 | Normal | 74.6922 | -0.18259 | Night | 202512 | 2025-12-02 | 0.18259
2025-12-02 02:25 | 74.0714 | FALSE | FALSE | -0.0022831 | -0.0030824 | -0.62076 | -0.8311 | -0.2808 |  |  | none | FALSE | 0 | 74.0691 | FALSE | FALSE | 0.1324 |  | 74.3806 | 0 | -0.2808 | 0 | 0.18308 | -1.5337 | 0.15576 | Normal | 74.6922 | -1.9853 | Night | 202512 | 2025-12-02 | 1.9853
2025-12-02 02:39 | 74.3522 | FALSE | FALSE | -0.23366 | -0.31525 | -0.31862 | -0.4267 | 0.2808 |  |  | none | FALSE | 0 | 74.1185 | FALSE | FALSE | 0.0205 |  | 74.3947 | 0 | 0.2808 | 0.01404 | 0.19355 | 1.3782 | 0.13807 | Normal | 74.6708 | -0.30767 | Night | 202512 | 2025-12-02 | 0.30767
2025-12-02 02:54 | 74.3522 | FALSE | FALSE | -0.23366 | -0.31525 | -0.31862 | -0.4267 | 0 |  |  | none | FALSE | 0 | 74.1185 | FALSE | FALSE | 0.0205 |  | 74.3947 | 0 | 0 | 0 | 0.18308 | 0 | 0.13807 | Normal | 74.6708 | -0.30767 | Night | 202512 | 2025-12-02 | 0.30767
2025-12-02 03:09 | 74.0714 | FALSE | FALSE | -0.0022831 | -0.0030824 | -0.62076 | -0.8311 | -0.2808 |  |  | none | FALSE | 0 | 74.0691 | FALSE | FALSE | 0.1324 |  | 74.3806 | 0 | -0.2808 | -0.01404 | 0.19355 | -1.3782 | 0.15576 | Normal | 74.6922 | -1.9853 | Night | 202512 | 2025-12-02 | 1.9853
2025-12-02 03:24 | 74.3522 | FALSE | FALSE | -0.28308 | -0.38219 | -0.33996 | -0.45515 | 0.2808 |  |  | none | FALSE | 0 | 74.0691 | FALSE | FALSE | 0.0122 |  | 74.3806 | 0 | 0.2808 | 0 | 0.2045 | 1.3731 | 0.15576 | Normal | 74.6922 | -0.18259 | Night | 202512 | 2025-12-02 | 0.18259
2025-12-02 03:39 | 74.3522 | FALSE | FALSE | -0.28308 | -0.38219 | -0.33996 | -0.45515 | 0 |  |  | none | FALSE | 0 | 74.0691 | FALSE | FALSE | 0.0122 |  | 74.3806 | 0 | 0 | 0 | 0.2045 | 0 | 0.15576 | Normal | 74.6922 | -0.18259 | Night | 202512 | 2025-12-02 | 0.18259
2025-12-02 03:54 | 74.0714 | FALSE | FALSE | -0.04565 | -0.061668 | -0.63605 | -0.85139 | -0.2808 |  |  | none | FALSE | 0 | 74.0257 | FALSE | FALSE | 0.1155 |  | 74.3666 | 0 | -0.2808 | -0.01404 | 0.21392 | -1.247 | 0.17043 | Normal | 74.7075 | -1.7321 | Night | 202512 | 2025-12-02 | 1.7321
2025-12-02 04:09 | 74.0714 | FALSE | FALSE | -0.084423 | -0.11411 | -0.64674 | -0.86558 | 0 |  |  | none | FALSE | 0 | 73.987 | FALSE | FALSE | 0.1025 |  | 74.3526 | 0 | 0 | -0.01404 | 0.21392 | 0.065632 | 0.18279 | Normal | 74.7181 | -1.5381 | Night | 202512 | 2025-12-02 | 1.5381
2025-12-02 04:24 | 74.0714 | FALSE | FALSE | -0.10782 | -0.14577 | -0.6138 | -0.82185 | 0 |  |  | none | FALSE | 0 | 73.9636 | FALSE | FALSE | 0.0935 |  | 74.3244 | 0 | 0 | -0.02817 | 0.20231 | 0.13924 | 0.1804 | Normal | 74.6852 | -1.4024 | Night | 202512 | 2025-12-02 | 1.4024
2025-12-02 04:39 | 74.0714 | FALSE | FALSE | -0.13876 | -0.18768 | -0.61666 | -0.82565 | 0 |  |  | none | FALSE | 0 | 73.9326 | FALSE | FALSE | 0.0844 |  | 74.3103 | 0 | 0 | -0.01404 | 0.19328 | 0.072642 | 0.18885 | Normal | 74.6881 | -1.2653 | Night | 202512 | 2025-12-02 | 1.2653
2025-12-02 04:54 | 74.0714 | FALSE | FALSE | -0.14864 | -0.20107 | -0.5702 | -0.76391 | 0 |  |  | none | FALSE | 0 | 73.9228 | FALSE | FALSE | 0.0782 |  | 74.2822 | 0 | 0 | -0.02817 | 0.18034 | 0.1562 | 0.17971 | Normal | 74.6416 | -1.1729 | Night | 202512 | 2025-12-02 | 1.1729
2025-12-02 05:09 | 74.0714 | FALSE | FALSE | -0.14757 | -0.19962 | -0.51279 | -0.68753 | 0 |  |  | none | FALSE | 0 | 73.9238 | FALSE | FALSE | 0.0737 |  | 74.254 | 0 | 0 | -0.02817 | 0.18034 | 0.1562 | 0.16509 | Normal | 74.5842 | -1.1061 | Night | 202512 | 2025-12-02 | 1.1061
2025-12-02 05:24 | 74.0714 | FALSE | FALSE | -0.16785 | -0.22712 | -0.50499 | -0.67714 | 0 |  |  | none | FALSE | 0 | 73.9036 | FALSE | FALSE | 0.0668 |  | 74.24 | 0 | 0 | -0.01404 | 0.17014 | 0.082519 | 0.16821 | Normal | 74.5764 | -1.0021 | Night | 202512 | 2025-12-02 | 1.0021
2025-12-02 05:38 | 74.0714 | FALSE | FALSE | -0.14769 | -0.19979 | -0.42849 | -0.57516 | 0 |  |  | none | FALSE | 0 | 73.9237 | FALSE | FALSE | 0.065 |  | 74.2118 | 0 | 0 | -0.02817 | 0.1553 | 0.18139 | 0.14405 | Normal | 74.4999 | -0.97468 | Night | 202512 | 2025-12-02 | 0.97468
2025-12-02 05:53 | 74.0714 | FALSE | FALSE | -0.16029 | -0.21687 | -0.41301 | -0.55449 | 0 |  |  | none | FALSE | 0 | 73.9111 | FALSE | FALSE | 0.0588 |  | 74.1978 | 0 | 0 | -0.01404 | 0.14333 | 0.097959 | 0.14333 | Normal | 74.4844 | -0.88163 | Night | 202512 | 2025-12-02 | 0.88163
2025-12-02 06:08 | 74.0714 | FALSE | FALSE | -0.16995 | -0.22997 | -0.39459 | -0.5299 | 0 |  |  | none | FALSE | 0 | 73.9014 | FALSE | FALSE | 0.0531 |  | 74.1837 | 0 | 0 | -0.01404 | 0.14333 | 0.097959 | 0.14114 | Normal | 74.466 | -0.79582 | Night | 202512 | 2025-12-02 | 0.79582
2025-12-02 06:23 | 74.0714 | FALSE | FALSE | -0.17654 | -0.23891 | -0.3731 | -0.50119 | 0 |  |  | none | FALSE | 0 | 73.8949 | FALSE | FALSE | 0.0477 |  | 74.1697 | 0 | 0 | -0.01404 | 0.14333 | 0.097959 | 0.13741 | Normal | 74.4445 | -0.71522 | Night | 202512 | 2025-12-02 | 0.71522
2025-12-02 06:38 | 74.0714 | FALSE | FALSE | -0.1798 | -0.24333 | -0.34828 | -0.468 | 0 |  |  | none | FALSE | 0 | 73.8916 | FALSE | FALSE | 0.0425 |  | 74.1556 | 0 | 0 | -0.01404 | 0.14333 | 0.097959 | 0.13202 | Normal | 74.4197 | -0.63808 | Night | 202512 | 2025-12-02 | 0.63808
2025-12-02 06:53 | 74.0714 | FALSE | FALSE | -0.1793 | -0.24265 | -0.3197 | -0.42975 | 0 |  |  | none | FALSE | 0 | 73.8921 | FALSE | FALSE | 0.0375 |  | 74.1416 | 0 | 0 | -0.01404 | 0.14333 | 0.097959 | 0.12475 | Normal | 74.3911 | -0.56273 | Night | 202512 | 2025-12-02 | 0.56273
2025-12-02 07:08 | 74.0714 | FALSE | FALSE | -0.17432 | -0.23589 | -0.28664 | -0.38548 | 0 |  |  | none | FALSE | 0 | 73.8971 | FALSE | FALSE | 0.0325 |  | 74.1276 | 0 | 0 | -0.01404 | 0.14333 | 0.097959 | 0.11524 | Normal | 74.358 | -0.48734 | Day | 202512 | 2025-12-02 | 0.48734
2025-12-02 07:23 | 74.0714 | FALSE | FALSE | -0.17432 | -0.23589 | -0.28664 | -0.38548 | 0 |  |  | none | FALSE | 0 | 73.8971 | FALSE | FALSE | 0.0325 |  | 74.1276 | 0 | 0 | 0 | 0.12884 | 0 | 0.11524 | Normal | 74.358 | -0.48734 | Day | 202512 | 2025-12-02 | 0.48734
2025-12-02 07:30 | 74.0714 | FALSE | FALSE | -0.16362 | -0.22139 | -0.24786 | -0.33351 | 0 |  |  | none | FALSE | 0 | 73.9078 | FALSE | FALSE | 0.0273 |  | 74.1135 | 0 | 0 | -0.01404 | 0.11064 | 0.12689 | 0.10287 | Normal | 74.3193 | -0.40945 | Day | 202512 | 2025-12-02 | 0.40945
2025-12-02 07:45 | 74.0714 | FALSE | FALSE | -0.14478 | -0.19584 | -0.20094 | -0.27054 | 0 |  |  | none | FALSE | 0 | 73.9266 | FALSE | FALSE | 0.0217 |  | 74.0995 | 0 | 0 | -0.01404 | 0.11064 | 0.12689 | 0.086428 | Normal | 74.2723 | -0.32489 | Day | 202512 | 2025-12-02 | 0.32489
2025-12-02 08:00 | 74.0714 | FALSE | FALSE | -0.14478 | -0.19584 | -0.20094 | -0.27054 | 0 |  |  | none | FALSE | 0 | 73.9266 | FALSE | FALSE | 0.0217 |  | 74.0995 | 0 | 0 | 0 | 0.091104 | 0 | 0.086428 | Normal | 74.2723 | -0.32489 | Day | 202512 | 2025-12-02 | 0.32489
2025-12-02 08:16 | 74.3522 | TRUE | FALSE | -0.42558 | -0.57567 | 0.079863 | 0.10753 | 0.2808 | 2025-12-02 11:44 | 2025-12-02 08:16 | upper | TRUE | 1 | 73.9266 | FALSE | FALSE | 0.2807 | 2.924 | 74.0995 | 1 | 0.2808 | 0 | 0.091104 | 3.0822 | 0.086428 | Extreme triggered | 74.2723 | 2.924 | Day | 202512 | 2025-12-02 | 2.924
2025-12-02 08:30 | 74.6348 | TRUE | FALSE | -0.79673 | -1.079 | 0.24565 | 0.33022 | 0.2826 |  | 2025-12-02 08:16 | upper | TRUE | 2 | 73.8381 | TRUE | FALSE | 0.4236 | 3.3535 | 74.1136 | 2 | 0.2826 | 0.01413 | 0.11087 | 2.4214 | 0.13777 | Extreme/elevated | 74.3892 | 3.783 | Day | 202512 | 2025-12-02 | 3.783
2025-12-02 08:45 | 74.9174 | TRUE | FALSE | -1.2132 | -1.646 | 0.30979 | 0.41523 | 0.2826 |  | 2025-12-02 08:16 | upper | TRUE | 3 | 73.7042 | TRUE | TRUE | 0.4819 | 3.3596 | 74.1559 | 3 | 0.2826 | 0.0423 | 0.10331 | 2.326 | 0.22585 | Persistent | 74.6076 | 3.3717 | Day | 202512 | 2025-12-02 | 3.3717
2025-12-02 08:45 | 74.9174 | FALSE | FALSE | -1.2823 | -1.7414 | 0.1561 | 0.2088 | 0 |  | 2025-12-02 08:16 | upper | TRUE | 3 | 73.6351 | FALSE | TRUE | 0.4846 | 3.1583 | 74.1982 | 4 | 0 | 0.0423 | 0.10331 | -0.40945 | 0.28155 | Persistent | 74.7613 | 2.5544 | Day | 202512 | 2025-12-02 | 2.5544
2025-12-02 08:48 | 74.9174 | FALSE | FALSE | -1.3211 | -1.7951 | 0.032652 | 0.043603 | 0 |  | 2025-12-02 08:16 | upper | TRUE | 3 | 73.5963 | FALSE | TRUE | 0.5115 | 2.9469 | 74.2405 | 5 | 0 | 0.0423 | 0.10331 | -0.40945 | 0.32212 | Persistent | 74.8847 | 2.1014 | Day | 202512 | 2025-12-02 | 2.1014
2025-12-02 09:03 | 74.6348 | TRUE | FALSE | -1.0282 | -1.3969 | -0.29601 | -0.39504 | -0.2826 |  | 2025-12-02 08:16 | none | FALSE | 4 | 73.6066 | TRUE | FALSE | 0.5309 | 2.6401 | 74.2687 | 6 | -0.2826 | 0.02817 | 0.12619 | -2.4627 | 0.33106 | Persistent | 74.9308 | 1.1059 | Day | 202512 | 2025-12-02 | 1.1059
2025-12-02 09:18 | 73.7888 | TRUE | TRUE | -0.22552 | -0.30657 | -1.157 | -1.5438 | -0.846 |  | 2025-12-02 08:16 | none | FALSE | 5 | 73.5633 | TRUE | FALSE | 0.6327 | 2.4554 | 74.2545 | 7 | -0.846 | -0.01413 | 0.23285 | -3.5726 | 0.34564 | Confirmed/Materialized Shift | 74.9458 | -1.3475 | Day | 202512 | 2025-12-02 | 1.3475
2025-12-02 09:33 | 73.2236 | FALSE | TRUE | 0.15971 | 0.21764 | -1.8174 | -2.4219 | -0.5652 |  | 2025-12-02 08:16 | lower | TRUE | 5 | 73.3833 | FALSE | TRUE | 0.7019 | 2.4467 | 74.2122 | 8 | -0.5652 | -0.04239 | 0.26335 | -1.9853 | 0.41442 | Confirmed/Materialized Shift | 75.041 | -2.3854 | Day | 202512 | 2025-12-02 | 2.3854
2025-12-02 09:44 | 73.2236 | FALSE | TRUE | 0.0075602 | 0.010324 | -1.8848 | -2.5094 | 0 |  | 2025-12-02 08:16 | lower | TRUE | 5 | 73.2312 | FALSE | TRUE | 0.6773 | 2.3988 | 74.1698 | 9 | 0 | -0.04239 | 0.26335 | 0.16097 | 0.4693 | Confirmed/Materialized Shift | 75.1084 | -2.0161 | Day | 202512 | 2025-12-02 | 2.0161
2025-12-02 09:59 | 73.2236 | FALSE | TRUE | -0.12571 | -0.17198 | -1.9333 | -2.5723 | 0 |  | 2025-12-02 08:16 | none | FALSE | 5 | 73.0979 | FALSE | FALSE | 0.6599 | 2.3345 | 74.1274 | 10 | 0 | -0.04239 | 0.26335 | 0.16097 | 0.51475 | Confirmed/Materialized Shift | 75.1569 | -1.7558 | Day | 202512 | 2025-12-02 | 1.7558
2025-12-02 10:14 | 72.941 | FALSE | TRUE | -0.028614 | -0.039244 | -2.2883 | -3.0418 | -0.2826 |  | 2025-12-02 08:16 | none | FALSE | 4 | 72.9124 | FALSE | FALSE | 0.6443 | 2.2996 | 74.0709 | 11 | -0.2826 | -0.05652 | 0.26848 | -0.84207 | 0.57924 | Confirmed/Materialized Shift | 75.2293 | -1.9506 | Day | 202512 | 2025-12-02 | 1.9506
2025-12-02 10:30 | 72.941 | FALSE | TRUE | -0.19053 | -0.26189 | -2.3372 | -3.1048 | 0 |  | 2025-12-02 08:16 | none | FALSE | 3 | 72.7505 | FALSE | FALSE | 0.5989 | 2.2495 | 74.0143 | 12 | 0 | -0.05652 | 0.26848 | 0.21052 | 0.63193 | Confirmed/Materialized Shift | 75.2782 | -1.6985 | Day | 202512 | 2025-12-02 | 1.6985
2025-12-02 10:44 | 72.941 | FALSE | TRUE | -0.33439 | -0.46055 | -2.368 | -3.1444 | 0 |  | 2025-12-02 08:16 | none | FALSE | 2 | 72.6066 | FALSE | FALSE | 0.5575 | 2.1923 | 73.9578 | 13 | 0 | -0.05652 | 0.26848 | 0.21052 | 0.6756 | Confirmed/Materialized Shift | 75.309 | -1.5051 | Day | 202512 | 2025-12-02 | 1.5051
2025-12-02 10:59 | 72.941 | FALSE | TRUE | -0.46352 | -0.63954 | -2.3841 | -3.1651 | 0 |  | 2025-12-02 08:16 | none | FALSE | 2 | 72.4775 | FALSE | FALSE | 0.5471 | 2.132 | 73.9013 | 14 | 0 | -0.05652 | 0.26848 | 0.21052 | 0.71191 | Confirmed/Materialized Shift | 75.3251 | -1.3489 | Day | 202512 | 2025-12-02 | 1.3489
2025-12-02 11:14 | 72.6584 | FALSE | TRUE | -0.35267 | -0.48775 | -2.6972 | -3.5793 | -0.2826 |  | 2025-12-02 08:16 | none | FALSE | 2 | 72.3057 | FALSE | FALSE | 0.5596 | 2.0924 | 73.8307 | 15 | -0.2826 | -0.07065 | 0.27275 | -0.77707 | 0.76246 | Confirmed/Materialized Shift | 75.3556 | -1.5375 | Day | 202512 | 2025-12-02 | 1.5375
2025-12-02 11:29 | 72.6584 | FALSE | TRUE | -0.50509 | -0.70003 | -2.7083 | -3.5935 | 0 |  | 2025-12-02 08:16 | none | FALSE | 1 | 72.1533 | FALSE | FALSE | 0.52 | 2.0473 | 73.76 | 16 | 0 | -0.07065 | 0.27275 | 0.25902 | 0.80335 | Confirmed/Materialized Shift | 75.3667 | -1.3713 | Day | 202512 | 2025-12-02 | 1.3713
2025-12-02 11:44 | 72.941 | FALSE | FALSE | -0.87728 | -1.2174 | -2.4022 | -3.1884 | 0.2826 |  |  | none | FALSE | 0 | 72.0637 | FALSE | FALSE | 0.062 |  | 73.7035 | 0 | 0.2826 | -0.05652 | 0.28371 | 1.1953 | 0.81988 | Persistence ends | 75.3432 | -0.92999 | Day | 202512 | 2025-12-02 | 0.92999
2025-12-02 11:59 | 72.941 | FALSE | FALSE | -0.95815 | -1.3311 | -2.3701 | -3.147 | 0 |  |  | none | FALSE | 0 | 71.9829 | FALSE | FALSE | 0.0566 |  | 73.647 | 0 | 0 | -0.05652 | 0.28371 | 0.19922 | 0.83205 | Normal | 75.3111 | -0.84845 | Day | 202512 | 2025-12-02 | 0.84845
2025-12-02 12:14 | 72.6584 | FALSE | FALSE | -0.78973 | -1.0989 | -2.6256 | -3.4875 | -0.2826 |  |  | none | FALSE | 0 | 71.8687 | FALSE | FALSE | 0.0717 |  | 73.5763 | 0 | -0.2826 | -0.07065 | 0.28775 | -0.73657 | 0.85382 | Normal | 75.284 | -1.0751 | Day | 202512 | 2025-12-02 | 1.0751
2025-12-02 12:29 | 72.6584 | FALSE | FALSE | -0.89079 | -1.2412 | -2.5853 | -3.4359 | 0 |  |  | none | FALSE | 0 | 71.7676 | FALSE | FALSE | 0.065 |  | 73.5057 | 0 | 0 | -0.07065 | 0.28775 | 0.24552 | 0.86902 | Normal | 75.2437 | -0.97496 | Day | 202512 | 2025-12-02 | 0.97496
2025-12-02 12:43 | 72.6584 | FALSE | FALSE | -0.96684 | -1.3486 | -2.492 | -3.316 | 0 |  |  | none | FALSE | 0 | 71.6916 | FALSE | FALSE | 0.0588 |  | 73.421 | 0 | 0 | -0.08469 | 0.27633 | 0.30649 | 0.86471 | Normal | 75.1504 | -0.88188 | Day | 202512 | 2025-12-02 | 0.88188
2025-12-02 12:59 | 72.6584 | FALSE | FALSE | -0.99817 | -1.3929 | -2.3257 | -3.1016 | 0 |  |  | none | FALSE | 0 | 71.6602 | FALSE | FALSE | 0.0533 |  | 73.3221 | 0 | 0 | -0.09882 | 0.26348 | 0.37505 | 0.83096 | Normal | 74.9841 | -0.79877 | Day | 202512 | 2025-12-02 | 0.79877
2025-12-02 13:14 | 72.6584 | FALSE | FALSE | -0.95428 | -1.3309 | -2.0559 | -2.7517 | 0 |  |  | none | FALSE | 0 | 71.7041 | FALSE | FALSE | 0.0488 |  | 73.2092 | 0 | 0 | -0.11295 | 0.24914 | 0.45336 | 0.75254 | Normal | 74.7143 | -0.73192 | Day | 202512 | 2025-12-02 | 0.73192
2025-12-02 13:29 | 72.3758 | FALSE | FALSE | -0.60867 | -0.84811 | -2.0213 | -2.7169 | -0.2826 |  |  | none | FALSE | 0 | 71.7671 | FALSE | FALSE | 0.0716 |  | 73.0821 | 0 | -0.2826 | -0.12708 | 0.25041 | -0.62107 | 0.65749 | Normal | 74.3971 | -1.0743 | Day | 202512 | 2025-12-02 | 1.0743
2025-12-02 13:43 | 72.3758 | FALSE | FALSE | -0.44892 | -0.62414 | -1.6074 | -2.1727 | 0 |  |  | none | FALSE | 0 | 71.9269 | FALSE | FALSE | 0.0751 |  | 72.955 | 0 | 0 | -0.12708 | 0.25041 | 0.5075 | 0.51408 | Normal | 73.9832 | -1.1267 | Day | 202512 | 2025-12-02 | 1.1267
2025-12-02 13:58 | 72.3758 | FALSE | FALSE | -0.22654 | -0.31399 | -1.1591 | -1.5763 | 0 |  |  | none | FALSE | 0 | 72.1493 | FALSE | FALSE | 0.0897 |  | 72.8421 | 0 | 0 | -0.11295 | 0.24914 | 0.45336 | 0.34642 | Normal | 73.5349 | -1.346 | Day | 202512 | 2025-12-02 | 1.346
2025-12-02 14:13 | 72.3758 | FALSE | FALSE | -0.16658 | -0.23069 | -0.95786 | -1.3062 | 0 |  |  | none | FALSE | 0 | 72.2092 | FALSE | FALSE | 0.0938 |  | 72.7714 | 0 | 0 | -0.07065 | 0.18049 | 0.39144 | 0.28111 | Normal | 73.3337 | -1.4074 | Day | 202512 | 2025-12-02 | 1.4074
2025-12-02 14:28 | 72.3758 | FALSE | FALSE | -0.19304 | -0.26743 | -0.89954 | -1.2276 | 0 |  |  | none | FALSE | 0 | 72.1828 | FALSE | FALSE | 0.0862 |  | 72.7291 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.27315 | Normal | 73.2753 | -1.2933 | Day | 202512 | 2025-12-02 | 1.2933
2025-12-02 14:43 | 72.3758 | FALSE | FALSE | -0.20455 | -0.28342 | -0.82627 | -1.1288 | 0 |  |  | none | FALSE | 0 | 72.1712 | FALSE | FALSE | 0.0804 |  | 72.6867 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.25771 | Normal | 73.2021 | -1.2063 | Day | 202512 | 2025-12-02 | 1.2063
2025-12-02 14:58 | 72.3758 | FALSE | FALSE | -0.19815 | -0.27453 | -0.73509 | -1.0054 | 0 |  |  | none | FALSE | 0 | 72.1777 | FALSE | FALSE | 0.0767 |  | 72.6443 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.23331 | Normal | 73.1109 | -1.1507 | Day | 202512 | 2025-12-02 | 1.1507
2025-12-02 15:13 | 72.3758 | FALSE | FALSE | -0.21914 | -0.30371 | -0.69956 | -0.95732 | 0 |  |  | none | FALSE | 0 | 72.1567 | FALSE | FALSE | 0.0697 |  | 72.616 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.22968 | Normal | 73.0754 | -1.0459 | Day | 202512 | 2025-12-02 | 1.0459
2025-12-02 15:28 | 72.095 | FALSE | FALSE | -0.009536 | -0.013229 | -0.96696 | -1.3235 | -0.2808 |  |  | none | FALSE | 0 | 72.0855 | FALSE | FALSE | 0.1307 |  | 72.5737 | 0 | -0.2808 | -0.0423 | 0.13813 | -1.7266 | 0.24412 | Normal | 73.062 | -1.9609 | Day | 202512 | 2025-12-02 | 1.9609
2025-12-02 15:43 | 72.095 | FALSE | FALSE | -0.064284 | -0.089246 | -0.9371 | -1.2831 | 0 |  |  | none | FALSE | 0 | 72.0307 | FALSE | FALSE | 0.1162 |  | 72.5314 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.25035 | Normal | 73.0321 | -1.7432 | Day | 202512 | 2025-12-02 | 1.7432
2025-12-02 15:58 | 72.095 | FALSE | FALSE | -0.10382 | -0.14422 | -0.89204 | -1.2222 | 0 |  |  | none | FALSE | 0 | 71.9912 | FALSE | FALSE | 0.1055 |  | 72.4891 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.24897 | Normal | 72.987 | -1.583 | Day | 202512 | 2025-12-02 | 1.583
2025-12-02 16:13 | 72.095 | FALSE | FALSE | -0.15489 | -0.2153 | -0.88677 | -1.2151 | 0 |  |  | none | FALSE | 0 | 71.9401 | FALSE | FALSE | 0.0937 |  | 72.4609 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.26041 | Normal | 72.9818 | -1.4052 | Day | 202512 | 2025-12-02 | 1.4052
2025-12-02 16:28 | 72.3758 | TRUE | FALSE | -0.44255 | -0.61522 | -0.58457 | -0.80121 | 0.2808 |  |  | none | FALSE | 1 | 71.9333 | FALSE | FALSE | 0.047 |  | 72.4468 | 0 | 0.2808 | -0.01413 | 0.14387 | 2.0499 | 0.25678 | Normal | 72.9604 | -0.27654 | Day | 202512 | 2025-12-02 | 0.27654
2025-12-02 16:42 | 72.3758 | FALSE | FALSE | -0.41553 | -0.57745 | -0.50103 | -0.68751 | 0 |  |  | none | FALSE | 1 | 71.9603 | FALSE | FALSE | 0.041 |  | 72.4185 | 0 | 0 | -0.02826 | 0.12596 | 0.22436 | 0.22914 | Normal | 72.8768 | -0.18657 | Day | 202512 | 2025-12-02 | 0.18657
2025-12-02 16:57 | 72.6584 | TRUE | FALSE | -0.65874 | -0.91492 | -0.15078 | -0.20709 | 0.2826 |  |  | none | FALSE | 2 | 71.9997 | TRUE | FALSE | 0.1408 |  | 72.4044 | 0 | 0.2826 | -0.01413 | 0.14387 | 2.0624 | 0.20238 | Normal | 72.8092 | 1.255 | Day | 202512 | 2025-12-02 | 1.255
2025-12-02 17:12 | 72.6584 | FALSE | FALSE | -0.65874 | -0.91492 | -0.15078 | -0.20709 | 0 |  |  | none | FALSE | 2 | 71.9997 | FALSE | FALSE | 0.1408 |  | 72.4044 | 0 | 0 | 0 | 0.12925 | 0 | 0.20238 | Normal | 72.8092 | 1.255 | Day | 202512 | 2025-12-02 | 1.255
2025-12-02 17:27 | 72.6584 | FALSE | FALSE | -0.65874 | -0.91492 | -0.15078 | -0.20709 | 0 |  |  | none | FALSE | 2 | 71.9997 | FALSE | FALSE | 0.1408 |  | 72.4044 | 0 | 0 | 0 | 0.12925 | 0 | 0.20238 | Normal | 72.8092 | 1.255 | Day | 202512 | 2025-12-02 | 1.255
2025-12-02 17:42 | 72.3758 | FALSE | FALSE | -0.37227 | -0.51701 | -0.40125 | -0.55134 | -0.2826 |  |  | none | FALSE | 2 | 72.0035 | FALSE | FALSE | 0.0621 |  | 72.3903 | 0 | -0.2826 | -0.01413 | 0.14387 | -1.866 | 0.19338 | Normal | 72.777 | -0.074931 | Night | 202512 | 2025-12-02 | 0.074931
2025-12-02 17:57 | 72.3758 | FALSE | FALSE | -0.36522 | -0.50718 | -0.36594 | -0.50307 | 0 |  |  | none | FALSE | 2 | 72.0106 | FALSE | FALSE | 0.0573 |  | 72.3762 | 0 | 0 | -0.01413 | 0.14387 | 0.098211 | 0.18279 | Normal | 72.7417 | -0.0019695 | Night | 202512 | 2025-12-02 | 0.0019695
2025-12-02 18:12 | 72.3758 | FALSE | FALSE | -0.35442 | -0.4921 | -0.32688 | -0.44961 | 0 |  |  | none | FALSE | 2 | 72.0214 | FALSE | FALSE | 0.0625 |  | 72.362 | 0 | 0 | -0.01413 | 0.14387 | 0.098211 | 0.17032 | Normal | 72.7027 | 0.080846 | Night | 202512 | 2025-12-02 | 0.080846
2025-12-02 18:27 | 72.3758 | FALSE | FALSE | -0.35442 | -0.4921 | -0.32688 | -0.44961 | 0 |  |  | none | FALSE | 2 | 72.0214 | FALSE | FALSE | 0.0625 |  | 72.362 | 0 | 0 | 0 | 0.12925 | 0 | 0.17032 | Normal | 72.7027 | 0.080846 | Night | 202512 | 2025-12-02 | 0.080846
2025-12-02 18:42 | 72.095 | FALSE | FALSE | -0.10782 | -0.14977 | -0.6138 | -0.84419 | -0.2808 |  |  | none | FALSE | 2 | 71.9872 | FALSE | FALSE | 0.1506 |  | 72.348 | 0 | -0.2808 | -0.01404 | 0.1437 | -1.8564 | 0.1804 | Normal | 72.7088 | -1.4024 | Night | 202512 | 2025-12-02 | 1.4024
2025-12-02 18:42 | 72.095 | FALSE | FALSE | -0.13876 | -0.19284 | -0.61666 | -0.84809 | 0 |  |  | none | FALSE | 1 | 71.9562 | FALSE | FALSE | 0.1129 |  | 72.334 | 0 | 0 | -0.01404 | 0.1437 | 0.097705 | 0.18885 | Normal | 72.7117 | -1.2653 | Night | 202512 | 2025-12-02 | 1.2653
2025-12-02 18:42 | 72.095 | FALSE | FALSE | -0.16686 | -0.23198 | -0.61668 | -0.84812 | 0 |  |  | none | FALSE | 1 | 71.9281 | FALSE | FALSE | 0.1051 |  | 72.3199 | 0 | 0 | -0.01404 | 0.1437 | 0.097705 | 0.19589 | Normal | 72.7117 | -1.1482 | Night | 202512 | 2025-12-02 | 1.1482
2025-12-02 18:57 | 72.941 | TRUE | FALSE | -1.0731 | -1.4932 | 0.11254 | 0.15453 | 0.846 | 2025-12-02 22:55 | 2025-12-02 18:57 | upper | TRUE | 1 | 71.8679 | FALSE | FALSE | 0.2503 | 2.4686 | 72.3482 | 1 | 0.846 | 0.02826 | 0.24018 | 3.4047 | 0.24014 | Extreme triggered | 72.8285 | 2.4686 | Night | 202512 | 2025-12-02 | 2.4686
2025-12-02 19:12 | 73.2236 | FALSE | FALSE | -1.453 | -2.0244 | 0.21313 | 0.29191 | 0.2826 |  | 2025-12-02 18:57 | upper | TRUE | 1 | 71.7706 | FALSE | FALSE | 0.322 | 2.5781 | 72.3906 | 2 | 0.2826 | 0.04239 | 0.24665 | 0.97388 | 0.30996 | Extreme/elevated | 73.0105 | 2.6876 | Night | 202512 | 2025-12-02 | 2.6876
2025-12-02 19:27 | 73.2236 | FALSE | FALSE | -1.5137 | -2.1108 | 0.067617 | 0.092429 | 0 |  | 2025-12-02 18:57 | upper | TRUE | 1 | 71.7099 | FALSE | TRUE | 0.3458 | 2.4478 | 72.433 | 3 | 0 | 0.04239 | 0.24665 | -0.17186 | 0.36152 | Persistent | 73.156 | 2.187 | Night | 202512 | 2025-12-02 | 2.187
2025-12-02 19:41 | 73.2236 | FALSE | FALSE | -1.5521 | -2.1655 | -0.055561 | -0.075821 | 0 |  | 2025-12-02 18:57 | none | FALSE | 1 | 71.6715 | FALSE | FALSE | 0.3813 | 2.3013 | 72.4753 | 4 | 0 | 0.04239 | 0.24665 | -0.17186 | 0.40191 | Persistent | 73.2792 | 1.8618 | Night | 202512 | 2025-12-02 | 1.8618
2025-12-02 19:56 | 73.5062 | FALSE | FALSE | -1.865 | -2.6032 | 0.055628 | 0.075735 | 0.2826 |  | 2025-12-02 18:57 | upper | TRUE | 1 | 71.6412 | FALSE | TRUE | 0.4558 | 2.2656 | 72.5459 | 5 | 0.2826 | 0.07056 | 0.23988 | 0.88395 | 0.45234 | Persistent | 73.4506 | 2.123 | Night | 202512 | 2025-12-02 | 2.123
2025-12-02 20:11 | 73.5062 | FALSE | FALSE | -1.8638 | -2.6015 | -0.084328 | -0.11459 | 0 |  | 2025-12-02 18:57 | none | FALSE | 1 | 71.6424 | FALSE | FALSE | 0.4932 | 2.1925 | 72.6165 | 6 | 0 | 0.07056 | 0.23988 | -0.29415 | 0.48703 | Persistent | 73.5905 | 1.8269 | Night | 202512 | 2025-12-02 | 1.8269
2025-12-02 20:27 | 73.5062 | FALSE | TRUE | -1.8376 | -2.5641 | -0.19928 | -0.27037 | 0 |  | 2025-12-02 18:57 | none | FALSE | 1 | 71.6686 | FALSE | FALSE | 0.5358 | 2.1091 | 72.687 | 7 | 0 | 0.07056 | 0.23988 | -0.29415 | 0.50923 | Confirmed/Materialized Shift | 73.7055 | 1.6087 | Night | 202512 | 2025-12-02 | 1.6087
2025-12-02 20:41 | 73.7888 | FALSE | TRUE | -2.1074 | -2.94 | -0.073247 | -0.099167 | 0.2826 |  | 2025-12-02 18:57 | none | FALSE | 1 | 71.6814 | FALSE | FALSE | 0.5529 | 2.0786 | 72.7717 | 8 | 0.2826 | 0.08469 | 0.24379 | 0.81179 | 0.54517 | Confirmed/Materialized Shift | 73.862 | 1.8656 | Night | 202512 | 2025-12-02 | 1.8656
2025-12-02 20:56 | 73.7888 | FALSE | TRUE | -2.1095 | -2.9429 | -0.21657 | -0.29265 | 0 |  | 2025-12-02 18:57 | none | FALSE | 1 | 71.6793 | FALSE | FALSE | 0.5371 | 2.0285 | 72.8424 | 9 | 0 | 0.07065 | 0.23996 | -0.29442 | 0.58151 | Confirmed/Materialized Shift | 74.0054 | 1.6276 | Night | 202512 | 2025-12-02 | 1.6276
2025-12-02 21:11 | 73.7888 | FALSE | TRUE | -2.09 | -2.915 | -0.33843 | -0.45656 | 0 |  | 2025-12-02 18:57 | none | FALSE | 1 | 71.6988 | FALSE | FALSE | 0.5247 | 1.9699 | 72.913 | 10 | 0 | 0.07065 | 0.23996 | -0.29442 | 0.60711 | Confirmed/Materialized Shift | 74.1272 | 1.4426 | Night | 202512 | 2025-12-02 | 1.4426
2025-12-02 21:26 | 73.7888 | FALSE | TRUE | -2.0876 | -2.9116 | -0.44908 | -0.60492 | 0 |  | 2025-12-02 18:57 | none | FALSE | 0 | 71.7012 | FALSE | FALSE | 0.4861 | 1.9083 | 72.9695 | 11 | 0 | 0.05652 | 0.2351 | -0.24041 | 0.63418 | Confirmed/Materialized Shift | 74.2379 | 1.2919 | Night | 202512 | 2025-12-02 | 1.2919
2025-12-02 21:41 | 74.0714 | FALSE | TRUE | -2.3814 | -3.3218 | -0.31894 | -0.42873 | 0.2826 |  | 2025-12-02 18:57 | none | FALSE | 0 | 71.69 | FALSE | FALSE | 0.5018 | 1.8766 | 73.0402 | 12 | 0.2826 | 0.07065 | 0.23996 | 0.88327 | 0.67508 | Confirmed/Materialized Shift | 74.3903 | 1.5276 | Night | 202512 | 2025-12-02 | 1.5276
2025-12-02 21:56 | 74.0714 | FALSE | TRUE | -2.373 | -3.3098 | -0.45191 | -0.6064 | 0 |  | 2025-12-02 18:57 | none | FALSE | 0 | 71.6984 | FALSE | FALSE | 0.4907 | 1.8368 | 73.1108 | 13 | 0 | 0.07065 | 0.23996 | -0.29442 | 0.70624 | Confirmed/Materialized Shift | 74.5233 | 1.3601 | Night | 202512 | 2025-12-02 | 1.3601
2025-12-02 22:11 | 74.0714 | FALSE | TRUE | -2.3059 | -3.2132 | -0.55437 | -0.74286 | 0 |  | 2025-12-02 18:57 | none | FALSE | 0 | 71.7655 | FALSE | FALSE | 0.4816 | 1.7931 | 73.1956 | 14 | 0 | 0.08478 | 0.22598 | -0.37517 | 0.71508 | Confirmed/Materialized Shift | 74.6258 | 1.2247 | Night | 202512 | 2025-12-02 | 1.2247
2025-12-02 22:26 | 74.0714 | FALSE | TRUE | -2.2176 | -3.0862 | -0.63555 | -0.85072 | 0 |  | 2025-12-02 18:57 | none | FALSE | 0 | 71.8538 | FALSE | FALSE | 0.4739 | 1.7475 | 73.2804 | 15 | 0 | 0.08478 | 0.22598 | -0.37517 | 0.71328 | Confirmed/Materialized Shift | 74.7069 | 1.109 | Night | 202512 | 2025-12-02 | 1.109
2025-12-02 22:40 | 74.0714 | FALSE | TRUE | -2.1077 | -2.9289 | -0.69529 | -0.92995 | 0 |  | 2025-12-02 18:57 | none | FALSE | 0 | 71.9637 | FALSE | FALSE | 0.4672 | 1.7013 | 73.3652 | 16 | 0 | 0.08478 | 0.22598 | -0.37517 | 0.70076 | Confirmed/Materialized Shift | 74.7667 | 1.0078 | Night | 202512 | 2025-12-02 | 1.0078
2025-12-02 22:55 | 74.0714 | FALSE | FALSE | -1.9753 | -2.7398 | -0.7324 | -0.9791 | 0 |  |  | none | FALSE | 0 | 72.0961 | FALSE | FALSE | 0.0612 |  | 73.45 | 0 | 0 | 0.08478 | 0.22598 | -0.37517 | 0.67693 | Persistence ends | 74.8038 | 0.91805 | Night | 202512 | 2025-12-02 | 0.91805
2025-12-02 23:11 | 74.0714 | FALSE | FALSE | -1.7419 | -2.4083 | -0.69663 | -0.93173 | 0 |  |  | none | FALSE | 0 | 72.3295 | FALSE | FALSE | 0.0572 |  | 73.5488 | 0 | 0 | 0.09882 | 0.21025 | -0.47002 | 0.60963 | Normal | 74.768 | 0.85729 | Night | 202512 | 2025-12-02 | 0.85729
2025-12-02 23:26 | 74.0714 | FALSE | FALSE | -1.4524 | -2.0001 | -0.60481 | -0.80991 | 0 |  |  | none | FALSE | 0 | 72.619 | FALSE | FALSE | 0.0549 |  | 73.6476 | 0 | 0 | 0.09882 | 0.21025 | -0.47002 | 0.51431 | Normal | 74.6762 | 0.82404 | Night | 202512 | 2025-12-02 | 0.82404
2025-12-02 23:40 | 74.0714 | FALSE | FALSE | -1.0648 | -1.4585 | -0.41479 | -0.55686 | 0 |  |  | none | FALSE | 0 | 73.0066 | FALSE | FALSE | 0.0586 |  | 73.7464 | 0 | 0 | 0.09882 | 0.21025 | -0.47002 | 0.36989 | Normal | 74.4862 | 0.87862 | Night | 202512 | 2025-12-02 | 0.87862
2025-12-02 23:55 | 74.0714 | FALSE | FALSE | -0.91615 | -1.2523 | -0.37921 | -0.50934 | 0 |  |  | none | FALSE | 0 | 73.1552 | FALSE | FALSE | 0.0553 |  | 73.8029 | 0 | 0 | 0.05652 | 0.11598 | -0.48734 | 0.32384 | Normal | 74.4506 | 0.82902 | Night | 202512 | 2025-12-02 | 0.82902
2025-12-03 00:10 | 74.0714 | FALSE | FALSE | -0.82311 | -1.1237 | -0.37095 | -0.4983 | 0 |  |  | none | FALSE | 0 | 73.2483 | FALSE | FALSE | 0.0505 |  | 73.8453 | 0 | 0 | 0.04239 | 0.10353 | -0.40945 | 0.29851 | Normal | 74.4423 | 0.75735 | Night | 202512 | 2025-12-03 | 0.75735
2025-12-03 00:25 | 74.0714 | FALSE | FALSE | -0.71119 | -0.96945 | -0.34381 | -0.46202 | 0 |  |  | none | FALSE | 0 | 73.3602 | FALSE | FALSE | 0.0464 |  | 73.8877 | 0 | 0 | 0.04239 | 0.10353 | -0.40945 | 0.26375 | Normal | 74.4152 | 0.69645 | Night | 202512 | 2025-12-03 | 0.69645
2025-12-03 00:40 | 74.0714 | FALSE | FALSE | -0.57135 | -0.77735 | -0.28875 | -0.38832 | 0 |  |  | none | FALSE | 0 | 73.5 | FALSE | FALSE | 0.0438 |  | 73.9301 | 0 | 0 | 0.04239 | 0.10353 | -0.40945 | 0.21503 | Normal | 74.3602 | 0.65713 | Night | 202512 | 2025-12-03 | 0.65713
2025-12-03 00:55 | 74.0714 | FALSE | FALSE | -0.49769 | -0.67645 | -0.27161 | -0.36535 | 0 |  |  | none | FALSE | 0 | 73.5737 | FALSE | FALSE | 0.0392 |  | 73.9584 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.19233 | Normal | 74.343 | 0.58775 | Night | 202512 | 2025-12-03 | 0.58775
2025-12-03 01:10 | 74.0714 | FALSE | FALSE | -0.40765 | -0.55339 | -0.23809 | -0.3204 | 0 |  |  | none | FALSE | 0 | 73.6638 | FALSE | FALSE | 0.035 |  | 73.9866 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.16143 | Normal | 74.3095 | 0.52517 | Night | 202512 | 2025-12-03 | 0.52517
2025-12-03 01:25 | 74.0714 | FALSE | FALSE | -0.28847 | -0.39098 | -0.17543 | -0.23628 | 0 |  |  | none | FALSE | 0 | 73.7829 | FALSE | FALSE | 0.0325 |  | 74.0149 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.11598 | Normal | 74.2468 | 0.48734 | Night | 202512 | 2025-12-03 | 0.48734
2025-12-03 01:39 | 74.0714 | FALSE | FALSE | -0.24945 | -0.33791 | -0.16467 | -0.22182 | 0 |  |  | none | FALSE | 0 | 73.822 | FALSE | FALSE | 0.0273 |  | 74.029 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.10353 | Normal | 74.2361 | 0.40945 | Night | 202512 | 2025-12-03 | 0.40945
2025-12-03 01:55 | 74.0714 | FALSE | FALSE | -0.20222 | -0.27376 | -0.1457 | -0.19632 | 0 |  |  | none | FALSE | 0 | 73.8692 | FALSE | FALSE | 0.0217 |  | 74.0431 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.086982 | Normal | 74.2171 | 0.32489 | Night | 202512 | 2025-12-03 | 0.32489
2025-12-03 02:10 | 74.3522 | TRUE | FALSE | -0.46368 | -0.62754 | 0.098098 | 0.13211 | 0.2808 | 2025-12-03 02:25 | 2025-12-03 02:10 | upper | TRUE | 1 | 73.8885 | FALSE | FALSE | 0.2906 | 3.0733 | 74.0713 | 1 | 0.2808 | 0.02817 | 0.086706 | 2.9136 | 0.091396 | Extreme triggered | 74.2541 | 3.0733 | Night | 202512 | 2025-12-03 | 3.0733
2025-12-03 02:25 | 74.0714 | TRUE | FALSE | -0.11154 | -0.15081 | -0.13962 | -0.18814 | -0.2808 |  |  | none | FALSE | 2 | 73.9599 | TRUE | FALSE | 0.072 |  | 74.0854 | 0 | -0.2808 | 0.01413 | 0.11087 | -2.6601 | 0.062789 | Persistence ends | 74.211 | -0.22361 | Night | 202512 | 2025-12-03 | 0.22361
2025-12-03 02:39 | 74.3522 | TRUE | FALSE | -0.42558 | -0.57567 | 0.079863 | 0.10753 | 0.2808 | 2025-12-03 02:54 | 2025-12-03 02:39 | upper | TRUE | 3 | 73.9266 | TRUE | FALSE | 0.3378 | 2.924 | 74.0995 | 1 | 0.2808 | 0.01404 | 0.11064 | 2.411 | 0.086428 | Extreme triggered | 74.2723 | 2.924 | Night | 202512 | 2025-12-03 | 2.924
2025-12-03 02:54 | 74.0714 | TRUE | FALSE | -0.14478 | -0.19584 | -0.20094 | -0.27054 | -0.2808 |  |  | none | FALSE | 4 | 73.9266 | TRUE | FALSE | 0.1359 |  | 74.0995 | 0 | -0.2808 | 0 | 0.12884 | -2.1794 | 0.086428 | Persistence ends | 74.2723 | -0.32489 | Night | 202512 | 2025-12-03 | 0.32489
2025-12-03 03:09 | 74.0714 | FALSE | FALSE | -0.14478 | -0.19584 | -0.20094 | -0.27054 | 0 |  |  | none | FALSE | 4 | 73.9266 | FALSE | FALSE | 0.1359 |  | 74.0995 | 0 | 0 | 0 | 0.12884 | 0 | 0.086428 | Normal | 74.2723 | -0.32489 | Night | 202512 | 2025-12-03 | 0.32489
2025-12-03 03:24 | 74.0714 | FALSE | FALSE | -0.14478 | -0.19584 | -0.20094 | -0.27054 | 0 |  |  | none | FALSE | 4 | 73.9266 | FALSE | FALSE | 0.1359 |  | 74.0995 | 0 | 0 | 0 | 0.12884 | 0 | 0.086428 | Normal | 74.2723 | -0.32489 | Night | 202512 | 2025-12-03 | 0.32489
2025-12-03 03:39 | 74.0714 | FALSE | FALSE | -0.14478 | -0.19584 | -0.20094 | -0.27054 | 0 |  |  | none | FALSE | 4 | 73.9266 | FALSE | FALSE | 0.1359 |  | 74.0995 | 0 | 0 | 0 | 0.12884 | 0 | 0.086428 | Normal | 74.2723 | -0.32489 | Night | 202512 | 2025-12-03 | 0.32489
2025-12-03 03:54 | 74.3522 | FALSE | FALSE | -0.44442 | -0.60132 | 0.032939 | 0.044321 | 0.2808 | 2025-12-03 04:24 | 2025-12-03 03:54 | upper | TRUE | 4 | 73.9078 | FALSE | FALSE | 0.3261 | 2.3202 | 74.1135 | 1 | 0.2808 | 0.01404 | 0.14333 | 1.8612 | 0.10287 | Extreme triggered | 74.3193 | 2.3202 | Night | 202512 | 2025-12-03 | 2.3202
2025-12-03 04:09 | 74.3522 | FALSE | FALSE | -0.45512 | -0.61588 | -0.0058358 | -0.0078482 | 0 |  | 2025-12-03 03:54 | none | FALSE | 4 | 73.8971 | FALSE | FALSE | 0.3585 | 2.1348 | 74.1276 | 2 | 0 | 0.01404 | 0.14333 | -0.097959 | 0.11524 | Extreme/elevated | 74.358 | 1.9494 | Night | 202512 | 2025-12-03 | 1.9494
2025-12-03 04:24 | 74.0714 | FALSE | FALSE | -0.17432 | -0.23589 | -0.28664 | -0.38548 | -0.2808 |  |  | none | FALSE | 4 | 73.8971 | FALSE | FALSE | 0.1468 |  | 74.1276 | 0 | -0.2808 | 0 | 0.1578 | -1.7795 | 0.11524 | Persistence ends | 74.358 | -0.48734 | Night | 202512 | 2025-12-03 | 0.48734
2025-12-03 04:39 | 74.0714 | FALSE | FALSE | -0.17432 | -0.23589 | -0.28664 | -0.38548 | 0 |  |  | none | FALSE | 3 | 73.8971 | FALSE | FALSE | 0.1182 |  | 74.1276 | 0 | 0 | 0 | 0.1578 | 0 | 0.11524 | Normal | 74.358 | -0.48734 | Night | 202512 | 2025-12-03 | 0.48734
2025-12-03 04:54 | 74.3522 | FALSE | FALSE | -0.4601 | -0.62266 | -0.038897 | -0.052288 | 0.2808 |  |  | none | FALSE | 2 | 73.8921 | FALSE | FALSE | 0.1697 |  | 74.1416 | 0 | 0.2808 | 0.01404 | 0.16983 | 1.5708 | 0.12475 | Normal | 74.3911 | 1.6882 | Night | 202512 | 2025-12-03 | 1.6882
2025-12-03 05:09 | 74.0714 | FALSE | FALSE | -0.1793 | -0.24265 | -0.3197 | -0.42975 | -0.2808 |  |  | none | FALSE | 1 | 73.8921 | FALSE | FALSE | 0.0661 |  | 74.1416 | 0 | -0.2808 | 0 | 0.18221 | -1.5411 | 0.12475 | Normal | 74.3911 | -0.56273 | Night | 202512 | 2025-12-03 | 0.56273
2025-12-03 05:24 | 74.0714 | FALSE | FALSE | -0.1793 | -0.24265 | -0.3197 | -0.42975 | 0 |  |  | none | FALSE | 0 | 73.8921 | FALSE | FALSE | 0.0375 |  | 74.1416 | 0 | 0 | 0 | 0.18221 | 0 | 0.12475 | Normal | 74.3911 | -0.56273 | Night | 202512 | 2025-12-03 | 0.56273
2025-12-03 05:38 | 74.0714 | FALSE | FALSE | -0.1793 | -0.24265 | -0.3197 | -0.42975 | 0 |  |  | none | FALSE | 0 | 73.8921 | FALSE | FALSE | 0.0375 |  | 74.1416 | 0 | 0 | 0 | 0.18221 | 0 | 0.12475 | Normal | 74.3911 | -0.56273 | Night | 202512 | 2025-12-03 | 0.56273
2025-12-03 05:53 | 74.0714 | FALSE | FALSE | -0.1793 | -0.24265 | -0.3197 | -0.42975 | 0 |  |  | none | FALSE | 0 | 73.8921 | FALSE | FALSE | 0.0375 |  | 74.1416 | 0 | 0 | 0 | 0.18221 | 0 | 0.12475 | Normal | 74.3911 | -0.56273 | Night | 202512 | 2025-12-03 | 0.56273
2025-12-03 06:08 | 74.0714 | FALSE | FALSE | -0.1793 | -0.24265 | -0.3197 | -0.42975 | 0 |  |  | none | FALSE | 0 | 73.8921 | FALSE | FALSE | 0.0375 |  | 74.1416 | 0 | 0 | 0 | 0.18221 | 0 | 0.12475 | Normal | 74.3911 | -0.56273 | Night | 202512 | 2025-12-03 | 0.56273
2025-12-03 06:23 | 74.0714 | FALSE | FALSE | -0.1793 | -0.24265 | -0.3197 | -0.42975 | 0 |  |  | none | FALSE | 0 | 73.8921 | FALSE | FALSE | 0.0375 |  | 74.1416 | 0 | 0 | 0 | 0.18221 | 0 | 0.12475 | Normal | 74.3911 | -0.56273 | Night | 202512 | 2025-12-03 | 0.56273
2025-12-03 06:38 | 74.0714 | FALSE | FALSE | -0.1793 | -0.24265 | -0.3197 | -0.42975 | 0 |  |  | none | FALSE | 0 | 73.8921 | FALSE | FALSE | 0.0375 |  | 74.1416 | 0 | 0 | 0 | 0.18221 | 0 | 0.12475 | Normal | 74.3911 | -0.56273 | Night | 202512 | 2025-12-03 | 0.56273
2025-12-03 06:53 | 74.0714 | FALSE | FALSE | -0.1793 | -0.24265 | -0.3197 | -0.42975 | 0 |  |  | none | FALSE | 0 | 73.8921 | FALSE | FALSE | 0.0375 |  | 74.1416 | 0 | 0 | 0 | 0.18221 | 0 | 0.12475 | Normal | 74.3911 | -0.56273 | Night | 202512 | 2025-12-03 | 0.56273
2025-12-03 07:08 | 74.0714 | FALSE | FALSE | -0.17432 | -0.23589 | -0.28664 | -0.38548 | 0 |  |  | none | FALSE | 0 | 73.8971 | FALSE | FALSE | 0.0325 |  | 74.1276 | 0 | 0 | -0.01404 | 0.16983 | 0.082671 | 0.11524 | Normal | 74.358 | -0.48734 | Day | 202512 | 2025-12-03 | 0.48734
2025-12-03 07:23 | 74.0714 | FALSE | FALSE | -0.17432 | -0.23589 | -0.28664 | -0.38548 | 0 |  |  | none | FALSE | 0 | 73.8971 | FALSE | FALSE | 0.0325 |  | 74.1276 | 0 | 0 | 0 | 0.1578 | 0 | 0.11524 | Normal | 74.358 | -0.48734 | Day | 202512 | 2025-12-03 | 0.48734
2025-12-03 07:30 | 74.0714 | FALSE | FALSE | -0.16362 | -0.22139 | -0.24786 | -0.33351 | 0 |  |  | none | FALSE | 0 | 73.9078 | FALSE | FALSE | 0.0273 |  | 74.1135 | 0 | 0 | -0.01404 | 0.14333 | 0.097959 | 0.10287 | Normal | 74.3193 | -0.40945 | Day | 202512 | 2025-12-03 | 0.40945
2025-12-03 07:45 | 74.0714 | FALSE | FALSE | -0.16362 | -0.22139 | -0.24786 | -0.33351 | 0 |  |  | none | FALSE | 0 | 73.9078 | FALSE | FALSE | 0.0273 |  | 74.1135 | 0 | 0 | 0 | 0.12884 | 0 | 0.10287 | Normal | 74.3193 | -0.40945 | Day | 202512 | 2025-12-03 | 0.40945
2025-12-03 08:01 | 74.0714 | FALSE | FALSE | -0.16362 | -0.22139 | -0.24786 | -0.33351 | 0 |  |  | none | FALSE | 0 | 73.9078 | FALSE | FALSE | 0.0273 |  | 74.1135 | 0 | 0 | 0 | 0.12884 | 0 | 0.10287 | Normal | 74.3193 | -0.40945 | Day | 202512 | 2025-12-03 | 0.40945
2025-12-03 08:16 | 74.0714 | FALSE | FALSE | -0.16362 | -0.22139 | -0.24786 | -0.33351 | 0 |  |  | none | FALSE | 0 | 73.9078 | FALSE | FALSE | 0.0273 |  | 74.1135 | 0 | 0 | 0 | 0.12884 | 0 | 0.10287 | Normal | 74.3193 | -0.40945 | Day | 202512 | 2025-12-03 | 0.40945
2025-12-03 08:30 | 74.0714 | FALSE | FALSE | -0.16362 | -0.22139 | -0.24786 | -0.33351 | 0 |  |  | none | FALSE | 0 | 73.9078 | FALSE | FALSE | 0.0273 |  | 74.1135 | 0 | 0 | 0 | 0.12884 | 0 | 0.10287 | Normal | 74.3193 | -0.40945 | Day | 202512 | 2025-12-03 | 0.40945
2025-12-03 08:45 | 74.0714 | FALSE | FALSE | -0.14478 | -0.19584 | -0.20094 | -0.27054 | 0 |  |  | none | FALSE | 0 | 73.9266 | FALSE | FALSE | 0.0217 |  | 74.0995 | 0 | 0 | -0.01404 | 0.11064 | 0.12689 | 0.086428 | Normal | 74.2723 | -0.32489 | Day | 202512 | 2025-12-03 | 0.32489
2025-12-03 08:45 | 74.0714 | FALSE | FALSE | -0.11154 | -0.15081 | -0.13962 | -0.18814 | 0 |  |  | none | FALSE | 0 | 73.9599 | FALSE | FALSE | 0.0149 |  | 74.0854 | 0 | 0 | -0.01404 | 0.11064 | 0.12689 | 0.062789 | Normal | 74.211 | -0.22361 | Day | 202512 | 2025-12-03 | 0.22361
2025-12-03 08:48 | 74.0714 | FALSE | FALSE | -0.11154 | -0.15081 | -0.13962 | -0.18814 | 0 |  |  | none | FALSE | 0 | 73.9599 | FALSE | FALSE | 0.0149 |  | 74.0854 | 0 | 0 | 0 | 0.091104 | 0 | 0.062789 | Normal | 74.211 | -0.22361 | Day | 202512 | 2025-12-03 | 0.22361
2025-12-03 09:00 | 72.941 | TRUE | FALSE | 0.56065 | 0.76277 | -1.6152 | -2.1664 | -1.1304 | 2025-12-03 10:15 | 2025-12-03 09:00 | lower | TRUE | 1 | 73.5017 | FALSE | FALSE | 0.3608 | 4.1266 | 74.0289 | 1 | -1.1304 | -0.05652 | 0.26868 | -3.9968 | 0.26363 | Extreme triggered | 74.5562 | -4.1266 | Day | 202512 | 2025-12-03 | 4.1266
2025-12-03 09:15 | 72.095 | TRUE | FALSE | 0.82619 | 1.133 | -2.8159 | -3.759 | -0.846 |  | 2025-12-03 09:00 | lower | TRUE | 2 | 72.9212 | TRUE | FALSE | 0.4155 | 3.8938 | 73.9161 | 2 | -0.846 | -0.11286 | 0.3093 | -2.3703 | 0.49743 | Extreme/elevated | 74.9109 | -3.6609 | Day | 202512 | 2025-12-03 | 3.6609
2025-12-03 09:30 | 72.095 | FALSE | FALSE | 0.44094 | 0.6079 | -3.0035 | -3.9995 | 0 |  | 2025-12-03 09:00 | lower | TRUE | 2 | 72.5359 | FALSE | TRUE | 0.4078 | 3.4919 | 73.8172 | 3 | 0 | -0.09882 | 0.30764 | 0.32122 | 0.64065 | Persistent | 75.0985 | -2.6883 | Day | 202512 | 2025-12-03 | 2.6883
2025-12-03 09:44 | 72.3758 | FALSE | FALSE | -0.069972 | -0.096772 | -2.7833 | -3.7032 | 0.2808 |  | 2025-12-03 09:00 | none | FALSE | 2 | 72.3058 | FALSE | FALSE | 0.4125 | 3.0944 | 73.7325 | 4 | 0.2808 | -0.08478 | 0.3186 | 1.1475 | 0.71332 | Persistent | 75.1591 | -1.9019 | Day | 202512 | 2025-12-03 | 1.9019
2025-12-03 09:59 | 72.6584 | FALSE | FALSE | -0.49089 | -0.68021 | -2.4977 | -3.3234 | 0.2826 |  | 2025-12-03 09:00 | none | FALSE | 2 | 72.1675 | FALSE | FALSE | 0.4324 | 2.7441 | 73.6618 | 5 | 0.2826 | -0.07065 | 0.32867 | 1.0748 | 0.74715 | Persistent | 75.1561 | -1.343 | Day | 202512 | 2025-12-03 | 1.343
2025-12-03 10:15 | 73.2236 | FALSE | FALSE | -1.0977 | -1.5219 | -1.8893 | -2.5153 | 0.5652 |  |  | none | FALSE | 2 | 72.1259 | FALSE | FALSE | 0.0925 |  | 73.6194 | 0 | 0.5652 | -0.04239 | 0.35805 | 1.697 | 0.74674 | Persistence ends | 75.1129 | -0.53006 | Day | 202512 | 2025-12-03 | 0.53006
2025-12-03 10:30 | 73.2236 | FALSE | FALSE | -1.1341 | -1.5733 | -1.841 | -2.4526 | 0 |  |  | none | FALSE | 2 | 72.0895 | FALSE | FALSE | 0.0888 |  | 73.577 | 0 | 0 | -0.04239 | 0.35805 | 0.11839 | 0.74379 | Normal | 75.0646 | -0.47517 | Day | 202512 | 2025-12-03 | 0.47517
2025-12-03 10:44 | 73.2236 | FALSE | FALSE | -1.1655 | -1.6174 | -1.7876 | -2.3831 | 0 |  |  | none | FALSE | 2 | 72.0581 | FALSE | FALSE | 0.0852 |  | 73.5346 | 0 | 0 | -0.04239 | 0.35805 | 0.11839 | 0.73827 | Normal | 75.0112 | -0.42131 | Day | 202512 | 2025-12-03 | 0.42131
2025-12-03 10:59 | 73.5062 | FALSE | FALSE | -1.4546 | -2.0188 | -1.4549 | -1.9409 | 0.2826 |  |  | none | FALSE | 2 | 72.0516 | FALSE | FALSE | 0.0572 |  | 73.5064 | 0 | 0.2826 | -0.02826 | 0.36531 | 0.85095 | 0.72738 | Normal | 74.9611 | -0.00024746 | Day | 202512 | 2025-12-03 | 0.00024746
2025-12-03 11:14 | 73.5062 | FALSE | FALSE | -1.4584 | -2.0242 | -1.4022 | -1.8719 | 0 |  |  | none | FALSE | 2 | 72.0478 | FALSE | FALSE | 0.0598 |  | 73.4781 | 0 | 0 | -0.02826 | 0.36531 | 0.077359 | 0.71515 | Normal | 74.9084 | 0.039265 | Day | 202512 | 2025-12-03 | 0.039265
2025-12-03 11:29 | 73.5062 | FALSE | FALSE | -1.4594 | -2.0256 | -1.3467 | -1.7991 | 0 |  |  | none | FALSE | 1 | 72.0468 | FALSE | FALSE | 0.0339 |  | 73.4499 | 0 | 0 | -0.02826 | 0.36531 | 0.077359 | 0.70151 | Normal | 74.8529 | 0.080313 | Day | 202512 | 2025-12-03 | 0.080313
2025-12-03 11:44 | 73.2236 | FALSE | FALSE | -1.191 | -1.6535 | -1.5588 | -2.0844 | -0.2826 |  |  | none | FALSE | 0 | 72.0326 | FALSE | FALSE | 0.0178 |  | 73.4075 | 0 | -0.2826 | -0.04239 | 0.3696 | -0.64992 | 0.68745 | Normal | 74.7824 | -0.26747 | Day | 202512 | 2025-12-03 | 0.26747
2025-12-03 11:59 | 72.941 | FALSE | FALSE | -0.94279 | -1.3095 | -1.7627 | -2.3596 | -0.2826 |  |  | none | FALSE | 0 | 71.9982 | FALSE | FALSE | 0.0404 |  | 73.3509 | 0 | -0.2826 | -0.05652 | 0.37328 | -0.60566 | 0.67637 | Normal | 74.7037 | -0.6061 | Day | 202512 | 2025-12-03 | 0.6061
2025-12-03 12:14 | 72.6584 | FALSE | FALSE | -0.71996 | -1.0008 | -1.9638 | -2.6316 | -0.2826 |  |  | none | FALSE | 0 | 71.9384 | FALSE | FALSE | 0.0618 |  | 73.2803 | 0 | -0.2826 | -0.07065 | 0.37636 | -0.56316 | 0.67093 | Normal | 74.6222 | -0.92692 | Day | 202512 | 2025-12-03 | 0.92692
2025-12-03 12:29 | 72.3758 | FALSE | FALSE | -0.52594 | -0.732 | -2.1654 | -2.9049 | -0.2826 |  |  | none | FALSE | 0 | 71.8499 | FALSE | FALSE | 0.0812 |  | 73.1955 | 0 | -0.2826 | -0.08478 | 0.37887 | -0.52214 | 0.67283 | Normal | 74.5412 | -1.2183 | Day | 202512 | 2025-12-03 | 1.2183
2025-12-03 12:44 | 72.095 | FALSE | FALSE | -0.36327 | -0.50643 | -2.3667 | -3.1784 | -0.2808 |  |  | none | FALSE | 0 | 71.7317 | FALSE | FALSE | 0.0978 |  | 73.0967 | 0 | -0.2808 | -0.09882 | 0.38076 | -0.47794 | 0.68249 | Normal | 74.4617 | -1.4677 | Day | 202512 | 2025-12-03 | 1.4677
2025-12-03 12:59 | 72.3758 | FALSE | FALSE | -0.68384 | -0.95385 | -1.9561 | -2.6315 | 0.2808 |  |  | none | FALSE | 0 | 71.692 | FALSE | FALSE | 0.0643 |  | 73.0119 | 0 | 0.2808 | -0.08478 | 0.38967 | 0.93819 | 0.65998 | Normal | 74.3319 | -0.96385 | Day | 202512 | 2025-12-03 | 0.96385
2025-12-03 13:14 | 72.3758 | FALSE | FALSE | -0.69802 | -0.97383 | -1.8007 | -2.4276 | 0 |  |  | none | FALSE | 0 | 71.6778 | FALSE | FALSE | 0.0588 |  | 72.9271 | 0 | 0 | -0.08478 | 0.38967 | 0.21757 | 0.62468 | Normal | 74.1765 | -0.8826 | Day | 202512 | 2025-12-03 | 0.8826
2025-12-03 13:29 | 72.6584 | FALSE | FALSE | -0.93303 | -1.3008 | -1.3292 | -1.7965 | 0.2826 |  |  | none | FALSE | 0 | 71.7254 | FALSE | FALSE | 0.0234 |  | 72.8565 | 0 | 0.2826 | -0.07065 | 0.39794 | 0.8877 | 0.56556 | Normal | 73.9876 | -0.35025 | Day | 202512 | 2025-12-03 | 0.35025
2025-12-03 13:43 | 72.6584 | FALSE | FALSE | -0.85028 | -1.1841 | -1.1052 | -1.4982 | 0 |  |  | none | FALSE | 0 | 71.8081 | FALSE | FALSE | 0.0174 |  | 72.7858 | 0 | 0 | -0.07065 | 0.39794 | 0.17754 | 0.48886 | Normal | 73.7636 | -0.26069 | Day | 202512 | 2025-12-03 | 0.26069
2025-12-03 13:58 | 72.941 | FALSE | FALSE | -1.1329 | -1.5777 | -0.82256 | -1.1151 | 0.2826 |  |  | none | FALSE | 0 | 71.8081 | FALSE | FALSE | 0.0212 |  | 72.7858 | 0 | 0.2826 | 0 | 0.31711 | 0.89117 | 0.48886 | Normal | 73.7636 | 0.31739 | Day | 202512 | 2025-12-03 | 0.31739
2025-12-03 14:13 | 72.941 | FALSE | FALSE | -1.0364 | -1.4414 | -0.81072 | -1.0993 | 0 |  |  | none | FALSE | 0 | 71.9046 | FALSE | FALSE | 0.0163 |  | 72.8281 | 0 | 0 | 0.0423 | 0.24699 | -0.17126 | 0.46179 | Normal | 73.7517 | 0.2444 | Day | 202512 | 2025-12-03 | 0.2444
2025-12-03 14:28 | 72.941 | FALSE | FALSE | -0.92788 | -1.2885 | -0.78676 | -1.0671 | 0 |  |  | none | FALSE | 0 | 72.0131 | FALSE | FALSE | 0.011 |  | 72.8704 | 0 | 0 | 0.0423 | 0.24699 | -0.17126 | 0.42866 | Normal | 73.7278 | 0.16461 | Day | 202512 | 2025-12-03 | 0.16461
2025-12-03 14:43 | 72.941 | FALSE | FALSE | -0.86763 | -1.2038 | -0.78303 | -1.0621 | 0 |  |  | none | FALSE | 0 | 72.0734 | FALSE | FALSE | 0.0068 |  | 72.8987 | 0 | 0 | 0.02826 | 0.24062 | -0.11745 | 0.41266 | Normal | 73.724 | 0.1025 | Day | 202512 | 2025-12-03 | 0.1025
2025-12-03 14:58 | 72.941 | FALSE | FALSE | -0.84582 | -1.1732 | -0.78948 | -1.0708 | 0 |  |  | none | FALSE | 0 | 72.0952 | FALSE | FALSE | 0.0046 |  | 72.9128 | 0 | 0 | 0.01413 | 0.23308 | -0.060623 | 0.40882 | Normal | 73.7305 | 0.068905 | Day | 202512 | 2025-12-03 | 0.068905
2025-12-03 15:13 | 72.941 | FALSE | FALSE | -0.847 | -1.1749 | -0.7624 | -1.0344 | 0 |  |  | none | FALSE | 0 | 72.094 | FALSE | FALSE | 0.007 |  | 72.8987 | 0 | 0 | -0.01413 | 0.19368 | 0.072955 | 0.40235 | Normal | 73.7034 | 0.10513 | Day | 202512 | 2025-12-03 | 0.10513
2025-12-03 15:28 | 73.2236 | FALSE | FALSE | -1.1296 | -1.5668 | -0.4798 | -0.65099 | 0.2826 |  |  | none | FALSE | 0 | 72.094 | FALSE | FALSE | 0.0538 |  | 72.8987 | 0 | 0.2826 | 0 | 0.20476 | 1.3802 | 0.40235 | Normal | 73.7034 | 0.80751 | Day | 202512 | 2025-12-03 | 0.80751
2025-12-03 15:43 | 72.941 | FALSE | FALSE | -0.84691 | -1.1747 | -0.73405 | -0.99633 | -0.2826 |  |  | none | FALSE | 0 | 72.0941 | FALSE | FALSE | 0.0095 |  | 72.8846 | 0 | -0.2826 | -0.01413 | 0.21429 | -1.2528 | 0.39524 | Normal | 73.675 | 0.14277 | Day | 202512 | 2025-12-03 | 0.14277
2025-12-03 15:58 | 72.941 | FALSE | FALSE | -0.82009 | -1.1371 | -0.65071 | -0.88421 | 0 |  |  | none | FALSE | 0 | 72.1209 | FALSE | FALSE | 0.0154 |  | 72.8563 | 0 | 0 | -0.02826 | 0.2027 | 0.13942 | 0.3677 | Normal | 73.5917 | 0.23032 | Day | 202512 | 2025-12-03 | 0.23032
2025-12-03 16:13 | 72.6584 | FALSE | FALSE | -0.51721 | -0.71695 | -0.82825 | -1.1271 | -0.2826 |  |  | none | FALSE | 0 | 72.1412 | FALSE | FALSE | 0.0308 |  | 72.8139 | 0 | -0.2826 | -0.04239 | 0.21033 | -1.1421 | 0.33637 | Normal | 73.4867 | -0.46235 | Day | 202512 | 2025-12-03 | 0.46235
2025-12-03 16:28 | 72.6584 | FALSE | FALSE | -0.4778 | -0.66195 | -0.70406 | -0.9597 | 0 |  |  | none | FALSE | 0 | 72.1806 | FALSE | FALSE | 0.0255 |  | 72.7715 | 0 | 0 | -0.04239 | 0.21033 | 0.20154 | 0.29547 | Normal | 73.3625 | -0.38289 | Day | 202512 | 2025-12-03 | 0.38289
2025-12-03 16:42 | 72.3758 | FALSE | FALSE | -0.22249 | -0.30836 | -0.92917 | -1.2675 | -0.2826 |  |  | none | FALSE | 0 | 72.1533 | FALSE | FALSE | 0.0818 |  | 72.7291 | 0 | -0.2826 | -0.04239 | 0.21033 | -1.1421 | 0.28791 | Normal | 73.305 | -1.2272 | Day | 202512 | 2025-12-03 | 1.2272
2025-12-03 16:57 | 72.3758 | FALSE | FALSE | -0.26233 | -0.36378 | -0.91249 | -1.2451 | 0 |  |  | none | FALSE | 0 | 72.1135 | FALSE | FALSE | 0.0738 |  | 72.7009 | 0 | 0 | -0.02826 | 0.2027 | 0.13942 | 0.29371 | Normal | 73.2883 | -1.1068 | Day | 202512 | 2025-12-03 | 1.1068
2025-12-03 17:12 | 72.3758 | FALSE | FALSE | -0.29409 | -0.408 | -0.91599 | -1.2498 | 0 |  |  | none | FALSE | 0 | 72.0817 | FALSE | FALSE | 0.0685 |  | 72.6868 | 0 | 0 | -0.01413 | 0.19368 | 0.072955 | 0.30252 | Normal | 73.2918 | -1.0279 | Day | 202512 | 2025-12-03 | 1.0279
2025-12-03 17:27 | 72.3758 | FALSE | FALSE | -0.29409 | -0.408 | -0.91599 | -1.2498 | 0 |  |  | none | FALSE | 0 | 72.0817 | FALSE | FALSE | 0.0685 |  | 72.6868 | 0 | 0 | 0 | 0.18308 | 0 | 0.30252 | Normal | 73.2918 | -1.0279 | Day | 202512 | 2025-12-03 | 1.0279
2025-12-03 17:42 | 72.3758 | FALSE | FALSE | -0.23348 | -0.32363 | -0.88346 | -1.2059 | 0 |  |  | none | FALSE | 0 | 72.1423 | FALSE | FALSE | 0.0776 |  | 72.7008 | 0 | 0 | 0.01404 | 0.17077 | -0.082216 | 0.27923 | Normal | 73.2593 | -1.1639 | Night | 202512 | 2025-12-03 | 1.1639
2025-12-03 17:57 | 72.941 | TRUE | FALSE | -0.75824 | -1.0504 | -0.33434 | -0.45628 | 0.5652 |  |  | none | FALSE | 1 | 72.1828 | FALSE | FALSE | 0.0803 |  | 72.7291 | 0 | 0.5652 | 0.02826 | 0.20296 | 2.6456 | 0.27315 | Normal | 73.2753 | 0.77596 | Night | 202512 | 2025-12-03 | 0.77596
2025-12-03 18:12 | 72.941 | FALSE | FALSE | -0.71119 | -0.98462 | -0.34381 | -0.46915 | 0 |  |  | none | FALSE | 1 | 72.2298 | FALSE | FALSE | 0.075 |  | 72.7573 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.26375 | Normal | 73.2848 | 0.69645 | Night | 202512 | 2025-12-03 | 0.69645
2025-12-03 18:27 | 72.941 | FALSE | FALSE | -0.70103 | -0.97042 | -0.36191 | -0.49372 | 0 |  |  | none | FALSE | 1 | 72.24 | FALSE | FALSE | 0.0711 |  | 72.7714 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.26574 | Normal | 73.3029 | 0.63808 | Night | 202512 | 2025-12-03 | 0.63808
2025-12-03 18:42 | 72.941 | FALSE | FALSE | -0.68927 | -0.95398 | -0.37841 | -0.51611 | 0 |  |  | none | FALSE | 1 | 72.2517 | FALSE | FALSE | 0.0674 |  | 72.7856 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.26692 | Normal | 73.3194 | 0.58231 | Night | 202512 | 2025-12-03 | 0.58231
2025-12-03 18:42 | 72.941 | FALSE | FALSE | -0.68927 | -0.95398 | -0.37841 | -0.51611 | 0 |  |  | none | FALSE | 1 | 72.2517 | FALSE | FALSE | 0.0674 |  | 72.7856 | 0 | 0 | 0 | 0.18338 | 0 | 0.26692 | Normal | 73.3194 | 0.58231 | Night | 202512 | 2025-12-03 | 0.58231
2025-12-03 18:42 | 72.941 | FALSE | FALSE | -0.68927 | -0.95398 | -0.37841 | -0.51611 | 0 |  |  | none | FALSE | 1 | 72.2517 | FALSE | FALSE | 0.0674 |  | 72.7856 | 0 | 0 | 0 | 0.18338 | 0 | 0.26692 | Normal | 73.3194 | 0.58231 | Night | 202512 | 2025-12-03 | 0.58231
2025-12-03 18:57 | 73.5062 | TRUE | FALSE | -1.3135 | -1.8195 | 0.071191 | 0.096944 | 0.5652 | 2025-12-03 21:26 | 2025-12-03 18:57 | upper | TRUE | 2 | 72.1927 | TRUE | FALSE | 0.2629 | 2.2292 | 72.8138 | 1 | 0.5652 | 0.02826 | 0.22271 | 2.411 | 0.31059 | Extreme triggered | 73.435 | 2.2292 | Night | 202512 | 2025-12-03 | 2.2292
2025-12-03 19:12 | 73.5062 | FALSE | FALSE | -1.3569 | -1.8807 | -0.028723 | -0.03906 | 0 |  | 2025-12-03 18:57 | none | FALSE | 2 | 72.1493 | FALSE | FALSE | 0.2992 | 2.0731 | 72.8421 | 2 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.34642 | Extreme/elevated | 73.5349 | 1.9171 | Night | 202512 | 2025-12-03 | 1.9171
2025-12-03 19:28 | 73.7888 | FALSE | FALSE | -1.7162 | -2.3811 | 0.092484 | 0.12549 | 0.2826 |  | 2025-12-03 18:57 | upper | TRUE | 2 | 72.0726 | FALSE | TRUE | 0.3771 | 2.1247 | 72.8845 | 3 | 0.2826 | 0.04239 | 0.22968 | 1.0459 | 0.40592 | Persistent | 73.6963 | 2.2278 | Night | 202512 | 2025-12-03 | 2.2278
2025-12-03 19:41 | 73.7888 | FALSE | FALSE | -1.7691 | -2.4564 | -0.045267 | -0.061309 | 0 |  | 2025-12-03 18:57 | none | FALSE | 2 | 72.0197 | FALSE | FALSE | 0.4124 | 2.0686 | 72.9269 | 4 | 0 | 0.04239 | 0.22968 | -0.18456 | 0.4536 | Persistent | 73.8341 | 1.9002 | Night | 202512 | 2025-12-03 | 1.9002
2025-12-03 19:56 | 73.7888 | FALSE | FALSE | -1.8122 | -2.5178 | -0.14486 | -0.19593 | 0 |  | 2025-12-03 18:57 | none | FALSE | 1 | 71.9766 | FALSE | FALSE | 0.4279 | 1.9957 | 72.9551 | 5 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.48926 | Persistent | 73.9337 | 1.7039 | Night | 202512 | 2025-12-03 | 1.7039
2025-12-03 20:12 | 73.7888 | FALSE | FALSE | -1.8383 | -2.5549 | -0.25573 | -0.34537 | 0 |  | 2025-12-03 18:57 | none | FALSE | 1 | 71.9505 | FALSE | FALSE | 0.4722 | 1.915 | 72.9975 | 6 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.5235 | Persistent | 74.0445 | 1.5115 | Night | 202512 | 2025-12-03 | 1.5115
2025-12-03 20:27 | 73.7888 | FALSE | TRUE | -1.8533 | -2.5764 | -0.35555 | -0.47954 | 0 |  | 2025-12-03 18:57 | none | FALSE | 1 | 71.9355 | FALSE | FALSE | 0.519 | 1.8351 | 73.0399 | 7 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.55222 | Confirmed/Materialized Shift | 74.1444 | 1.3561 | Night | 202512 | 2025-12-03 | 1.3561
2025-12-03 20:41 | 73.7888 | FALSE | TRUE | -1.8298 | -2.5429 | -0.44507 | -0.59956 | 0 |  | 2025-12-03 18:57 | none | FALSE | 1 | 71.959 | FALSE | FALSE | 0.5097 | 1.7579 | 73.0964 | 8 | 0 | 0.05652 | 0.19665 | -0.28742 | 0.56872 | Confirmed/Materialized Shift | 74.2339 | 1.2174 | Night | 202512 | 2025-12-03 | 1.2174
2025-12-03 20:56 | 73.7888 | FALSE | TRUE | -1.7938 | -2.4916 | -0.5221 | -0.70259 | 0 |  | 2025-12-03 18:57 | none | FALSE | 1 | 71.995 | FALSE | FALSE | 0.5018 | 1.6846 | 73.153 | 9 | 0 | 0.05652 | 0.19665 | -0.28742 | 0.57898 | Confirmed/Materialized Shift | 74.3109 | 1.0982 | Night | 202512 | 2025-12-03 | 1.0982
2025-12-03 21:11 | 73.7888 | FALSE | TRUE | -1.6956 | -2.352 | -0.5652 | -0.76015 | 0 |  | 2025-12-03 18:57 | none | FALSE | 1 | 72.0932 | FALSE | FALSE | 0.4952 | 1.6162 | 73.2236 | 10 | 0 | 0.07065 | 0.18049 | -0.39144 | 0.5652 | Confirmed/Materialized Shift | 74.354 | 1 | Night | 202512 | 2025-12-03 | 1
2025-12-03 21:26 | 73.7888 | FALSE | FALSE | -1.5775 | -2.1845 | -0.58837 | -0.79107 | 0 |  |  | none | FALSE | 0 | 72.2113 | FALSE | FALSE | 0.0609 |  | 73.2943 | 0 | 0 | 0.07065 | 0.18049 | -0.39144 | 0.54146 | Persistence ends | 74.3772 | 0.91336 | Night | 202512 | 2025-12-03 | 0.91336
2025-12-03 21:41 | 73.7888 | FALSE | FALSE | -1.4366 | -1.9856 | -0.58882 | -0.79167 | 0 |  |  | none | FALSE | 0 | 72.3522 | FALSE | FALSE | 0.0558 |  | 73.3649 | 0 | 0 | 0.07065 | 0.18049 | -0.39144 | 0.50636 | Normal | 74.3776 | 0.83715 | Night | 202512 | 2025-12-03 | 0.83715
2025-12-03 21:56 | 73.5062 | FALSE | FALSE | -0.985 | -1.3582 | -0.81544 | -1.0972 | -0.2826 |  |  | none | FALSE | 0 | 72.5212 | FALSE | FALSE | 0.0126 |  | 73.4214 | 0 | -0.2826 | 0.05652 | 0.19665 | -1.7245 | 0.45011 | Normal | 74.3216 | 0.18835 | Night | 202512 | 2025-12-03 | 0.18835
2025-12-03 22:11 | 73.7888 | FALSE | FALSE | -1.0633 | -1.4621 | -0.46983 | -0.6327 | 0.2826 |  |  | none | FALSE | 0 | 72.7255 | FALSE | FALSE | 0.0516 |  | 73.4921 | 0 | 0.2826 | 0.07065 | 0.20244 | 1.047 | 0.38328 | Normal | 74.2586 | 0.77418 | Night | 202512 | 2025-12-03 | 0.77418
2025-12-03 22:26 | 73.5062 | FALSE | FALSE | -0.70724 | -0.97149 | -0.7355 | -0.99068 | -0.2826 |  |  | none | FALSE | 0 | 72.799 | FALSE | FALSE | 0.0026 |  | 73.5203 | 0 | -0.2826 | 0.02826 | 0.18107 | -1.7168 | 0.36068 | Normal | 74.2417 | -0.039176 | Night | 202512 | 2025-12-03 | 0.039176
2025-12-03 22:41 | 73.5062 | FALSE | FALSE | -0.62573 | -0.85858 | -0.71051 | -0.95735 | 0 |  |  | none | FALSE | 0 | 72.8805 | FALSE | FALSE | 0.0085 |  | 73.5486 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.33406 | Normal | 74.2167 | -0.12689 | Night | 202512 | 2025-12-03 | 0.12689
2025-12-03 22:56 | 73.5062 | FALSE | FALSE | -0.53407 | -0.73188 | -0.67537 | -0.91043 | 0 |  |  | none | FALSE | 0 | 72.9721 | FALSE | FALSE | 0.0156 |  | 73.5768 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.30236 | Normal | 74.1816 | -0.23366 | Night | 202512 | 2025-12-03 | 0.23366
2025-12-03 23:11 | 73.5062 | FALSE | FALSE | -0.42859 | -0.58649 | -0.62641 | -0.84499 | 0 |  |  | none | FALSE | 0 | 73.0776 | FALSE | FALSE | 0.025 |  | 73.6051 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.26375 | Normal | 74.1326 | -0.37501 | Night | 202512 | 2025-12-03 | 0.37501
2025-12-03 23:26 | 73.5062 | FALSE | FALSE | -0.3019 | -0.41241 | -0.55624 | -0.75105 | 0 |  |  | none | FALSE | 0 | 73.2043 | FALSE | FALSE | 0.0395 |  | 73.6334 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.21454 | Normal | 74.0624 | -0.59276 | Night | 202512 | 2025-12-03 | 0.59276
2025-12-03 23:40 | 73.5062 | FALSE | FALSE | -0.13306 | -0.18134 | -0.44392 | -0.60029 | 0 |  |  | none | FALSE | 0 | 73.3731 | FALSE | FALSE | 0.0718 |  | 73.6616 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.14424 | Normal | 73.9501 | -1.0775 | Night | 202512 | 2025-12-03 | 1.0775
2025-12-03 23:55 | 73.2236 | FALSE | FALSE | 0.080837 | 0.11028 | -0.76696 | -1.0366 | -0.2826 | 2025-12-04 05:09 | 2025-12-03 23:55 | lower | TRUE | 0 | 73.3044 | FALSE | FALSE | 0.2219 | 2.4713 | 73.6475 | 1 | -0.2826 | -0.01413 | 0.14424 | -1.8612 | 0.17153 | Extreme triggered | 73.9906 | -2.4713 | Night | 202512 | 2025-12-03 | 2.4713
2025-12-04 00:10 | 73.2236 | FALSE | FALSE | 0.021855 | 0.029838 | -0.79769 | -1.0776 | 0 |  | 2025-12-03 23:55 | lower | TRUE | 0 | 73.2455 | FALSE | FALSE | 0.2551 | 2.292 | 73.6334 | 2 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.19396 | Extreme/elevated | 74.0213 | -2.1127 | Night | 202512 | 2025-12-04 | 2.1127
2025-12-04 00:25 | 73.2236 | FALSE | FALSE | -0.039654 | -0.054184 | -0.80267 | -1.0843 | 0 |  | 2025-12-03 23:55 | none | FALSE | 0 | 73.1839 | FALSE | FALSE | 0.2922 | 2.1319 | 73.6051 | 3 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21058 | Persistent | 74.0263 | -1.8117 | Night | 202512 | 2025-12-04 | 1.8117
2025-12-04 00:40 | 73.2236 | FALSE | FALSE | -0.091222 | -0.12474 | -0.79772 | -1.0777 | 0 |  | 2025-12-03 23:55 | none | FALSE | 0 | 73.1324 | FALSE | FALSE | 0.3345 | 1.9963 | 73.5768 | 4 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.22224 | Persistent | 74.0213 | -1.5895 | Night | 202512 | 2025-12-04 | 1.5895
2025-12-04 00:55 | 73.2236 | FALSE | FALSE | -0.13436 | -0.18384 | -0.78434 | -1.0598 | 0 |  | 2025-12-03 23:55 | none | FALSE | 0 | 73.0892 | FALSE | FALSE | 0.38 | 1.88 | 73.5486 | 5 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.22968 | Persistent | 74.0079 | -1.415 | Night | 202512 | 2025-12-04 | 1.415
2025-12-04 01:10 | 73.2236 | FALSE | FALSE | -0.16989 | -0.23255 | -0.76335 | -1.0317 | 0 |  | 2025-12-03 23:55 | none | FALSE | 0 | 73.0537 | FALSE | FALSE | 0.4276 | 1.7787 | 73.5203 | 6 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.23331 | Persistent | 73.9869 | -1.2718 | Night | 202512 | 2025-12-04 | 1.2718
2025-12-04 01:25 | 73.2236 | FALSE | TRUE | -0.19815 | -0.27134 | -0.73509 | -0.99392 | 0 |  | 2025-12-03 23:55 | none | FALSE | 0 | 73.0255 | FALSE | FALSE | 0.4767 | 1.689 | 73.4921 | 7 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.23331 | Confirmed/Materialized Shift | 73.9587 | -1.1507 | Night | 202512 | 2025-12-04 | 1.1507
2025-12-04 01:40 | 72.941 | FALSE | TRUE | 0.0031498 | 0.004318 | -1.0142 | -1.3714 | -0.2826 |  | 2025-12-03 23:55 | lower | TRUE | 0 | 72.9441 | FALSE | TRUE | 0.5342 | 1.7294 | 73.4497 | 8 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.25277 | Confirmed/Materialized Shift | 73.9552 | -2.0125 | Night | 202512 | 2025-12-04 | 2.0125
2025-12-04 01:55 | 72.941 | FALSE | TRUE | -0.061212 | -0.083991 | -0.99379 | -1.3441 | 0 |  | 2025-12-03 23:55 | none | FALSE | 0 | 72.8798 | FALSE | FALSE | 0.5179 | 1.7337 | 73.4073 | 9 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.26375 | Confirmed/Materialized Shift | 73.9348 | -1.7679 | Night | 202512 | 2025-12-04 | 1.7679
2025-12-04 02:10 | 72.941 | FALSE | TRUE | -0.11073 | -0.15203 | -0.95853 | -1.2971 | 0 |  | 2025-12-03 23:55 | none | FALSE | 0 | 72.8303 | FALSE | FALSE | 0.5057 | 1.7189 | 73.3649 | 10 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.26731 | Confirmed/Materialized Shift | 73.8995 | -1.5858 | Night | 202512 | 2025-12-04 | 1.5858
2025-12-04 02:25 | 72.941 | FALSE | TRUE | -0.14599 | -0.20055 | -0.90901 | -1.2309 | 0 |  | 2025-12-03 23:55 | none | FALSE | 0 | 72.795 | FALSE | FALSE | 0.4964 | 1.6941 | 73.3225 | 11 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.26375 | Confirmed/Materialized Shift | 73.85 | -1.4465 | Night | 202512 | 2025-12-04 | 1.4465
2025-12-04 02:39 | 72.941 | FALSE | TRUE | -0.16641 | -0.22867 | -0.84465 | -1.1447 | 0 |  | 2025-12-03 23:55 | none | FALSE | 0 | 72.7746 | FALSE | FALSE | 0.4894 | 1.6647 | 73.2801 | 12 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.25277 | Confirmed/Materialized Shift | 73.7857 | -1.3416 | Night | 202512 | 2025-12-04 | 1.3416
2025-12-04 02:54 | 72.941 | FALSE | TRUE | -0.20455 | -0.28122 | -0.82627 | -1.1201 | 0 |  | 2025-12-03 23:55 | none | FALSE | 0 | 72.7364 | FALSE | FALSE | 0.4804 | 1.6295 | 73.2519 | 13 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.25771 | Confirmed/Materialized Shift | 73.7673 | -1.2063 | Night | 202512 | 2025-12-04 | 1.2063
2025-12-04 03:09 | 72.6584 | FALSE | TRUE | 0.021529 | 0.029621 | -1.0524 | -1.4277 | -0.2826 |  | 2025-12-03 23:55 | lower | TRUE | 0 | 72.6799 | FALSE | TRUE | 0.5389 | 1.6619 | 73.1953 | 14 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.25771 | Confirmed/Materialized Shift | 73.7108 | -2.0835 | Night | 202512 | 2025-12-04 | 2.0835
2025-12-04 03:24 | 72.6584 | FALSE | TRUE | -0.051742 | -0.071263 | -1.0408 | -1.4123 | 0 |  | 2025-12-03 23:55 | none | FALSE | 0 | 72.6067 | FALSE | FALSE | 0.5207 | 1.6718 | 73.153 | 15 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27315 | Confirmed/Materialized Shift | 73.6992 | -1.8106 | Night | 202512 | 2025-12-04 | 1.8106
2025-12-04 03:39 | 72.6584 | FALSE | TRUE | -0.11006 | -0.1517 | -1.0144 | -1.3769 | 0 |  | 2025-12-03 23:55 | none | FALSE | 0 | 72.5483 | FALSE | FALSE | 0.5072 | 1.6679 | 73.1106 | 16 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.28111 | Confirmed/Materialized Shift | 73.6728 | -1.6085 | Night | 202512 | 2025-12-04 | 1.6085
2025-12-04 03:54 | 72.6584 | FALSE | TRUE | -0.15469 | -0.21335 | -0.97423 | -1.3231 | 0 |  | 2025-12-03 23:55 | none | FALSE | 0 | 72.5037 | FALSE | FALSE | 0.4968 | 1.6552 | 73.0682 | 17 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.28223 | Confirmed/Materialized Shift | 73.6326 | -1.4519 | Night | 202512 | 2025-12-04 | 1.4519
2025-12-04 04:09 | 72.6584 | FALSE | TRUE | -0.18579 | -0.25636 | -0.92055 | -1.2511 | 0 |  | 2025-12-03 23:55 | none | FALSE | 0 | 72.4726 | FALSE | FALSE | 0.4886 | 1.637 | 73.0258 | 18 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27659 | Confirmed/Materialized Shift | 73.579 | -1.3283 | Night | 202512 | 2025-12-04 | 1.3283
2025-12-04 04:24 | 72.6584 | FALSE | TRUE | -0.20251 | -0.2795 | -0.85249 | -1.1597 | 0 |  | 2025-12-03 23:55 | none | FALSE | 0 | 72.4559 | FALSE | FALSE | 0.4821 | 1.6157 | 72.9834 | 19 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.26375 | Confirmed/Materialized Shift | 73.5109 | -1.2322 | Night | 202512 | 2025-12-04 | 1.2322
2025-12-04 04:39 | 72.6584 | FALSE | TRUE | -0.20256 | -0.27957 | -0.76776 | -1.0456 | 0 |  | 2025-12-03 23:55 | none | FALSE | 0 | 72.4558 | FALSE | FALSE | 0.4777 | 1.5932 | 72.941 | 20 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.24258 | Confirmed/Materialized Shift | 73.4262 | -1.165 | Night | 202512 | 2025-12-04 | 1.165
2025-12-04 04:54 | 72.6584 | FALSE | TRUE | -0.22735 | -0.31388 | -0.73603 | -1.0028 | 0 |  | 2025-12-03 23:55 | none | FALSE | 0 | 72.4311 | FALSE | FALSE | 0.4704 | 1.5676 | 72.9127 | 21 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.24084 | Confirmed/Materialized Shift | 73.3944 | -1.056 | Night | 202512 | 2025-12-04 | 1.056
2025-12-04 05:09 | 72.6584 | FALSE | FALSE | -0.24502 | -0.33836 | -0.69718 | -0.95041 | 0 |  |  | none | FALSE | 0 | 72.4134 | FALSE | FALSE | 0.064 |  | 72.8845 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.23555 | Persistence ends | 73.3556 | -0.9598 | Night | 202512 | 2025-12-04 | 0.9598
2025-12-04 05:24 | 72.3758 | TRUE | FALSE | -0.028313 | -0.039135 | -0.96089 | -1.3102 | -0.2826 |  |  | none | FALSE | 1 | 72.3475 | FALSE | FALSE | 0.1543 |  | 72.8421 | 0 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.2473 | Normal | 73.3367 | -1.8855 | Night | 202512 | 2025-12-04 | 1.8855
2025-12-04 05:38 | 72.3758 | FALSE | FALSE | -0.078293 | -0.10829 | -0.92609 | -1.2634 | 0 |  |  | none | FALSE | 1 | 72.2975 | FALSE | FALSE | 0.1411 |  | 72.7997 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.2511 | Normal | 73.3019 | -1.6882 | Night | 202512 | 2025-12-04 | 1.6882
2025-12-04 05:53 | 72.3758 | FALSE | FALSE | -0.11309 | -0.1565 | -0.87611 | -1.196 | 0 |  |  | none | FALSE | 1 | 72.2627 | FALSE | FALSE | 0.1314 |  | 72.7573 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.2473 | Normal | 73.2519 | -1.5427 | Night | 202512 | 2025-12-04 | 1.5427
2025-12-04 06:09 | 72.3758 | FALSE | FALSE | -0.13198 | -0.18269 | -0.81022 | -1.1071 | 0 |  |  | none | FALSE | 1 | 72.2438 | FALSE | FALSE | 0.1246 |  | 72.7149 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.23555 | Normal | 73.186 | -1.4397 | Night | 202512 | 2025-12-04 | 1.4397
2025-12-04 06:24 | 72.3758 | FALSE | FALSE | -0.13234 | -0.18319 | -0.7258 | -0.99287 | 0 |  |  | none | FALSE | 1 | 72.2435 | FALSE | FALSE | 0.1208 |  | 72.6725 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.21454 | Normal | 73.1016 | -1.3831 | Night | 202512 | 2025-12-04 | 1.3831
2025-12-04 06:38 | 72.3758 | FALSE | FALSE | -0.1606 | -0.2224 | -0.69754 | -0.95458 | 0 |  |  | none | FALSE | 1 | 72.2152 | FALSE | FALSE | 0.112 |  | 72.6443 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21454 | Normal | 73.0733 | -1.2514 | Night | 202512 | 2025-12-04 | 1.2514
2025-12-04 06:53 | 72.3758 | FALSE | FALSE | -0.18095 | -0.25065 | -0.66137 | -0.90553 | 0 |  |  | none | FALSE | 1 | 72.1948 | FALSE | FALSE | 0.1046 |  | 72.616 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21058 | Normal | 73.0372 | -1.1407 | Night | 202512 | 2025-12-04 | 1.1407
2025-12-04 07:08 | 72.095 | TRUE | FALSE | 0.026208 | 0.036339 | -0.93121 | -1.2752 | -0.2808 | 2025-12-04 07:31 | 2025-12-04 07:08 | lower | TRUE | 2 | 72.1212 | TRUE | FALSE | 0.2553 | 2.1158 | 72.5737 | 1 | -0.2808 | -0.0423 | 0.10331 | -2.3086 | 0.22625 | Extreme triggered | 73.0262 | -2.1158 | Day | 202512 | 2025-12-04 | 2.1158
2025-12-04 07:23 | 72.095 | FALSE | FALSE | -0.029496 | -0.040929 | -0.90232 | -1.2361 | 0 |  | 2025-12-04 07:08 | none | FALSE | 2 | 72.0655 | FALSE | FALSE | 0.2963 | 1.9946 | 72.5314 | 2 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.23295 | Extreme/elevated | 72.9973 | -1.8734 | Day | 202512 | 2025-12-04 | 1.8734
2025-12-04 07:31 | 72.3758 | TRUE | FALSE | -0.301 | -0.41762 | -0.5557 | -0.76195 | 0.2808 |  |  | none | FALSE | 3 | 72.0748 | TRUE | FALSE | 0.1254 |  | 72.5032 | 0 | 0.2808 | -0.02826 | 0.12596 | 2.4536 | 0.21418 | Persistence ends | 72.9315 | -0.59461 | Day | 202512 | 2025-12-04 | 0.59461
2025-12-04 07:46 | 72.095 | FALSE | FALSE | -0.047262 | -0.065598 | -0.77896 | -1.0689 | -0.2808 |  |  | none | FALSE | 2 | 72.0477 | FALSE | FALSE | 0.1752 |  | 72.4608 | 0 | -0.2808 | -0.0423 | 0.13774 | -1.7315 | 0.20656 | Normal | 72.874 | -1.7712 | Day | 202512 | 2025-12-04 | 1.7712
2025-12-04 08:01 | 72.095 | FALSE | FALSE | -0.095081 | -0.13206 | -0.77044 | -1.0573 | 0 |  |  | none | FALSE | 2 | 71.9999 | FALSE | FALSE | 0.1612 |  | 72.4327 | 0 | 0 | -0.02817 | 0.12577 | 0.22398 | 0.21638 | Normal | 72.8654 | -1.5606 | Day | 202512 | 2025-12-04 | 1.5606
2025-12-04 08:16 | 72.3758 | TRUE | FALSE | -0.37725 | -0.52396 | -0.46275 | -0.6353 | 0.2808 |  |  | none | FALSE | 3 | 71.9986 | TRUE | FALSE | 0.0993 |  | 72.4185 | 0 | 0.2808 | -0.01413 | 0.1435 | 2.0552 | 0.21 | Normal | 72.8385 | -0.20357 | Day | 202512 | 2025-12-04 | 0.20357
2025-12-04 08:30 | 72.6584 | FALSE | FALSE | -0.65985 | -0.91647 | -0.18015 | -0.24732 | 0.2826 |  |  | none | FALSE | 3 | 71.9986 | FALSE | FALSE | 0.1619 |  | 72.4185 | 0 | 0.2826 | 0 | 0.15813 | 1.7871 | 0.21 | Normal | 72.8385 | 1.1422 | Day | 202512 | 2025-12-04 | 1.1422
2025-12-04 08:31 | 72.6584 | FALSE | FALSE | -0.65985 | -0.91647 | -0.18015 | -0.24732 | 0 |  |  | none | FALSE | 3 | 71.9986 | FALSE | FALSE | 0.1619 |  | 72.4185 | 0 | 0 | 0 | 0.15813 | 0 | 0.21 | Normal | 72.8385 | 1.1422 | Day | 202512 | 2025-12-04 | 1.1422
2025-12-04 08:46 | 72.941 | FALSE | FALSE | -0.97833 | -1.3595 | 0.038311 | 0.052551 | 0.2826 | 2025-12-04 11:19 | 2025-12-04 08:46 | upper | TRUE | 3 | 71.9627 | FALSE | FALSE | 0.2871 | 2.163 | 72.4327 | 1 | 0.2826 | 0.01413 | 0.17029 | 1.5765 | 0.235 | Extreme triggered | 72.9027 | 2.163 | Day | 202512 | 2025-12-04 | 2.163
2025-12-04 09:01 | 73.2236 | FALSE | FALSE | -1.3445 | -1.8705 | 0.18084 | 0.24758 | 0.2826 |  | 2025-12-04 08:46 | upper | TRUE | 3 | 71.8791 | FALSE | FALSE | 0.3748 | 2.3923 | 72.4609 | 2 | 0.2826 | 0.02826 | 0.18048 | 1.4093 | 0.29091 | Extreme/elevated | 73.0428 | 2.6216 | Day | 202512 | 2025-12-04 | 2.6216
2025-12-04 09:16 | 73.2236 | FALSE | FALSE | -1.4048 | -1.956 | 0.064029 | 0.08752 | 0 |  | 2025-12-04 08:46 | upper | TRUE | 2 | 71.8188 | FALSE | TRUE | 0.3746 | 2.3252 | 72.4892 | 3 | 0 | 0.02826 | 0.18048 | -0.15658 | 0.33519 | Persistent | 73.1596 | 2.191 | Day | 202512 | 2025-12-04 | 2.191
2025-12-04 09:30 | 73.2236 | FALSE | FALSE | -1.4502 | -2.0205 | -0.037872 | -0.051694 | 0 |  | 2025-12-04 08:46 | none | FALSE | 2 | 71.7734 | FALSE | FALSE | 0.4123 | 2.2185 | 72.5175 | 4 | 0 | 0.02826 | 0.18048 | -0.15658 | 0.37201 | Persistent | 73.2615 | 1.8982 | Day | 202512 | 2025-12-04 | 1.8982
2025-12-04 09:31 | 73.2236 | FALSE | FALSE | -1.4847 | -2.0696 | -0.12896 | -0.1758 | 0 |  | 2025-12-04 08:46 | none | FALSE | 1 | 71.7389 | FALSE | FALSE | 0.4263 | 2.1108 | 72.5457 | 5 | 0 | 0.02826 | 0.18048 | -0.15658 | 0.40342 | Persistent | 73.3526 | 1.6803 | Day | 202512 | 2025-12-04 | 1.6803
2025-12-04 09:46 | 73.2236 | FALSE | FALSE | -1.4923 | -2.0804 | -0.2213 | -0.30131 | 0 |  | 2025-12-04 08:46 | none | FALSE | 1 | 71.7313 | FALSE | FALSE | 0.4703 | 2.0063 | 72.5881 | 6 | 0 | 0.04239 | 0.16528 | -0.25647 | 0.42839 | Persistent | 73.4449 | 1.4834 | Day | 202512 | 2025-12-04 | 1.4834
2025-12-04 10:01 | 73.5062 | FALSE | TRUE | -1.8042 | -2.5163 | -0.081081 | -0.11018 | 0.2826 |  | 2025-12-04 08:46 | none | FALSE | 1 | 71.702 | FALSE | FALSE | 0.5504 | 1.9808 | 72.6446 | 7 | 0.2826 | 0.05652 | 0.17335 | 1.3042 | 0.47133 | Confirmed/Materialized Shift | 73.5873 | 1.828 | Day | 202512 | 2025-12-04 | 1.828
2025-12-04 10:16 | 73.7888 | FALSE | TRUE | -2.1356 | -2.9804 | 0.011463 | 0.015537 | 0.2826 |  | 2025-12-04 08:46 | upper | TRUE | 0 | 71.6532 | FALSE | TRUE | 0.5348 | 1.9859 | 72.7153 | 8 | 0.2826 | 0.07065 | 0.17989 | 1.1782 | 0.53103 | Confirmed/Materialized Shift | 73.7773 | 2.0216 | Day | 202512 | 2025-12-04 | 2.0216
2025-12-04 10:30 | 73.7888 | FALSE | TRUE | -2.1541 | -3.007 | -0.14835 | -0.20064 | 0 |  | 2025-12-04 08:46 | none | FALSE | 0 | 71.6347 | FALSE | FALSE | 0.5162 | 1.9588 | 72.7859 | 9 | 0 | 0.07065 | 0.17989 | -0.39273 | 0.57561 | Confirmed/Materialized Shift | 73.9371 | 1.7423 | Day | 202512 | 2025-12-04 | 1.7423
2025-12-04 10:31 | 74.0714 | FALSE | TRUE | -2.4686 | -3.4476 | -0.067187 | -0.090623 | 0.2826 |  | 2025-12-04 08:46 | none | FALSE | 0 | 71.6028 | FALSE | FALSE | 0.5263 | 1.9523 | 72.8707 | 10 | 0.2826 | 0.08478 | 0.18508 | 1.0689 | 0.63394 | Confirmed/Materialized Shift | 74.1386 | 1.894 | Day | 202512 | 2025-12-04 | 1.894
2025-12-04 10:34 | 74.0714 | FALSE | TRUE | -2.4684 | -3.4473 | -0.23657 | -0.31836 | 0 |  | 2025-12-04 08:46 | none | FALSE | 0 | 71.603 | FALSE | FALSE | 0.51 | 1.9249 | 72.9555 | 11 | 0 | 0.08478 | 0.18508 | -0.45808 | 0.67624 | Confirmed/Materialized Shift | 74.308 | 1.6502 | Day | 202512 | 2025-12-04 | 1.6502
2025-12-04 10:49 | 73.7888 | FALSE | TRUE | -2.1351 | -2.9798 | -0.60979 | -0.81962 | -0.2826 |  | 2025-12-04 08:46 | none | FALSE | 0 | 71.6537 | FALSE | FALSE | 0.4741 | 1.8571 | 73.0261 | 12 | -0.2826 | 0.07065 | 0.20191 | -1.7495 | 0.68622 | Confirmed/Materialized Shift | 74.3986 | 1.1114 | Day | 202512 | 2025-12-04 | 1.1114
2025-12-04 11:04 | 73.7888 | FALSE | TRUE | -2.0171 | -2.8105 | -0.66119 | -0.88809 | 0 |  | 2025-12-04 08:46 | none | FALSE | 0 | 71.7717 | FALSE | FALSE | 0.4675 | 1.7921 | 73.1108 | 13 | 0 | 0.08469 | 0.18526 | -0.45713 | 0.66958 | Confirmed/Materialized Shift | 74.45 | 1.0125 | Day | 202512 | 2025-12-04 | 1.0125
2025-12-04 11:19 | 73.7888 | FALSE | FALSE | -1.8749 | -2.6072 | -0.68838 | -0.92429 | 0 |  |  | none | FALSE | 0 | 71.9139 | FALSE | FALSE | 0.0617 |  | 73.1955 | 0 | 0 | 0.08469 | 0.18526 | -0.45713 | 0.64083 | Persistence ends | 74.4772 | 0.9258 | Day | 202512 | 2025-12-04 | 0.9258
2025-12-04 11:30 | 73.7888 | FALSE | FALSE | -1.7693 | -2.4568 | -0.72408 | -0.97175 | 0 |  |  | none | FALSE | 0 | 72.0195 | FALSE | FALSE | 0.0559 |  | 73.2662 | 0 | 0 | 0.07065 | 0.18019 | -0.39208 | 0.62336 | Normal | 74.5129 | 0.83841 | Day | 202512 | 2025-12-04 | 0.83841
2025-12-04 11:45 | 73.7888 | FALSE | FALSE | -1.575 | -2.181 | -0.69908 | -0.93852 | 0 |  |  | none | FALSE | 0 | 72.2138 | FALSE | FALSE | 0.0514 |  | 73.3509 | 0 | 0 | 0.08469 | 0.16132 | -0.52499 | 0.56851 | Normal | 74.4879 | 0.77033 | Day | 202512 | 2025-12-04 | 0.77033
2025-12-04 12:00 | 73.5062 | FALSE | FALSE | -1.0568 | -1.4587 | -0.88728 | -1.1927 | -0.2826 |  |  | none | FALSE | 0 | 72.4494 | FALSE | FALSE | 0.0116 |  | 73.4214 | 0 | -0.2826 | 0.07056 | 0.18038 | -1.9579 | 0.48603 | Normal | 74.3935 | 0.17443 | Day | 202512 | 2025-12-04 | 0.17443
2025-12-04 12:15 | 73.5062 | FALSE | FALSE | -0.86659 | -1.193 | -0.81007 | -1.09 | 0 |  |  | none | FALSE | 0 | 72.6396 | FALSE | FALSE | 0.0045 |  | 73.4779 | 0 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.41916 | Normal | 74.3163 | 0.06742 | Day | 202512 | 2025-12-04 | 0.06742
2025-12-04 12:30 | 73.5062 | FALSE | FALSE | -0.73018 | -1.0033 | -0.75844 | -1.0213 | 0 |  |  | none | FALSE | 0 | 72.776 | FALSE | FALSE | 0.0025 |  | 73.5203 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.37215 | Normal | 74.2646 | -0.037968 | Day | 202512 | 2025-12-04 | 0.037968
2025-12-04 12:45 | 73.5062 | FALSE | FALSE | -0.56803 | -0.77879 | -0.68107 | -0.91805 | 0 |  |  | none | FALSE | 0 | 72.9382 | FALSE | FALSE | 0.0121 |  | 73.5627 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.31228 | Normal | 74.1873 | -0.18099 | Day | 202512 | 2025-12-04 | 0.18099
2025-12-04 13:00 | 73.7888 | FALSE | FALSE | -0.74216 | -1.016 | -0.37478 | -0.50534 | 0.2826 |  |  | none | FALSE | 0 | 73.0466 | FALSE | FALSE | 0.0439 |  | 73.6051 | 0 | 0.2826 | 0.04239 | 0.16593 | 1.4477 | 0.27923 | Normal | 74.1636 | 0.65784 | Day | 202512 | 2025-12-04 | 0.65784
2025-12-04 13:15 | 73.7888 | FALSE | FALSE | -0.68927 | -0.94292 | -0.37841 | -0.51021 | 0 |  |  | none | FALSE | 0 | 73.0995 | FALSE | FALSE | 0.0388 |  | 73.6334 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.26692 | Normal | 74.1672 | 0.58231 | Day | 202512 | 2025-12-04 | 0.58231
2025-12-04 13:30 | 73.5062 | FALSE | FALSE | -0.36089 | -0.49339 | -0.64349 | -0.86783 | -0.2826 |  |  | none | FALSE | 0 | 73.1453 | FALSE | FALSE | 0.0375 |  | 73.6475 | 0 | -0.2826 | 0.01413 | 0.17092 | -1.7361 | 0.2511 | Normal | 74.1497 | -0.56273 | Day | 202512 | 2025-12-04 | 0.56273
2025-12-04 13:45 | 73.5062 | FALSE | FALSE | -0.31119 | -0.42515 | -0.62205 | -0.83915 | 0 |  |  | none | FALSE | 0 | 73.195 | FALSE | FALSE | 0.0444 |  | 73.6616 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.23331 | Normal | 74.1282 | -0.6662 | Day | 202512 | 2025-12-04 | 0.6662
2025-12-04 14:00 | 73.5062 | FALSE | FALSE | -0.25657 | -0.35026 | -0.59569 | -0.80387 | 0 |  |  | none | FALSE | 0 | 73.2496 | FALSE | FALSE | 0.0531 |  | 73.6758 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.21306 | Normal | 74.1019 | -0.79582 | Day | 202512 | 2025-12-04 | 0.79582
2025-12-04 14:15 | 73.5062 | FALSE | FALSE | -0.19546 | -0.26662 | -0.56284 | -0.75988 | 0 |  |  | none | FALSE | 0 | 73.3107 | FALSE | FALSE | 0.0646 |  | 73.6899 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.18957 | Normal | 74.069 | -0.96896 | Day | 202512 | 2025-12-04 | 0.96896
2025-12-04 14:29 | 73.7888 | FALSE | FALSE | -0.45609 | -0.62194 | -0.28653 | -0.3868 | 0.2826 |  |  | none | FALSE | 0 | 73.3327 | FALSE | FALSE | 0.0304 |  | 73.704 | 0 | 0.2826 | 0.01413 | 0.17092 | 1.5708 | 0.18565 | Normal | 74.0753 | 0.45666 | Day | 202512 | 2025-12-04 | 0.45666
2025-12-04 14:44 | 73.5062 | FALSE | FALSE | -0.19546 | -0.26662 | -0.56284 | -0.75988 | -0.2826 |  |  | none | FALSE | 0 | 73.3107 | FALSE | FALSE | 0.0646 |  | 73.6899 | 0 | -0.2826 | -0.01413 | 0.17092 | -1.5708 | 0.18957 | Normal | 74.069 | -0.96896 | Day | 202512 | 2025-12-04 | 0.96896
2025-12-04 14:59 | 73.5062 | FALSE | FALSE | -0.21509 | -0.29347 | -0.55421 | -0.74832 | 0 |  |  | none | FALSE | 0 | 73.2911 | FALSE | FALSE | 0.0588 |  | 73.6758 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.19233 | Normal | 74.0604 | -0.88163 | Day | 202512 | 2025-12-04 | 0.88163
2025-12-04 15:14 | 73.7888 | FALSE | FALSE | -0.46901 | -0.63967 | -0.21467 | -0.29008 | 0.2826 |  |  | none | FALSE | 0 | 73.3198 | FALSE | FALSE | 0.0496 |  | 73.6616 | 0 | 0.2826 | -0.01413 | 0.17092 | 1.7361 | 0.17092 | Normal | 74.0035 | 0.74404 | Day | 202512 | 2025-12-04 | 0.74404
2025-12-04 15:29 | 73.7888 | FALSE | FALSE | -0.43124 | -0.58786 | -0.14864 | -0.20104 | 0 |  |  | none | FALSE | 0 | 73.3576 | FALSE | FALSE | 0.065 |  | 73.6475 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.14497 | Normal | 73.9374 | 0.97468 | Day | 202512 | 2025-12-04 | 0.97468
2025-12-04 15:44 | 73.5062 | FALSE | FALSE | -0.16132 | -0.21994 | -0.41566 | -0.56229 | -0.2826 |  |  | none | FALSE | 0 | 73.3449 | FALSE | FALSE | 0.0588 |  | 73.6334 | 0 | -0.2826 | -0.01413 | 0.17092 | -1.5708 | 0.14424 | Normal | 73.9219 | -0.88163 | Day | 202512 | 2025-12-04 | 0.88163
2025-12-04 15:59 | 73.5062 | FALSE | FALSE | -0.17104 | -0.23324 | -0.39712 | -0.53736 | 0 |  |  | none | FALSE | 0 | 73.3352 | FALSE | FALSE | 0.0531 |  | 73.6192 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.14204 | Normal | 73.9033 | -0.79582 | Day | 202512 | 2025-12-04 | 0.79582
2025-12-04 16:14 | 73.2236 | FALSE | FALSE | 0.044515 | 0.060756 | -0.69025 | -0.93385 | -0.2826 | 2025-12-04 18:28 | 2025-12-04 16:14 | lower | TRUE | 0 | 73.2681 | FALSE | FALSE | 0.2089 | 2.2757 | 73.591 | 1 | -0.2826 | -0.02826 | 0.18107 | -1.4047 | 0.16143 | Extreme triggered | 73.9138 | -2.2757 | Day | 202512 | 2025-12-04 | 2.2757
2025-12-04 16:29 | 73.2236 | FALSE | FALSE | -0.0088098 | -0.012033 | -0.68705 | -0.92957 | 0 |  | 2025-12-04 16:14 | none | FALSE | 0 | 73.2148 | FALSE | FALSE | 0.2442 | 2.1126 | 73.5627 | 2 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.17396 | Extreme/elevated | 73.9106 | -1.9494 | Day | 202512 | 2025-12-04 | 1.9494
2025-12-04 16:44 | 73.2236 | FALSE | FALSE | -0.051277 | -0.070077 | -0.673 | -0.91073 | 0 |  | 2025-12-04 16:14 | none | FALSE | 0 | 73.1723 | FALSE | FALSE | 0.2859 | 1.9806 | 73.5345 | 3 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.18107 | Persistent | 73.8966 | -1.7168 | Day | 202512 | 2025-12-04 | 1.7168
2025-12-04 16:59 | 72.941 | FALSE | FALSE | 0.11602 | 0.15881 | -1.0144 | -1.3716 | -0.2826 |  | 2025-12-04 16:14 | lower | TRUE | 0 | 73.057 | FALSE | TRUE | 0.3963 | 2.1146 | 73.5062 | 4 | -0.2826 | -0.02826 | 0.18107 | -1.4047 | 0.22459 | Persistent | 73.9554 | -2.5166 | Day | 202512 | 2025-12-04 | 2.5166
2025-12-04 17:14 | 72.6584 | FALSE | FALSE | 0.21761 | 0.2986 | -1.3932 | -1.8814 | -0.2826 |  | 2025-12-04 16:14 | lower | TRUE | 0 | 72.876 | FALSE | TRUE | 0.4684 | 2.2398 | 73.4638 | 5 | -0.2826 | -0.04239 | 0.18957 | -1.2671 | 0.2939 | Persistent | 74.0516 | -2.7404 | Day | 202512 | 2025-12-04 | 2.7404
2025-12-04 17:28 | 72.6584 | FALSE | FALSE | 0.074447 | 0.10236 | -1.4516 | -1.9587 | 0 |  | 2025-12-04 16:14 | lower | TRUE | 0 | 72.7328 | FALSE | TRUE | 0.4906 | 2.2359 | 73.4214 | 6 | 0 | -0.04239 | 0.18957 | 0.22361 | 0.34429 | Persistent | 74.11 | -2.2162 | Day | 202512 | 2025-12-04 | 2.2162
2025-12-04 17:43 | 72.3758 | FALSE | TRUE | 0.15883 | 0.21898 | -1.8194 | -2.4521 | -0.2826 |  | 2025-12-04 16:14 | lower | TRUE | 0 | 72.5346 | FALSE | TRUE | 0.5588 | 2.2568 | 73.3649 | 7 | -0.2826 | -0.05652 | 0.19665 | -1.1497 | 0.41513 | Confirmed/Materialized Shift | 74.1952 | -2.3826 | Night | 202512 | 2025-12-04 | 2.3826
2025-12-04 17:58 | 72.3758 | FALSE | TRUE | 0.0038696 | 0.0053462 | -1.833 | -2.4701 | 0 |  | 2025-12-04 16:14 | lower | TRUE | 0 | 72.3797 | FALSE | TRUE | 0.5339 | 2.2258 | 73.2943 | 8 | 0 | -0.07065 | 0.18049 | 0.39144 | 0.45729 | Confirmed/Materialized Shift | 74.2088 | -2.0085 | Night | 202512 | 2025-12-04 | 2.0085
2025-12-04 18:13 | 72.095 | FALSE | TRUE | 0.086189 | 0.11941 | -2.1429 | -2.8866 | -0.2808 |  | 2025-12-04 16:14 | lower | TRUE | 0 | 72.1812 | FALSE | TRUE | 0.5445 | 2.2193 | 73.2096 | 9 | -0.2808 | -0.08469 | 0.18555 | -1.0569 | 0.51419 | Confirmed/Materialized Shift | 74.2379 | -2.1676 | Night | 202512 | 2025-12-04 | 2.1676
2025-12-04 18:28 | 72.6584 | TRUE | FALSE | -0.53785 | -0.74576 | -1.5554 | -2.0958 | 0.5634 |  |  | none | FALSE | 1 | 72.1206 | FALSE | FALSE | 0.0934 |  | 73.1672 | 0 | 0.5634 | -0.04239 | 0.22933 | 2.6416 | 0.52331 | Persistence ends | 74.2138 | -0.97222 | Night | 202512 | 2025-12-04 | 0.97222
2025-12-04 18:31 | 72.6584 | FALSE | FALSE | -0.59104 | -0.82012 | -1.5238 | -2.0541 | 0 |  |  | none | FALSE | 1 | 72.0674 | FALSE | FALSE | 0.0874 |  | 73.1248 | 0 | 0 | -0.04239 | 0.22933 | 0.18484 | 0.52871 | Normal | 74.1822 | -0.88211 | Night | 202512 | 2025-12-04 | 0.88211
2025-12-04 18:31 | 72.6584 | FALSE | FALSE | -0.63702 | -0.88448 | -1.485 | -2.0029 | 0 |  |  | none | FALSE | 1 | 72.0214 | FALSE | FALSE | 0.0819 |  | 73.0824 | 0 | 0 | -0.04239 | 0.22933 | 0.18484 | 0.5305 | Normal | 74.1434 | -0.79922 | Night | 202512 | 2025-12-04 | 0.79922
2025-12-04 18:46 | 73.2236 | TRUE | FALSE | -1.2 | -1.6661 | -0.8893 | -1.1999 | 0.5652 |  |  | none | FALSE | 2 | 72.0236 | TRUE | FALSE | 0.077 |  | 73.0683 | 0 | 0.5652 | -0.01413 | 0.26662 | 2.1729 | 0.52232 | Normal | 74.1129 | 0.2974 | Night | 202512 | 2025-12-04 | 0.2974
2025-12-04 19:01 | 73.5062 | FALSE | FALSE | -1.4628 | -2.0304 | -0.55863 | -0.75425 | 0.2826 |  |  | none | FALSE | 2 | 72.0434 | FALSE | FALSE | 0.1168 |  | 73.0541 | 0 | 0.2826 | -0.01413 | 0.26662 | 1.1129 | 0.50535 | Normal | 74.0648 | 0.89457 | Night | 202512 | 2025-12-04 | 0.89457
2025-12-04 19:16 | 73.7888 | FALSE | FALSE | -1.7652 | -2.4508 | -0.3241 | -0.43731 | 0.2826 |  |  | none | FALSE | 2 | 72.0236 | FALSE | FALSE | 0.1491 |  | 73.0683 | 0 | 0.2826 | 0.01413 | 0.26662 | 1.0069 | 0.52232 | Normal | 74.1129 | 1.3795 | Night | 202512 | 2025-12-04 | 1.3795
2025-12-04 19:30 | 73.7888 | FALSE | FALSE | -1.7831 | -2.4764 | -0.37033 | -0.49937 | 0 |  |  | none | FALSE | 2 | 72.0057 | FALSE | FALSE | 0.1446 |  | 73.0824 | 0 | 0 | 0.01413 | 0.26662 | -0.052997 | 0.53837 | Normal | 74.1591 | 1.3121 | Night | 202512 | 2025-12-04 | 1.3121
2025-12-04 19:45 | 73.7888 | FALSE | FALSE | -1.7831 | -2.4764 | -0.37033 | -0.49937 | 0 |  |  | none | FALSE | 2 | 72.0057 | FALSE | FALSE | 0.1446 |  | 73.0824 | 0 | 0 | 0 | 0.25902 | 0 | 0.53837 | Normal | 74.1591 | 1.3121 | Night | 202512 | 2025-12-04 | 1.3121
2025-12-04 20:00 | 73.7888 | FALSE | FALSE | -1.7831 | -2.4764 | -0.37033 | -0.49937 | 0 |  |  | none | FALSE | 2 | 72.0057 | FALSE | FALSE | 0.1446 |  | 73.0824 | 0 | 0 | 0 | 0.25902 | 0 | 0.53837 | Normal | 74.1591 | 1.3121 | Night | 202512 | 2025-12-04 | 1.3121
2025-12-04 20:15 | 74.0714 | FALSE | FALSE | -2.1115 | -2.9342 | -0.18995 | -0.25579 | 0.2826 |  |  | none | FALSE | 2 | 71.9599 | FALSE | FALSE | 0.1685 |  | 73.1107 | 0 | 0.2826 | 0.02826 | 0.25739 | 0.98813 | 0.57535 | Normal | 74.2614 | 1.6699 | Night | 202512 | 2025-12-04 | 1.6699
2025-12-04 20:30 | 74.0714 | FALSE | FALSE | -2.1499 | -2.9893 | -0.28494 | -0.38321 | 0 |  |  | none | FALSE | 1 | 71.9215 | FALSE | FALSE | 0.1307 |  | 73.1389 | 0 | 0 | 0.02826 | 0.25739 | -0.10979 | 0.60871 | Normal | 74.3563 | 1.5319 | Night | 202512 | 2025-12-04 | 1.5319
2025-12-04 20:45 | 74.0714 | FALSE | FALSE | -2.177 | -3.0281 | -0.3968 | -0.53285 | 0 |  |  | none | FALSE | 1 | 71.8944 | FALSE | FALSE | 0.1208 |  | 73.1813 | 0 | 0 | 0.04239 | 0.24698 | -0.17164 | 0.64345 | Normal | 74.4682 | 1.3833 | Night | 202512 | 2025-12-04 | 1.3833
2025-12-04 21:00 | 74.0714 | FALSE | FALSE | -2.1949 | -3.0537 | -0.4995 | -0.66983 | 0 |  |  | none | FALSE | 1 | 71.8765 | FALSE | FALSE | 0.1125 |  | 73.2237 | 0 | 0 | 0.04239 | 0.24698 | -0.17164 | 0.6736 | Normal | 74.5709 | 1.2585 | Night | 202512 | 2025-12-04 | 1.2585
2025-12-04 21:15 | 74.0714 | FALSE | FALSE | -2.2049 | -3.068 | -0.59421 | -0.79583 | 0 |  |  | none | FALSE | 0 | 71.8665 | FALSE | FALSE | 0.0767 |  | 73.2661 | 0 | 0 | 0.04239 | 0.24698 | -0.17164 | 0.69977 | Normal | 74.6656 | 1.1508 | Night | 202512 | 2025-12-04 | 1.1508
2025-12-04 21:30 | 74.0714 | FALSE | FALSE | -2.1839 | -3.0379 | -0.68631 | -0.91804 | 0 |  |  | none | FALSE | 0 | 71.8875 | FALSE | FALSE | 0.0696 |  | 73.3226 | 0 | 0 | 0.05652 | 0.23521 | -0.2403 | 0.71755 | Normal | 74.7577 | 1.0435 | Night | 202512 | 2025-12-04 | 1.0435
2025-12-04 21:45 | 74.0714 | FALSE | FALSE | -2.1147 | -2.9389 | -0.7584 | -1.0135 | 0 |  |  | none | FALSE | 0 | 71.9567 | FALSE | FALSE | 0.0629 |  | 73.3932 | 0 | 0 | 0.07065 | 0.22188 | -0.31842 | 0.71828 | Normal | 74.8298 | 0.94414 | Night | 202512 | 2025-12-04 | 0.94414
2025-12-04 22:00 | 74.0714 | FALSE | FALSE | -2.0308 | -2.819 | -0.8158 | -1.0894 | 0 |  |  | none | FALSE | 0 | 72.0406 | FALSE | FALSE | 0.0569 |  | 73.4639 | 0 | 0 | 0.07065 | 0.22188 | -0.31842 | 0.71165 | Normal | 74.8872 | 0.85365 | Night | 202512 | 2025-12-04 | 0.85365
2025-12-04 22:15 | 74.0714 | FALSE | FALSE | -1.8733 | -2.5946 | -0.82783 | -1.1053 | 0 |  |  | none | FALSE | 0 | 72.1981 | FALSE | FALSE | 0.0516 |  | 73.5487 | 0 | 0 | 0.08478 | 0.20667 | -0.41021 | 0.67527 | Normal | 74.8992 | 0.77409 | Night | 202512 | 2025-12-04 | 0.77409
2025-12-04 22:29 | 74.0714 | FALSE | FALSE | -1.6876 | -2.3314 | -0.81171 | -1.084 | 0 |  |  | none | FALSE | 0 | 72.3838 | FALSE | FALSE | 0.0467 |  | 73.6335 | 0 | 0 | 0.08478 | 0.20667 | -0.41021 | 0.62482 | Normal | 74.8831 | 0.7009 | Night | 202512 | 2025-12-04 | 0.7009
2025-12-04 22:44 | 74.0714 | FALSE | FALSE | -1.3699 | -1.8843 | -0.6917 | -0.92519 | 0 |  |  | none | FALSE | 0 | 72.7015 | FALSE | FALSE | 0.0439 |  | 73.7323 | 0 | 0 | 0.09882 | 0.18934 | -0.52192 | 0.51541 | Normal | 74.7631 | 0.65796 | Night | 202512 | 2025-12-04 | 0.65796
2025-12-04 22:59 | 74.0714 | FALSE | FALSE | -1.1757 | -1.6128 | -0.63873 | -0.85494 | 0 |  |  | none | FALSE | 0 | 72.8957 | FALSE | FALSE | 0.0395 |  | 73.8029 | 0 | 0 | 0.07065 | 0.15546 | -0.45445 | 0.4536 | Normal | 74.7101 | 0.59187 | Night | 202512 | 2025-12-04 | 0.59187
2025-12-04 23:14 | 74.0714 | FALSE | FALSE | -0.93361 | -1.2765 | -0.53797 | -0.72105 | 0 |  |  | none | FALSE | 0 | 73.1378 | FALSE | FALSE | 0.0358 |  | 73.8736 | 0 | 0 | 0.07065 | 0.15546 | -0.45445 | 0.36789 | Normal | 74.6094 | 0.53771 | Night | 202512 | 2025-12-04 | 0.53771
2025-12-04 23:29 | 74.0714 | FALSE | FALSE | -0.59379 | -0.80812 | -0.33945 | -0.45618 | 0 |  |  | none | FALSE | 0 | 73.4776 | FALSE | FALSE | 0.0363 |  | 73.9442 | 0 | 0 | 0.07065 | 0.15546 | -0.45445 | 0.23331 | Normal | 74.4108 | 0.54507 | Night | 202512 | 2025-12-04 | 0.54507
2025-12-04 23:44 | 74.0714 | FALSE | FALSE | -0.40765 | -0.55339 | -0.23809 | -0.3204 | 0 |  |  | none | FALSE | 0 | 73.6638 | FALSE | FALSE | 0.035 |  | 73.9866 | 0 | 0 | 0.04239 | 0.10353 | -0.40945 | 0.16143 | Normal | 74.3095 | 0.52517 | Night | 202512 | 2025-12-04 | 0.52517
2025-12-04 23:59 | 74.0714 | FALSE | FALSE | -0.28847 | -0.39098 | -0.17543 | -0.23628 | 0 |  |  | none | FALSE | 0 | 73.7829 | FALSE | FALSE | 0.0325 |  | 74.0149 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.11598 | Normal | 74.2468 | 0.48734 | Night | 202512 | 2025-12-04 | 0.48734
2025-12-05 00:14 | 74.0714 | FALSE | FALSE | -0.24945 | -0.33791 | -0.16467 | -0.22182 | 0 |  |  | none | FALSE | 0 | 73.822 | FALSE | FALSE | 0.0273 |  | 74.029 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.10353 | Normal | 74.2361 | 0.40945 | Night | 202512 | 2025-12-05 | 0.40945
2025-12-05 00:29 | 73.7888 | TRUE | FALSE | 0.03315 | 0.044906 | -0.44727 | -0.6025 | -0.2826 | 2025-12-05 05:13 | 2025-12-05 00:29 | lower | TRUE | 1 | 73.822 | FALSE | FALSE | 0.2404 | 2.3202 | 74.029 | 1 | -0.2826 | 0 | 0.091688 | -3.0822 | 0.10353 | Extreme triggered | 74.2361 | -2.3202 | Night | 202512 | 2025-12-05 | 2.3202
2025-12-05 00:44 | 73.7888 | FALSE | FALSE | 0.03315 | 0.044906 | -0.44727 | -0.6025 | 0 |  | 2025-12-05 00:29 | lower | TRUE | 1 | 73.822 | FALSE | FALSE | 0.2975 | 2.3202 | 74.029 | 2 | 0 | 0 | 0.091688 | 0 | 0.10353 | Extreme/elevated | 74.2361 | -2.3202 | Night | 202512 | 2025-12-05 | 2.3202
2025-12-05 00:59 | 73.7888 | FALSE | FALSE | 0.03315 | 0.044906 | -0.44727 | -0.6025 | 0 |  | 2025-12-05 00:29 | lower | TRUE | 1 | 73.822 | FALSE | TRUE | 0.3547 | 2.3202 | 74.029 | 3 | 0 | 0 | 0.091688 | 0 | 0.10353 | Persistent | 74.2361 | -2.3202 | Night | 202512 | 2025-12-05 | 2.3202
2025-12-05 01:14 | 73.7888 | FALSE | FALSE | -0.0058732 | -0.0079601 | -0.45803 | -0.61691 | 0 |  | 2025-12-05 00:29 | none | FALSE | 1 | 73.7829 | FALSE | FALSE | 0.3871 | 2.2275 | 74.0149 | 4 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.11598 | Persistent | 74.2468 | -1.9494 | Night | 202512 | 2025-12-05 | 1.9494
2025-12-05 01:28 | 73.7888 | FALSE | FALSE | -0.039147 | -0.053081 | -0.46305 | -0.62362 | 0 |  | 2025-12-05 00:29 | none | FALSE | 1 | 73.7497 | FALSE | FALSE | 0.4268 | 2.1196 | 74.0007 | 5 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.12555 | Persistent | 74.2518 | -1.6882 | Night | 202512 | 2025-12-05 | 1.6882
2025-12-05 01:43 | 73.5062 | TRUE | FALSE | 0.13444 | 0.18256 | -0.79814 | -1.0742 | -0.2826 |  | 2025-12-05 00:29 | lower | TRUE | 2 | 73.6406 | TRUE | TRUE | 0.5873 | 2.2347 | 73.9725 | 6 | -0.2826 | -0.02826 | 0.086982 | -2.924 | 0.16593 | Persistent | 74.3043 | -2.8102 | Night | 202512 | 2025-12-05 | 2.8102
2025-12-05 01:58 | 73.5062 | FALSE | TRUE | 0.050115 | 0.068131 | -0.82595 | -1.1112 | 0 |  | 2025-12-05 00:29 | lower | TRUE | 2 | 73.5563 | FALSE | TRUE | 0.6077 | 2.2381 | 73.9442 | 7 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.19396 | Confirmed/Materialized Shift | 74.3321 | -2.2584 | Night | 202512 | 2025-12-05 | 2.2584
2025-12-05 02:13 | 73.5062 | FALSE | TRUE | -0.019304 | -0.026269 | -0.83884 | -1.1283 | 0 |  | 2025-12-05 00:29 | none | FALSE | 2 | 73.4869 | FALSE | FALSE | 0.5845 | 2.1971 | 73.916 | 8 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21454 | Confirmed/Materialized Shift | 74.345 | -1.91 | Night | 202512 | 2025-12-05 | 1.91
2025-12-05 02:28 | 73.5062 | FALSE | TRUE | -0.077844 | -0.10601 | -0.84086 | -1.131 | 0 |  | 2025-12-05 00:29 | none | FALSE | 2 | 73.4284 | FALSE | FALSE | 0.5679 | 2.1375 | 73.8877 | 9 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22968 | Confirmed/Materialized Shift | 74.3471 | -1.6611 | Night | 202512 | 2025-12-05 | 1.6611
2025-12-05 02:43 | 73.5062 | FALSE | TRUE | -0.12756 | -0.17384 | -0.83406 | -1.122 | 0 |  | 2025-12-05 00:29 | none | FALSE | 2 | 73.3786 | FALSE | FALSE | 0.5551 | 2.0707 | 73.8594 | 10 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.24041 | Confirmed/Materialized Shift | 74.3403 | -1.4694 | Night | 202512 | 2025-12-05 | 1.4694
2025-12-05 02:58 | 73.5062 | FALSE | TRUE | -0.16961 | -0.23128 | -0.81959 | -1.1027 | 0 |  | 2025-12-05 00:29 | none | FALSE | 1 | 73.3366 | FALSE | FALSE | 0.5162 | 2.0019 | 73.8312 | 11 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.2473 | Confirmed/Materialized Shift | 74.3258 | -1.3141 | Night | 202512 | 2025-12-05 | 1.3141
2025-12-05 03:13 | 73.2236 | TRUE | TRUE | 0.015075 | 0.020583 | -1.1153 | -1.5003 | -0.2826 |  | 2025-12-05 00:29 | lower | TRUE | 2 | 73.2387 | TRUE | TRUE | 0.5941 | 2.0063 | 73.7888 | 12 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.27506 | Confirmed/Materialized Shift | 74.3389 | -2.0548 | Night | 202512 | 2025-12-05 | 2.0548
2025-12-05 03:28 | 73.2236 | FALSE | TRUE | -0.064992 | -0.088838 | -1.1106 | -1.4941 | 0 |  | 2025-12-05 00:29 | none | FALSE | 2 | 73.1586 | FALSE | FALSE | 0.5757 | 1.9888 | 73.7464 | 13 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.2939 | Confirmed/Materialized Shift | 74.3342 | -1.7789 | Night | 202512 | 2025-12-05 | 1.7789
2025-12-05 03:43 | 73.2236 | FALSE | TRUE | -0.13052 | -0.17857 | -1.0914 | -1.4686 | 0 |  | 2025-12-05 00:29 | none | FALSE | 2 | 73.0931 | FALSE | FALSE | 0.562 | 1.9591 | 73.704 | 14 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.30547 | Confirmed/Materialized Shift | 74.315 | -1.5727 | Night | 202512 | 2025-12-05 | 1.5727
2025-12-05 03:58 | 73.2236 | FALSE | TRUE | -0.18315 | -0.25075 | -1.0592 | -1.4259 | 0 |  | 2025-12-05 00:29 | none | FALSE | 2 | 73.0405 | FALSE | FALSE | 0.5512 | 1.9225 | 73.6616 | 15 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.31059 | Confirmed/Materialized Shift | 74.2828 | -1.4103 | Night | 202512 | 2025-12-05 | 1.4103
2025-12-05 04:13 | 73.2236 | FALSE | TRUE | -0.22351 | -0.30617 | -1.0148 | -1.3669 | 0 |  | 2025-12-05 00:29 | none | FALSE | 1 | 73.0001 | FALSE | FALSE | 0.5138 | 1.8823 | 73.6192 | 16 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.30957 | Confirmed/Materialized Shift | 74.2384 | -1.278 | Night | 202512 | 2025-12-05 | 1.278
2025-12-05 04:27 | 73.2236 | FALSE | TRUE | -0.25147 | -0.34461 | -0.95797 | -1.2914 | 0 |  | 2025-12-05 00:29 | none | FALSE | 1 | 72.9721 | FALSE | FALSE | 0.5065 | 1.8403 | 73.5768 | 17 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.30236 | Confirmed/Materialized Shift | 74.1816 | -1.1683 | Night | 202512 | 2025-12-05 | 1.1683
2025-12-05 04:42 | 73.2236 | FALSE | TRUE | -0.26612 | -0.36476 | -0.88784 | -1.198 | 0 |  | 2025-12-05 00:29 | none | FALSE | 1 | 72.9575 | FALSE | FALSE | 0.5004 | 1.7979 | 73.5345 | 18 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.28849 | Confirmed/Materialized Shift | 74.1114 | -1.0775 | Night | 202512 | 2025-12-05 | 1.0775
2025-12-05 04:57 | 73.2236 | FALSE | TRUE | -0.26537 | -0.36373 | -0.80231 | -1.0838 | 0 |  | 2025-12-05 00:29 | none | FALSE | 1 | 72.9582 | FALSE | FALSE | 0.4956 | 1.7562 | 73.4921 | 19 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.26692 | Confirmed/Materialized Shift | 74.0259 | -1.0058 | Night | 202512 | 2025-12-05 | 1.0058
2025-12-05 05:13 | 73.2236 | FALSE | FALSE | -0.24502 | -0.33574 | -0.69718 | -0.94314 | 0 |  |  | none | FALSE | 1 | 72.9786 | FALSE | FALSE | 0.0926 |  | 73.4497 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.23555 | Persistence ends | 73.9208 | -0.9598 | Night | 202512 | 2025-12-05 | 0.9598
2025-12-05 05:27 | 72.941 | TRUE | FALSE | -0.028313 | -0.038832 | -0.96089 | -1.3002 | -0.2826 |  |  | none | FALSE | 2 | 72.9127 | TRUE | FALSE | 0.1828 |  | 73.4073 | 0 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.2473 | Normal | 73.9019 | -1.8855 | Night | 202512 | 2025-12-05 | 1.8855
2025-12-05 05:42 | 72.941 | FALSE | FALSE | -0.078293 | -0.10745 | -0.92609 | -1.2537 | 0 |  |  | none | FALSE | 1 | 72.8627 | FALSE | FALSE | 0.1411 |  | 73.3649 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.2511 | Normal | 73.8671 | -1.6882 | Night | 202512 | 2025-12-05 | 1.6882
2025-12-05 05:57 | 72.941 | FALSE | FALSE | -0.11309 | -0.15529 | -0.87611 | -1.1869 | 0 |  |  | none | FALSE | 1 | 72.8279 | FALSE | FALSE | 0.1314 |  | 73.3225 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.2473 | Normal | 73.8171 | -1.5427 | Night | 202512 | 2025-12-05 | 1.5427
2025-12-05 06:12 | 72.941 | FALSE | FALSE | -0.13198 | -0.18127 | -0.81022 | -1.0986 | 0 |  |  | none | FALSE | 1 | 72.809 | FALSE | FALSE | 0.1246 |  | 73.2801 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.23555 | Normal | 73.7512 | -1.4397 | Night | 202512 | 2025-12-05 | 1.4397
2025-12-05 06:27 | 72.941 | FALSE | FALSE | -0.13234 | -0.18177 | -0.7258 | -0.98525 | 0 |  |  | none | FALSE | 1 | 72.8087 | FALSE | FALSE | 0.1208 |  | 73.2377 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.21454 | Normal | 73.6668 | -1.3831 | Night | 202512 | 2025-12-05 | 1.3831
2025-12-05 06:42 | 72.941 | FALSE | FALSE | -0.1606 | -0.22067 | -0.69754 | -0.94725 | 0 |  |  | none | FALSE | 1 | 72.7804 | FALSE | FALSE | 0.112 |  | 73.2095 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21454 | Normal | 73.6385 | -1.2514 | Night | 202512 | 2025-12-05 | 1.2514
2025-12-05 06:57 | 72.941 | FALSE | FALSE | -0.18095 | -0.2487 | -0.66137 | -0.89858 | 0 |  |  | none | FALSE | 1 | 72.76 | FALSE | FALSE | 0.1046 |  | 73.1812 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21058 | Normal | 73.6024 | -1.1407 | Night | 202512 | 2025-12-05 | 1.1407
2025-12-05 07:12 | 72.941 | FALSE | FALSE | -0.19293 | -0.2652 | -0.61683 | -0.83857 | 0 |  |  | none | FALSE | 1 | 72.7481 | FALSE | FALSE | 0.0984 |  | 73.153 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.20244 | Normal | 73.5578 | -1.047 | Day | 202512 | 2025-12-05 | 1.047
2025-12-05 07:26 | 72.6584 | TRUE | FALSE | 0.026035 | 0.035819 | -0.87829 | -1.1943 | -0.2826 | 2025-12-05 07:46 | 2025-12-05 07:26 | lower | TRUE | 2 | 72.6844 | TRUE | FALSE | 0.2558 | 2.1222 | 73.1106 | 1 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.21306 | Extreme triggered | 73.5367 | -2.1222 | Day | 202512 | 2025-12-05 | 2.1222
2025-12-05 07:31 | 72.6584 | FALSE | FALSE | -0.019304 | -0.026576 | -0.83884 | -1.1413 | 0 |  | 2025-12-05 07:26 | none | FALSE | 2 | 72.6391 | FALSE | FALSE | 0.2988 | 2.0161 | 73.0682 | 2 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.21454 | Extreme/elevated | 73.4972 | -1.91 | Day | 202512 | 2025-12-05 | 1.91
2025-12-05 07:46 | 72.941 | TRUE | FALSE | -0.28024 | -0.38568 | -0.47806 | -0.65114 | 0.2826 |  |  | none | FALSE | 2 | 72.6608 | TRUE | FALSE | 0.0919 |  | 73.0399 | 0 | 0.2826 | -0.02826 | 0.12638 | 2.4597 | 0.18957 | Persistence ends | 73.4191 | -0.52175 | Day | 202512 | 2025-12-05 | 0.52175
2025-12-05 08:01 | 72.941 | FALSE | FALSE | -0.28653 | -0.39437 | -0.45609 | -0.6214 | 0 |  |  | none | FALSE | 2 | 72.6545 | FALSE | FALSE | 0.0876 |  | 73.0258 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.18565 | Normal | 73.3971 | -0.45666 | Day | 202512 | 2025-12-05 | 0.45666
2025-12-05 08:17 | 72.941 | FALSE | FALSE | -0.29032 | -0.39962 | -0.43162 | -0.58826 | 0 |  |  | none | FALSE | 2 | 72.6507 | FALSE | FALSE | 0.0832 |  | 73.0117 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.18049 | Normal | 73.3726 | -0.39144 | Day | 202512 | 2025-12-05 | 0.39144
2025-12-05 08:31 | 73.2236 | TRUE | FALSE | -0.57292 | -0.7886 | -0.14902 | -0.20311 | 0.2826 |  |  | none | FALSE | 3 | 72.6507 | TRUE | FALSE | 0.164 |  | 73.0117 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.18049 | Normal | 73.3726 | 1.1743 | Day | 202512 | 2025-12-05 | 1.1743
2025-12-05 08:31 | 73.2236 | FALSE | FALSE | -0.57292 | -0.7886 | -0.14902 | -0.20311 | 0 |  |  | none | FALSE | 3 | 72.6507 | FALSE | FALSE | 0.164 |  | 73.0117 | 0 | 0 | 0 | 0.12967 | 0 | 0.18049 | Normal | 73.3726 | 1.1743 | Day | 202512 | 2025-12-05 | 1.1743
2025-12-05 08:46 | 73.5062 | FALSE | FALSE | -0.89454 | -1.2319 | 0.066301 | 0.090279 | 0.2826 | 2025-12-05 09:31 | 2025-12-05 08:46 | upper | TRUE | 3 | 72.6117 | FALSE | FALSE | 0.2975 | 2.3202 | 73.0258 | 1 | 0.2826 | 0.01413 | 0.14424 | 1.8612 | 0.20706 | Extreme triggered | 73.4399 | 2.3202 | Day | 202512 | 2025-12-05 | 2.3202
2025-12-05 08:46 | 73.5062 | FALSE | FALSE | -0.92564 | -1.2753 | 0.0069363 | 0.0094372 | 0 |  | 2025-12-05 08:46 | upper | TRUE | 3 | 72.5806 | FALSE | FALSE | 0.3353 | 2.1752 | 73.0399 | 2 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.22968 | Extreme/elevated | 73.4993 | 2.0302 | Day | 202512 | 2025-12-05 | 2.0302
2025-12-05 09:01 | 73.7888 | FALSE | FALSE | -1.2851 | -1.7724 | 0.15617 | 0.2121 | 0.2826 |  | 2025-12-05 08:46 | upper | TRUE | 3 | 72.5037 | FALSE | TRUE | 0.4274 | 2.3013 | 73.0682 | 3 | 0.2826 | 0.02826 | 0.15614 | 1.6289 | 0.28223 | Persistent | 73.6326 | 2.5534 | Day | 202512 | 2025-12-05 | 2.5534
2025-12-05 09:16 | 73.7888 | FALSE | FALSE | -1.3401 | -1.8497 | 0.04469 | 0.060601 | 0 |  | 2025-12-05 08:46 | upper | TRUE | 2 | 72.4487 | FALSE | TRUE | 0.4282 | 2.2604 | 73.0964 | 4 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.32384 | Persistent | 73.7441 | 2.138 | Day | 202512 | 2025-12-05 | 2.138
2025-12-05 09:31 | 73.2236 | TRUE | FALSE | -0.77485 | -1.0695 | -0.52051 | -0.70583 | -0.5652 |  |  | none | FALSE | 3 | 72.4487 | TRUE | FALSE | 0.1119 |  | 73.0964 | 0 | -0.5652 | 0 | 0.20502 | -2.7568 | 0.32384 | Persistence ends | 73.7441 | 0.39269 | Day | 202512 | 2025-12-05 | 0.39269
2025-12-05 09:46 | 72.941 | FALSE | FALSE | -0.49225 | -0.67945 | -0.80311 | -1.089 | -0.2826 |  |  | none | FALSE | 2 | 72.4487 | FALSE | FALSE | 0.0891 |  | 73.0964 | 0 | -0.2826 | 0 | 0.20502 | -1.3784 | 0.32384 | Normal | 73.7441 | -0.47996 | Day | 202512 | 2025-12-05 | 0.47996
2025-12-05 10:01 | 72.941 | FALSE | FALSE | -0.49225 | -0.67945 | -0.80311 | -1.089 | 0 |  |  | none | FALSE | 2 | 72.4487 | FALSE | FALSE | 0.0891 |  | 73.0964 | 0 | 0 | 0 | 0.20502 | 0 | 0.32384 | Normal | 73.7441 | -0.47996 | Day | 202512 | 2025-12-05 | 0.47996
2025-12-05 10:16 | 73.2236 | FALSE | FALSE | -0.75877 | -1.0471 | -0.53269 | -0.72223 | 0.2826 |  |  | none | FALSE | 2 | 72.4648 | FALSE | FALSE | 0.0805 |  | 73.1106 | 0 | 0.2826 | 0.01413 | 0.21454 | 1.2514 | 0.32287 | Normal | 73.7563 | 0.35012 | Day | 202512 | 2025-12-05 | 0.35012
2025-12-05 10:31 | 73.2236 | FALSE | FALSE | -0.74138 | -1.0228 | -0.54356 | -0.73686 | 0 |  |  | none | FALSE | 1 | 72.4822 | FALSE | FALSE | 0.0491 |  | 73.1247 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.32123 | Normal | 73.7672 | 0.30791 | Day | 202512 | 2025-12-05 | 0.30791
2025-12-05 10:45 | 73.2236 | FALSE | FALSE | -0.72265 | -0.99675 | -0.55309 | -0.74968 | 0 |  |  | none | FALSE | 1 | 72.5009 | FALSE | FALSE | 0.0463 |  | 73.1388 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.31894 | Normal | 73.7767 | 0.26582 | Day | 202512 | 2025-12-05 | 0.26582
2025-12-05 11:01 | 73.2236 | FALSE | FALSE | -0.70256 | -0.96877 | -0.56126 | -0.76067 | 0 |  |  | none | FALSE | 1 | 72.521 | FALSE | FALSE | 0.0435 |  | 73.153 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.31596 | Normal | 73.7849 | 0.22361 | Day | 202512 | 2025-12-05 | 0.22361
2025-12-05 11:16 | 73.5062 | FALSE | FALSE | -0.96746 | -1.3337 | -0.31748 | -0.43005 | 0.2826 |  |  | none | FALSE | 1 | 72.5387 | FALSE | FALSE | 0.096 |  | 73.1812 | 0 | 0.2826 | 0.02826 | 0.22271 | 1.142 | 0.32123 | Normal | 73.8237 | 1.0117 | Day | 202512 | 2025-12-05 | 1.0117
2025-12-05 11:31 | 73.5062 | FALSE | FALSE | -0.94441 | -1.3015 | -0.35095 | -0.47517 | 0 |  |  | none | FALSE | 1 | 72.5618 | FALSE | FALSE | 0.0897 |  | 73.2095 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.32384 | Normal | 73.8572 | 0.91629 | Day | 202512 | 2025-12-05 | 0.91629
2025-12-05 11:45 | 73.5062 | FALSE | FALSE | -0.85976 | -1.1835 | -0.35108 | -0.47534 | 0 |  |  | none | FALSE | 1 | 72.6464 | FALSE | FALSE | 0.0846 |  | 73.2519 | 0 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.30271 | Normal | 73.8573 | 0.84022 | Day | 202512 | 2025-12-05 | 0.84022
2025-12-05 12:00 | 73.7888 | FALSE | FALSE | -1.0632 | -1.4619 | -0.10236 | -0.13852 | 0.2826 |  |  | none | FALSE | 0 | 72.7256 | FALSE | FALSE | 0.1099 |  | 73.3084 | 0 | 0.2826 | 0.05652 | 0.21697 | 1.042 | 0.29139 | Normal | 73.8912 | 1.6487 | Day | 202512 | 2025-12-05 | 1.6487
2025-12-05 12:11 | 74.0714 | FALSE | FALSE | -1.3548 | -1.8632 | 0.058171 | 0.078596 | 0.2826 | 2025-12-05 12:44 | 2025-12-05 12:11 | upper | TRUE | 0 | 72.7166 | FALSE | FALSE | 0.2024 | 2.1794 | 73.3649 | 1 | 0.2826 | 0.05652 | 0.21697 | 1.042 | 0.32416 | Extreme triggered | 74.0132 | 2.1794 | Day | 202512 | 2025-12-05 | 2.1794
2025-12-05 12:14 | 73.7888 | FALSE | FALSE | -1.024 | -1.4072 | -0.26096 | -0.35241 | -0.2826 |  | 2025-12-05 12:11 | none | FALSE | 0 | 72.7648 | FALSE | FALSE | 0.1935 | 1.6835 | 73.4073 | 2 | -0.2826 | 0.04239 | 0.22968 | -1.415 | 0.32123 | Extreme/elevated | 74.0498 | 1.1876 | Day | 202512 | 2025-12-05 | 1.1876
2025-12-05 12:29 | 73.7888 | FALSE | FALSE | -0.96367 | -1.3233 | -0.28543 | -0.38533 | 0 |  | 2025-12-05 12:11 | none | FALSE | 0 | 72.8251 | FALSE | FALSE | 0.2438 | 1.4844 | 73.4497 | 3 | 0 | 0.04239 | 0.22968 | -0.18456 | 0.31228 | Persistent | 74.0742 | 1.086 | Day | 202512 | 2025-12-05 | 1.086
2025-12-05 12:44 | 73.7888 | FALSE | FALSE | -0.94344 | -1.2951 | -0.32172 | -0.43411 | 0 |  |  | none | FALSE | 0 | 72.8454 | FALSE | FALSE | 0.0655 |  | 73.4779 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.31629 | Persistence ends | 74.1105 | 0.98284 | Day | 202512 | 2025-12-05 | 0.98284
2025-12-05 12:45 | 73.7888 | FALSE | FALSE | -0.91783 | -1.2595 | -0.35263 | -0.47562 | 0 |  |  | none | FALSE | 0 | 72.871 | FALSE | FALSE | 0.0593 |  | 73.5062 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.31761 | Normal | 74.1414 | 0.88976 | Day | 202512 | 2025-12-05 | 0.88976
2025-12-05 13:00 | 73.7888 | FALSE | FALSE | -0.91615 | -1.2572 | -0.37921 | -0.51129 | 0 |  |  | none | FALSE | 0 | 72.8726 | FALSE | FALSE | 0.0553 |  | 73.5203 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.32384 | Normal | 74.168 | 0.82902 | Day | 202512 | 2025-12-05 | 0.82902
2025-12-05 13:15 | 73.5062 | FALSE | FALSE | -0.63355 | -0.86939 | -0.66181 | -0.89231 | -0.2826 |  |  | none | FALSE | 0 | 72.8726 | FALSE | FALSE | 0.0029 |  | 73.5203 | 0 | -0.2826 | 0 | 0.22459 | -1.2583 | 0.32384 | Normal | 74.168 | -0.043633 | Day | 202512 | 2025-12-05 | 0.043633
2025-12-05 13:30 | 73.2236 | FALSE | FALSE | -0.37921 | -0.52058 | -0.91615 | -1.2357 | -0.2826 |  |  | none | FALSE | 0 | 72.8444 | FALSE | FALSE | 0.0553 |  | 73.4921 | 0 | -0.2826 | -0.02826 | 0.22271 | -1.142 | 0.32384 | Normal | 74.1398 | -0.82902 | Day | 202512 | 2025-12-05 | 0.82902
2025-12-05 13:45 | 73.2236 | FALSE | FALSE | -0.40226 | -0.55239 | -0.88268 | -1.1911 | 0 |  |  | none | FALSE | 0 | 72.8213 | FALSE | FALSE | 0.0499 |  | 73.4638 | 0 | 0 | -0.02826 | 0.22271 | 0.12689 | 0.32123 | Normal | 74.1063 | -0.74777 | Day | 202512 | 2025-12-05 | 0.74777
2025-12-05 14:00 | 73.2236 | FALSE | FALSE | -0.40226 | -0.55239 | -0.88268 | -1.1911 | 0 |  |  | none | FALSE | 0 | 72.8213 | FALSE | FALSE | 0.0499 |  | 73.4638 | 0 | 0 | 0 | 0.18338 | 0 | 0.32123 | Normal | 74.1063 | -0.74777 | Day | 202512 | 2025-12-05 | 0.74777
2025-12-05 14:15 | 73.2236 | FALSE | FALSE | -0.35108 | -0.48177 | -0.85976 | -1.1605 | 0 |  |  | none | FALSE | 0 | 72.8725 | FALSE | FALSE | 0.056 |  | 73.4779 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.30271 | Normal | 74.0834 | -0.84022 | Day | 202512 | 2025-12-05 | 0.84022
2025-12-05 14:30 | 73.2236 | FALSE | FALSE | -0.29599 | -0.40586 | -0.83293 | -1.1247 | 0 |  |  | none | FALSE | 0 | 72.9276 | FALSE | FALSE | 0.0634 |  | 73.4921 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.28223 | Normal | 74.0565 | -0.95125 | Day | 202512 | 2025-12-05 | 0.95125
2025-12-05 14:44 | 73.2236 | FALSE | FALSE | -0.29599 | -0.40586 | -0.83293 | -1.1247 | 0 |  |  | none | FALSE | 0 | 72.9276 | FALSE | FALSE | 0.0634 |  | 73.4921 | 0 | 0 | 0 | 0.15881 | 0 | 0.28223 | Normal | 74.0565 | -0.95125 | Day | 202512 | 2025-12-05 | 0.95125
2025-12-05 14:59 | 73.2236 | FALSE | FALSE | -0.29599 | -0.40586 | -0.83293 | -1.1247 | 0 |  |  | none | FALSE | 0 | 72.9276 | FALSE | FALSE | 0.0634 |  | 73.4921 | 0 | 0 | 0 | 0.15881 | 0 | 0.28223 | Normal | 74.0565 | -0.95125 | Day | 202512 | 2025-12-05 | 0.95125
2025-12-05 15:14 | 73.2236 | FALSE | FALSE | -0.29599 | -0.40586 | -0.83293 | -1.1247 | 0 |  |  | none | FALSE | 0 | 72.9276 | FALSE | FALSE | 0.0634 |  | 73.4921 | 0 | 0 | 0 | 0.15881 | 0 | 0.28223 | Normal | 74.0565 | -0.95125 | Day | 202512 | 2025-12-05 | 0.95125
2025-12-05 15:29 | 73.2236 | FALSE | FALSE | -0.29599 | -0.40586 | -0.83293 | -1.1247 | 0 |  |  | none | FALSE | 0 | 72.9276 | FALSE | FALSE | 0.0634 |  | 73.4921 | 0 | 0 | 0 | 0.15881 | 0 | 0.28223 | Normal | 74.0565 | -0.95125 | Day | 202512 | 2025-12-05 | 0.95125
2025-12-05 15:44 | 72.941 | FALSE | FALSE | -0.092932 | -0.12757 | -1.1386 | -1.5369 | -0.2826 |  |  | none | FALSE | 0 | 72.8481 | FALSE | FALSE | 0.1132 |  | 73.4638 | 0 | -0.2826 | -0.02826 | 0.15614 | -1.6289 | 0.30787 | Normal | 74.0796 | -1.6981 | Day | 202512 | 2025-12-05 | 1.6981
2025-12-05 15:59 | 72.941 | FALSE | FALSE | -0.16343 | -0.22456 | -1.1525 | -1.5555 | 0 |  |  | none | FALSE | 0 | 72.7776 | FALSE | FALSE | 0.1002 |  | 73.4356 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.32899 | Normal | 74.0935 | -1.5032 | Day | 202512 | 2025-12-05 | 1.5032
2025-12-05 16:14 | 72.6584 | FALSE | FALSE | -0.0078525 | -0.010809 | -1.4774 | -1.9928 | -0.2826 |  |  | none | FALSE | 0 | 72.6505 | FALSE | FALSE | 0.1319 |  | 73.3932 | 0 | -0.2826 | -0.04239 | 0.16593 | -1.4477 | 0.37131 | Normal | 74.1358 | -1.9789 | Day | 202512 | 2025-12-05 | 1.9789
2025-12-05 16:29 | 72.6584 | FALSE | FALSE | -0.10835 | -0.14935 | -1.4648 | -1.9762 | 0 |  |  | none | FALSE | 0 | 72.55 | FALSE | FALSE | 0.115 |  | 73.3366 | 0 | 0 | -0.05652 | 0.14784 | 0.3823 | 0.3933 | Normal | 74.1232 | -1.7245 | Day | 202512 | 2025-12-05 | 1.7245
2025-12-05 16:44 | 72.3758 | FALSE | FALSE | 0.058034 | 0.080121 | -1.6941 | -2.2871 | -0.2826 | 2025-12-05 18:28 | 2025-12-05 16:44 | lower | TRUE | 0 | 72.4338 | FALSE | FALSE | 0.1999 | 2.1419 | 73.2519 | 1 | -0.2826 | -0.08478 | 0.13287 | -1.4888 | 0.40901 | Extreme triggered | 74.0699 | -2.1419 | Day | 202512 | 2025-12-05 | 2.1419
2025-12-05 16:59 | 72.3758 | FALSE | FALSE | -0.060054 | -0.083045 | -1.6709 | -2.2565 | 0 |  | 2025-12-05 16:44 | none | FALSE | 0 | 72.3157 | FALSE | FALSE | 0.2384 | 2.0016 | 73.1812 | 2 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.43273 | Extreme/elevated | 74.0467 | -1.8612 | Day | 202512 | 2025-12-05 | 1.8612
2025-12-05 17:14 | 72.095 | FALSE | FALSE | 0.058387 | 0.080921 | -1.9447 | -2.6265 | -0.2808 |  | 2025-12-05 16:44 | lower | TRUE | 0 | 72.1534 | FALSE | TRUE | 0.313 | 2.0423 | 73.0965 | 3 | -0.2808 | -0.08469 | 0.13273 | -1.4775 | 0.47157 | Persistent | 74.0397 | -2.1238 | Day | 202512 | 2025-12-05 | 2.1238
2025-12-05 17:29 | 72.095 | FALSE | FALSE | -0.067839 | -0.094185 | -1.9015 | -2.5697 | 0 |  | 2025-12-05 16:44 | none | FALSE | 0 | 72.0272 | FALSE | FALSE | 0.3527 | 1.9973 | 73.0118 | 4 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.49233 | Persistent | 73.9965 | -1.8622 | Night | 202512 | 2025-12-05 | 1.8622
2025-12-05 17:43 | 72.3758 | TRUE | FALSE | -0.38679 | -0.53729 | -1.5176 | -2.0537 | 0.2808 |  | 2025-12-05 16:44 | none | FALSE | 1 | 71.989 | FALSE | FALSE | 0.3935 | 1.8353 | 72.9412 | 5 | 0.2808 | -0.07065 | 0.15512 | 2.2657 | 0.47609 | Persistent | 73.8934 | -1.1876 | Night | 202512 | 2025-12-05 | 1.1876
2025-12-05 17:58 | 72.3758 | FALSE | FALSE | -0.40062 | -0.55661 | -1.3901 | -1.8845 | 0 |  | 2025-12-05 16:44 | none | FALSE | 1 | 71.9752 | FALSE | FALSE | 0.4451 | 1.7136 | 72.8705 | 6 | 0 | -0.07065 | 0.15512 | 0.45545 | 0.44768 | Persistent | 73.7659 | -1.1051 | Night | 202512 | 2025-12-05 | 1.1051
2025-12-05 18:13 | 72.3758 | FALSE | TRUE | -0.4305 | -0.59838 | -1.3069 | -1.7737 | 0 |  | 2025-12-05 16:44 | none | FALSE | 1 | 71.9453 | FALSE | FALSE | 0.4958 | 1.613 | 72.814 | 7 | 0 | -0.05652 | 0.14748 | 0.38324 | 0.43436 | Confirmed/Materialized Shift | 73.6827 | -1.0089 | Night | 202512 | 2025-12-05 | 1.0089
2025-12-05 18:28 | 72.3758 | FALSE | FALSE | -0.47148 | -0.6557 | -1.2631 | -1.7153 | 0 |  |  | none | FALSE | 1 | 71.9043 | FALSE | FALSE | 0.0894 |  | 72.7716 | 0 | 0 | -0.04239 | 0.13791 | 0.30738 | 0.43365 | Persistence ends | 73.6389 | -0.91277 | Night | 202512 | 2025-12-05 | 0.91277
2025-12-05 18:31 | 72.095 | FALSE | FALSE | -0.26985 | -0.3757 | -1.5102 | -2.0518 | -0.2808 |  |  | none | FALSE | 1 | 71.8251 | FALSE | FALSE | 0.1215 |  | 72.7152 | 0 | -0.2808 | -0.05643 | 0.14734 | -1.5229 | 0.44502 | Normal | 73.6052 | -1.3936 | Night | 202512 | 2025-12-05 | 1.3936
2025-12-05 18:31 | 72.095 | FALSE | FALSE | -0.33364 | -0.46493 | -1.4612 | -1.9865 | 0 |  |  | none | FALSE | 1 | 71.7614 | FALSE | FALSE | 0.1123 |  | 72.6588 | 0 | 0 | -0.05643 | 0.14734 | 0.383 | 0.4487 | Normal | 73.5562 | -1.2564 | Night | 202512 | 2025-12-05 | 1.2564
2025-12-05 18:47 | 72.941 | TRUE | FALSE | -1.1648 | -1.6228 | -0.57201 | -0.77811 | 0.846 |  |  | none | FALSE | 2 | 71.7762 | TRUE | FALSE | 0.1026 |  | 72.6446 | 0 | 0.846 | -0.01413 | 0.25004 | 3.44 | 0.43419 | Normal | 73.513 | 0.68258 | Night | 202512 | 2025-12-05 | 0.68258
2025-12-05 19:02 | 73.2236 | FALSE | FALSE | -1.4474 | -2.0165 | -0.28941 | -0.39369 | 0.2826 |  |  | none | FALSE | 2 | 71.7762 | FALSE | FALSE | 0.146 |  | 72.6446 | 0 | 0.2826 | 0 | 0.25871 | 1.0923 | 0.43419 | Normal | 73.513 | 1.3334 | Night | 202512 | 2025-12-05 | 1.3334
2025-12-05 19:17 | 73.5062 | FALSE | FALSE | -1.7634 | -2.4579 | -0.068502 | -0.093105 | 0.2826 |  |  | none | FALSE | 2 | 71.7428 | FALSE | FALSE | 0.1805 |  | 72.6588 | 0 | 0.2826 | 0.01413 | 0.26632 | 1.0081 | 0.45797 | Normal | 73.5747 | 1.8504 | Night | 202512 | 2025-12-05 | 1.8504
2025-12-05 19:31 | 73.7888 | FALSE | FALSE | -2.1202 | -2.9584 | 0.083321 | 0.11305 | 0.2826 | 2025-12-05 22:00 | 2025-12-05 19:31 | upper | TRUE | 2 | 71.6686 | FALSE | FALSE | 0.2585 | 2.1636 | 72.687 | 1 | 0.2826 | 0.02826 | 0.27294 | 0.93184 | 0.50923 | Extreme triggered | 73.7055 | 2.1636 | Night | 202512 | 2025-12-05 | 2.1636
2025-12-05 19:46 | 73.7888 | FALSE | FALSE | -2.1821 | -3.0473 | -0.035013 | -0.047427 | 0 |  | 2025-12-05 19:31 | none | FALSE | 1 | 71.6067 | FALSE | FALSE | 0.272 | 2.0502 | 72.7153 | 2 | 0 | 0.02826 | 0.27294 | -0.10354 | 0.55427 | Extreme/elevated | 73.8238 | 1.9368 | Night | 202512 | 2025-12-05 | 1.9368
2025-12-05 20:01 | 73.7888 | FALSE | FALSE | -2.2343 | -3.1224 | -0.14373 | -0.19441 | 0 |  | 2025-12-05 19:31 | none | FALSE | 1 | 71.5545 | FALSE | FALSE | 0.3172 | 1.9529 | 72.7435 | 3 | 0 | 0.02826 | 0.27294 | -0.10354 | 0.5945 | Persistent | 73.9325 | 1.7582 | Night | 202512 | 2025-12-05 | 1.7582
2025-12-05 20:16 | 73.7888 | FALSE | FALSE | -2.2788 | -3.1867 | -0.27304 | -0.36866 | 0 |  | 2025-12-05 19:31 | none | FALSE | 1 | 71.51 | FALSE | FALSE | 0.3619 | 1.8577 | 72.7859 | 4 | 0 | 0.04239 | 0.26314 | -0.16109 | 0.63795 | Persistent | 74.0618 | 1.572 | Night | 202512 | 2025-12-05 | 1.572
2025-12-05 20:30 | 73.7888 | FALSE | FALSE | -2.3122 | -3.2349 | -0.3912 | -0.52737 | 0 |  | 2025-12-05 19:31 | none | FALSE | 1 | 71.4766 | FALSE | FALSE | 0.409 | 1.7704 | 72.8283 | 5 | 0 | 0.04239 | 0.26314 | -0.16109 | 0.67584 | Persistent | 74.18 | 1.4212 | Night | 202512 | 2025-12-05 | 1.4212
2025-12-05 20:45 | 74.0714 | FALSE | FALSE | -2.6303 | -3.6817 | -0.2854 | -0.38383 | 0.2826 |  | 2025-12-05 19:31 | none | FALSE | 1 | 71.4411 | FALSE | FALSE | 0.4787 | 1.7434 | 72.899 | 6 | 0.2826 | 0.07065 | 0.25667 | 0.82576 | 0.72892 | Persistent | 74.3568 | 1.6085 | Night | 202512 | 2025-12-05 | 1.6085
2025-12-05 21:00 | 74.0714 | FALSE | TRUE | -2.645 | -3.7031 | -0.44142 | -0.59241 | 0 |  | 2025-12-05 19:31 | none | FALSE | 1 | 71.4264 | FALSE | FALSE | 0.5238 | 1.6983 | 72.9696 | 7 | 0 | 0.07065 | 0.25667 | -0.27525 | 0.7716 | Confirmed/Materialized Shift | 74.5128 | 1.4279 | Night | 202512 | 2025-12-05 | 1.4279
2025-12-05 21:15 | 74.0714 | FALSE | TRUE | -2.6084 | -3.65 | -0.57439 | -0.76949 | 0 |  | 2025-12-05 19:31 | none | FALSE | 0 | 71.463 | FALSE | FALSE | 0.4852 | 1.6458 | 73.0544 | 8 | 0 | 0.08478 | 0.24365 | -0.34796 | 0.79569 | Confirmed/Materialized Shift | 74.6458 | 1.2781 | Night | 202512 | 2025-12-05 | 1.2781
2025-12-05 21:30 | 74.0714 | FALSE | TRUE | -2.5518 | -3.568 | -0.68737 | -0.91944 | 0 |  | 2025-12-05 19:31 | none | FALSE | 0 | 71.5196 | FALSE | FALSE | 0.4767 | 1.5908 | 73.1392 | 9 | 0 | 0.08478 | 0.24365 | -0.34796 | 0.80979 | Confirmed/Materialized Shift | 74.7588 | 1.1512 | Night | 202512 | 2025-12-05 | 1.1512
2025-12-05 21:45 | 74.0714 | FALSE | TRUE | -2.4257 | -3.3857 | -0.75888 | -1.0141 | 0 |  | 2025-12-05 19:31 | none | FALSE | 0 | 71.6457 | FALSE | FALSE | 0.4698 | 1.5364 | 73.238 | 10 | 0 | 0.09882 | 0.22914 | -0.43127 | 0.79614 | Confirmed/Materialized Shift | 74.8303 | 1.0468 | Night | 202512 | 2025-12-05 | 1.0468
2025-12-05 22:00 | 74.0714 | FALSE | FALSE | -2.2726 | -3.1652 | -0.80341 | -1.073 | 0 |  |  | none | FALSE | 0 | 71.7988 | FALSE | FALSE | 0.0637 |  | 73.3368 | 0 | 0 | 0.09882 | 0.22914 | -0.43127 | 0.769 | Persistence ends | 74.8748 | 0.95525 | Night | 202512 | 2025-12-05 | 0.95525
2025-12-05 22:15 | 74.0714 | FALSE | FALSE | -2.1512 | -2.9911 | -0.85164 | -1.1367 | 0 |  |  | none | FALSE | 0 | 71.9202 | FALSE | FALSE | 0.0577 |  | 73.4216 | 0 | 0 | 0.08478 | 0.22598 | -0.37517 | 0.75072 | Normal | 74.923 | 0.86557 | Night | 202512 | 2025-12-05 | 0.86557
2025-12-05 22:30 | 74.3522 | FALSE | FALSE | -2.3033 | -3.1968 | -0.63971 | -0.85303 | 0.2808 |  |  | none | FALSE | 0 | 72.0489 | FALSE | FALSE | 0.0754 |  | 73.5204 | 0 | 0.2808 | 0.09882 | 0.22914 | 0.7942 | 0.73574 | Normal | 74.9919 | 1.1305 | Night | 202512 | 2025-12-05 | 1.1305
2025-12-05 22:45 | 74.3522 | FALSE | FALSE | -2.145 | -2.9707 | -0.67913 | -0.90512 | 0 |  |  | none | FALSE | 0 | 72.2072 | FALSE | FALSE | 0.0692 |  | 73.6192 | 0 | 0 | 0.09882 | 0.22914 | -0.43127 | 0.70604 | Normal | 75.0313 | 1.0381 | Night | 202512 | 2025-12-05 | 1.0381
2025-12-05 23:00 | 74.3522 | FALSE | FALSE | -1.9534 | -2.6981 | -0.68513 | -0.91305 | 0 |  |  | none | FALSE | 0 | 72.3988 | FALSE | FALSE | 0.0641 |  | 73.7181 | 0 | 0 | 0.09882 | 0.22914 | -0.43127 | 0.65963 | Normal | 75.0373 | 0.96135 | Night | 202512 | 2025-12-05 | 0.96135
2025-12-05 23:15 | 74.0714 | FALSE | FALSE | -1.3367 | -1.8377 | -0.82762 | -1.105 | -0.2808 |  |  | none | FALSE | 0 | 72.7347 | FALSE | FALSE | 0.0314 |  | 73.8169 | 0 | -0.2808 | 0.09882 | 0.22914 | -1.6568 | 0.54107 | Normal | 74.899 | 0.4704 | Night | 202512 | 2025-12-05 | 0.4704
2025-12-05 23:29 | 74.0714 | FALSE | FALSE | -0.87638 | -1.1973 | -0.56498 | -0.75697 | 0 |  |  | none | FALSE | 0 | 73.195 | FALSE | FALSE | 0.0288 |  | 73.9157 | 0 | 0 | 0.09882 | 0.22914 | -0.43127 | 0.36034 | Normal | 74.6364 | 0.43209 | Night | 202512 | 2025-12-05 | 0.43209
2025-12-05 23:44 | 74.0714 | FALSE | FALSE | -0.65687 | -0.89474 | -0.45851 | -0.6152 | 0 |  |  | none | FALSE | 0 | 73.4145 | FALSE | FALSE | 0.0237 |  | 73.9722 | 0 | 0 | 0.05652 | 0.14748 | -0.38324 | 0.27885 | Normal | 74.5299 | 0.35568 | Night | 202512 | 2025-12-05 | 0.35568
2025-12-05 23:59 | 74.0714 | FALSE | FALSE | -0.48985 | -0.66572 | -0.37627 | -0.50541 | 0 |  |  | none | FALSE | 0 | 73.5816 | FALSE | FALSE | 0.0175 |  | 74.0146 | 0 | 0 | 0.04239 | 0.13791 | -0.30738 | 0.21653 | Normal | 74.4477 | 0.26227 | Night | 202512 | 2025-12-05 | 0.26227
2025-12-06 00:14 | 74.0714 | FALSE | FALSE | -0.38969 | -0.52889 | -0.33263 | -0.44706 | 0 |  |  | none | FALSE | 0 | 73.6817 | FALSE | FALSE | 0.0105 |  | 74.0429 | 0 | 0 | 0.02826 | 0.12596 | -0.22436 | 0.18058 | Normal | 74.404 | 0.15799 | Night | 202512 | 2025-12-06 | 0.15799
2025-12-06 00:29 | 74.0714 | FALSE | FALSE | -0.35525 | -0.48192 | -0.32645 | -0.43879 | 0 |  |  | none | FALSE | 0 | 73.7161 | FALSE | FALSE | 0.0056 |  | 74.057 | 0 | 0 | 0.01413 | 0.11087 | -0.12744 | 0.17043 | Normal | 74.3979 | 0.084495 | Night | 202512 | 2025-12-06 | 0.084495
2025-12-06 00:44 | 74.0714 | FALSE | FALSE | -0.31687 | -0.42963 | -0.31633 | -0.42525 | 0 |  |  | none | FALSE | 0 | 73.7545 | FALSE | FALSE | 0.0001 |  | 74.0711 | 0 | 0 | 0.01413 | 0.11087 | -0.12744 | 0.1583 | Normal | 74.3877 | 0.0017056 | Night | 202512 | 2025-12-06 | 0.0017056
2025-12-06 00:59 | 74.0714 | FALSE | FALSE | -0.27357 | -0.3707 | -0.30129 | -0.40511 | 0 |  |  | none | FALSE | 0 | 73.7978 | FALSE | FALSE | 0.0064 |  | 74.0853 | 0 | 0 | 0.01413 | 0.11087 | -0.12744 | 0.14372 | Normal | 74.3727 | -0.09644 | Night | 202512 | 2025-12-06 | 0.09644
2025-12-06 01:14 | 74.0714 | FALSE | FALSE | -0.22363 | -0.30283 | -0.27961 | -0.37607 | 0 |  |  | none | FALSE | 0 | 73.8478 | FALSE | FALSE | 0.0148 |  | 74.0994 | 0 | 0 | 0.01413 | 0.11087 | -0.12744 | 0.12581 | Normal | 74.351 | -0.22248 | Night | 202512 | 2025-12-06 | 0.22248
2025-12-06 01:29 | 74.0714 | FALSE | FALSE | -0.16362 | -0.22139 | -0.24786 | -0.33351 | 0 |  |  | none | FALSE | 0 | 73.9078 | FALSE | FALSE | 0.0273 |  | 74.1135 | 0 | 0 | 0.01413 | 0.11087 | -0.12744 | 0.10287 | Normal | 74.3193 | -0.40945 | Night | 202512 | 2025-12-06 | 0.40945
2025-12-06 01:44 | 74.0714 | FALSE | FALSE | -0.16362 | -0.22139 | -0.24786 | -0.33351 | 0 |  |  | none | FALSE | 0 | 73.9078 | FALSE | FALSE | 0.0273 |  | 74.1135 | 0 | 0 | 0 | 0.091104 | 0 | 0.10287 | Normal | 74.3193 | -0.40945 | Night | 202512 | 2025-12-06 | 0.40945
2025-12-06 01:59 | 74.0714 | FALSE | FALSE | -0.16362 | -0.22139 | -0.24786 | -0.33351 | 0 |  |  | none | FALSE | 0 | 73.9078 | FALSE | FALSE | 0.0273 |  | 74.1135 | 0 | 0 | 0 | 0.091104 | 0 | 0.10287 | Normal | 74.3193 | -0.40945 | Night | 202512 | 2025-12-06 | 0.40945
2025-12-06 02:14 | 74.0714 | FALSE | FALSE | -0.16362 | -0.22139 | -0.24786 | -0.33351 | 0 |  |  | none | FALSE | 0 | 73.9078 | FALSE | FALSE | 0.0273 |  | 74.1135 | 0 | 0 | 0 | 0.091104 | 0 | 0.10287 | Normal | 74.3193 | -0.40945 | Night | 202512 | 2025-12-06 | 0.40945
2025-12-06 02:28 | 74.0714 | FALSE | FALSE | -0.16362 | -0.22139 | -0.24786 | -0.33351 | 0 |  |  | none | FALSE | 0 | 73.9078 | FALSE | FALSE | 0.0273 |  | 74.1135 | 0 | 0 | 0 | 0.091104 | 0 | 0.10287 | Normal | 74.3193 | -0.40945 | Night | 202512 | 2025-12-06 | 0.40945
2025-12-06 02:43 | 74.0714 | FALSE | FALSE | -0.16362 | -0.22139 | -0.24786 | -0.33351 | 0 |  |  | none | FALSE | 0 | 73.9078 | FALSE | FALSE | 0.0273 |  | 74.1135 | 0 | 0 | 0 | 0.091104 | 0 | 0.10287 | Normal | 74.3193 | -0.40945 | Night | 202512 | 2025-12-06 | 0.40945
2025-12-06 02:58 | 74.0714 | FALSE | FALSE | -0.16362 | -0.22139 | -0.24786 | -0.33351 | 0 |  |  | none | FALSE | 0 | 73.9078 | FALSE | FALSE | 0.0273 |  | 74.1135 | 0 | 0 | 0 | 0.091104 | 0 | 0.10287 | Normal | 74.3193 | -0.40945 | Night | 202512 | 2025-12-06 | 0.40945
2025-12-06 03:13 | 73.7888 | TRUE | FALSE | 0.058968 | 0.079851 | -0.56221 | -0.75616 | -0.2826 | 2025-12-06 05:13 | 2025-12-06 03:13 | lower | TRUE | 1 | 73.8478 | FALSE | FALSE | 0.2503 | 2.4687 | 74.0994 | 1 | -0.2826 | -0.01413 | 0.11087 | -2.4214 | 0.12581 | Extreme triggered | 74.351 | -2.4687 | Night | 202512 | 2025-12-06 | 2.4687
2025-12-06 03:28 | 73.7888 | FALSE | FALSE | 0.023913 | 0.032397 | -0.54093 | -0.72774 | 0 |  | 2025-12-06 03:13 | lower | TRUE | 1 | 73.8127 | FALSE | FALSE | 0.2885 | 2.3269 | 74.0712 | 2 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.12925 | Extreme/elevated | 74.3297 | -2.185 | Night | 202512 | 2025-12-06 | 2.185
2025-12-06 03:43 | 73.7888 | FALSE | FALSE | 0.0019501 | 0.0026427 | -0.50655 | -0.68181 | 0 |  | 2025-12-06 03:13 | lower | TRUE | 1 | 73.7908 | FALSE | TRUE | 0.3344 | 2.2231 | 74.043 | 3 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.12615 | Persistent | 74.2953 | -2.0155 | Night | 202512 | 2025-12-06 | 2.0155
2025-12-06 03:58 | 73.7888 | FALSE | FALSE | -0.0058732 | -0.0079601 | -0.45803 | -0.61691 | 0 |  | 2025-12-06 03:13 | none | FALSE | 1 | 73.7829 | FALSE | FALSE | 0.3871 | 2.1546 | 74.0149 | 4 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.11598 | Persistent | 74.2468 | -1.9494 | Night | 202512 | 2025-12-06 | 1.9494
2025-12-06 04:13 | 73.7888 | FALSE | FALSE | -0.039147 | -0.053081 | -0.46305 | -0.62362 | 0 |  | 2025-12-06 03:13 | none | FALSE | 1 | 73.7497 | FALSE | FALSE | 0.4268 | 2.0613 | 74.0007 | 5 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.12555 | Persistent | 74.2518 | -1.6882 | Night | 202512 | 2025-12-06 | 1.6882
2025-12-06 04:28 | 73.7888 | FALSE | FALSE | -0.067916 | -0.092126 | -0.46356 | -0.6243 | 0 |  | 2025-12-06 03:13 | none | FALSE | 1 | 73.7209 | FALSE | FALSE | 0.4707 | 1.9659 | 73.9866 | 6 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13287 | Persistent | 74.2524 | -1.4888 | Night | 202512 | 2025-12-06 | 1.4888
2025-12-06 04:43 | 73.7888 | FALSE | TRUE | -0.092897 | -0.12605 | -0.46028 | -0.61991 | 0 |  | 2025-12-06 03:13 | none | FALSE | 1 | 73.6959 | FALSE | FALSE | 0.5171 | 1.8748 | 73.9725 | 7 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13829 | Confirmed/Materialized Shift | 74.2491 | -1.3283 | Night | 202512 | 2025-12-06 | 1.3283
2025-12-06 04:58 | 73.5062 | TRUE | TRUE | 0.096194 | 0.13069 | -0.77987 | -1.0498 | -0.2826 |  | 2025-12-06 03:13 | lower | TRUE | 2 | 73.6024 | TRUE | TRUE | 0.628 | 1.9608 | 73.9442 | 8 | -0.2826 | -0.02826 | 0.086982 | -2.924 | 0.17092 | Confirmed/Materialized Shift | 74.2861 | -2.5628 | Night | 202512 | 2025-12-06 | 2.5628
2025-12-06 05:13 | 73.7888 | TRUE | FALSE | -0.20176 | -0.27418 | -0.48436 | -0.65214 | 0.2826 |  |  | none | FALSE | 3 | 73.587 | TRUE | FALSE | 0.1406 |  | 73.9301 | 0 | 0.2826 | -0.01413 | 0.11135 | 2.6647 | 0.17153 | Persistence ends | 74.2732 | -0.82375 | Night | 202512 | 2025-12-06 | 0.82375
2025-12-06 05:27 | 73.7888 | FALSE | FALSE | -0.21467 | -0.29177 | -0.46901 | -0.63159 | 0 |  |  | none | FALSE | 3 | 73.5741 | FALSE | FALSE | 0.1353 |  | 73.916 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.17092 | Normal | 74.2578 | -0.74404 | Night | 202512 | 2025-12-06 | 0.74404
2025-12-06 05:42 | 73.5062 | TRUE | FALSE | 0.0023623 | 0.0032137 | -0.76066 | -1.0242 | -0.2826 | 2025-12-06 07:27 | 2025-12-06 05:42 | lower | TRUE | 3 | 73.5086 | TRUE | FALSE | 0.277 | 2.0125 | 73.8877 | 1 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.18957 | Extreme triggered | 74.2669 | -2.0125 | Night | 202512 | 2025-12-06 | 2.0125
2025-12-06 05:57 | 73.5062 | FALSE | FALSE | -0.051631 | -0.07029 | -0.75813 | -1.0209 | 0 |  | 2025-12-06 05:42 | none | FALSE | 3 | 73.4546 | FALSE | FALSE | 0.3163 | 1.8787 | 73.8594 | 2 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.20244 | Extreme/elevated | 74.2643 | -1.745 | Night | 202512 | 2025-12-06 | 1.745
2025-12-06 06:13 | 73.5062 | FALSE | FALSE | -0.096174 | -0.13101 | -0.74615 | -1.0049 | 0 |  | 2025-12-06 05:42 | none | FALSE | 3 | 73.41 | FALSE | FALSE | 0.36 | 1.7669 | 73.8312 | 3 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21058 | Persistent | 74.2524 | -1.5433 | Night | 202512 | 2025-12-06 | 1.5433
2025-12-06 06:27 | 73.5062 | FALSE | FALSE | -0.13234 | -0.18037 | -0.7258 | -0.97775 | 0 |  | 2025-12-06 05:42 | none | FALSE | 3 | 73.3739 | FALSE | FALSE | 0.4065 | 1.671 | 73.8029 | 4 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21454 | Persistent | 74.232 | -1.3831 | Night | 202512 | 2025-12-06 | 1.3831
2025-12-06 06:42 | 73.5062 | FALSE | FALSE | -0.1606 | -0.21897 | -0.69754 | -0.94004 | 0 |  | 2025-12-06 05:42 | none | FALSE | 3 | 73.3456 | FALSE | FALSE | 0.4549 | 1.587 | 73.7747 | 5 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21454 | Persistent | 74.2037 | -1.2514 | Night | 202512 | 2025-12-06 | 1.2514
2025-12-06 06:57 | 73.5062 | FALSE | FALSE | -0.18095 | -0.24678 | -0.66137 | -0.89173 | 0 |  | 2025-12-06 05:42 | none | FALSE | 3 | 73.3252 | FALSE | FALSE | 0.5046 | 1.5127 | 73.7464 | 6 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21058 | Persistent | 74.1676 | -1.1407 | Night | 202512 | 2025-12-06 | 1.1407
2025-12-06 07:12 | 73.5062 | FALSE | TRUE | -0.19293 | -0.26316 | -0.61683 | -0.83217 | 0 |  | 2025-12-06 05:42 | none | FALSE | 3 | 73.3133 | FALSE | FALSE | 0.5555 | 1.4461 | 73.7181 | 7 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.20244 | Confirmed/Materialized Shift | 74.123 | -1.047 | Day | 202512 | 2025-12-06 | 1.047
2025-12-06 07:27 | 73.5062 | FALSE | FALSE | -0.19546 | -0.26662 | -0.56284 | -0.75988 | 0 |  |  | none | FALSE | 2 | 73.3107 | FALSE | FALSE | 0.1217 |  | 73.6899 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.18957 | Persistence ends | 74.069 | -0.96896 | Day | 202512 | 2025-12-06 | 0.96896
2025-12-06 07:31 | 73.5062 | FALSE | FALSE | -0.18641 | -0.25424 | -0.49727 | -0.67195 | 0 |  |  | none | FALSE | 1 | 73.3198 | FALSE | FALSE | 0.0892 |  | 73.6616 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.17092 | Normal | 74.0035 | -0.90938 | Day | 202512 | 2025-12-06 | 0.90938
2025-12-06 07:46 | 73.5062 | FALSE | FALSE | -0.16132 | -0.21994 | -0.41566 | -0.56229 | 0 |  |  | none | FALSE | 1 | 73.3449 | FALSE | FALSE | 0.0873 |  | 73.6334 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.14424 | Normal | 73.9219 | -0.88163 | Day | 202512 | 2025-12-06 | 0.88163
2025-12-06 08:01 | 73.5062 | FALSE | FALSE | -0.17104 | -0.23324 | -0.39712 | -0.53736 | 0 |  |  | none | FALSE | 0 | 73.3352 | FALSE | FALSE | 0.0531 |  | 73.6192 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14204 | Normal | 73.9033 | -0.79582 | Day | 202512 | 2025-12-06 | 0.79582
2025-12-06 08:16 | 73.5062 | FALSE | FALSE | -0.17768 | -0.2423 | -0.3755 | -0.50824 | 0 |  |  | none | FALSE | 0 | 73.3285 | FALSE | FALSE | 0.0477 |  | 73.6051 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13829 | Normal | 73.8817 | -0.71522 | Day | 202512 | 2025-12-06 | 0.71522
2025-12-06 08:30 | 73.5062 | FALSE | FALSE | -0.18096 | -0.24679 | -0.35052 | -0.47459 | 0 |  |  | none | FALSE | 0 | 73.3252 | FALSE | FALSE | 0.0425 |  | 73.591 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13287 | Normal | 73.8567 | -0.63808 | Day | 202512 | 2025-12-06 | 0.63808
2025-12-06 08:31 | 73.7888 | TRUE | FALSE | -0.46356 | -0.63219 | -0.067916 | -0.091956 | 0.2826 |  |  | none | FALSE | 1 | 73.3252 | FALSE | FALSE | 0.1278 |  | 73.591 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.13287 | Normal | 73.8567 | 1.4888 | Day | 202512 | 2025-12-06 | 1.4888
2025-12-06 08:46 | 73.7888 | FALSE | FALSE | -0.46356 | -0.63219 | -0.067916 | -0.091956 | 0 |  |  | none | FALSE | 1 | 73.3252 | FALSE | FALSE | 0.1278 |  | 73.591 | 0 | 0 | 0 | 0.12967 | 0 | 0.13287 | Normal | 73.8567 | 1.4888 | Day | 202512 | 2025-12-06 | 1.4888
2025-12-06 08:46 | 73.7888 | FALSE | FALSE | -0.46356 | -0.63219 | -0.067916 | -0.091956 | 0 |  |  | none | FALSE | 1 | 73.3252 | FALSE | FALSE | 0.1278 |  | 73.591 | 0 | 0 | 0 | 0.12967 | 0 | 0.13287 | Normal | 73.8567 | 1.4888 | Day | 202512 | 2025-12-06 | 1.4888
2025-12-06 09:01 | 73.7888 | FALSE | FALSE | -0.46356 | -0.63219 | -0.067916 | -0.091956 | 0 |  |  | none | FALSE | 1 | 73.3252 | FALSE | FALSE | 0.1278 |  | 73.591 | 0 | 0 | 0 | 0.12967 | 0 | 0.13287 | Normal | 73.8567 | 1.4888 | Day | 202512 | 2025-12-06 | 1.4888
2025-12-06 09:16 | 73.7888 | FALSE | FALSE | -0.46028 | -0.62769 | -0.092897 | -0.12574 | 0 |  |  | none | FALSE | 1 | 73.3285 | FALSE | FALSE | 0.1171 |  | 73.6051 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.13829 | Normal | 73.8817 | 1.3283 | Day | 202512 | 2025-12-06 | 1.3283
2025-12-06 09:17 | 74.0714 | TRUE | FALSE | -0.79029 | -1.0784 | 0.11403 | 0.15419 | 0.2826 | 2025-12-06 09:35 | 2025-12-06 09:17 | upper | TRUE | 2 | 73.2811 | TRUE | FALSE | 0.2926 | 2.6745 | 73.6192 | 1 | 0.2826 | 0.01413 | 0.11135 | 2.411 | 0.16906 | Extreme triggered | 73.9574 | 2.6745 | Day | 202512 | 2025-12-06 | 2.6745
2025-12-06 09:20 | 74.0714 | FALSE | FALSE | -0.82595 | -1.1276 | 0.050115 | 0.067703 | 0 |  | 2025-12-06 09:17 | upper | TRUE | 2 | 73.2455 | FALSE | FALSE | 0.322 | 2.4664 | 73.6334 | 2 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.19396 | Extreme/elevated | 74.0213 | 2.2584 | Day | 202512 | 2025-12-06 | 2.2584
2025-12-06 09:35 | 73.5062 | TRUE | FALSE | -0.26075 | -0.35599 | -0.51509 | -0.69586 | -0.5652 |  |  | none | FALSE | 3 | 73.2455 | TRUE | FALSE | 0.1294 |  | 73.6334 | 0 | -0.5652 | 0 | 0.15881 | -3.559 | 0.19396 | Persistence ends | 74.0213 | -0.65566 | Day | 202512 | 2025-12-06 | 0.65566
2025-12-06 09:45 | 73.2236 | FALSE | FALSE | -0.030485 | -0.04165 | -0.82177 | -1.1098 | -0.2826 |  |  | none | FALSE | 3 | 73.1931 | FALSE | FALSE | 0.2095 |  | 73.6192 | 0 | -0.2826 | -0.01413 | 0.17092 | -1.5708 | 0.21306 | Normal | 74.0454 | -1.8569 | Day | 202512 | 2025-12-06 | 1.8569
2025-12-06 10:01 | 72.941 | FALSE | FALSE | 0.12809 | 0.17529 | -1.1719 | -1.5812 | -0.2826 | 2025-12-06 12:00 | 2025-12-06 10:01 | lower | TRUE | 3 | 73.0691 | FALSE | FALSE | 0.3089 | 2.4908 | 73.591 | 1 | -0.2826 | -0.02826 | 0.18107 | -1.4047 | 0.26095 | Extreme triggered | 74.1129 | -2.4908 | Day | 202512 | 2025-12-06 | 2.4908
2025-12-06 10:16 | 72.941 | FALSE | FALSE | 0.024694 | 0.033843 | -1.2187 | -1.6434 | 0 |  | 2025-12-06 10:01 | lower | TRUE | 2 | 72.9657 | FALSE | FALSE | 0.3103 | 2.2868 | 73.5627 | 2 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.29851 | Extreme/elevated | 74.1597 | -2.0827 | Day | 202512 | 2025-12-06 | 2.0827
2025-12-06 10:31 | 72.941 | FALSE | FALSE | -0.06516 | -0.089413 | -1.2521 | -1.6876 | 0 |  | 2025-12-06 10:01 | none | FALSE | 2 | 72.8758 | FALSE | FALSE | 0.3487 | 2.1252 | 73.5345 | 3 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.32931 | Persistent | 74.1931 | -1.8021 | Day | 202512 | 2025-12-06 | 1.8021
2025-12-06 10:45 | 72.941 | FALSE | FALSE | -0.14501 | -0.1992 | -1.2754 | -1.7185 | 0 |  | 2025-12-06 10:01 | none | FALSE | 2 | 72.796 | FALSE | FALSE | 0.3918 | 1.9918 | 73.5062 | 4 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.3551 | Persistent | 74.2164 | -1.5916 | Day | 202512 | 2025-12-06 | 1.5916
2025-12-06 11:00 | 72.941 | FALSE | FALSE | -0.21691 | -0.29826 | -1.2908 | -1.7389 | 0 |  | 2025-12-06 10:01 | none | FALSE | 2 | 72.7241 | FALSE | FALSE | 0.4378 | 1.8784 | 73.4779 | 5 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.37692 | Persistent | 74.2318 | -1.4245 | Day | 202512 | 2025-12-06 | 1.4245
2025-12-06 11:15 | 72.941 | FALSE | FALSE | -0.28217 | -0.38836 | -1.2995 | -1.7504 | 0 |  | 2025-12-06 10:01 | none | FALSE | 2 | 72.6588 | FALSE | FALSE | 0.4858 | 1.7797 | 73.4497 | 6 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.39543 | Persistent | 74.2405 | -1.2864 | Day | 202512 | 2025-12-06 | 1.2864
2025-12-06 11:30 | 72.941 | FALSE | TRUE | -0.34171 | -0.47067 | -1.3025 | -1.7544 | 0 |  | 2025-12-06 10:01 | none | FALSE | 1 | 72.5993 | FALSE | FALSE | 0.5065 | 1.6924 | 73.4214 | 7 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.41106 | Confirmed/Materialized Shift | 74.2435 | -1.1687 | Day | 202512 | 2025-12-06 | 1.1687
2025-12-06 11:45 | 72.941 | FALSE | TRUE | -0.39614 | -0.54606 | -1.3005 | -1.7517 | 0 |  | 2025-12-06 10:01 | none | FALSE | 1 | 72.5449 | FALSE | FALSE | 0.4996 | 1.6141 | 73.3932 | 8 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.42415 | Confirmed/Materialized Shift | 74.2415 | -1.066 | Day | 202512 | 2025-12-06 | 1.066
2025-12-06 12:00 | 72.941 | FALSE | FALSE | -0.44592 | -0.61511 | -1.2937 | -1.7427 | 0 |  |  | none | FALSE | 0 | 72.4951 | FALSE | FALSE | 0.065 |  | 73.3649 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.43491 | Persistence ends | 74.2347 | -0.97468 | Day | 202512 | 2025-12-06 | 0.97468
2025-12-06 12:15 | 72.941 | FALSE | FALSE | -0.49141 | -0.67828 | -1.2827 | -1.7281 | 0 |  |  | none | FALSE | 0 | 72.4496 | FALSE | FALSE | 0.0595 |  | 73.3366 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.44353 | Normal | 74.2237 | -0.89204 | Day | 202512 | 2025-12-06 | 0.89204
2025-12-06 12:30 | 72.941 | FALSE | FALSE | -0.53284 | -0.73588 | -1.2676 | -1.7082 | 0 |  |  | none | FALSE | 0 | 72.4082 | FALSE | FALSE | 0.0544 |  | 73.3084 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.45011 | Normal | 74.2086 | -0.8162 | Day | 202512 | 2025-12-06 | 0.8162
2025-12-06 12:45 | 72.941 | FALSE | FALSE | -0.55969 | -0.77325 | -1.2097 | -1.6314 | 0 |  |  | none | FALSE | 0 | 72.3813 | FALSE | FALSE | 0.049 |  | 73.266 | 0 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.44234 | Normal | 74.1507 | -0.73471 | Day | 202512 | 2025-12-06 | 0.73471
2025-12-06 13:00 | 72.941 | FALSE | FALSE | -0.57751 | -0.79806 | -1.1427 | -1.5425 | 0 |  |  | none | FALSE | 0 | 72.3635 | FALSE | FALSE | 0.0438 |  | 73.2236 | 0 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.43005 | Normal | 74.0837 | -0.65713 | Day | 202512 | 2025-12-06 | 0.65713
2025-12-06 13:15 | 73.2236 | FALSE | FALSE | -0.84629 | -1.1693 | -0.78977 | -1.0671 | 0.2826 |  |  | none | FALSE | 0 | 72.3773 | FALSE | FALSE | 0.0046 |  | 73.1953 | 0 | 0.2826 | -0.02826 | 0.18107 | 1.7168 | 0.40901 | Normal | 74.0134 | 0.069093 | Day | 202512 | 2025-12-06 | 0.069093
2025-12-06 13:30 | 72.941 | FALSE | FALSE | -0.56334 | -0.77833 | -0.98724 | -1.3354 | -0.2826 |  |  | none | FALSE | 0 | 72.3777 | FALSE | FALSE | 0.0365 |  | 73.153 | 0 | -0.2826 | -0.04239 | 0.18957 | -1.2671 | 0.38764 | Normal | 73.9282 | -0.54676 | Day | 202512 | 2025-12-06 | 0.54676
2025-12-06 13:44 | 72.941 | FALSE | FALSE | -0.55006 | -0.75984 | -0.88918 | -1.2044 | 0 |  |  | none | FALSE | 0 | 72.3909 | FALSE | FALSE | 0.0314 |  | 73.1106 | 0 | 0 | -0.04239 | 0.18957 | 0.22361 | 0.35981 | Normal | 73.8302 | -0.47125 | Day | 202512 | 2025-12-06 | 0.47125
2025-12-06 13:59 | 72.941 | FALSE | FALSE | -0.44918 | -0.61962 | -0.67526 | -0.91727 | 0 |  |  | none | FALSE | 0 | 72.4918 | FALSE | FALSE | 0.0268 |  | 73.054 | 0 | 0 | -0.05652 | 0.17396 | 0.32489 | 0.28111 | Normal | 73.6163 | -0.40212 | Day | 202512 | 2025-12-06 | 0.40212
2025-12-06 14:14 | 72.941 | FALSE | FALSE | -0.23916 | -0.32896 | -0.3522 | -0.48054 | 0 |  |  | none | FALSE | 0 | 72.7018 | FALSE | FALSE | 0.0255 |  | 72.9975 | 0 | 0 | -0.05652 | 0.17396 | 0.32489 | 0.14784 | Normal | 73.2932 | -0.3823 | Day | 202512 | 2025-12-06 | 0.3823
2025-12-06 14:29 | 72.941 | FALSE | FALSE | -0.1457 | -0.20016 | -0.20222 | -0.27648 | 0 |  |  | none | FALSE | 0 | 72.7953 | FALSE | FALSE | 0.0217 |  | 72.9693 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.086982 | Normal | 73.1432 | -0.32489 | Day | 202512 | 2025-12-06 | 0.32489
2025-12-06 14:44 | 72.941 | FALSE | FALSE | -0.11225 | -0.15413 | -0.14051 | -0.19227 | 0 |  |  | none | FALSE | 0 | 72.8287 | FALSE | FALSE | 0.0149 |  | 72.9551 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.063191 | Normal | 73.0815 | -0.22361 | Day | 202512 | 2025-12-06 | 0.22361
2025-12-06 14:59 | 72.941 | FALSE | FALSE | -0.11225 | -0.15413 | -0.14051 | -0.19227 | 0 |  |  | none | FALSE | 0 | 72.8287 | FALSE | FALSE | 0.0149 |  | 72.9551 | 0 | 0 | 0 | 0.091688 | 0 | 0.063191 | Normal | 73.0815 | -0.22361 | Day | 202512 | 2025-12-06 | 0.22361
2025-12-06 15:14 | 72.941 | FALSE | FALSE | -0.11225 | -0.15413 | -0.14051 | -0.19227 | 0 |  |  | none | FALSE | 0 | 72.8287 | FALSE | FALSE | 0.0149 |  | 72.9551 | 0 | 0 | 0 | 0.091688 | 0 | 0.063191 | Normal | 73.0815 | -0.22361 | Day | 202512 | 2025-12-06 | 0.22361
2025-12-06 15:29 | 72.6584 | TRUE | FALSE | 0.099225 | 0.13638 | -0.46598 | -0.63724 | -0.2826 | 2025-12-06 17:36 | 2025-12-06 15:29 | lower | TRUE | 1 | 72.7576 | FALSE | FALSE | 0.2912 | 3.0822 | 72.941 | 1 | -0.2826 | -0.01413 | 0.11135 | -2.411 | 0.091688 | Extreme triggered | 73.1244 | -3.0822 | Day | 202512 | 2025-12-06 | 3.0822
2025-12-06 15:44 | 72.6584 | FALSE | FALSE | 0.045762 | 0.062942 | -0.49118 | -0.67147 | 0 |  | 2025-12-06 15:29 | lower | TRUE | 1 | 72.7042 | FALSE | FALSE | 0.3036 | 2.7466 | 72.9269 | 2 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.11135 | Extreme/elevated | 73.1496 | -2.411 | Day | 202512 | 2025-12-06 | 2.411
2025-12-06 15:59 | 72.6584 | FALSE | FALSE | 0.0015749 | 0.0021675 | -0.50711 | -0.69309 | 0 |  | 2025-12-06 15:29 | lower | TRUE | 1 | 72.66 | FALSE | TRUE | 0.3342 | 2.5019 | 72.9127 | 3 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.12638 | Persistent | 73.1655 | -2.0125 | Day | 202512 | 2025-12-06 | 2.0125
2025-12-06 16:14 | 72.3758 | TRUE | FALSE | 0.16075 | 0.22161 | -0.85661 | -1.1697 | -0.2826 |  | 2025-12-06 15:29 | lower | TRUE | 2 | 72.5366 | TRUE | TRUE | 0.4807 | 2.6074 | 72.8845 | 4 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.17396 | Persistent | 73.2324 | -2.924 | Day | 202512 | 2025-12-06 | 2.924
2025-12-06 16:29 | 72.3758 | FALSE | FALSE | 0.066301 | 0.091522 | -0.89454 | -1.2209 | 0 |  | 2025-12-06 15:29 | lower | TRUE | 2 | 72.4421 | FALSE | TRUE | 0.4975 | 2.55 | 72.8562 | 5 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.20706 | Persistent | 73.2703 | -2.3202 | Day | 202512 | 2025-12-06 | 2.3202
2025-12-06 16:43 | 72.3758 | FALSE | FALSE | -0.011746 | -0.016232 | -0.91607 | -1.2499 | 0 |  | 2025-12-06 15:29 | none | FALSE | 2 | 72.3641 | FALSE | FALSE | 0.53 | 2.4499 | 72.828 | 6 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.23195 | Persistent | 73.2919 | -1.9494 | Day | 202512 | 2025-12-06 | 1.9494
2025-12-06 16:58 | 72.095 | FALSE | TRUE | 0.12667 | 0.17539 | -1.2547 | -1.7105 | -0.2808 |  | 2025-12-06 15:29 | lower | TRUE | 2 | 72.2217 | FALSE | TRUE | 0.6204 | 2.4498 | 72.7857 | 7 | -0.2808 | -0.0423 | 0.13813 | -1.7266 | 0.282 | Confirmed/Materialized Shift | 73.3497 | -2.4492 | Day | 202512 | 2025-12-06 | 2.4492
2025-12-06 17:13 | 72.095 | FALSE | TRUE | 0.011261 | 0.015617 | -1.2855 | -1.7518 | 0 |  | 2025-12-06 15:29 | lower | TRUE | 2 | 72.1063 | FALSE | TRUE | 0.5928 | 2.398 | 72.7434 | 8 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.31855 | Confirmed/Materialized Shift | 73.3805 | -2.0353 | Day | 202512 | 2025-12-06 | 2.0353
2025-12-06 17:21 | 71.8124 | FALSE | TRUE | 0.12172 | 0.16921 | -1.6273 | -2.2159 | -0.2826 |  | 2025-12-06 15:29 | lower | TRUE | 2 | 71.9341 | FALSE | TRUE | 0.612 | 2.3897 | 72.6869 | 9 | -0.2826 | -0.05643 | 0.1477 | -1.5313 | 0.37641 | Confirmed/Materialized Shift | 73.4397 | -2.3234 | Day | 202512 | 2025-12-06 | 2.3234
2025-12-06 17:36 | 72.941 | TRUE | FALSE | -1.0069 | -1.3997 | -0.49874 | -0.67912 | 1.1286 |  |  | none | FALSE | 3 | 71.9341 | TRUE | FALSE | 0.1307 |  | 72.6869 | 0 | 1.1286 | 0 | 0.30365 | 3.7167 | 0.37641 | Persistence ends | 73.4397 | 0.67499 | Night | 202512 | 2025-12-06 | 0.67499
2025-12-06 17:36 | 72.941 | FALSE | FALSE | -1.0069 | -1.3997 | -0.49874 | -0.67912 | 0 |  |  | none | FALSE | 2 | 71.9341 | FALSE | FALSE | 0.1021 |  | 72.6869 | 0 | 0 | 0 | 0.30365 | 0 | 0.37641 | Normal | 73.4397 | 0.67499 | Night | 202512 | 2025-12-06 | 0.67499
2025-12-06 17:51 | 72.941 | FALSE | FALSE | -0.9885 | -1.3738 | -0.4521 | -0.616 | 0 |  |  | none | FALSE | 2 | 71.9525 | FALSE | FALSE | 0.1068 |  | 72.6728 | 0 | 0 | -0.01413 | 0.2963 | 0.047689 | 0.36015 | Normal | 73.3931 | 0.74468 | Night | 202512 | 2025-12-06 | 0.74468
2025-12-06 18:06 | 73.5062 | FALSE | FALSE | -1.6092 | -2.2382 | 0.0010533 | 0.0014329 | 0.5652 | 2025-12-06 21:20 | 2025-12-06 18:06 | upper | TRUE | 2 | 71.897 | FALSE | FALSE | 0.2478 | 2.0026 | 72.7011 | 1 | 0.5652 | 0.02826 | 0.31587 | 1.6999 | 0.40204 | Extreme triggered | 73.5051 | 2.0026 | Night | 202512 | 2025-12-06 | 2.0026
2025-12-06 18:21 | 73.7888 | FALSE | FALSE | -1.9813 | -2.7591 | 0.10942 | 0.14851 | 0.2826 |  | 2025-12-06 18:06 | upper | TRUE | 1 | 71.8075 | FALSE | FALSE | 0.2918 | 2.1182 | 72.7434 | 2 | 0.2826 | 0.04239 | 0.32082 | 0.74874 | 0.46796 | Extreme/elevated | 73.6794 | 2.2338 | Night | 202512 | 2025-12-06 | 2.2338
2025-12-06 18:36 | 74.0714 | FALSE | FALSE | -2.3785 | -3.3176 | 0.16439 | 0.22242 | 0.2826 |  | 2025-12-06 18:06 | upper | TRUE | 1 | 71.6929 | FALSE | TRUE | 0.3531 | 2.1778 | 72.8 | 3 | 0.2826 | 0.05652 | 0.32505 | 0.69553 | 0.55352 | Persistent | 73.907 | 2.297 | Night | 202512 | 2025-12-06 | 2.297
2025-12-06 18:51 | 74.0714 | FALSE | FALSE | -2.4592 | -3.434 | -0.029369 | -0.039634 | 0 |  | 2025-12-06 18:06 | none | FALSE | 1 | 71.6122 | FALSE | FALSE | 0.3873 | 2.1216 | 72.8565 | 4 | 0 | 0.05652 | 0.32505 | -0.17388 | 0.62214 | Persistent | 74.1008 | 1.9528 | Night | 202512 | 2025-12-06 | 1.9528
2025-12-06 19:06 | 74.3522 | FALSE | FALSE | -2.8382 | -3.9688 | 0.012088 | 0.016261 | 0.2808 |  | 2025-12-06 18:06 | upper | TRUE | 1 | 71.514 | FALSE | TRUE | 0.4488 | 2.1007 | 72.927 | 5 | 0.2808 | 0.07056 | 0.32852 | 0.63995 | 0.70653 | Persistent | 74.3401 | 2.0171 | Night | 202512 | 2025-12-06 | 2.0171
2025-12-06 19:21 | 74.3522 | FALSE | FALSE | -2.9049 | -4.0657 | -0.19568 | -0.26249 | 0 |  | 2025-12-06 18:06 | none | FALSE | 1 | 71.4473 | FALSE | FALSE | 0.4879 | 2.0418 | 72.9976 | 6 | 0 | 0.07056 | 0.32852 | -0.21478 | 0.77513 | Persistent | 74.5479 | 1.7476 | Night | 202512 | 2025-12-06 | 1.7476
2025-12-06 19:36 | 74.6348 | FALSE | TRUE | -3.2662 | -4.5765 | -0.16119 | -0.21551 | 0.2826 |  | 2025-12-06 18:06 | none | FALSE | 1 | 71.3686 | FALSE | FALSE | 0.5494 | 2.009 | 73.0823 | 7 | 0.2826 | 0.08469 | 0.33139 | 0.5972 | 0.85685 | Confirmed/Materialized Shift | 74.796 | 1.8119 | Night | 202512 | 2025-12-06 | 1.8119
2025-12-06 19:51 | 74.6348 | FALSE | TRUE | -3.3144 | -4.6471 | -0.37875 | -0.5049 | 0 |  | 2025-12-06 18:06 | none | FALSE | 0 | 71.3204 | FALSE | FALSE | 0.506 | 1.9566 | 73.167 | 8 | 0 | 0.08469 | 0.33139 | -0.25556 | 0.92328 | Confirmed/Materialized Shift | 75.0135 | 1.5898 | Night | 202512 | 2025-12-06 | 1.5898
2025-12-06 20:06 | 74.6348 | FALSE | TRUE | -3.3101 | -4.6408 | -0.57208 | -0.76068 | 0 |  | 2025-12-06 18:06 | none | FALSE | 0 | 71.3247 | FALSE | FALSE | 0.494 | 1.8959 | 73.2658 | 9 | 0 | 0.09882 | 0.32076 | -0.30808 | 0.97054 | Confirmed/Materialized Shift | 75.2069 | 1.4105 | Night | 202512 | 2025-12-06 | 1.4105
2025-12-06 20:21 | 74.9174 | FALSE | TRUE | -3.5906 | -5.034 | -0.51334 | -0.68055 | 0.2826 |  | 2025-12-06 18:06 | none | FALSE | 0 | 71.3268 | FALSE | FALSE | 0.5 | 1.8563 | 73.3788 | 10 | 0.2826 | 0.11295 | 0.3224 | 0.52621 | 1.026 | Confirmed/Materialized Shift | 75.4307 | 1.4997 | Night | 202512 | 2025-12-06 | 1.4997
2025-12-06 20:35 | 74.9174 | FALSE | TRUE | -3.5578 | -4.9858 | -0.70646 | -0.93418 | 0 |  | 2025-12-06 18:06 | none | FALSE | 0 | 71.3596 | FALSE | FALSE | 0.4892 | 1.8091 | 73.4917 | 11 | 0 | 0.11295 | 0.3224 | -0.35034 | 1.0661 | Confirmed/Materialized Shift | 75.6239 | 1.3373 | Night | 202512 | 2025-12-06 | 1.3373
2025-12-06 20:50 | 74.9174 | FALSE | TRUE | -3.4536 | -4.8326 | -0.85635 | -1.1301 | 0 |  | 2025-12-06 18:06 | none | FALSE | 0 | 71.4638 | FALSE | FALSE | 0.4803 | 1.7588 | 73.6188 | 12 | 0 | 0.12708 | 0.31011 | -0.40979 | 1.0775 | Confirmed/Materialized Shift | 75.7737 | 1.2052 | Night | 202512 | 2025-12-06 | 1.2052
2025-12-06 21:05 | 74.9174 | FALSE | TRUE | -3.3176 | -4.6335 | -0.97454 | -1.2841 | 0 |  | 2025-12-06 18:06 | none | FALSE | 0 | 71.5998 | FALSE | FALSE | 0.4728 | 1.7075 | 73.7459 | 13 | 0 | 0.12708 | 0.31011 | -0.40979 | 1.073 | Confirmed/Materialized Shift | 75.8919 | 1.0918 | Night | 202512 | 2025-12-06 | 1.0918
2025-12-06 21:20 | 74.9174 | FALSE | FALSE | -3.1495 | -4.3885 | -1.0606 | -1.396 | 0 |  |  | none | FALSE | 0 | 71.7679 | FALSE | FALSE | 0.0662 |  | 73.873 | 0 | 0 | 0.12708 | 0.31011 | -0.40979 | 1.0525 | Persistence ends | 75.978 | 0.99231 | Night | 202512 | 2025-12-06 | 0.99231
2025-12-06 21:35 | 74.9174 | FALSE | FALSE | -2.8811 | -3.9996 | -1.0745 | -1.4139 | 0 |  |  | none | FALSE | 0 | 72.0363 | FALSE | FALSE | 0.0609 |  | 74.0141 | 0 | 0 | 0.14112 | 0.29674 | -0.47557 | 0.9889 | Normal | 75.9919 | 0.91347 | Night | 202512 | 2025-12-06 | 0.91347
2025-12-06 21:50 | 74.9174 | FALSE | FALSE | -2.5578 | -3.5349 | -1.0334 | -1.3606 | 0 |  |  | none | FALSE | 0 | 72.3596 | FALSE | FALSE | 0.0566 |  | 74.1552 | 0 | 0 | 0.14112 | 0.29674 | -0.47557 | 0.89781 | Normal | 75.9508 | 0.84896 | Night | 202512 | 2025-12-06 | 0.84896
2025-12-06 22:05 | 75.2 | FALSE | FALSE | -2.3512 | -3.2275 | -0.60031 | -0.79196 | 0.2826 |  |  | none | FALSE | 0 | 72.8488 | FALSE | FALSE | 0.0791 |  | 74.3246 | 0 | 0.2826 | 0.16938 | 0.28075 | 0.40328 | 0.73787 | Normal | 75.8003 | 1.1864 | Night | 202512 | 2025-12-06 | 1.1864
2025-12-06 22:20 | 75.2 | FALSE | FALSE | -2.1345 | -2.9213 | -0.60953 | -0.80403 | 0 |  |  | none | FALSE | 0 | 73.0655 | FALSE | FALSE | 0.0741 |  | 74.4375 | 0 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.68601 | Normal | 75.8095 | 1.1115 | Night | 202512 | 2025-12-06 | 1.1115
2025-12-06 22:35 | 75.2 | FALSE | FALSE | -1.8659 | -2.5444 | -0.56686 | -0.74817 | 0 |  |  | none | FALSE | 0 | 73.3341 | FALSE | FALSE | 0.0712 |  | 74.5505 | 0 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.6082 | Normal | 75.7669 | 1.068 | Night | 202512 | 2025-12-06 | 1.068
2025-12-06 22:50 | 75.2 | FALSE | FALSE | -1.5211 | -2.0646 | -0.44798 | -0.59219 | 0 |  |  | none | FALSE | 0 | 73.6789 | FALSE | FALSE | 0.0727 |  | 74.6634 | 0 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.49228 | Normal | 75.648 | 1.09 | Night | 202512 | 2025-12-06 | 1.09
2025-12-06 23:05 | 75.2 | FALSE | FALSE | -1.2992 | -1.758 | -0.39537 | -0.52301 | 0 |  |  | none | FALSE | 0 | 73.9008 | FALSE | FALSE | 0.0711 |  | 74.7481 | 0 | 0 | 0.08469 | 0.13273 | -0.63807 | 0.42363 | Normal | 75.5954 | 1.0667 | Night | 202512 | 2025-12-06 | 1.0667
2025-12-06 23:20 | 75.2 | FALSE | FALSE | -1.1203 | -1.5123 | -0.35768 | -0.47339 | 0 |  |  | none | FALSE | 0 | 74.0797 | FALSE | FALSE | 0.0688 |  | 74.8187 | 0 | 0 | 0.07056 | 0.12539 | -0.56273 | 0.36951 | Normal | 75.5577 | 1.032 | Night | 202512 | 2025-12-06 | 1.032
2025-12-06 23:34 | 75.2 | FALSE | FALSE | -0.99257 | -1.3376 | -0.34277 | -0.45374 | 0 |  |  | none | FALSE | 0 | 74.2074 | FALSE | FALSE | 0.0649 |  | 74.8751 | 0 | 0 | 0.05643 | 0.11579 | -0.48734 | 0.33383 | Normal | 75.5428 | 0.97324 | Night | 202512 | 2025-12-06 | 0.97324
2025-12-06 23:49 | 75.2 | FALSE | FALSE | -0.83293 | -1.12 | -0.29599 | -0.39206 | 0 |  |  | none | FALSE | 0 | 74.3671 | FALSE | FALSE | 0.0634 |  | 74.9315 | 0 | 0 | 0.05643 | 0.11579 | -0.48734 | 0.28223 | Normal | 75.496 | 0.95125 | Night | 202512 | 2025-12-06 | 0.95125
2025-12-07 00:04 | 75.2 | FALSE | FALSE | -0.73161 | -0.98244 | -0.27945 | -0.37023 | 0 |  |  | none | FALSE | 0 | 74.4684 | FALSE | FALSE | 0.0596 |  | 74.9739 | 0 | 0 | 0.04239 | 0.10353 | -0.40945 | 0.25277 | Normal | 75.4795 | 0.89443 | Night | 202512 | 2025-12-07 | 0.89443
2025-12-07 00:19 | 75.2 | FALSE | FALSE | -0.60485 | -0.81085 | -0.23747 | -0.3148 | 0 |  |  | none | FALSE | 0 | 74.5951 | FALSE | FALSE | 0.0582 |  | 75.0163 | 0 | 0 | 0.04239 | 0.10353 | -0.40945 | 0.21058 | Normal | 75.4375 | 0.8723 | Night | 202512 | 2025-12-07 | 0.8723
2025-12-07 00:34 | 75.2 | FALSE | FALSE | -0.54335 | -0.72779 | -0.23249 | -0.3082 | 0 |  |  | none | FALSE | 0 | 74.6567 | FALSE | FALSE | 0.0534 |  | 75.0446 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.19396 | Normal | 75.4325 | 0.80136 | Night | 202512 | 2025-12-07 | 0.80136
2025-12-07 00:49 | 75.2 | FALSE | FALSE | -0.46901 | -0.62759 | -0.21467 | -0.28465 | 0 |  |  | none | FALSE | 0 | 74.731 | FALSE | FALSE | 0.0496 |  | 75.0728 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.17092 | Normal | 75.4147 | 0.74404 | Night | 202512 | 2025-12-07 | 0.74404
2025-12-07 01:04 | 75.2 | FALSE | FALSE | -0.3755 | -0.50184 | -0.17768 | -0.23572 | 0 |  |  | none | FALSE | 0 | 74.8245 | FALSE | FALSE | 0.0477 |  | 75.1011 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.13829 | Normal | 75.3777 | 0.71522 | Night | 202512 | 2025-12-07 | 0.71522
2025-12-07 01:19 | 75.2 | FALSE | FALSE | -0.35052 | -0.46829 | -0.18096 | -0.24006 | 0 |  |  | none | FALSE | 0 | 74.8495 | FALSE | FALSE | 0.0425 |  | 75.1152 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.13287 | Normal | 75.381 | 0.63808 | Night | 202512 | 2025-12-07 | 0.63808
2025-12-07 01:34 | 75.2 | FALSE | FALSE | -0.32175 | -0.42969 | -0.18045 | -0.23938 | 0 |  |  | none | FALSE | 0 | 74.8783 | FALSE | FALSE | 0.0375 |  | 75.1294 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.12555 | Normal | 75.3804 | 0.56273 | Night | 202512 | 2025-12-07 | 0.56273
2025-12-07 01:49 | 75.2 | FALSE | FALSE | -0.28847 | -0.38509 | -0.17543 | -0.23275 | 0 |  |  | none | FALSE | 0 | 74.9115 | FALSE | FALSE | 0.0325 |  | 75.1435 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.11598 | Normal | 75.3754 | 0.48734 | Night | 202512 | 2025-12-07 | 0.48734
2025-12-07 02:04 | 75.2 | FALSE | FALSE | -0.24945 | -0.33282 | -0.16467 | -0.2185 | 0 |  |  | none | FALSE | 0 | 74.9506 | FALSE | FALSE | 0.0273 |  | 75.1576 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.10353 | Normal | 75.3647 | 0.40945 | Night | 202512 | 2025-12-07 | 0.40945
2025-12-07 02:19 | 75.2 | FALSE | FALSE | -0.20222 | -0.26964 | -0.1457 | -0.19338 | 0 |  |  | none | FALSE | 0 | 74.9978 | FALSE | FALSE | 0.0217 |  | 75.1717 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.086982 | Normal | 75.3457 | 0.32489 | Night | 202512 | 2025-12-07 | 0.32489
2025-12-07 02:33 | 74.9174 | TRUE | FALSE | 0.080375 | 0.10717 | -0.4283 | -0.56845 | -0.2826 | 2025-12-07 04:48 | 2025-12-07 02:33 | lower | TRUE | 1 | 74.9978 | FALSE | FALSE | 0.2807 | 2.924 | 75.1717 | 1 | -0.2826 | 0 | 0.091688 | -3.0822 | 0.086982 | Extreme triggered | 75.3457 | -2.924 | Night | 202512 | 2025-12-07 | 2.924
2025-12-07 02:48 | 74.9174 | FALSE | FALSE | 0.080375 | 0.10717 | -0.4283 | -0.56845 | 0 |  | 2025-12-07 02:33 | lower | TRUE | 1 | 74.9978 | FALSE | FALSE | 0.3378 | 2.924 | 75.1717 | 2 | 0 | 0 | 0.091688 | 0 | 0.086982 | Extreme/elevated | 75.3457 | -2.924 | Night | 202512 | 2025-12-07 | 2.924
2025-12-07 03:03 | 74.9174 | FALSE | FALSE | 0.03315 | 0.04423 | -0.44727 | -0.59347 | 0 |  | 2025-12-07 02:33 | lower | TRUE | 1 | 74.9506 | FALSE | TRUE | 0.3547 | 2.7228 | 75.1576 | 3 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.10353 | Persistent | 75.3647 | -2.3202 | Night | 202512 | 2025-12-07 | 2.3202
2025-12-07 03:18 | 74.9174 | FALSE | FALSE | -0.0058732 | -0.0078402 | -0.45803 | -0.60767 | 0 |  | 2025-12-07 02:33 | none | FALSE | 1 | 74.9115 | FALSE | FALSE | 0.3871 | 2.5294 | 75.1435 | 4 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.11598 | Persistent | 75.3754 | -1.9494 | Night | 202512 | 2025-12-07 | 1.9494
2025-12-07 03:33 | 74.9174 | FALSE | FALSE | -0.039147 | -0.05228 | -0.46305 | -0.61428 | 0 |  | 2025-12-07 02:33 | none | FALSE | 1 | 74.8783 | FALSE | FALSE | 0.4268 | 2.3612 | 75.1294 | 5 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.12555 | Persistent | 75.3804 | -1.6882 | Night | 202512 | 2025-12-07 | 1.6882
2025-12-07 03:48 | 74.9174 | FALSE | FALSE | -0.067916 | -0.090736 | -0.46356 | -0.61495 | 0 |  | 2025-12-07 02:33 | none | FALSE | 1 | 74.8495 | FALSE | FALSE | 0.4707 | 2.2158 | 75.1152 | 6 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13287 | Persistent | 75.381 | -1.4888 | Night | 202512 | 2025-12-07 | 1.4888
2025-12-07 04:03 | 74.9174 | FALSE | TRUE | -0.092897 | -0.12415 | -0.46028 | -0.61063 | 0 |  | 2025-12-07 02:33 | none | FALSE | 1 | 74.8245 | FALSE | FALSE | 0.5171 | 2.089 | 75.1011 | 7 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13829 | Confirmed/Materialized Shift | 75.3777 | -1.3283 | Night | 202512 | 2025-12-07 | 1.3283
2025-12-07 04:18 | 74.9174 | FALSE | TRUE | -0.11452 | -0.1531 | -0.45364 | -0.60188 | 0 |  | 2025-12-07 02:33 | none | FALSE | 1 | 74.8029 | FALSE | FALSE | 0.5082 | 1.9771 | 75.087 | 8 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14204 | Confirmed/Materialized Shift | 75.371 | -1.1937 | Night | 202512 | 2025-12-07 | 1.1937
2025-12-07 04:33 | 74.9174 | FALSE | TRUE | -0.13306 | -0.17792 | -0.44392 | -0.58905 | 0 |  | 2025-12-07 02:33 | none | FALSE | 1 | 74.7843 | FALSE | FALSE | 0.5004 | 1.8771 | 75.0728 | 9 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14424 | Confirmed/Materialized Shift | 75.3613 | -1.0775 | Night | 202512 | 2025-12-07 | 1.0775
2025-12-07 04:48 | 74.9174 | FALSE | FALSE | -0.14864 | -0.1988 | -0.43124 | -0.57233 | 0 |  |  | none | FALSE | 1 | 74.7688 | FALSE | FALSE | 0.0936 |  | 75.0587 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14497 | Persistence ends | 75.3486 | -0.97468 | Night | 202512 | 2025-12-07 | 0.97468
2025-12-07 05:03 | 74.9174 | FALSE | FALSE | -0.16132 | -0.21579 | -0.41566 | -0.55176 | 0 |  |  | none | FALSE | 0 | 74.7561 | FALSE | FALSE | 0.0588 |  | 75.0446 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14424 | Normal | 75.3331 | -0.88163 | Night | 202512 | 2025-12-07 | 0.88163
2025-12-07 05:18 | 74.6348 | TRUE | FALSE | 0.049657 | 0.066489 | -0.71336 | -0.94676 | -0.2826 | 2025-12-07 08:17 | 2025-12-07 05:18 | lower | TRUE | 1 | 74.6845 | FALSE | FALSE | 0.239 | 2.2993 | 75.0163 | 1 | -0.2826 | -0.02826 | 0.086982 | -2.924 | 0.16593 | Extreme triggered | 75.3482 | -2.2993 | Night | 202512 | 2025-12-07 | 2.2993
2025-12-07 05:32 | 74.6348 | FALSE | FALSE | -0.0077242 | -0.01035 | -0.71422 | -0.94789 | 0 |  | 2025-12-07 05:18 | none | FALSE | 1 | 74.6271 | FALSE | FALSE | 0.2733 | 2.1282 | 74.9881 | 2 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18049 | Extreme/elevated | 75.349 | -1.9572 | Night | 202512 | 2025-12-07 | 1.9572
2025-12-07 05:47 | 74.6348 | FALSE | FALSE | -0.054158 | -0.072616 | -0.70414 | -0.93463 | 0 |  | 2025-12-07 05:18 | none | FALSE | 1 | 74.5806 | FALSE | FALSE | 0.3143 | 1.9903 | 74.9598 | 3 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18957 | Persistent | 75.3389 | -1.7143 | Night | 202512 | 2025-12-07 | 1.7143
2025-12-07 06:02 | 74.6348 | FALSE | FALSE | -0.091185 | -0.12232 | -0.68465 | -0.90899 | 0 |  | 2025-12-07 05:18 | none | FALSE | 1 | 74.5436 | FALSE | FALSE | 0.3591 | 1.8752 | 74.9315 | 4 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.19396 | Persistent | 75.3194 | -1.5299 | Night | 202512 | 2025-12-07 | 1.5299
2025-12-07 06:18 | 74.6348 | FALSE | FALSE | -0.11945 | -0.1603 | -0.65639 | -0.8718 | 0 |  | 2025-12-07 05:18 | none | FALSE | 1 | 74.5154 | FALSE | FALSE | 0.4066 | 1.777 | 74.9033 | 5 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.19396 | Persistent | 75.2912 | -1.3842 | Night | 202512 | 2025-12-07 | 1.3842
2025-12-07 06:32 | 74.3522 | TRUE | FALSE | 0.074735 | 0.10041 | -0.94262 | -1.2519 | -0.2826 |  | 2025-12-07 05:18 | lower | TRUE | 2 | 74.4269 | TRUE | TRUE | 0.5563 | 1.8715 | 74.8609 | 6 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.21697 | Persistent | 75.2948 | -2.3444 | Night | 202512 | 2025-12-07 | 2.3444
2025-12-07 06:47 | 74.3522 | FALSE | TRUE | 0.0069363 | 0.0093281 | -0.92564 | -1.2296 | 0 |  | 2025-12-07 05:18 | lower | TRUE | 2 | 74.3591 | FALSE | TRUE | 0.5925 | 1.8942 | 74.8185 | 7 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.22968 | Confirmed/Materialized Shift | 75.2778 | -2.0302 | Night | 202512 | 2025-12-07 | 2.0302
2025-12-07 07:02 | 74.3522 | FALSE | TRUE | -0.043617 | -0.058697 | -0.89142 | -1.1847 | 0 |  | 2025-12-07 05:18 | none | FALSE | 2 | 74.3086 | FALSE | FALSE | 0.578 | 1.8841 | 74.7761 | 8 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.23376 | Confirmed/Materialized Shift | 75.2436 | -1.8134 | Day | 202512 | 2025-12-07 | 1.8134
2025-12-07 07:17 | 74.0714 | FALSE | TRUE | 0.12685 | 0.17096 | -1.1697 | -1.5546 | -0.2808 |  | 2025-12-07 05:18 | lower | TRUE | 2 | 74.1982 | FALSE | TRUE | 0.6229 | 1.951 | 74.7197 | 9 | -0.2808 | -0.05643 | 0.11579 | -1.9377 | 0.26071 | Confirmed/Materialized Shift | 75.2411 | -2.4865 | Day | 202512 | 2025-12-07 | 2.4865
2025-12-07 07:32 | 74.3522 | TRUE | TRUE | -0.19811 | -0.26716 | -0.87653 | -1.1652 | 0.2808 |  | 2025-12-07 05:18 | none | FALSE | 3 | 74.1541 | TRUE | FALSE | 0.5699 | 1.8822 | 74.6914 | 10 | 0.2808 | -0.02826 | 0.12596 | 2.4536 | 0.26866 | Confirmed/Materialized Shift | 75.2287 | -1.2626 | Day | 202512 | 2025-12-07 | 1.2626
2025-12-07 07:47 | 74.0714 | FALSE | TRUE | -0.015046 | -0.020317 | -1.1705 | -1.5556 | -0.2808 |  | 2025-12-07 05:18 | none | FALSE | 2 | 74.0564 | FALSE | FALSE | 0.5871 | 1.8883 | 74.6491 | 11 | -0.2808 | -0.0423 | 0.13774 | -1.7315 | 0.29638 | Confirmed/Materialized Shift | 75.2419 | -1.9492 | Day | 202512 | 2025-12-07 | 1.9492
2025-12-07 08:02 | 74.0714 | FALSE | TRUE | -0.096203 | -0.13005 | -1.167 | -1.5511 | 0 |  | 2025-12-07 05:18 | none | FALSE | 2 | 73.9752 | FALSE | FALSE | 0.5702 | 1.8722 | 74.6068 | 12 | 0 | -0.0423 | 0.13774 | 0.3071 | 0.31581 | Confirmed/Materialized Shift | 75.2384 | -1.6954 | Day | 202512 | 2025-12-07 | 1.6954
2025-12-07 08:17 | 74.3522 | FALSE | FALSE | -0.39728 | -0.53719 | -0.84998 | -1.1303 | 0.2808 |  |  | none | FALSE | 2 | 73.9549 | FALSE | FALSE | 0.1055 |  | 74.5786 | 0 | 0.2808 | -0.02826 | 0.15545 | 1.9881 | 0.31181 | Persistence ends | 75.2022 | -0.72591 | Day | 202512 | 2025-12-07 | 0.72591
2025-12-07 08:30 | 74.3522 | FALSE | FALSE | -0.41196 | -0.55715 | -0.80814 | -1.0752 | 0 |  |  | none | FALSE | 2 | 73.9402 | FALSE | FALSE | 0.1004 |  | 74.5503 | 0 | 0 | -0.02826 | 0.15545 | 0.18179 | 0.30503 | Normal | 75.1603 | -0.64942 | Day | 202512 | 2025-12-07 | 0.64942
2025-12-07 08:45 | 74.9174 | TRUE | FALSE | -0.97716 | -1.3216 | -0.24294 | -0.32323 | 0.5652 |  |  | none | FALSE | 3 | 73.9402 | TRUE | FALSE | 0.166 |  | 74.5503 | 0 | 0.5652 | 0 | 0.2045 | 2.7638 | 0.30503 | Normal | 75.1603 | 1.2035 | Day | 202512 | 2025-12-07 | 1.2035
2025-12-07 09:01 | 74.9174 | FALSE | FALSE | -0.97716 | -1.3216 | -0.24294 | -0.32323 | 0 |  |  | none | FALSE | 2 | 73.9402 | FALSE | FALSE | 0.1374 |  | 74.5503 | 0 | 0 | 0 | 0.2045 | 0 | 0.30503 | Normal | 75.1603 | 1.2035 | Day | 202512 | 2025-12-07 | 1.2035
2025-12-07 09:16 | 75.2 | FALSE | FALSE | -1.2927 | -1.7491 | -0.021548 | -0.028646 | 0.2826 |  |  | none | FALSE | 2 | 73.9073 | FALSE | FALSE | 0.1861 |  | 74.5644 | 0 | 0.2826 | 0.01413 | 0.21404 | 1.2543 | 0.32856 | Normal | 75.2215 | 1.9344 | Day | 202512 | 2025-12-07 | 1.9344
2025-12-07 09:30 | 75.4826 | FALSE | FALSE | -1.6513 | -2.2366 | 0.12853 | 0.17057 | 0.2826 | 2025-12-07 10:03 | 2025-12-07 09:30 | upper | TRUE | 2 | 73.8313 | FALSE | FALSE | 0.2701 | 2.3376 | 74.5927 | 1 | 0.2826 | 0.02826 | 0.22223 | 1.1445 | 0.38069 | Extreme triggered | 75.3541 | 2.3376 | Day | 202512 | 2025-12-07 | 2.3376
2025-12-07 09:30 | 75.4826 | FALSE | FALSE | -1.7107 | -2.3189 | 0.012616 | 0.016716 | 0 |  | 2025-12-07 09:30 | upper | TRUE | 2 | 73.7719 | FALSE | FALSE | 0.3067 | 2.1837 | 74.6209 | 2 | 0 | 0.02826 | 0.22223 | -0.12717 | 0.42452 | Extreme/elevated | 75.47 | 2.0297 | Day | 202512 | 2025-12-07 | 2.0297
2025-12-07 09:33 | 75.4826 | FALSE | FALSE | -1.7582 | -2.3849 | -0.091434 | -0.12099 | 0 |  | 2025-12-07 09:30 | none | FALSE | 1 | 73.7244 | FALSE | FALSE | 0.3202 | 2.0565 | 74.6492 | 3 | 0 | 0.02826 | 0.22223 | -0.12717 | 0.46242 | Persistent | 75.574 | 1.8023 | Day | 202512 | 2025-12-07 | 1.8023
2025-12-07 09:48 | 75.4826 | FALSE | FALSE | -1.788 | -2.4262 | -0.20595 | -0.2721 | 0 |  | 2025-12-07 09:30 | none | FALSE | 1 | 73.6946 | FALSE | FALSE | 0.3629 | 1.9391 | 74.6916 | 4 | 0 | 0.04239 | 0.21007 | -0.20179 | 0.49848 | Persistent | 75.6886 | 1.5868 | Day | 202512 | 2025-12-07 | 1.5868
2025-12-07 10:03 | 74.3522 | TRUE | FALSE | -0.68304 | -0.92717 | -1.3336 | -1.762 | -1.1304 |  |  | none | FALSE | 2 | 73.6692 | TRUE | FALSE | 0.1002 |  | 74.6775 | 0 | -1.1304 | -0.01413 | 0.33625 | -3.3197 | 0.50415 | Persistence ends | 75.6858 | -0.64517 | Day | 202512 | 2025-12-07 | 0.64517
2025-12-07 10:18 | 73.7888 | FALSE | FALSE | -0.23761 | -0.32306 | -1.9303 | -2.5493 | -0.5634 |  |  | none | FALSE | 2 | 73.5512 | FALSE | FALSE | 0.1612 |  | 74.6352 | 0 | -0.5634 | -0.0423 | 0.35791 | -1.456 | 0.54199 | Normal | 75.7191 | -1.5616 | Day | 202512 | 2025-12-07 | 1.5616
2025-12-07 10:30 | 73.7888 | FALSE | FALSE | -0.3441 | -0.46852 | -1.9522 | -2.5775 | 0 |  |  | none | FALSE | 2 | 73.4447 | FALSE | FALSE | 0.1505 |  | 74.5929 | 0 | 0 | -0.0423 | 0.35791 | 0.11819 | 0.57408 | Normal | 75.741 | -1.4006 | Day | 202512 | 2025-12-07 | 1.4006
2025-12-07 10:45 | 73.5062 | FALSE | FALSE | -0.216 | -0.29472 | -2.2765 | -3.0039 | -0.2826 |  |  | none | FALSE | 1 | 73.2902 | FALSE | FALSE | 0.1388 |  | 74.5364 | 0 | -0.2826 | -0.05643 | 0.36171 | -0.62528 | 0.62311 | Normal | 75.7827 | -1.6534 | Day | 202512 | 2025-12-07 | 1.6534
2025-12-07 11:00 | 73.5062 | FALSE | FALSE | -0.33942 | -0.4639 | -2.3153 | -3.0536 | 0 |  |  | none | FALSE | 1 | 73.1668 | FALSE | FALSE | 0.1278 |  | 74.4941 | 0 | 0 | -0.0423 | 0.35791 | 0.11819 | 0.66367 | Normal | 75.8215 | -1.4886 | Day | 202512 | 2025-12-07 | 1.4886
2025-12-07 11:15 | 73.5062 | FALSE | FALSE | -0.45278 | -0.6198 | -2.344 | -3.0904 | 0 |  |  | none | FALSE | 1 | 73.0534 | FALSE | FALSE | 0.1187 |  | 74.4518 | 0 | 0 | -0.0423 | 0.35791 | 0.11819 | 0.69921 | Normal | 75.8502 | -1.3524 | Day | 202512 | 2025-12-07 | 1.3524
2025-12-07 11:30 | 73.5062 | FALSE | FALSE | -0.55756 | -0.76431 | -2.3642 | -3.1161 | 0 |  |  | none | FALSE | 1 | 72.9486 | FALSE | FALSE | 0.111 |  | 74.4095 | 0 | 0 | -0.0423 | 0.35791 | 0.11819 | 0.73044 | Normal | 75.8704 | -1.2367 | Day | 202512 | 2025-12-07 | 1.2367
2025-12-07 11:45 | 73.5062 | FALSE | FALSE | -0.63442 | -0.87059 | -2.3846 | -3.1421 | 0 |  |  | none | FALSE | 1 | 72.8718 | FALSE | FALSE | 0.1059 |  | 74.3813 | 0 | 0 | -0.02826 | 0.35354 | 0.079934 | 0.75474 | Normal | 75.8908 | -1.1594 | Day | 202512 | 2025-12-07 | 1.1594
2025-12-07 12:00 | 73.5062 | FALSE | FALSE | -0.72673 | -0.99854 | -2.3923 | -3.1519 | 0 |  |  | none | FALSE | 1 | 72.7795 | FALSE | FALSE | 0.0998 |  | 74.339 | 0 | 0 | -0.0423 | 0.34612 | 0.12221 | 0.77975 | Normal | 75.8985 | -1.068 | Day | 202512 | 2025-12-07 | 1.068
2025-12-07 12:15 | 73.5062 | FALSE | FALSE | -0.79537 | -1.0939 | -2.4044 | -3.1674 | 0 |  |  | none | FALSE | 1 | 72.7108 | FALSE | FALSE | 0.0956 |  | 74.3107 | 0 | 0 | -0.02826 | 0.3416 | 0.082728 | 0.79994 | Normal | 75.9106 | -1.0057 | Day | 202512 | 2025-12-07 | 1.0057
2025-12-07 12:29 | 73.5062 | FALSE | FALSE | -0.86096 | -1.1852 | -2.4135 | -3.179 | 0 |  |  | none | FALSE | 0 | 72.6452 | FALSE | FALSE | 0.0632 |  | 74.2824 | 0 | 0 | -0.02826 | 0.3416 | 0.082728 | 0.8186 | Normal | 75.9197 | -0.94826 | Day | 202512 | 2025-12-07 | 0.94826
2025-12-07 12:44 | 73.7888 | FALSE | FALSE | -1.186 | -1.6335 | -2.117 | -2.7889 | 0.2826 |  |  | none | FALSE | 0 | 72.6028 | FALSE | FALSE | 0.0376 |  | 74.2543 | 0 | 0.2826 | -0.02817 | 0.34169 | 0.90952 | 0.82574 | Normal | 75.9058 | -0.56371 | Day | 202512 | 2025-12-07 | 0.56371
2025-12-07 12:59 | 73.5062 | FALSE | FALSE | -0.97816 | -1.3487 | -2.3897 | -3.1487 | -0.2826 |  |  | none | FALSE | 0 | 72.528 | FALSE | FALSE | 0.0559 |  | 74.212 | 0 | -0.2826 | -0.0423 | 0.34627 | -0.69396 | 0.84197 | Normal | 75.8959 | -0.83825 | Day | 202512 | 2025-12-07 | 0.83825
2025-12-07 13:14 | 73.5062 | FALSE | FALSE | -1.0425 | -1.4387 | -2.313 | -3.0506 | 0 |  |  | none | FALSE | 0 | 72.4637 | FALSE | FALSE | 0.0505 |  | 74.1414 | 0 | 0 | -0.07056 | 0.31581 | 0.22343 | 0.83887 | Normal | 75.8192 | -0.75723 | Day | 202512 | 2025-12-07 | 0.75723
2025-12-07 13:29 | 73.5062 | FALSE | FALSE | -1.0943 | -1.5112 | -2.2236 | -2.9362 | 0 |  |  | none | FALSE | 0 | 72.4119 | FALSE | FALSE | 0.0454 |  | 74.0709 | 0 | 0 | -0.07056 | 0.31581 | 0.22343 | 0.82946 | Normal | 75.7298 | -0.68076 | Day | 202512 | 2025-12-07 | 0.68076
2025-12-07 13:44 | 73.7888 | FALSE | FALSE | -1.3631 | -1.8821 | -1.7861 | -2.3634 | 0.2826 |  |  | none | FALSE | 0 | 72.4257 | FALSE | FALSE | 0.0179 |  | 74.0003 | 0 | 0.2826 | -0.07056 | 0.31581 | 1.1183 | 0.7873 | Normal | 75.5749 | -0.26864 | Day | 202512 | 2025-12-07 | 0.26864
2025-12-07 13:59 | 73.5062 | FALSE | FALSE | -1.0285 | -1.419 | -1.819 | -2.4149 | -0.2826 |  |  | none | FALSE | 0 | 72.4777 | FALSE | FALSE | 0.037 |  | 73.9015 | 0 | -0.2826 | -0.09882 | 0.30773 | -0.59722 | 0.71188 | Normal | 75.3252 | -0.55526 | Day | 202512 | 2025-12-07 | 0.55526
2025-12-07 14:14 | 73.5062 | FALSE | FALSE | -0.92525 | -1.2748 | -1.5182 | -2.0236 | 0 |  |  | none | FALSE | 0 | 72.581 | FALSE | FALSE | 0.0324 |  | 73.8027 | 0 | 0 | -0.09882 | 0.30773 | 0.32113 | 0.61085 | Normal | 75.0244 | -0.48532 | Day | 202512 | 2025-12-07 | 0.48532
2025-12-07 14:29 | 73.7888 | FALSE | FALSE | -1.0026 | -1.3775 | -0.86098 | -1.1534 | 0.2826 |  |  | none | FALSE | 0 | 72.7862 | FALSE | FALSE | 0.0101 |  | 73.718 | 0 | 0.2826 | -0.08469 | 0.31879 | 1.1521 | 0.4659 | Normal | 74.6498 | 0.15203 | Day | 202512 | 2025-12-07 | 0.15203
2025-12-07 14:44 | 73.2236 | FALSE | FALSE | -0.077316 | -0.1057 | -0.84016 | -1.1344 | -0.5652 |  |  | none | FALSE | 0 | 73.1463 | FALSE | FALSE | 0.1109 |  | 73.605 | 0 | -0.5652 | -0.11295 | 0.3355 | -1.348 | 0.22937 | Normal | 74.0638 | -1.6629 | Day | 202512 | 2025-12-07 | 1.6629
2025-12-07 14:59 | 73.2236 | FALSE | FALSE | -0.0068632 | -0.0093738 | -0.65684 | -0.88906 | 0 |  |  | none | FALSE | 0 | 73.2167 | FALSE | FALSE | 0.1306 |  | 73.5486 | 0 | 0 | -0.05643 | 0.23535 | 0.23978 | 0.16593 | Normal | 73.8804 | -1.9586 | Day | 202512 | 2025-12-07 | 1.9586
2025-12-07 15:14 | 73.2236 | FALSE | FALSE | -0.045106 | -0.061638 | -0.63857 | -0.86454 | 0 |  |  | none | FALSE | 0 | 73.1785 | FALSE | FALSE | 0.1157 |  | 73.5203 | 0 | 0 | -0.02826 | 0.20296 | 0.13924 | 0.17092 | Normal | 73.8622 | -1.7361 | Day | 202512 | 2025-12-07 | 1.7361
2025-12-07 15:28 | 72.941 | FALSE | FALSE | 0.13102 | 0.17931 | -0.94286 | -1.2761 | -0.2826 | 2025-12-07 17:50 | 2025-12-07 15:28 | lower | TRUE | 0 | 73.072 | FALSE | FALSE | 0.2335 | 2.6456 | 73.4779 | 1 | -0.2826 | -0.04239 | 0.21058 | -1.1407 | 0.20296 | Extreme triggered | 73.8839 | -2.6456 | Day | 202512 | 2025-12-07 | 2.6456
2025-12-07 15:43 | 72.941 | FALSE | FALSE | 0.037581 | 0.051496 | -0.97978 | -1.3254 | 0 |  | 2025-12-07 15:28 | lower | TRUE | 0 | 72.9786 | FALSE | FALSE | 0.2583 | 2.4026 | 73.4497 | 2 | 0 | -0.02826 | 0.20296 | 0.13924 | 0.23555 | Extreme/elevated | 73.9208 | -2.1595 | Day | 202512 | 2025-12-07 | 2.1595
2025-12-07 15:58 | 72.6584 | FALSE | FALSE | 0.16109 | 0.22122 | -1.3367 | -1.8065 | -0.2826 |  | 2025-12-07 15:28 | lower | TRUE | 0 | 72.8195 | FALSE | TRUE | 0.3413 | 2.4511 | 73.4073 | 3 | -0.2826 | -0.04239 | 0.21058 | -1.1407 | 0.2939 | Persistent | 73.9951 | -2.5481 | Day | 202512 | 2025-12-07 | 2.5481
2025-12-07 16:13 | 72.6584 | FALSE | FALSE | 0.032737 | 0.045036 | -1.3803 | -1.8642 | 0 |  | 2025-12-07 15:28 | lower | TRUE | 0 | 72.6911 | FALSE | TRUE | 0.3684 | 2.3626 | 73.3649 | 4 | 0 | -0.04239 | 0.21058 | 0.2013 | 0.33688 | Persistent | 74.0387 | -2.0972 | Day | 202512 | 2025-12-07 | 2.0972
2025-12-07 16:28 | 72.6584 | FALSE | FALSE | -0.075667 | -0.10425 | -1.4039 | -1.8955 | 0 |  | 2025-12-07 15:28 | none | FALSE | 0 | 72.5827 | FALSE | FALSE | 0.4054 | 2.2492 | 73.3225 | 5 | 0 | -0.04239 | 0.21058 | 0.2013 | 0.36989 | Persistent | 74.0623 | -1.7954 | Day | 202512 | 2025-12-07 | 1.7954
2025-12-07 16:43 | 72.3758 | FALSE | FALSE | 0.044375 | 0.061275 | -1.736 | -2.3424 | -0.2826 |  | 2025-12-07 15:28 | lower | TRUE | 0 | 72.4202 | FALSE | TRUE | 0.4832 | 2.2251 | 73.266 | 6 | -0.2826 | -0.05652 | 0.21697 | -1.042 | 0.42291 | Persistent | 74.1118 | -2.1049 | Day | 202512 | 2025-12-07 | 2.1049
2025-12-07 16:58 | 72.3758 | FALSE | TRUE | -0.091875 | -0.1271 | -1.7592 | -2.373 | 0 |  | 2025-12-07 15:28 | none | FALSE | 0 | 72.2839 | FALSE | FALSE | 0.5201 | 2.1646 | 73.2095 | 7 | 0 | -0.05652 | 0.21697 | 0.26049 | 0.46277 | Confirmed/Materialized Shift | 74.135 | -1.8015 | Day | 202512 | 2025-12-07 | 1.8015
2025-12-07 17:13 | 72.095 | FALSE | TRUE | 0.0053454 | 0.0074138 | -2.0825 | -2.8074 | -0.2808 |  | 2025-12-07 15:28 | lower | TRUE | 0 | 72.1003 | FALSE | TRUE | 0.534 | 2.1453 | 73.1389 | 8 | -0.2808 | -0.07056 | 0.22215 | -0.9464 | 0.51928 | Confirmed/Materialized Shift | 74.1775 | -2.0103 | Day | 202512 | 2025-12-07 | 2.0103
2025-12-07 17:28 | 72.095 | FALSE | TRUE | -0.14856 | -0.20648 | -2.0953 | -2.8242 | 0 |  | 2025-12-07 15:28 | none | FALSE | 0 | 71.9464 | FALSE | FALSE | 0.5157 | 2.0997 | 73.0683 | 9 | 0 | -0.07056 | 0.22215 | 0.31763 | 0.56095 | Confirmed/Materialized Shift | 74.1903 | -1.7352 | Day | 202512 | 2025-12-07 | 1.7352
2025-12-07 17:35 | 71.8124 | FALSE | TRUE | -0.043024 | -0.059947 | -2.3573 | -3.1782 | -0.2826 |  | 2025-12-07 15:28 | none | FALSE | 0 | 71.7694 | FALSE | FALSE | 0.5286 | 2.0826 | 72.9695 | 10 | -0.2826 | -0.09882 | 0.2105 | -0.87306 | 0.60008 | Confirmed/Materialized Shift | 74.1697 | -1.9283 | Night | 202512 | 2025-12-07 | 1.9283
2025-12-07 17:50 | 72.3758 | TRUE | FALSE | -0.663 | -0.92452 | -1.7374 | -2.3443 | 0.5634 |  |  | none | FALSE | 1 | 71.7128 | FALSE | FALSE | 0.0883 |  | 72.913 | 0 | 0.5634 | -0.05652 | 0.25245 | 2.4556 | 0.6001 | Persistence ends | 74.1132 | -0.8952 | Night | 202512 | 2025-12-07 | 0.8952
2025-12-07 17:50 | 72.3758 | FALSE | FALSE | -0.70831 | -0.98833 | -1.6697 | -2.255 | 0 |  |  | none | FALSE | 1 | 71.6675 | FALSE | FALSE | 0.0825 |  | 72.8565 | 0 | 0 | -0.05652 | 0.25245 | 0.22389 | 0.5945 | Normal | 74.0455 | -0.80856 | Night | 202512 | 2025-12-07 | 0.80856
2025-12-07 18:05 | 73.2236 | TRUE | FALSE | -1.5442 | -2.1543 | -0.78168 | -1.0563 | 0.8478 |  |  | none | FALSE | 2 | 71.6794 | TRUE | FALSE | 0.1009 |  | 72.8424 | 0 | 0.8478 | -0.01413 | 0.32359 | 2.6636 | 0.58146 | Normal | 74.0053 | 0.65566 | Night | 202512 | 2025-12-07 | 0.65566
2025-12-07 18:20 | 73.7888 | FALSE | FALSE | -2.1094 | -2.9428 | -0.21648 | -0.29252 | 0.5652 |  |  | none | FALSE | 2 | 71.6794 | FALSE | FALSE | 0.1657 |  | 72.8424 | 0 | 0.5652 | 0 | 0.34283 | 1.6486 | 0.58146 | Normal | 74.0053 | 1.6277 | Night | 202512 | 2025-12-07 | 1.6277
2025-12-07 18:35 | 73.7888 | FALSE | FALSE | -2.1354 | -2.9801 | -0.27075 | -0.36558 | 0 |  |  | none | FALSE | 2 | 71.6534 | FALSE | FALSE | 0.1605 |  | 72.8565 | 0 | 0 | 0.01413 | 0.33633 | -0.042012 | 0.60153 | Normal | 74.0595 | 1.5499 | Night | 202512 | 2025-12-07 | 1.5499
2025-12-07 18:50 | 74.0714 | FALSE | FALSE | -2.4773 | -3.4602 | -0.10403 | -0.14025 | 0.2826 |  |  | none | FALSE | 2 | 71.5941 | FALSE | FALSE | 0.1797 |  | 72.8847 | 0 | 0.2826 | 0.02826 | 0.3416 | 0.74455 | 0.64534 | Normal | 74.1754 | 1.8388 | Night | 202512 | 2025-12-07 | 1.8388
2025-12-07 19:05 | 74.0714 | FALSE | FALSE | -2.5102 | -3.5078 | -0.16517 | -0.22249 | 0 |  |  | none | FALSE | 2 | 71.5612 | FALSE | FALSE | 0.174 |  | 72.8989 | 0 | 0 | 0.01413 | 0.33633 | -0.042012 | 0.66884 | Normal | 74.2366 | 1.7531 | Night | 202512 | 2025-12-07 | 1.7531
2025-12-07 19:20 | 74.0714 | FALSE | FALSE | -2.5616 | -3.5821 | -0.30133 | -0.40516 | 0 |  |  | none | FALSE | 2 | 71.5098 | FALSE | FALSE | 0.1624 |  | 72.9413 | 0 | 0 | 0.04239 | 0.30761 | -0.1378 | 0.71573 | Normal | 74.3727 | 1.579 | Night | 202512 | 2025-12-07 | 1.579
2025-12-07 19:35 | 74.3522 | FALSE | FALSE | -2.9159 | -4.0818 | -0.2069 | -0.2775 | 0.2808 |  |  | none | FALSE | 2 | 71.4363 | FALSE | FALSE | 0.1728 |  | 72.9977 | 0 | 0.2808 | 0.05643 | 0.31195 | 0.71925 | 0.7807 | Normal | 74.5591 | 1.735 | Night | 202512 | 2025-12-07 | 1.735
2025-12-07 19:49 | 74.3522 | FALSE | FALSE | -2.9714 | -4.1628 | -0.37527 | -0.50219 | 0 |  |  | none | FALSE | 2 | 71.3808 | FALSE | FALSE | 0.1606 |  | 73.0541 | 0 | 0 | 0.05643 | 0.31195 | -0.18089 | 0.83667 | Normal | 74.7275 | 1.5515 | Night | 202512 | 2025-12-07 | 1.5515
2025-12-07 20:04 | 74.6348 | FALSE | FALSE | -3.3107 | -4.6418 | -0.31873 | -0.42524 | 0.2826 |  |  | none | FALSE | 1 | 71.3241 | FALSE | FALSE | 0.1385 |  | 73.1388 | 0 | 0.2826 | 0.08469 | 0.30515 | 0.64857 | 0.90736 | Normal | 74.9535 | 1.6487 | Night | 202512 | 2025-12-07 | 1.6487
2025-12-07 20:19 | 74.6348 | FALSE | FALSE | -3.3415 | -4.687 | -0.51897 | -0.69054 | 0 |  |  | none | FALSE | 1 | 71.2933 | FALSE | FALSE | 0.1261 |  | 73.2235 | 0 | 0 | 0.08469 | 0.30515 | -0.27754 | 0.96513 | Normal | 75.1538 | 1.4623 | Night | 202512 | 2025-12-07 | 1.4623
2025-12-07 20:34 | 74.6348 | FALSE | FALSE | -3.3217 | -4.6579 | -0.69672 | -0.92488 | 0 |  |  | none | FALSE | 0 | 71.3131 | FALSE | FALSE | 0.0871 |  | 73.3223 | 0 | 0 | 0.09882 | 0.29357 | -0.33662 | 1.0046 | Normal | 75.3315 | 1.3065 | Night | 202512 | 2025-12-07 | 1.3065
2025-12-07 20:49 | 74.9174 | FALSE | FALSE | -3.5859 | -5.0271 | -0.62168 | -0.82299 | 0.2826 |  |  | none | FALSE | 0 | 71.3315 | FALSE | FALSE | 0.0939 |  | 73.4353 | 0 | 0.2826 | 0.11295 | 0.29536 | 0.57439 | 1.0519 | Normal | 75.5391 | 1.409 | Night | 202512 | 2025-12-07 | 1.409
2025-12-07 21:04 | 74.9174 | FALSE | FALSE | -3.5389 | -4.9579 | -0.80054 | -1.0573 | 0 |  |  | none | FALSE | 0 | 71.3785 | FALSE | FALSE | 0.0841 |  | 73.5482 | 0 | 0 | 0.11295 | 0.29536 | -0.38242 | 1.0849 | Normal | 75.7179 | 1.2621 | Night | 202512 | 2025-12-07 | 1.2621
2025-12-07 21:19 | 74.9174 | FALSE | FALSE | -3.4204 | -4.7839 | -0.9362 | -1.2342 | 0 |  |  | none | FALSE | 0 | 71.497 | FALSE | FALSE | 0.076 |  | 73.6753 | 0 | 0 | 0.12708 | 0.28189 | -0.45081 | 1.0891 | Normal | 75.8536 | 1.1404 | Night | 202512 | 2025-12-07 | 1.1404
2025-12-07 21:34 | 74.9174 | FALSE | FALSE | -3.2705 | -4.5648 | -1.0405 | -1.3698 | 0 |  |  | none | FALSE | 0 | 71.6469 | FALSE | FALSE | 0.069 |  | 73.8024 | 0 | 0 | 0.12708 | 0.28189 | -0.45081 | 1.0778 | Normal | 75.9579 | 1.0346 | Night | 202512 | 2025-12-07 | 1.0346
2025-12-07 21:49 | 74.9174 | FALSE | FALSE | -3.0258 | -4.2088 | -1.078 | -1.4185 | 0 |  |  | none | FALSE | 0 | 71.8916 | FALSE | FALSE | 0.0633 |  | 73.9435 | 0 | 0 | 0.14112 | 0.26711 | -0.52832 | 1.026 | Normal | 75.9954 | 0.94925 | Night | 202512 | 2025-12-07 | 0.94925
2025-12-07 22:04 | 74.9174 | FALSE | FALSE | -2.7319 | -3.7846 | -1.0664 | -1.4035 | 0 |  |  | none | FALSE | 0 | 72.1855 | FALSE | FALSE | 0.0585 |  | 74.0846 | 0 | 0 | 0.14112 | 0.26711 | -0.52832 | 0.94958 | Normal | 75.9838 | 0.87699 | Night | 202512 | 2025-12-07 | 0.87699
2025-12-07 22:19 | 74.9174 | FALSE | FALSE | -2.2789 | -3.1373 | -0.92385 | -1.2181 | 0 |  |  | none | FALSE | 0 | 72.6385 | FALSE | FALSE | 0.0564 |  | 74.2399 | 0 | 0 | 0.15525 | 0.25048 | -0.61982 | 0.80069 | Normal | 75.8413 | 0.84617 | Night | 202512 | 2025-12-07 | 0.84617
2025-12-07 22:34 | 75.2 | FALSE | FALSE | -2.2128 | -3.0318 | -0.57499 | -0.75882 | 0.2826 |  |  | none | FALSE | 0 | 72.9872 | FALSE | FALSE | 0.0783 |  | 74.3811 | 0 | 0.2826 | 0.14121 | 0.2337 | 0.605 | 0.69695 | Normal | 75.775 | 1.175 | Night | 202512 | 2025-12-07 | 1.175
2025-12-07 22:48 | 74.9174 | FALSE | FALSE | -1.4528 | -1.9775 | -0.6343 | -0.83956 | -0.2826 |  |  | none | FALSE | 0 | 73.4646 | FALSE | FALSE | 0.0523 |  | 74.5082 | 0 | -0.2826 | 0.12708 | 0.25062 | -1.6347 | 0.52177 | Normal | 75.5517 | 0.78432 | Night | 202512 | 2025-12-07 | 0.78432
2025-12-07 23:03 | 75.2 | FALSE | FALSE | -1.4881 | -2.0188 | -0.30209 | -0.40011 | 0.2826 |  |  | none | FALSE | 0 | 73.7119 | FALSE | FALSE | 0.0883 |  | 74.607 | 0 | 0.2826 | 0.09882 | 0.18948 | 0.96991 | 0.44755 | Normal | 75.5021 | 1.325 | Night | 202512 | 2025-12-07 | 1.325
2025-12-07 23:18 | 75.2 | FALSE | FALSE | -1.367 | -1.8515 | -0.32215 | -0.42656 | 0 |  |  | none | FALSE | 0 | 73.833 | FALSE | FALSE | 0.0825 |  | 74.6775 | 0 | 0 | 0.07056 | 0.15534 | -0.45424 | 0.4223 | Normal | 75.5221 | 1.2372 | Night | 202512 | 2025-12-07 | 1.2372
2025-12-07 23:33 | 75.2 | FALSE | FALSE | -1.2158 | -1.6433 | -0.31202 | -0.41321 | 0 |  |  | none | FALSE | 0 | 73.9842 | FALSE | FALSE | 0.0789 |  | 74.7481 | 0 | 0 | 0.07056 | 0.15534 | -0.45424 | 0.38196 | Normal | 75.512 | 1.1831 | Night | 202512 | 2025-12-07 | 1.1831
2025-12-07 23:48 | 75.2 | FALSE | FALSE | -1.1143 | -1.5041 | -0.32338 | -0.42819 | 0 |  |  | none | FALSE | 0 | 74.0857 | FALSE | FALSE | 0.0734 |  | 74.8045 | 0 | 0 | 0.05643 | 0.1477 | -0.38207 | 0.35942 | Normal | 75.5234 | 1.1003 | Night | 202512 | 2025-12-07 | 1.1003
2025-12-08 00:03 | 75.2 | FALSE | FALSE | -0.98949 | -1.3334 | -0.31143 | -0.41242 | 0 |  |  | none | FALSE | 0 | 74.2105 | FALSE | FALSE | 0.0695 |  | 74.861 | 0 | 0 | 0.05643 | 0.1477 | -0.38207 | 0.32523 | Normal | 75.5114 | 1.0424 | Night | 202512 | 2025-12-08 | 1.0424
2025-12-08 00:18 | 75.2 | FALSE | FALSE | -0.83273 | -1.1197 | -0.26753 | -0.35449 | 0 |  |  | none | FALSE | 0 | 74.3673 | FALSE | FALSE | 0.0685 |  | 74.9174 | 0 | 0 | 0.05643 | 0.1477 | -0.38207 | 0.27506 | Normal | 75.4675 | 1.0274 | Night | 202512 | 2025-12-08 | 1.0274
2025-12-08 00:33 | 75.2 | FALSE | FALSE | -0.73481 | -0.98679 | -0.25439 | -0.33715 | 0 |  |  | none | FALSE | 0 | 74.4652 | FALSE | FALSE | 0.0648 |  | 74.9598 | 0 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.2473 | Normal | 75.4544 | 0.97132 | Night | 202512 | 2025-12-08 | 0.97132
2025-12-08 00:48 | 75.2 | FALSE | FALSE | -0.61194 | -0.82043 | -0.2163 | -0.28681 | 0 |  |  | none | FALSE | 0 | 74.5881 | FALSE | FALSE | 0.0637 |  | 75.0022 | 0 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.20706 | Normal | 75.4163 | 0.95538 | Night | 202512 | 2025-12-08 | 0.95538
2025-12-08 01:03 | 75.2 | FALSE | FALSE | -0.55421 | -0.74245 | -0.21509 | -0.28521 | 0 |  |  | none | FALSE | 0 | 74.6458 | FALSE | FALSE | 0.0588 |  | 75.0304 | 0 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.19233 | Normal | 75.4151 | 0.88163 | Night | 202512 | 2025-12-08 | 0.88163
2025-12-08 01:18 | 75.2 | FALSE | FALSE | -0.48436 | -0.64828 | -0.20176 | -0.26758 | 0 |  |  | none | FALSE | 0 | 74.7156 | FALSE | FALSE | 0.0549 |  | 75.0587 | 0 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.17153 | Normal | 75.4018 | 0.82375 | Night | 202512 | 2025-12-08 | 0.82375
2025-12-08 01:33 | 75.2 | FALSE | FALSE | -0.39712 | -0.53089 | -0.17104 | -0.22694 | 0 |  |  | none | FALSE | 0 | 74.8029 | FALSE | FALSE | 0.0531 |  | 75.087 | 0 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.14204 | Normal | 75.371 | 0.79582 | Night | 202512 | 2025-12-08 | 0.79582
2025-12-08 01:47 | 75.2 | FALSE | FALSE | -0.3755 | -0.50184 | -0.17768 | -0.23572 | 0 |  |  | none | FALSE | 0 | 74.8245 | FALSE | FALSE | 0.0477 |  | 75.1011 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.13829 | Normal | 75.3777 | 0.71522 | Night | 202512 | 2025-12-08 | 0.71522
2025-12-08 02:02 | 75.2 | FALSE | FALSE | -0.35052 | -0.46829 | -0.18096 | -0.24006 | 0 |  |  | none | FALSE | 0 | 74.8495 | FALSE | FALSE | 0.0425 |  | 75.1152 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.13287 | Normal | 75.381 | 0.63808 | Night | 202512 | 2025-12-08 | 0.63808
2025-12-08 02:17 | 75.2 | FALSE | FALSE | -0.32175 | -0.42969 | -0.18045 | -0.23938 | 0 |  |  | none | FALSE | 0 | 74.8783 | FALSE | FALSE | 0.0375 |  | 75.1294 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.12555 | Normal | 75.3804 | 0.56273 | Night | 202512 | 2025-12-08 | 0.56273
2025-12-08 02:32 | 75.2 | FALSE | FALSE | -0.28847 | -0.38509 | -0.17543 | -0.23275 | 0 |  |  | none | FALSE | 0 | 74.9115 | FALSE | FALSE | 0.0325 |  | 75.1435 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.11598 | Normal | 75.3754 | 0.48734 | Night | 202512 | 2025-12-08 | 0.48734
2025-12-08 02:47 | 75.2 | FALSE | FALSE | -0.24945 | -0.33282 | -0.16467 | -0.2185 | 0 |  |  | none | FALSE | 0 | 74.9506 | FALSE | FALSE | 0.0273 |  | 75.1576 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.10353 | Normal | 75.3647 | 0.40945 | Night | 202512 | 2025-12-08 | 0.40945
2025-12-08 03:02 | 75.2 | FALSE | FALSE | -0.20222 | -0.26964 | -0.1457 | -0.19338 | 0 |  |  | none | FALSE | 0 | 74.9978 | FALSE | FALSE | 0.0217 |  | 75.1717 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.086982 | Normal | 75.3457 | 0.32489 | Night | 202512 | 2025-12-08 | 0.32489
2025-12-08 03:17 | 75.2 | FALSE | FALSE | -0.14051 | -0.1872 | -0.11225 | -0.14905 | 0 |  |  | none | FALSE | 0 | 75.0595 | FALSE | FALSE | 0.0149 |  | 75.1859 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.063191 | Normal | 75.3123 | 0.22361 | Night | 202512 | 2025-12-08 | 0.22361
2025-12-08 03:32 | 75.2 | FALSE | FALSE | -0.14051 | -0.1872 | -0.11225 | -0.14905 | 0 |  |  | none | FALSE | 0 | 75.0595 | FALSE | FALSE | 0.0149 |  | 75.1859 | 0 | 0 | 0 | 0.091688 | 0 | 0.063191 | Normal | 75.3123 | 0.22361 | Night | 202512 | 2025-12-08 | 0.22361
2025-12-08 03:47 | 75.2 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 75.2 | FALSE | FALSE | 0 |  | 75.2 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0 | Normal | 75.2 |  | Night | 202512 | 2025-12-08
2025-12-08 04:02 | 75.2 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 75.2 | FALSE | FALSE | 0 |  | 75.2 | 0 | 0 | 0 | 0 |  | 0 | Normal | 75.2 |  | Night | 202512 | 2025-12-08
2025-12-08 04:17 | 75.2 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 75.2 | FALSE | FALSE | 0 |  | 75.2 | 0 | 0 | 0 | 0 |  | 0 | Normal | 75.2 |  | Night | 202512 | 2025-12-08
2025-12-08 04:32 | 75.2 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 75.2 | FALSE | FALSE | 0 |  | 75.2 | 0 | 0 | 0 | 0 |  | 0 | Normal | 75.2 |  | Night | 202512 | 2025-12-08
2025-12-08 04:46 | 75.2 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 75.2 | FALSE | FALSE | 0 |  | 75.2 | 0 | 0 | 0 | 0 |  | 0 | Normal | 75.2 |  | Night | 202512 | 2025-12-08
2025-12-08 05:01 | 75.2 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 75.2 | FALSE | FALSE | 0 |  | 75.2 | 0 | 0 | 0 | 0 |  | 0 | Normal | 75.2 |  | Night | 202512 | 2025-12-08
2025-12-08 05:16 | 75.2 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 75.2 | FALSE | FALSE | 0 |  | 75.2 | 0 | 0 | 0 | 0 |  | 0 | Normal | 75.2 |  | Night | 202512 | 2025-12-08
2025-12-08 05:32 | 75.2 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 75.2 | FALSE | FALSE | 0 |  | 75.2 | 0 | 0 | 0 | 0 |  | 0 | Normal | 75.2 |  | Night | 202512 | 2025-12-08
2025-12-08 05:46 | 75.2 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 75.2 | FALSE | FALSE | 0 |  | 75.2 | 0 | 0 | 0 | 0 |  | 0 | Normal | 75.2 |  | Night | 202512 | 2025-12-08
2025-12-08 06:01 | 75.2 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 75.2 | FALSE | FALSE | 0 |  | 75.2 | 0 | 0 | 0 | 0 |  | 0 | Normal | 75.2 |  | Night | 202512 | 2025-12-08
2025-12-08 06:16 | 75.2 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 75.2 | FALSE | FALSE | 0 |  | 75.2 | 0 | 0 | 0 | 0 |  | 0 | Normal | 75.2 |  | Night | 202512 | 2025-12-08
2025-12-08 06:31 | 75.2 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 75.2 | FALSE | FALSE | 0 |  | 75.2 | 0 | 0 | 0 | 0 |  | 0 | Normal | 75.2 |  | Night | 202512 | 2025-12-08
2025-12-08 06:46 | 75.2 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 75.2 | FALSE | FALSE | 0 |  | 75.2 | 0 | 0 | 0 | 0 |  | 0 | Normal | 75.2 |  | Night | 202512 | 2025-12-08
2025-12-08 07:01 | 74.9174 | TRUE | FALSE | 0.14209 | 0.1893 | -0.39485 | -0.52429 | -0.2826 | 2025-12-08 07:30 | 2025-12-08 07:01 | lower | TRUE | 1 | 75.0595 | FALSE | FALSE | 0.3689 | 4.2485 | 75.1859 | 1 | -0.2826 | -0.01413 | 0.063191 | -4.2485 | 0.063191 | Extreme triggered | 75.3123 | -4.2485 | Day | 202512 | 2025-12-08 | 4.2485
2025-12-08 07:16 | 74.9174 | FALSE | FALSE | 0.080375 | 0.10717 | -0.4283 | -0.56845 | 0 |  | 2025-12-08 07:01 | lower | TRUE | 1 | 74.9978 | FALSE | FALSE | 0.3378 | 3.5863 | 75.1717 | 2 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.086982 | Extreme/elevated | 75.3457 | -2.924 | Day | 202512 | 2025-12-08 | 2.924
2025-12-08 07:30 | 75.2 | TRUE | FALSE | -0.20222 | -0.26964 | -0.1457 | -0.19338 | 0.2826 |  |  | none | FALSE | 2 | 74.9978 | TRUE | FALSE | 0.0788 |  | 75.1717 | 0 | 0.2826 | 0 | 0.091688 | 3.0822 | 0.086982 | Persistence ends | 75.3457 | 0.32489 | Day | 202512 | 2025-12-08 | 0.32489
2025-12-08 07:45 | 74.9174 | TRUE | FALSE | 0.03315 | 0.04423 | -0.44727 | -0.59347 | -0.2826 | 2025-12-08 08:45 | 2025-12-08 07:45 | lower | TRUE | 3 | 74.9506 | TRUE | FALSE | 0.2975 | 2.3202 | 75.1576 | 1 | -0.2826 | -0.01413 | 0.11135 | -2.411 | 0.10353 | Extreme triggered | 75.3647 | -2.3202 | Day | 202512 | 2025-12-08 | 2.3202
2025-12-08 08:00 | 74.9174 | FALSE | FALSE | -0.0058732 | -0.0078402 | -0.45803 | -0.60767 | 0 |  | 2025-12-08 07:45 | none | FALSE | 3 | 74.9115 | FALSE | FALSE | 0.33 | 2.1348 | 75.1435 | 2 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.11598 | Extreme/elevated | 75.3754 | -1.9494 | Day | 202512 | 2025-12-08 | 1.9494
2025-12-08 08:15 | 74.9174 | FALSE | FALSE | -0.039147 | -0.05228 | -0.46305 | -0.61428 | 0 |  | 2025-12-08 07:45 | none | FALSE | 3 | 74.8783 | FALSE | FALSE | 0.3697 | 1.9859 | 75.1294 | 3 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.12555 | Persistent | 75.3804 | -1.6882 | Day | 202512 | 2025-12-08 | 1.6882
2025-12-08 08:30 | 74.9174 | FALSE | FALSE | -0.067916 | -0.090736 | -0.46356 | -0.61495 | 0 |  | 2025-12-08 07:45 | none | FALSE | 3 | 74.8495 | FALSE | FALSE | 0.4135 | 1.8617 | 75.1152 | 4 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13287 | Persistent | 75.381 | -1.4888 | Day | 202512 | 2025-12-08 | 1.4888
2025-12-08 08:45 | 75.2 | TRUE | FALSE | -0.35052 | -0.46829 | -0.18096 | -0.24006 | 0.2826 |  |  | none | FALSE | 4 | 74.8495 | TRUE | FALSE | 0.1568 |  | 75.1152 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.13287 | Persistence ends | 75.381 | 0.63808 | Day | 202512 | 2025-12-08 | 0.63808
2025-12-08 08:45 | 75.2 | FALSE | FALSE | -0.35052 | -0.46829 | -0.18096 | -0.24006 | 0 |  |  | none | FALSE | 4 | 74.8495 | FALSE | FALSE | 0.1568 |  | 75.1152 | 0 | 0 | 0 | 0.12967 | 0 | 0.13287 | Normal | 75.381 | 0.63808 | Day | 202512 | 2025-12-08 | 0.63808
2025-12-08 08:48 | 75.2 | FALSE | FALSE | -0.35052 | -0.46829 | -0.18096 | -0.24006 | 0 |  |  | none | FALSE | 4 | 74.8495 | FALSE | FALSE | 0.1568 |  | 75.1152 | 0 | 0 | 0 | 0.12967 | 0 | 0.13287 | Normal | 75.381 | 0.63808 | Day | 202512 | 2025-12-08 | 0.63808
2025-12-08 09:03 | 74.6348 | TRUE | FALSE | 0.11403 | 0.15255 | -0.79029 | -1.0478 | -0.5652 | 2025-12-08 10:38 | 2025-12-08 09:03 | lower | TRUE | 4 | 74.7488 | TRUE | FALSE | 0.3497 | 2.6745 | 75.087 | 1 | -0.5652 | -0.02826 | 0.18107 | -2.9654 | 0.16906 | Extreme triggered | 75.4251 | -2.6745 | Day | 202512 | 2025-12-08 | 2.6745
2025-12-08 09:18 | 74.0714 | TRUE | FALSE | 0.39756 | 0.53386 | -1.5207 | -2.0117 | -0.5634 |  | 2025-12-08 09:03 | lower | TRUE | 5 | 74.469 | TRUE | FALSE | 0.4849 | 3.0452 | 75.0305 | 2 | -0.5634 | -0.05643 | 0.21675 | -2.339 | 0.28078 | Extreme/elevated | 75.5921 | -3.4159 | Day | 202512 | 2025-12-08 | 3.4159
2025-12-08 09:33 | 73.5062 | FALSE | FALSE | 0.56312 | 0.76026 | -2.3162 | -3.0547 | -0.5652 |  | 2025-12-08 09:03 | lower | TRUE | 4 | 74.0693 | FALSE | TRUE | 0.5047 | 3.1251 | 74.9458 | 3 | -0.5652 | -0.08469 | 0.24412 | -1.9683 | 0.43826 | Persistent | 75.8224 | -3.2849 | Day | 202512 | 2025-12-08 | 3.2849
2025-12-08 09:44 | 72.941 | FALSE | FALSE | 0.64804 | 0.88062 | -3.1357 | -4.1218 | -0.5652 |  | 2025-12-08 09:03 | lower | TRUE | 3 | 73.589 | FALSE | TRUE | 0.5171 | 3.1043 | 74.8329 | 4 | -0.5652 | -0.11295 | 0.26557 | -1.7029 | 0.62192 | Persistent | 76.0767 | -3.042 | Day | 202512 | 2025-12-08 | 3.042
2025-12-08 09:59 | 72.3758 | FALSE | FALSE | 0.67094 | 0.9185 | -3.9608 | -5.1886 | -0.5652 |  | 2025-12-08 09:03 | lower | TRUE | 3 | 73.0467 | FALSE | TRUE | 0.5591 | 3.0466 | 74.6917 | 5 | -0.5652 | -0.14121 | 0.28246 | -1.5011 | 0.82247 | Persistent | 76.3366 | -2.8158 | Day | 202512 | 2025-12-08 | 2.8158
2025-12-08 10:08 | 71.8124 | FALSE | FALSE | 0.64206 | 0.88616 | -4.7777 | -6.2381 | -0.5634 |  | 2025-12-08 09:03 | lower | TRUE | 3 | 72.4545 | FALSE | TRUE | 0.6033 | 2.9757 | 74.5223 | 6 | -0.5634 | -0.16938 | 0.29543 | -1.3337 | 1.0339 | Persistent | 76.5901 | -2.621 | Day | 202512 | 2025-12-08 | 2.621
2025-12-08 10:23 | 72.6584 | TRUE | TRUE | -0.46379 | -0.64241 | -3.9374 | -5.1405 | 0.846 |  | 2025-12-08 09:03 | none | FALSE | 4 | 72.1946 | TRUE | FALSE | 0.6195 | 2.7761 | 74.3952 | 7 | 0.846 | -0.12708 | 0.37168 | 2.618 | 1.1003 | Confirmed/Materialized Shift | 76.5958 | -1.5785 | Day | 202512 | 2025-12-08 | 1.5785
2025-12-08 10:38 | 73.2236 | FALSE | FALSE | -1.153 | -1.5998 | -3.2986 | -4.3106 | 0.5652 |  |  | none | FALSE | 3 | 72.0706 | FALSE | FALSE | 0.15 |  | 74.2964 | 0 | 0.5652 | -0.09882 | 0.4021 | 1.6514 | 1.1129 | Persistence ends | 76.5222 | -0.96397 | Day | 202512 | 2025-12-08 | 0.96397
2025-12-08 10:44 | 73.2236 | FALSE | FALSE | -1.2584 | -1.7486 | -3.2063 | -4.1951 | 0 |  |  | none | FALSE | 3 | 71.9652 | FALSE | FALSE | 0.1439 |  | 74.1976 | 0 | 0 | -0.09882 | 0.4021 | 0.24576 | 1.1162 | Normal | 76.4299 | -0.8726 | Day | 202512 | 2025-12-08 | 0.8726
2025-12-08 10:59 | 73.5062 | FALSE | FALSE | -1.5938 | -2.2164 | -2.8072 | -3.6785 | 0.2826 |  |  | none | FALSE | 3 | 71.9124 | FALSE | FALSE | 0.1225 |  | 74.1129 | 0 | 0.2826 | -0.08469 | 0.41063 | 0.89446 | 1.1003 | Normal | 76.3134 | -0.5514 | Day | 202512 | 2025-12-08 | 0.5514
2025-12-08 11:14 | 73.7888 | FALSE | FALSE | -1.9037 | -2.6483 | -2.439 | -3.1996 | 0.2826 |  |  | none | FALSE | 2 | 71.8851 | FALSE | FALSE | 0.0736 |  | 74.0565 | 0 | 0.2826 | -0.05643 | 0.41571 | 0.81555 | 1.0857 | Normal | 76.2278 | -0.24654 | Day | 202512 | 2025-12-08 | 0.24654
2025-12-08 11:20 | 74.0714 | FALSE | FALSE | -2.1906 | -3.0476 | -2.0761 | -2.7265 | 0.2826 |  |  | none | FALSE | 1 | 71.8808 | FALSE | FALSE | 0.0321 |  | 74.0142 | 0 | 0.2826 | -0.0423 | 0.42247 | 0.76904 | 1.0667 | Normal | 76.1475 | 0.053662 | Day | 202512 | 2025-12-08 | 0.053662
2025-12-08 11:23 | 73.7888 | FALSE | FALSE | -1.9055 | -2.6509 | -2.2151 | -2.9145 | -0.2826 |  |  | none | FALSE | 1 | 71.8833 | FALSE | FALSE | 0.0386 |  | 73.9436 | 0 | -0.2826 | -0.07056 | 0.41848 | -0.50669 | 1.0302 | Normal | 76.0039 | -0.15027 | Day | 202512 | 2025-12-08 | 0.15027
2025-12-08 11:38 | 72.941 | FALSE | FALSE | -1.1495 | -1.6011 | -2.957 | -3.8961 | -0.8478 |  |  | none | FALSE | 1 | 71.7915 | FALSE | FALSE | 0.0873 |  | 73.8448 | 0 | -0.8478 | -0.09882 | 0.45135 | -1.6594 | 1.0266 | Normal | 75.898 | -0.88034 | Day | 202512 | 2025-12-08 | 0.88034
2025-12-08 11:44 | 72.6584 | FALSE | FALSE | -0.97991 | -1.3671 | -3.1268 | -4.1258 | -0.2826 |  |  | none | FALSE | 1 | 71.6785 | FALSE | FALSE | 0.0983 |  | 73.7318 | 0 | -0.2826 | -0.11295 | 0.45251 | -0.37491 | 1.0267 | Normal | 75.7852 | -1.0455 | Day | 202512 | 2025-12-08 | 1.0455
2025-12-08 11:59 | 72.3758 | FALSE | FALSE | -0.83003 | -1.1601 | -3.2879 | -4.3455 | -0.2826 |  |  | none | FALSE | 1 | 71.5458 | FALSE | FALSE | 0.1082 |  | 73.6047 | 0 | -0.2826 | -0.12708 | 0.45321 | -0.34315 | 1.0295 | Normal | 75.6637 | -1.1937 | Day | 202512 | 2025-12-08 | 1.1937
2025-12-08 12:14 | 72.095 | FALSE | FALSE | -0.69841 | -0.97822 | -3.4357 | -4.5487 | -0.2808 |  |  | none | FALSE | 0 | 71.3966 | FALSE | FALSE | 0.0883 |  | 73.4636 | 0 | -0.2808 | -0.14112 | 0.45342 | -0.30806 | 1.0335 | Normal | 75.5307 | -1.3242 | Day | 202512 | 2025-12-08 | 1.3242
2025-12-08 12:29 | 72.095 | FALSE | FALSE | -0.76925 | -1.0785 | -3.196 | -4.2449 | 0 |  |  | none | FALSE | 0 | 71.3258 | FALSE | FALSE | 0.0816 |  | 73.3084 | 0 | 0 | -0.15525 | 0.44382 | 0.3498 | 0.99131 | Normal | 75.291 | -1.224 | Day | 202512 | 2025-12-08 | 1.224
2025-12-08 12:33 | 71.8124 | FALSE | FALSE | -0.55166 | -0.77414 | -3.2049 | -4.2722 | -0.2826 |  |  | none | FALSE | 0 | 71.2607 | FALSE | FALSE | 0.0942 |  | 73.139 | 0 | -0.2826 | -0.16938 | 0.44312 | -0.25551 | 0.93913 | Normal | 75.0173 | -1.4126 | Day | 202512 | 2025-12-08 | 1.4126
2025-12-08 12:43 | 72.6584 | FALSE | FALSE | -1.2633 | -1.7695 | -1.9704 | -2.6402 | 0.846 |  |  | none | FALSE | 0 | 71.3951 | FALSE | FALSE | 0.0292 |  | 73.0119 | 0 | 0.846 | -0.12708 | 0.49721 | 1.9571 | 0.80843 | Normal | 74.6288 | -0.43729 | Day | 202512 | 2025-12-08 | 0.43729
2025-12-08 12:58 | 73.5062 | FALSE | FALSE | -1.9991 | -2.7956 | -0.89766 | -1.2065 | 0.8478 |  |  | none | FALSE | 0 | 71.5071 | FALSE | FALSE | 0.0507 |  | 72.9555 | 0 | 0.8478 | -0.05643 | 0.53093 | 1.7031 | 0.72418 | Normal | 74.4039 | 0.76046 | Day | 202512 | 2025-12-08 | 0.76046
2025-12-08 13:14 | 73.7888 | FALSE | FALSE | -2.2549 | -3.1522 | -0.56003 | -0.75324 | 0.2826 |  |  | none | FALSE | 0 | 71.5339 | FALSE | FALSE | 0.0803 |  | 72.9414 | 0 | 0.2826 | -0.01413 | 0.52204 | 0.56841 | 0.70373 | Normal | 74.3488 | 1.2042 | Day | 202512 | 2025-12-08 | 1.2042
2025-12-08 13:27 | 74.0714 | FALSE | FALSE | -2.578 | -3.606 | -0.37446 | -0.50299 | 0.2826 |  |  | none | FALSE | 0 | 71.4934 | FALSE | FALSE | 0.0995 |  | 72.9696 | 0 | 0.2826 | 0.02826 | 0.5092 | 0.49949 | 0.73812 | Normal | 74.4459 | 1.4927 | Day | 202512 | 2025-12-08 | 1.4927
2025-12-08 13:30 | 74.0714 | FALSE | FALSE | -2.6013 | -3.6397 | -0.51076 | -0.68483 | 0 |  |  | none | FALSE | 0 | 71.4701 | FALSE | FALSE | 0.0896 |  | 73.0261 | 0 | 0 | 0.05652 | 0.48984 | -0.11538 | 0.77801 | Normal | 74.5822 | 1.3435 | Day | 202512 | 2025-12-08 | 1.3435
2025-12-08 13:43 | 73.5062 | FALSE | FALSE | -1.9621 | -2.7425 | -1.115 | -1.4943 | -0.5652 |  |  | none | FALSE | 0 | 71.5441 | FALSE | FALSE | 0.0367 |  | 73.0827 | 0 | -0.5652 | 0.05652 | 0.48984 | -1.2692 | 0.76929 | Normal | 74.6212 | 0.55056 | Day | 202512 | 2025-12-08 | 0.55056
2025-12-08 13:58 | 72.6584 | FALSE | FALSE | -0.96798 | -1.3502 | -1.9011 | -2.5498 | -0.8478 |  |  | none | FALSE | 0 | 71.6904 | FALSE | FALSE | 0.0434 |  | 73.125 | 0 | -0.8478 | 0.0423 | 0.5124 | -1.7371 | 0.71727 | Normal | 74.5595 | -0.65047 | Day | 202512 | 2025-12-08 | 0.65047
2025-12-08 14:13 | 73.2236 | FALSE | FALSE | -1.4884 | -2.0748 | -1.3476 | -1.8072 | 0.5652 |  |  | none | FALSE | 0 | 71.7352 | FALSE | FALSE | 0.0066 |  | 73.1532 | 0 | 0.5652 | 0.02826 | 0.49268 | 1.0898 | 0.70901 | Normal | 74.5712 | 0.099266 | Day | 202512 | 2025-12-08 | 0.099266
2025-12-08 14:28 | 73.2236 | FALSE | FALSE | -1.4884 | -2.0748 | -1.3476 | -1.8072 | 0 |  |  | none | FALSE | 0 | 71.7352 | FALSE | FALSE | 0.0066 |  | 73.1532 | 0 | 0 | 0 | 0.4762 | 0 | 0.70901 | Normal | 74.5712 | 0.099266 | Day | 202512 | 2025-12-08 | 0.099266
2025-12-08 14:43 | 73.2236 | FALSE | FALSE | -1.4884 | -2.0748 | -1.3476 | -1.8072 | 0 |  |  | none | FALSE | 0 | 71.7352 | FALSE | FALSE | 0.0066 |  | 73.1532 | 0 | 0 | 0 | 0.4762 | 0 | 0.70901 | Normal | 74.5712 | 0.099266 | Day | 202512 | 2025-12-08 | 0.099266
2025-12-08 14:58 | 73.2236 | FALSE | FALSE | -1.4933 | -2.0818 | -1.3243 | -1.7764 | 0 |  |  | none | FALSE | 0 | 71.7303 | FALSE | FALSE | 0.008 |  | 73.1391 | 0 | 0 | -0.01413 | 0.47154 | 0.029966 | 0.7044 | Normal | 74.5479 | 0.11997 | Day | 202512 | 2025-12-08 | 0.11997
2025-12-08 15:13 | 73.2236 | FALSE | FALSE | -1.489 | -2.0757 | -1.2635 | -1.6962 | 0 |  |  | none | FALSE | 0 | 71.7346 | FALSE | FALSE | 0.0109 |  | 73.1108 | 0 | 0 | -0.02826 | 0.46639 | 0.060593 | 0.68811 | Normal | 74.4871 | 0.16388 | Day | 202512 | 2025-12-08 | 0.16388
2025-12-08 15:28 | 72.941 | FALSE | FALSE | -1.1876 | -1.6551 | -1.4142 | -1.902 | -0.2826 |  |  | none | FALSE | 0 | 71.7534 | FALSE | FALSE | 0.0116 |  | 73.0543 | 0 | -0.2826 | -0.05652 | 0.46368 | -0.48758 | 0.65046 | Normal | 74.3552 | -0.1742 | Day | 202512 | 2025-12-08 | 0.1742
2025-12-08 15:43 | 72.941 | FALSE | FALSE | -1.1836 | -1.6495 | -1.3255 | -1.7848 | 0 |  |  | none | FALSE | 0 | 71.7574 | FALSE | FALSE | 0.0075 |  | 73.0119 | 0 | 0 | -0.04239 | 0.46072 | 0.092008 | 0.62728 | Normal | 74.2665 | -0.11306 | Day | 202512 | 2025-12-08 | 0.11306
2025-12-08 15:58 | 72.941 | FALSE | FALSE | -1.1836 | -1.6495 | -1.3255 | -1.7848 | 0 |  |  | none | FALSE | 0 | 71.7574 | FALSE | FALSE | 0.0075 |  | 73.0119 | 0 | 0 | 0 | 0.41991 | 0 | 0.62728 | Normal | 74.2665 | -0.11306 | Day | 202512 | 2025-12-08 | 0.11306
2025-12-08 16:13 | 72.941 | FALSE | FALSE | -1.1591 | -1.6147 | -1.3292 | -1.7896 | 0 |  |  | none | FALSE | 0 | 71.7819 | FALSE | FALSE | 0.0091 |  | 73.026 | 0 | 0 | 0.01413 | 0.41462 | -0.034079 | 0.62206 | Normal | 74.2702 | -0.13672 | Day | 202512 | 2025-12-08 | 0.13672
2025-12-08 16:28 | 72.6584 | FALSE | FALSE | -0.83742 | -1.166 | -1.601 | -2.1559 | -0.2826 |  |  | none | FALSE | 0 | 71.821 | FALSE | FALSE | 0.0418 |  | 73.0402 | 0 | -0.2826 | 0.01413 | 0.41462 | -0.71566 | 0.6096 | Normal | 74.2594 | -0.62628 | Day | 202512 | 2025-12-08 | 0.62628
2025-12-08 16:42 | 72.6584 | FALSE | FALSE | -0.74145 | -1.031 | -1.5613 | -2.1037 | 0 |  |  | none | FALSE | 0 | 71.917 | FALSE | FALSE | 0.0475 |  | 73.0683 | 0 | 0 | 0.02817 | 0.40882 | -0.068905 | 0.5757 | Normal | 74.2197 | -0.71209 | Day | 202512 | 2025-12-08 | 0.71209
2025-12-08 16:57 | 72.3758 | FALSE | FALSE | -0.40084 | -0.55692 | -1.814 | -2.4451 | -0.2826 |  |  | none | FALSE | 0 | 71.975 | FALSE | FALSE | 0.0851 |  | 73.0824 | 0 | -0.2826 | 0.01404 | 0.41469 | -0.71533 | 0.55372 | Normal | 74.1898 | -1.2761 | Day | 202512 | 2025-12-08 | 1.2761
2025-12-08 17:12 | 72.3758 | FALSE | FALSE | -0.25953 | -0.35988 | -1.7291 | -2.3333 | 0 |  |  | none | FALSE | 0 | 72.1163 | FALSE | FALSE | 0.0985 |  | 73.1106 | 0 | 0 | 0.02817 | 0.40882 | -0.068905 | 0.49715 | Normal | 74.1049 | -1.478 | Day | 202512 | 2025-12-08 | 1.478
2025-12-08 17:27 | 72.095 | FALSE | FALSE | -0.089347 | -0.12408 | -2.0641 | -2.7834 | -0.2808 |  |  | none | FALSE | 0 | 72.0057 | FALSE | FALSE | 0.1223 |  | 73.0824 | 0 | -0.2808 | -0.02817 | 0.36554 | -0.69112 | 0.53837 | Normal | 74.1591 | -1.834 | Day | 202512 | 2025-12-08 | 1.834
2025-12-08 17:42 | 72.3758 | FALSE | FALSE | -0.45139 | -0.62759 | -1.7515 | -2.3629 | 0.2808 |  |  | none | FALSE | 0 | 71.9244 | FALSE | FALSE | 0.0787 |  | 73.0259 | 0 | 0.2808 | -0.05652 | 0.31211 | 1.0808 | 0.55073 | Normal | 74.1273 | -1.1804 | Night | 202512 | 2025-12-08 | 1.1804
2025-12-08 17:57 | 72.6584 | FALSE | FALSE | -0.74055 | -1.0297 | -1.3624 | -1.8406 | 0.2826 |  |  | none | FALSE | 0 | 71.9179 | FALSE | FALSE | 0.0394 |  | 72.9694 | 0 | 0.2826 | -0.05652 | 0.31211 | 1.0866 | 0.52575 | Normal | 74.0208 | -0.59144 | Night | 202512 | 2025-12-08 | 0.59144
2025-12-08 18:12 | 72.941 | FALSE | FALSE | -0.94287 | -1.3096 | -0.88653 | -1.2008 | 0.2826 |  |  | none | FALSE | 0 | 71.9981 | FALSE | FALSE | 0.0041 |  | 72.9128 | 0 | 0.2826 | -0.05652 | 0.31211 | 1.0866 | 0.45735 | Normal | 73.8275 | 0.061594 | Night | 202512 | 2025-12-08 | 0.061594
2025-12-08 18:27 | 72.941 | FALSE | FALSE | -0.82009 | -1.1371 | -0.65071 | -0.88421 | 0 |  |  | none | FALSE | 0 | 72.1209 | FALSE | FALSE | 0.0154 |  | 72.8563 | 0 | 0 | -0.05652 | 0.31211 | 0.18109 | 0.3677 | Normal | 73.5917 | 0.23032 | Night | 202512 | 2025-12-08 | 0.23032
2025-12-08 18:42 | 72.941 | FALSE | FALSE | -0.7838 | -1.0862 | -0.5579 | -0.75906 | 0 |  |  | none | FALSE | 0 | 72.1572 | FALSE | FALSE | 0.0224 |  | 72.8281 | 0 | 0 | -0.02826 | 0.2883 | 0.098022 | 0.33542 | Normal | 73.4989 | 0.33674 | Night | 202512 | 2025-12-08 | 0.33674
2025-12-08 18:42 | 72.941 | FALSE | FALSE | -0.76652 | -1.062 | -0.56888 | -0.77388 | 0 |  |  | none | FALSE | 0 | 72.1745 | FALSE | FALSE | 0.0197 |  | 72.8422 | 0 | 0 | 0.01413 | 0.21429 | -0.065939 | 0.33385 | Normal | 73.5099 | 0.296 | Night | 202512 | 2025-12-08 | 0.296
2025-12-08 18:42 | 72.941 | FALSE | FALSE | -0.75825 | -1.0505 | -0.53235 | -0.72455 | 0 |  |  | none | FALSE | 0 | 72.1828 | FALSE | FALSE | 0.0233 |  | 72.8281 | 0 | 0 | -0.01413 | 0.17061 | 0.082823 | 0.32265 | Normal | 73.4733 | 0.35007 | Night | 202512 | 2025-12-08 | 0.35007
2025-12-08 18:57 | 73.5062 | TRUE | FALSE | -1.3564 | -1.88 | -0.028403 | -0.038626 | 0.5652 |  |  | none | FALSE | 1 | 72.1498 | FALSE | FALSE | 0.1564 |  | 72.8422 | 0 | 0.5652 | 0.01413 | 0.21429 | 2.5716 | 0.34621 | Normal | 73.5346 | 1.918 | Night | 202512 | 2025-12-08 | 1.918
2025-12-08 19:12 | 73.5062 | FALSE | FALSE | -1.3853 | -1.9208 | -0.085506 | -0.11619 | 0 |  |  | none | FALSE | 1 | 72.1209 | FALSE | FALSE | 0.1464 |  | 72.8563 | 0 | 0 | 0.01413 | 0.21429 | -0.065939 | 0.3677 | Normal | 73.5917 | 1.7675 | Night | 202512 | 2025-12-08 | 1.7675
2025-12-08 19:27 | 73.5062 | FALSE | FALSE | -1.4107 | -1.9567 | -0.13915 | -0.18894 | 0 |  |  | none | FALSE | 1 | 72.0955 | FALSE | FALSE | 0.138 |  | 72.8704 | 0 | 0 | 0.01413 | 0.21429 | -0.065939 | 0.38745 | Normal | 73.6453 | 1.6409 | Night | 202512 | 2025-12-08 | 1.6409
2025-12-08 19:41 | 73.7888 | FALSE | FALSE | -1.7552 | -2.4367 | 0.024988 | 0.033876 | 0.2826 | 2025-12-08 22:40 | 2025-12-08 19:41 | upper | TRUE | 1 | 72.0336 | FALSE | FALSE | 0.2229 | 2.0578 | 72.8987 | 1 | 0.2826 | 0.02826 | 0.22247 | 1.1433 | 0.43256 | Extreme triggered | 73.7638 | 2.0578 | Night | 202512 | 2025-12-08 | 2.0578
2025-12-08 19:56 | 73.7888 | FALSE | FALSE | -1.8002 | -2.5007 | -0.1048 | -0.14182 | 0 |  | 2025-12-08 19:41 | none | FALSE | 1 | 71.9886 | FALSE | FALSE | 0.2615 | 1.9189 | 72.9411 | 2 | 0 | 0.04239 | 0.21033 | -0.20154 | 0.47625 | Extreme/elevated | 73.8936 | 1.78 | Night | 202512 | 2025-12-08 | 1.78
2025-12-08 20:11 | 73.7888 | FALSE | FALSE | -1.8305 | -2.5438 | -0.21986 | -0.29707 | 0 |  | 2025-12-08 19:41 | none | FALSE | 1 | 71.9583 | FALSE | FALSE | 0.3047 | 1.8029 | 72.9835 | 3 | 0 | 0.04239 | 0.21033 | -0.20154 | 0.51259 | Persistent | 74.0087 | 1.5711 | Night | 202512 | 2025-12-08 | 1.5711
2025-12-08 20:26 | 73.7888 | FALSE | FALSE | -1.849 | -2.5702 | -0.32316 | -0.43604 | 0 |  | 2025-12-08 19:41 | none | FALSE | 1 | 71.9398 | FALSE | FALSE | 0.3508 | 1.7034 | 73.0259 | 4 | 0 | 0.04239 | 0.21033 | -0.20154 | 0.54304 | Persistent | 74.112 | 1.4049 | Night | 202512 | 2025-12-08 | 1.4049
2025-12-08 20:41 | 73.7888 | FALSE | FALSE | -1.8577 | -2.5826 | -0.41658 | -0.56139 | 0 |  | 2025-12-08 19:41 | none | FALSE | 1 | 71.9311 | FALSE | FALSE | 0.3988 | 1.6162 | 73.0683 | 5 | 0 | 0.04239 | 0.21033 | -0.20154 | 0.56856 | Persistent | 74.2054 | 1.2673 | Night | 202512 | 2025-12-08 | 1.2673
2025-12-08 20:56 | 74.0714 | FALSE | FALSE | -2.136 | -2.9694 | -0.27105 | -0.3646 | 0.2826 |  | 2025-12-08 19:41 | none | FALSE | 1 | 71.9354 | FALSE | FALSE | 0.4747 | 1.6051 | 73.1389 | 6 | 0.2826 | 0.07065 | 0.20218 | 1.0483 | 0.60177 | Persistent | 74.3424 | 1.5496 | Night | 202512 | 2025-12-08 | 1.5496
2025-12-08 21:11 | 74.0714 | FALSE | TRUE | -2.1116 | -2.9344 | -0.38794 | -0.52101 | 0 |  | 2025-12-08 19:41 | none | FALSE | 1 | 71.9598 | FALSE | FALSE | 0.5205 | 1.5728 | 73.2096 | 7 | 0 | 0.07065 | 0.20218 | -0.34945 | 0.62489 | Confirmed/Materialized Shift | 74.4593 | 1.3792 | Night | 202512 | 2025-12-08 | 1.3792
2025-12-08 21:26 | 74.0714 | FALSE | TRUE | -2.0187 | -2.8017 | -0.46459 | -0.62331 | 0 |  | 2025-12-08 19:41 | none | FALSE | 0 | 72.0527 | FALSE | FALSE | 0.4834 | 1.5327 | 73.2943 | 8 | 0 | 0.08478 | 0.18537 | -0.45737 | 0.62083 | Confirmed/Materialized Shift | 74.536 | 1.2517 | Night | 202512 | 2025-12-08 | 1.2517
2025-12-08 21:41 | 74.0714 | FALSE | TRUE | -1.901 | -2.634 | -0.51641 | -0.69235 | 0 |  | 2025-12-08 19:41 | none | FALSE | 0 | 72.1704 | FALSE | FALSE | 0.4764 | 1.4897 | 73.3791 | 9 | 0 | 0.08478 | 0.18537 | -0.45737 | 0.60435 | Confirmed/Materialized Shift | 74.5878 | 1.1455 | Night | 202512 | 2025-12-08 | 1.1455
2025-12-08 21:56 | 74.0714 | FALSE | TRUE | -1.6768 | -2.3162 | -0.48985 | -0.65698 | 0 |  | 2025-12-08 19:41 | none | FALSE | 0 | 72.3946 | FALSE | FALSE | 0.473 | 1.4503 | 73.4779 | 10 | 0 | 0.09882 | 0.16582 | -0.59594 | 0.54166 | Confirmed/Materialized Shift | 74.5613 | 1.0956 | Night | 202512 | 2025-12-08 | 1.0956
2025-12-08 22:11 | 74.0714 | FALSE | TRUE | -1.4894 | -2.052 | -0.47199 | -0.63318 | 0 |  | 2025-12-08 19:41 | none | FALSE | 0 | 72.582 | FALSE | FALSE | 0.4692 | 1.4127 | 73.5627 | 11 | 0 | 0.08478 | 0.16143 | -0.52517 | 0.49034 | Confirmed/Materialized Shift | 74.5434 | 1.0374 | Night | 202512 | 2025-12-08 | 1.0374
2025-12-08 22:26 | 74.3522 | FALSE | TRUE | -1.6485 | -2.2674 | -0.23891 | -0.32029 | 0.2808 |  | 2025-12-08 19:41 | none | FALSE | 0 | 72.7037 | FALSE | FALSE | 0.4996 | 1.4195 | 73.6474 | 12 | 0.2808 | 0.08469 | 0.16132 | 1.2157 | 0.47185 | Confirmed/Materialized Shift | 74.5911 | 1.4937 | Night | 202512 | 2025-12-08 | 1.4937
2025-12-08 22:40 | 74.0714 | FALSE | FALSE | -1.2674 | -1.7409 | -0.53248 | -0.71374 | -0.2808 |  |  | none | FALSE | 0 | 72.804 | FALSE | FALSE | 0.0544 |  | 73.7039 | 0 | -0.2808 | 0.05652 | 0.17366 | -1.9424 | 0.44997 | Persistence ends | 74.6039 | 0.81665 | Night | 202512 | 2025-12-08 | 0.81665
2025-12-08 22:55 | 74.0714 | FALSE | FALSE | -1.149 | -1.5757 | -0.52711 | -0.70659 | 0 |  |  | none | FALSE | 0 | 72.9224 | FALSE | FALSE | 0.0495 |  | 73.7605 | 0 | 0 | 0.05652 | 0.17366 | -0.32547 | 0.41903 | Normal | 74.5985 | 0.74207 | Night | 202512 | 2025-12-08 | 0.74207
2025-12-08 23:10 | 74.0714 | FALSE | FALSE | -1.008 | -1.3796 | -0.49915 | -0.66936 | 0 |  |  | none | FALSE | 0 | 73.0634 | FALSE | FALSE | 0.045 |  | 73.817 | 0 | 0 | 0.05652 | 0.17366 | -0.32547 | 0.37679 | Normal | 74.5705 | 0.67526 | Night | 202512 | 2025-12-08 | 0.67526
2025-12-08 23:26 | 74.0714 | FALSE | FALSE | -0.8355 | -1.1408 | -0.43968 | -0.59008 | 0 |  |  | none | FALSE | 0 | 73.2359 | FALSE | FALSE | 0.0414 |  | 73.8735 | 0 | 0 | 0.05652 | 0.17366 | -0.32547 | 0.31879 | Normal | 74.5111 | 0.62081 | Night | 202512 | 2025-12-08 | 0.62081
2025-12-08 23:40 | 74.0714 | FALSE | FALSE | -0.60856 | -0.8284 | -0.32578 | -0.4379 | 0 |  |  | none | FALSE | 0 | 73.4628 | FALSE | FALSE | 0.0404 |  | 73.93 | 0 | 0 | 0.05652 | 0.17366 | -0.32547 | 0.23359 | Normal | 74.3972 | 0.6053 | Night | 202512 | 2025-12-08 | 0.6053
2025-12-08 23:55 | 74.0714 | FALSE | FALSE | -0.5389 | -0.73288 | -0.31264 | -0.42031 | 0 |  |  | none | FALSE | 0 | 73.5325 | FALSE | FALSE | 0.0354 |  | 73.9583 | 0 | 0 | 0.02826 | 0.12596 | -0.22436 | 0.21289 | Normal | 74.384 | 0.53141 | Night | 202512 | 2025-12-08 | 0.53141
2025-12-09 00:10 | 74.0714 | FALSE | FALSE | -0.4558 | -0.61916 | -0.28606 | -0.38471 | 0 |  |  | none | FALSE | 0 | 73.6156 | FALSE | FALSE | 0.0305 |  | 73.9865 | 0 | 0 | 0.02826 | 0.12596 | -0.22436 | 0.18547 | Normal | 74.3575 | 0.4576 | Night | 202512 | 2025-12-09 | 0.4576
2025-12-09 00:25 | 74.0714 | FALSE | FALSE | -0.35186 | -0.47729 | -0.23864 | -0.32114 | 0 |  |  | none | FALSE | 0 | 73.7195 | FALSE | FALSE | 0.0256 |  | 74.0148 | 0 | 0 | 0.02826 | 0.12596 | -0.22436 | 0.14762 | Normal | 74.31 | 0.38347 | Night | 202512 | 2025-12-09 | 0.38347
2025-12-09 00:40 | 74.0714 | FALSE | FALSE | -0.31862 | -0.43201 | -0.23366 | -0.31446 | 0 |  |  | none | FALSE | 0 | 73.7528 | FALSE | FALSE | 0.0205 |  | 74.0289 | 0 | 0 | 0.01413 | 0.11087 | -0.12744 | 0.13807 | Normal | 74.3051 | 0.30767 | Night | 202512 | 2025-12-09 | 0.30767
2025-12-09 00:55 | 74.0714 | FALSE | FALSE | -0.28065 | -0.38033 | -0.22395 | -0.30143 | 0 |  |  | none | FALSE | 0 | 73.7908 | FALSE | FALSE | 0.015 |  | 74.043 | 0 | 0 | 0.01413 | 0.11087 | -0.12744 | 0.12615 | Normal | 74.2953 | 0.22473 | Night | 202512 | 2025-12-09 | 0.22473
2025-12-09 01:10 | 74.0714 | FALSE | FALSE | -0.23642 | -0.32021 | -0.20798 | -0.28 | 0 |  |  | none | FALSE | 0 | 73.835 | FALSE | FALSE | 0.0085 |  | 74.0572 | 0 | 0 | 0.01413 | 0.11087 | -0.12744 | 0.1111 | Normal | 74.2794 | 0.12799 | Night | 202512 | 2025-12-09 | 0.12799
2025-12-09 01:25 | 74.0714 | FALSE | FALSE | -0.18288 | -0.24751 | -0.1827 | -0.24605 | 0 |  |  | none | FALSE | 0 | 73.8885 | FALSE | FALSE | 0.0001 |  | 74.0713 | 0 | 0 | 0.01413 | 0.11087 | -0.12744 | 0.091396 | Normal | 74.2541 | 0.00098473 | Night | 202512 | 2025-12-09 | 0.00098473
2025-12-09 01:39 | 74.0714 | FALSE | FALSE | -0.11154 | -0.15081 | -0.13962 | -0.18814 | 0 |  |  | none | FALSE | 0 | 73.9599 | FALSE | FALSE | 0.0149 |  | 74.0854 | 0 | 0 | 0.01413 | 0.11087 | -0.12744 | 0.062789 | Normal | 74.211 | -0.22361 | Night | 202512 | 2025-12-09 | 0.22361
2025-12-09 01:54 | 74.0714 | FALSE | FALSE | -0.11154 | -0.15081 | -0.13962 | -0.18814 | 0 |  |  | none | FALSE | 0 | 73.9599 | FALSE | FALSE | 0.0149 |  | 74.0854 | 0 | 0 | 0 | 0.091104 | 0 | 0.062789 | Normal | 74.211 | -0.22361 | Night | 202512 | 2025-12-09 | 0.22361
2025-12-09 02:10 | 74.0714 | FALSE | FALSE | -0.11154 | -0.15081 | -0.13962 | -0.18814 | 0 |  |  | none | FALSE | 0 | 73.9599 | FALSE | FALSE | 0.0149 |  | 74.0854 | 0 | 0 | 0 | 0.091104 | 0 | 0.062789 | Normal | 74.211 | -0.22361 | Night | 202512 | 2025-12-09 | 0.22361
2025-12-09 02:25 | 73.7888 | TRUE | FALSE | 0.099718 | 0.13496 | -0.4653 | -0.62663 | -0.2826 | 2025-12-09 04:38 | 2025-12-09 02:25 | lower | TRUE | 1 | 73.8885 | FALSE | FALSE | 0.2918 | 3.0911 | 74.0713 | 1 | -0.2826 | -0.01413 | 0.11087 | -2.4214 | 0.091396 | Extreme triggered | 74.2541 | -3.0911 | Night | 202512 | 2025-12-09 | 3.0911
2025-12-09 02:39 | 73.7888 | FALSE | FALSE | 0.046176 | 0.062539 | -0.49058 | -0.66046 | 0 |  | 2025-12-09 02:25 | lower | TRUE | 1 | 73.835 | FALSE | FALSE | 0.3039 | 2.7533 | 74.0572 | 2 | 0 | -0.01413 | 0.11087 | 0.12744 | 0.1111 | Extreme/elevated | 74.2794 | -2.4156 | Night | 202512 | 2025-12-09 | 2.4156
2025-12-09 02:54 | 73.7888 | FALSE | FALSE | 0.0019501 | 0.0026427 | -0.50655 | -0.68181 | 0 |  | 2025-12-09 02:25 | lower | TRUE | 1 | 73.7908 | FALSE | TRUE | 0.3344 | 2.5074 | 74.043 | 3 | 0 | -0.01413 | 0.11087 | 0.12744 | 0.12615 | Persistent | 74.2953 | -2.0155 | Night | 202512 | 2025-12-09 | 2.0155
2025-12-09 03:09 | 73.7888 | FALSE | FALSE | -0.036022 | -0.048842 | -0.51626 | -0.69479 | 0 |  | 2025-12-09 02:25 | none | FALSE | 1 | 73.7528 | FALSE | FALSE | 0.3731 | 2.3153 | 74.0289 | 4 | 0 | -0.01413 | 0.11087 | 0.12744 | 0.13807 | Persistent | 74.3051 | -1.7391 | Night | 202512 | 2025-12-09 | 1.7391
2025-12-09 03:24 | 73.7888 | FALSE | FALSE | -0.039147 | -0.053081 | -0.46305 | -0.62362 | 0 |  | 2025-12-09 02:25 | none | FALSE | 1 | 73.7497 | FALSE | FALSE | 0.4268 | 2.1899 | 74.0007 | 5 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.12555 | Persistent | 74.2518 | -1.6882 | Night | 202512 | 2025-12-09 | 1.6882
2025-12-09 03:39 | 73.7888 | FALSE | FALSE | -0.067916 | -0.092126 | -0.46356 | -0.6243 | 0 |  | 2025-12-09 02:25 | none | FALSE | 1 | 73.7209 | FALSE | FALSE | 0.4707 | 2.073 | 73.9866 | 6 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13287 | Persistent | 74.2524 | -1.4888 | Night | 202512 | 2025-12-09 | 1.4888
2025-12-09 03:54 | 73.7888 | FALSE | TRUE | -0.092897 | -0.12605 | -0.46028 | -0.61991 | 0 |  | 2025-12-09 02:25 | none | FALSE | 1 | 73.6959 | FALSE | FALSE | 0.5171 | 1.9666 | 73.9725 | 7 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13829 | Confirmed/Materialized Shift | 74.2491 | -1.3283 | Night | 202512 | 2025-12-09 | 1.3283
2025-12-09 04:09 | 73.7888 | FALSE | TRUE | -0.11452 | -0.15545 | -0.45364 | -0.61103 | 0 |  | 2025-12-09 02:25 | none | FALSE | 1 | 73.6743 | FALSE | FALSE | 0.5082 | 1.87 | 73.9584 | 8 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14204 | Confirmed/Materialized Shift | 74.2424 | -1.1937 | Night | 202512 | 2025-12-09 | 1.1937
2025-12-09 04:24 | 73.7888 | FALSE | TRUE | -0.13306 | -0.18065 | -0.44392 | -0.59801 | 0 |  | 2025-12-09 02:25 | none | FALSE | 1 | 73.6557 | FALSE | FALSE | 0.5004 | 1.782 | 73.9442 | 9 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14424 | Confirmed/Materialized Shift | 74.2327 | -1.0775 | Night | 202512 | 2025-12-09 | 1.0775
2025-12-09 04:38 | 73.7888 | FALSE | FALSE | -0.14864 | -0.20185 | -0.43124 | -0.58103 | 0 |  |  | none | FALSE | 1 | 73.6402 | FALSE | FALSE | 0.0936 |  | 73.9301 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14497 | Persistence ends | 74.22 | -0.97468 | Night | 202512 | 2025-12-09 | 0.97468
2025-12-09 04:54 | 73.7888 | FALSE | FALSE | -0.16132 | -0.2191 | -0.41566 | -0.56015 | 0 |  |  | none | FALSE | 0 | 73.6275 | FALSE | FALSE | 0.0588 |  | 73.916 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14424 | Normal | 74.2045 | -0.88163 | Night | 202512 | 2025-12-09 | 0.88163
2025-12-09 05:09 | 73.7888 | FALSE | FALSE | -0.17104 | -0.23234 | -0.39712 | -0.53531 | 0 |  |  | none | FALSE | 0 | 73.6178 | FALSE | FALSE | 0.0531 |  | 73.9018 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14204 | Normal | 74.1859 | -0.79582 | Night | 202512 | 2025-12-09 | 0.79582
2025-12-09 05:24 | 73.7888 | FALSE | FALSE | -0.17768 | -0.24137 | -0.3755 | -0.5063 | 0 |  |  | none | FALSE | 0 | 73.6111 | FALSE | FALSE | 0.0477 |  | 73.8877 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13829 | Normal | 74.1643 | -0.71522 | Night | 202512 | 2025-12-09 | 0.71522
2025-12-09 05:38 | 73.5062 | TRUE | FALSE | 0.042322 | 0.057544 | -0.66418 | -0.89548 | -0.2826 | 2025-12-09 07:45 | 2025-12-09 05:38 | lower | TRUE | 1 | 73.5485 | FALSE | FALSE | 0.2372 | 2.2722 | 73.8594 | 1 | -0.2826 | -0.02826 | 0.086982 | -2.924 | 0.15546 | Extreme triggered | 74.1704 | -2.2722 | Night | 202512 | 2025-12-09 | 2.2722
2025-12-09 05:53 | 73.5062 | FALSE | FALSE | -0.0068632 | -0.0093378 | -0.65684 | -0.88567 | 0 |  | 2025-12-09 05:38 | none | FALSE | 1 | 73.4993 | FALSE | FALSE | 0.2734 | 2.1154 | 73.8312 | 2 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.16593 | Extreme/elevated | 74.163 | -1.9586 | Night | 202512 | 2025-12-09 | 1.9586
2025-12-09 06:08 | 73.5062 | FALSE | FALSE | -0.045106 | -0.061401 | -0.63857 | -0.86124 | 0 |  | 2025-12-09 05:38 | none | FALSE | 1 | 73.4611 | FALSE | FALSE | 0.3157 | 1.989 | 73.8029 | 3 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.17092 | Persistent | 74.1448 | -1.7361 | Night | 202512 | 2025-12-09 | 1.7361
2025-12-09 06:23 | 73.5062 | FALSE | FALSE | -0.073366 | -0.099909 | -0.61031 | -0.82344 | 0 |  | 2025-12-09 05:38 | none | FALSE | 1 | 73.4328 | FALSE | FALSE | 0.3619 | 1.8844 | 73.7747 | 4 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.17092 | Persistent | 74.1165 | -1.5708 | Night | 202512 | 2025-12-09 | 1.5708
2025-12-09 06:38 | 73.5062 | FALSE | FALSE | -0.091643 | -0.12483 | -0.57206 | -0.77224 | 0 |  | 2025-12-09 05:38 | none | FALSE | 1 | 73.4146 | FALSE | FALSE | 0.4108 | 1.7971 | 73.7464 | 5 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.16593 | Persistent | 74.0783 | -1.4477 | Night | 202512 | 2025-12-09 | 1.4477
2025-12-09 06:53 | 73.5062 | FALSE | FALSE | -0.098978 | -0.13483 | -0.52288 | -0.70631 | 0 |  | 2025-12-09 05:38 | none | FALSE | 1 | 73.4072 | FALSE | FALSE | 0.4623 | 1.7248 | 73.7181 | 6 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.15546 | Persistent | 74.0291 | -1.3633 | Night | 202512 | 2025-12-09 | 1.3633
2025-12-09 07:08 | 73.5062 | FALSE | TRUE | -0.092897 | -0.12654 | -0.46028 | -0.62228 | 0 |  | 2025-12-09 05:38 | none | FALSE | 1 | 73.4133 | FALSE | FALSE | 0.5171 | 1.6681 | 73.6899 | 7 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.13829 | Confirmed/Materialized Shift | 73.9665 | -1.3283 | Day | 202512 | 2025-12-09 | 1.3283
2025-12-09 07:23 | 73.5062 | FALSE | TRUE | -0.11452 | -0.15604 | -0.45364 | -0.61336 | 0 |  | 2025-12-09 05:38 | none | FALSE | 1 | 73.3917 | FALSE | FALSE | 0.5082 | 1.6088 | 73.6758 | 8 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14204 | Confirmed/Materialized Shift | 73.9598 | -1.1937 | Day | 202512 | 2025-12-09 | 1.1937
2025-12-09 07:30 | 73.5062 | FALSE | TRUE | -0.13306 | -0.18134 | -0.44392 | -0.60029 | 0 |  | 2025-12-09 05:38 | none | FALSE | 1 | 73.3731 | FALSE | FALSE | 0.5004 | 1.5498 | 73.6616 | 9 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14424 | Confirmed/Materialized Shift | 73.9501 | -1.0775 | Day | 202512 | 2025-12-09 | 1.0775
2025-12-09 07:45 | 73.5062 | FALSE | FALSE | -0.14864 | -0.20263 | -0.43124 | -0.58325 | 0 |  |  | none | FALSE | 1 | 73.3576 | FALSE | FALSE | 0.0936 |  | 73.6475 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14497 | Persistence ends | 73.9374 | -0.97468 | Day | 202512 | 2025-12-09 | 0.97468
2025-12-09 08:00 | 73.5062 | FALSE | FALSE | -0.16132 | -0.21994 | -0.41566 | -0.56229 | 0 |  |  | none | FALSE | 0 | 73.3449 | FALSE | FALSE | 0.0588 |  | 73.6334 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14424 | Normal | 73.9219 | -0.88163 | Day | 202512 | 2025-12-09 | 0.88163
2025-12-09 08:16 | 73.5062 | FALSE | FALSE | -0.17104 | -0.23324 | -0.39712 | -0.53736 | 0 |  |  | none | FALSE | 0 | 73.3352 | FALSE | FALSE | 0.0531 |  | 73.6192 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14204 | Normal | 73.9033 | -0.79582 | Day | 202512 | 2025-12-09 | 0.79582
2025-12-09 08:30 | 73.5062 | FALSE | FALSE | -0.17768 | -0.2423 | -0.3755 | -0.50824 | 0 |  |  | none | FALSE | 0 | 73.3285 | FALSE | FALSE | 0.0477 |  | 73.6051 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13829 | Normal | 73.8817 | -0.71522 | Day | 202512 | 2025-12-09 | 0.71522
2025-12-09 08:45 | 73.5062 | FALSE | FALSE | -0.18096 | -0.24679 | -0.35052 | -0.47459 | 0 |  |  | none | FALSE | 0 | 73.3252 | FALSE | FALSE | 0.0425 |  | 73.591 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13287 | Normal | 73.8567 | -0.63808 | Day | 202512 | 2025-12-09 | 0.63808
2025-12-09 08:45 | 73.5062 | FALSE | FALSE | -0.18045 | -0.24609 | -0.32175 | -0.43581 | 0 |  |  | none | FALSE | 0 | 73.3258 | FALSE | FALSE | 0.0375 |  | 73.5768 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.12555 | Normal | 73.8279 | -0.56273 | Day | 202512 | 2025-12-09 | 0.56273
2025-12-09 09:00 | 73.5062 | FALSE | FALSE | -0.17543 | -0.23924 | -0.28847 | -0.39091 | 0 |  |  | none | FALSE | 0 | 73.3308 | FALSE | FALSE | 0.0325 |  | 73.5627 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.11598 | Normal | 73.7947 | -0.48734 | Day | 202512 | 2025-12-09 | 0.48734
2025-12-09 09:15 | 73.5062 | FALSE | FALSE | -0.16467 | -0.22452 | -0.24945 | -0.33821 | 0 |  |  | none | FALSE | 0 | 73.3415 | FALSE | FALSE | 0.0273 |  | 73.5486 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.10353 | Normal | 73.7556 | -0.40945 | Day | 202512 | 2025-12-09 | 0.40945
2025-12-09 09:30 | 73.2236 | TRUE | FALSE | 0.074022 | 0.10099 | -0.51944 | -0.70439 | -0.2826 | 2025-12-09 09:59 | 2025-12-09 09:30 | lower | TRUE | 1 | 73.2976 | FALSE | FALSE | 0.2634 | 2.6647 | 73.5203 | 1 | -0.2826 | -0.02826 | 0.086982 | -2.924 | 0.11135 | Extreme triggered | 73.743 | -2.6647 | Day | 202512 | 2025-12-09 | 2.6647
2025-12-09 09:44 | 73.2236 | FALSE | FALSE | 0.045762 | 0.062457 | -0.49118 | -0.66632 | 0 |  | 2025-12-09 09:30 | lower | TRUE | 1 | 73.2694 | FALSE | FALSE | 0.3036 | 2.5378 | 73.4921 | 2 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.11135 | Extreme/elevated | 73.7148 | -2.411 | Day | 202512 | 2025-12-09 | 2.411
2025-12-09 09:59 | 73.5062 | TRUE | FALSE | -0.20222 | -0.27587 | -0.1457 | -0.19783 | 0.2826 |  |  | none | FALSE | 2 | 73.304 | TRUE | FALSE | 0.0788 |  | 73.4779 | 0 | 0.2826 | -0.01413 | 0.11135 | 2.6647 | 0.086982 | Persistence ends | 73.6519 | 0.32489 | Day | 202512 | 2025-12-09 | 0.32489
2025-12-09 10:15 | 73.5062 | FALSE | FALSE | -0.20222 | -0.27587 | -0.1457 | -0.19783 | 0 |  |  | none | FALSE | 2 | 73.304 | FALSE | FALSE | 0.0788 |  | 73.4779 | 0 | 0 | 0 | 0.091688 | 0 | 0.086982 | Normal | 73.6519 | 0.32489 | Day | 202512 | 2025-12-09 | 0.32489
2025-12-09 10:30 | 73.5062 | FALSE | FALSE | -0.20222 | -0.27587 | -0.1457 | -0.19783 | 0 |  |  | none | FALSE | 2 | 73.304 | FALSE | FALSE | 0.0788 |  | 73.4779 | 0 | 0 | 0 | 0.091688 | 0 | 0.086982 | Normal | 73.6519 | 0.32489 | Day | 202512 | 2025-12-09 | 0.32489
2025-12-09 10:44 | 73.5062 | FALSE | FALSE | -0.20222 | -0.27587 | -0.1457 | -0.19783 | 0 |  |  | none | FALSE | 2 | 73.304 | FALSE | FALSE | 0.0788 |  | 73.4779 | 0 | 0 | 0 | 0.091688 | 0 | 0.086982 | Normal | 73.6519 | 0.32489 | Day | 202512 | 2025-12-09 | 0.32489
2025-12-09 10:59 | 73.2236 | TRUE | FALSE | 0.03315 | 0.045252 | -0.44727 | -0.60712 | -0.2826 | 2025-12-09 11:29 | 2025-12-09 10:59 | lower | TRUE | 3 | 73.2568 | TRUE | FALSE | 0.2975 | 2.3202 | 73.4638 | 1 | -0.2826 | -0.01413 | 0.11135 | -2.411 | 0.10353 | Extreme triggered | 73.6709 | -2.3202 | Day | 202512 | 2025-12-09 | 2.3202
2025-12-09 11:14 | 73.2236 | FALSE | FALSE | -0.0058732 | -0.0080215 | -0.45803 | -0.62164 | 0 |  | 2025-12-09 10:59 | none | FALSE | 3 | 73.2177 | FALSE | FALSE | 0.33 | 2.1348 | 73.4497 | 2 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.11598 | Extreme/elevated | 73.6816 | -1.9494 | Day | 202512 | 2025-12-09 | 1.9494
2025-12-09 11:29 | 73.5062 | TRUE | FALSE | -0.28847 | -0.39399 | -0.17543 | -0.2381 | 0.2826 |  |  | none | FALSE | 4 | 73.2177 | TRUE | FALSE | 0.1468 |  | 73.4497 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.11598 | Persistence ends | 73.6816 | 0.48734 | Day | 202512 | 2025-12-09 | 0.48734
2025-12-09 11:44 | 73.5062 | FALSE | FALSE | -0.28847 | -0.39399 | -0.17543 | -0.2381 | 0 |  |  | none | FALSE | 4 | 73.2177 | FALSE | FALSE | 0.1468 |  | 73.4497 | 0 | 0 | 0 | 0.12967 | 0 | 0.11598 | Normal | 73.6816 | 0.48734 | Day | 202512 | 2025-12-09 | 0.48734
2025-12-09 11:59 | 73.5062 | FALSE | FALSE | -0.28847 | -0.39399 | -0.17543 | -0.2381 | 0 |  |  | none | FALSE | 3 | 73.2177 | FALSE | FALSE | 0.1182 |  | 73.4497 | 0 | 0 | 0 | 0.12967 | 0 | 0.11598 | Normal | 73.6816 | 0.48734 | Day | 202512 | 2025-12-09 | 0.48734
2025-12-09 12:14 | 73.5062 | FALSE | FALSE | -0.28847 | -0.39399 | -0.17543 | -0.2381 | 0 |  |  | none | FALSE | 3 | 73.2177 | FALSE | FALSE | 0.1182 |  | 73.4497 | 0 | 0 | 0 | 0.12967 | 0 | 0.11598 | Normal | 73.6816 | 0.48734 | Day | 202512 | 2025-12-09 | 0.48734
2025-12-09 12:29 | 73.2236 | FALSE | FALSE | -0.039147 | -0.05349 | -0.46305 | -0.6284 | -0.2826 |  |  | none | FALSE | 2 | 73.1845 | FALSE | FALSE | 0.1697 |  | 73.4356 | 0 | -0.2826 | -0.01413 | 0.14424 | -1.8612 | 0.12555 | Normal | 73.6866 | -1.6882 | Day | 202512 | 2025-12-09 | 1.6882
2025-12-09 12:44 | 73.5062 | FALSE | FALSE | -0.32175 | -0.43964 | -0.18045 | -0.24488 | 0.2826 |  |  | none | FALSE | 2 | 73.1845 | FALSE | FALSE | 0.0947 |  | 73.4356 | 0 | 0.2826 | 0 | 0.15881 | 1.7795 | 0.12555 | Normal | 73.6866 | 0.56273 | Day | 202512 | 2025-12-09 | 0.56273
2025-12-09 12:59 | 73.2236 | FALSE | FALSE | -0.067916 | -0.092837 | -0.46356 | -0.62909 | -0.2826 |  |  | none | FALSE | 2 | 73.1557 | FALSE | FALSE | 0.1564 |  | 73.4214 | 0 | -0.2826 | -0.01413 | 0.17092 | -1.5708 | 0.13287 | Normal | 73.6872 | -1.4888 | Day | 202512 | 2025-12-09 | 1.4888
2025-12-09 13:14 | 73.2236 | FALSE | FALSE | -0.092897 | -0.12703 | -0.46028 | -0.62466 | 0 |  |  | none | FALSE | 2 | 73.1307 | FALSE | FALSE | 0.1457 |  | 73.4073 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.13829 | Normal | 73.6839 | -1.3283 | Day | 202512 | 2025-12-09 | 1.3283
2025-12-09 13:29 | 73.2236 | FALSE | FALSE | -0.11452 | -0.15665 | -0.45364 | -0.61572 | 0 |  |  | none | FALSE | 1 | 73.1091 | FALSE | FALSE | 0.1082 |  | 73.3932 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.14204 | Normal | 73.6772 | -1.1937 | Day | 202512 | 2025-12-09 | 1.1937
2025-12-09 13:43 | 73.2236 | FALSE | FALSE | -0.13306 | -0.18205 | -0.44392 | -0.6026 | 0 |  |  | none | FALSE | 1 | 73.0905 | FALSE | FALSE | 0.1004 |  | 73.379 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.14424 | Normal | 73.6675 | -1.0775 | Day | 202512 | 2025-12-09 | 1.0775
2025-12-09 13:58 | 73.2236 | FALSE | FALSE | -0.14864 | -0.20341 | -0.43124 | -0.58549 | 0 |  |  | none | FALSE | 0 | 73.075 | FALSE | FALSE | 0.065 |  | 73.3649 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.14497 | Normal | 73.6548 | -0.97468 | Day | 202512 | 2025-12-09 | 0.97468
2025-12-09 14:13 | 73.5062 | FALSE | FALSE | -0.43124 | -0.59014 | -0.14864 | -0.20181 | 0.2826 |  |  | none | FALSE | 0 | 73.075 | FALSE | FALSE | 0.065 |  | 73.3649 | 0 | 0.2826 | 0 | 0.18338 | 1.5411 | 0.14497 | Normal | 73.6548 | 0.97468 | Day | 202512 | 2025-12-09 | 0.97468
2025-12-09 14:28 | 73.5062 | FALSE | FALSE | -0.41566 | -0.56869 | -0.16132 | -0.21898 | 0 |  |  | none | FALSE | 0 | 73.0905 | FALSE | FALSE | 0.0588 |  | 73.379 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.14424 | Normal | 73.6675 | 0.88163 | Day | 202512 | 2025-12-09 | 0.88163
2025-12-09 14:43 | 73.5062 | FALSE | FALSE | -0.39712 | -0.54319 | -0.17104 | -0.23215 | 0 |  |  | none | FALSE | 0 | 73.1091 | FALSE | FALSE | 0.0531 |  | 73.3932 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.14204 | Normal | 73.6772 | 0.79582 | Day | 202512 | 2025-12-09 | 0.79582
2025-12-09 14:58 | 73.5062 | FALSE | FALSE | -0.39712 | -0.54319 | -0.17104 | -0.23215 | 0 |  |  | none | FALSE | 0 | 73.1091 | FALSE | FALSE | 0.0531 |  | 73.3932 | 0 | 0 | 0 | 0.15881 | 0 | 0.14204 | Normal | 73.6772 | 0.79582 | Day | 202512 | 2025-12-09 | 0.79582
2025-12-09 15:13 | 73.5062 | FALSE | FALSE | -0.39712 | -0.54319 | -0.17104 | -0.23215 | 0 |  |  | none | FALSE | 0 | 73.1091 | FALSE | FALSE | 0.0531 |  | 73.3932 | 0 | 0 | 0 | 0.15881 | 0 | 0.14204 | Normal | 73.6772 | 0.79582 | Day | 202512 | 2025-12-09 | 0.79582
2025-12-09 15:28 | 73.5062 | FALSE | FALSE | -0.39712 | -0.54319 | -0.17104 | -0.23215 | 0 |  |  | none | FALSE | 0 | 73.1091 | FALSE | FALSE | 0.0531 |  | 73.3932 | 0 | 0 | 0 | 0.15881 | 0 | 0.14204 | Normal | 73.6772 | 0.79582 | Day | 202512 | 2025-12-09 | 0.79582
2025-12-09 15:43 | 73.5062 | FALSE | FALSE | -0.39712 | -0.54319 | -0.17104 | -0.23215 | 0 |  |  | none | FALSE | 0 | 73.1091 | FALSE | FALSE | 0.0531 |  | 73.3932 | 0 | 0 | 0 | 0.15881 | 0 | 0.14204 | Normal | 73.6772 | 0.79582 | Day | 202512 | 2025-12-09 | 0.79582
2025-12-09 15:58 | 73.7888 | FALSE | FALSE | -0.69025 | -0.94427 | 0.044515 | 0.060364 | 0.2826 | 2025-12-09 16:28 | 2025-12-09 15:58 | upper | TRUE | 0 | 73.0986 | FALSE | FALSE | 0.2089 | 2.2757 | 73.4214 | 1 | 0.2826 | 0.02826 | 0.15614 | 1.6289 | 0.16143 | Extreme triggered | 73.7443 | 2.2757 | Day | 202512 | 2025-12-09 | 2.2757
2025-12-09 16:13 | 73.7888 | FALSE | FALSE | -0.68705 | -0.93985 | -0.0088098 | -0.011938 | 0 |  | 2025-12-09 15:58 | none | FALSE | 0 | 73.1018 | FALSE | FALSE | 0.2442 | 2.1126 | 73.4497 | 2 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.17396 | Extreme/elevated | 73.7976 | 1.9494 | Day | 202512 | 2025-12-09 | 1.9494
2025-12-09 16:28 | 73.5062 | FALSE | FALSE | -0.40445 | -0.55327 | -0.29141 | -0.39488 | -0.2826 |  |  | none | FALSE | 0 | 73.1018 | FALSE | FALSE | 0.0217 |  | 73.4497 | 0 | -0.2826 | 0 | 0.15881 | -1.7795 | 0.17396 | Persistence ends | 73.7976 | 0.32489 | Day | 202512 | 2025-12-09 | 0.32489
2025-12-09 16:42 | 73.5062 | FALSE | FALSE | -0.40445 | -0.55327 | -0.29141 | -0.39488 | 0 |  |  | none | FALSE | 0 | 73.1018 | FALSE | FALSE | 0.0217 |  | 73.4497 | 0 | 0 | 0 | 0.15881 | 0 | 0.17396 | Normal | 73.7976 | 0.32489 | Day | 202512 | 2025-12-09 | 0.32489
2025-12-09 16:57 | 73.5062 | FALSE | FALSE | -0.40445 | -0.55327 | -0.29141 | -0.39488 | 0 |  |  | none | FALSE | 0 | 73.1018 | FALSE | FALSE | 0.0217 |  | 73.4497 | 0 | 0 | 0 | 0.15881 | 0 | 0.17396 | Normal | 73.7976 | 0.32489 | Day | 202512 | 2025-12-09 | 0.32489
2025-12-09 17:12 | 73.5062 | FALSE | FALSE | -0.40445 | -0.55327 | -0.29141 | -0.39488 | 0 |  |  | none | FALSE | 0 | 73.1018 | FALSE | FALSE | 0.0217 |  | 73.4497 | 0 | 0 | 0 | 0.15881 | 0 | 0.17396 | Normal | 73.7976 | 0.32489 | Day | 202512 | 2025-12-09 | 0.32489
2025-12-09 17:27 | 73.5062 | FALSE | FALSE | -0.37424 | -0.51174 | -0.28946 | -0.39225 | 0 |  |  | none | FALSE | 0 | 73.132 | FALSE | FALSE | 0.017 |  | 73.4638 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.16593 | Normal | 73.7957 | 0.25547 | Day | 202512 | 2025-12-09 | 0.25547
2025-12-09 17:42 | 73.5062 | FALSE | FALSE | -0.37424 | -0.51174 | -0.28946 | -0.39225 | 0 |  |  | none | FALSE | 0 | 73.132 | FALSE | FALSE | 0.017 |  | 73.4638 | 0 | 0 | 0 | 0.12967 | 0 | 0.16593 | Normal | 73.7957 | 0.25547 | Night | 202512 | 2025-12-09 | 0.25547
2025-12-09 17:57 | 73.5062 | FALSE | FALSE | -0.34054 | -0.46543 | -0.28402 | -0.3849 | 0 |  |  | none | FALSE | 0 | 73.1657 | FALSE | FALSE | 0.0121 |  | 73.4779 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.15614 | Normal | 73.7902 | 0.18099 | Night | 202512 | 2025-12-09 | 0.18099
2025-12-09 18:12 | 73.5062 | FALSE | FALSE | -0.30262 | -0.41339 | -0.27436 | -0.37186 | 0 |  |  | none | FALSE | 0 | 73.2036 | FALSE | FALSE | 0.0065 |  | 73.4921 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.14424 | Normal | 73.7806 | 0.097959 | Night | 202512 | 2025-12-09 | 0.097959
2025-12-09 18:27 | 73.5062 | FALSE | FALSE | -0.25933 | -0.35405 | -0.25933 | -0.35156 | 0 |  |  | none | FALSE | 0 | 73.2469 | FALSE | FALSE | 0 |  | 73.5062 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.12967 | Normal | 73.7655 | 0 | Night | 202512 | 2025-12-09 | 0
2025-12-09 18:42 | 73.5062 | FALSE | FALSE | -0.20858 | -0.28456 | -0.23684 | -0.32117 | 0 |  |  | none | FALSE | 0 | 73.2976 | FALSE | FALSE | 0.0085 |  | 73.5203 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.11135 | Normal | 73.743 | -0.12689 | Night | 202512 | 2025-12-09 | 0.12689
2025-12-09 18:42 | 73.5062 | FALSE | FALSE | -0.1457 | -0.19861 | -0.20222 | -0.27436 | 0 |  |  | none | FALSE | 0 | 73.3605 | FALSE | FALSE | 0.0217 |  | 73.5345 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.086982 | Normal | 73.7084 | -0.32489 | Night | 202512 | 2025-12-09 | 0.32489
2025-12-09 18:57 | 73.5062 | FALSE | FALSE | -0.1457 | -0.19861 | -0.20222 | -0.27436 | 0 |  |  | none | FALSE | 0 | 73.3605 | FALSE | FALSE | 0.0217 |  | 73.5345 | 0 | 0 | 0 | 0.091688 | 0 | 0.086982 | Normal | 73.7084 | -0.32489 | Night | 202512 | 2025-12-09 | 0.32489
2025-12-09 19:12 | 73.5062 | FALSE | FALSE | -0.1457 | -0.19861 | -0.20222 | -0.27436 | 0 |  |  | none | FALSE | 0 | 73.3605 | FALSE | FALSE | 0.0217 |  | 73.5345 | 0 | 0 | 0 | 0.091688 | 0 | 0.086982 | Normal | 73.7084 | -0.32489 | Night | 202512 | 2025-12-09 | 0.32489
2025-12-09 19:27 | 73.7888 | TRUE | FALSE | -0.44727 | -0.60984 | 0.03315 | 0.044946 | 0.2826 | 2025-12-09 21:11 | 2025-12-09 19:27 | upper | TRUE | 1 | 73.3415 | FALSE | FALSE | 0.2404 | 2.3202 | 73.5486 | 1 | 0.2826 | 0.01413 | 0.11135 | 2.411 | 0.10353 | Extreme triggered | 73.7556 | 2.3202 | Night | 202512 | 2025-12-09 | 2.3202
2025-12-09 19:41 | 73.7888 | FALSE | FALSE | -0.45803 | -0.62461 | -0.0058732 | -0.0079588 | 0 |  | 2025-12-09 19:27 | none | FALSE | 1 | 73.3308 | FALSE | FALSE | 0.2728 | 2.1348 | 73.5627 | 2 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.11598 | Extreme/elevated | 73.7947 | 1.9494 | Night | 202512 | 2025-12-09 | 1.9494
2025-12-09 19:56 | 74.0714 | TRUE | FALSE | -0.80329 | -1.0964 | 0.15755 | 0.21316 | 0.2826 |  | 2025-12-09 19:27 | upper | TRUE | 2 | 73.2681 | TRUE | TRUE | 0.427 | 2.4152 | 73.591 | 3 | 0.2826 | 0.02826 | 0.12638 | 2.0125 | 0.16143 | Persistent | 73.9138 | 2.976 | Night | 202512 | 2025-12-09 | 2.976
2025-12-09 20:11 | 73.7888 | TRUE | FALSE | -0.51554 | -0.70359 | -0.14816 | -0.20039 | -0.2826 |  | 2025-12-09 19:27 | none | FALSE | 3 | 73.2733 | TRUE | FALSE | 0.3881 | 2.0881 | 73.6051 | 4 | -0.2826 | 0.01413 | 0.14424 | -2.0571 | 0.16593 | Persistent | 73.937 | 1.1071 | Night | 202512 | 2025-12-09 | 1.1071
2025-12-09 20:27 | 73.7888 | FALSE | FALSE | -0.50769 | -0.69279 | -0.16857 | -0.22792 | 0 |  | 2025-12-09 19:27 | none | FALSE | 3 | 73.2811 | FALSE | FALSE | 0.4383 | 1.8711 | 73.6192 | 5 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.16906 | Persistent | 73.9574 | 1.0029 | Night | 202512 | 2025-12-09 | 1.0029
2025-12-09 20:41 | 73.7888 | FALSE | FALSE | -0.50769 | -0.69279 | -0.16857 | -0.22792 | 0 |  | 2025-12-09 19:27 | none | FALSE | 3 | 73.2811 | FALSE | FALSE | 0.4954 | 1.7264 | 73.6192 | 6 | 0 | 0 | 0.12967 | 0 | 0.16906 | Persistent | 73.9574 | 1.0029 | Night | 202512 | 2025-12-09 | 1.0029
2025-12-09 20:56 | 73.7888 | FALSE | TRUE | -0.50769 | -0.69279 | -0.16857 | -0.22792 | 0 |  | 2025-12-09 19:27 | none | FALSE | 3 | 73.2811 | FALSE | FALSE | 0.5526 | 1.6231 | 73.6192 | 7 | 0 | 0 | 0.12967 | 0 | 0.16906 | Confirmed/Materialized Shift | 73.9574 | 1.0029 | Night | 202512 | 2025-12-09 | 1.0029
2025-12-09 21:11 | 73.7888 | FALSE | FALSE | -0.49727 | -0.67848 | -0.18641 | -0.25198 | 0 |  |  | none | FALSE | 3 | 73.2915 | FALSE | FALSE | 0.1463 |  | 73.6334 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.17092 | Persistence ends | 73.9752 | 0.90938 | Night | 202512 | 2025-12-09 | 0.90938
2025-12-09 21:26 | 73.7888 | FALSE | FALSE | -0.48436 | -0.66076 | -0.20176 | -0.27269 | 0 |  |  | none | FALSE | 3 | 73.3044 | FALSE | FALSE | 0.1406 |  | 73.6475 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.17153 | Normal | 73.9906 | 0.82375 | Night | 202512 | 2025-12-09 | 0.82375
2025-12-09 21:41 | 73.7888 | FALSE | FALSE | -0.46901 | -0.63967 | -0.21467 | -0.29008 | 0 |  |  | none | FALSE | 3 | 73.3198 | FALSE | FALSE | 0.1353 |  | 73.6616 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.17092 | Normal | 74.0035 | 0.74404 | Night | 202512 | 2025-12-09 | 0.74404
2025-12-09 21:56 | 73.7888 | FALSE | FALSE | -0.45117 | -0.61519 | -0.22509 | -0.30411 | 0 |  |  | none | FALSE | 2 | 73.3376 | FALSE | FALSE | 0.1017 |  | 73.6758 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.16906 | Normal | 74.0139 | 0.66862 | Night | 202512 | 2025-12-09 | 0.66862
2025-12-09 22:11 | 73.7888 | FALSE | FALSE | -0.43076 | -0.58721 | -0.23294 | -0.3147 | 0 |  |  | none | FALSE | 2 | 73.358 | FALSE | FALSE | 0.0969 |  | 73.6899 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.16593 | Normal | 74.0217 | 0.59611 | Night | 202512 | 2025-12-09 | 0.59611
2025-12-09 22:26 | 73.7888 | FALSE | FALSE | -0.40765 | -0.55552 | -0.23809 | -0.32162 | 0 |  |  | none | FALSE | 1 | 73.3812 | FALSE | FALSE | 0.0636 |  | 73.704 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.16143 | Normal | 74.0269 | 0.52517 | Night | 202512 | 2025-12-09 | 0.52517
2025-12-09 22:40 | 73.7888 | FALSE | FALSE | -0.38158 | -0.51981 | -0.24028 | -0.32457 | 0 |  |  | none | FALSE | 0 | 73.4072 | FALSE | FALSE | 0.0303 |  | 73.7181 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.15546 | Normal | 74.0291 | 0.45445 | Night | 202512 | 2025-12-09 | 0.45445
2025-12-09 22:55 | 73.7888 | FALSE | FALSE | -0.3522 | -0.4796 | -0.23916 | -0.32307 | 0 |  |  | none | FALSE | 0 | 73.4366 | FALSE | FALSE | 0.0255 |  | 73.7323 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.14784 | Normal | 74.028 | 0.3823 | Night | 202512 | 2025-12-09 | 0.3823
2025-12-09 23:11 | 73.7888 | FALSE | FALSE | -0.31898 | -0.43416 | -0.2342 | -0.31638 | 0 |  |  | none | FALSE | 0 | 73.4698 | FALSE | FALSE | 0.0204 |  | 73.7464 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.13829 | Normal | 74.023 | 0.30652 | Night | 202512 | 2025-12-09 | 0.30652
2025-12-09 23:26 | 73.7888 | FALSE | FALSE | -0.28103 | -0.38231 | -0.22451 | -0.30333 | 0 |  |  | none | FALSE | 0 | 73.5078 | FALSE | FALSE | 0.0149 |  | 73.7605 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.12638 | Normal | 74.0133 | 0.22361 | Night | 202512 | 2025-12-09 | 0.22361
2025-12-09 23:40 | 73.7888 | FALSE | FALSE | -0.23684 | -0.322 | -0.20858 | -0.28187 | 0 |  |  | none | FALSE | 0 | 73.552 | FALSE | FALSE | 0.0085 |  | 73.7747 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.11135 | Normal | 73.9974 | 0.12689 | Night | 202512 | 2025-12-09 | 0.12689
2025-12-09 23:55 | 73.7888 | FALSE | FALSE | -0.18338 | -0.24913 | -0.18338 | -0.2479 | 0 |  |  | none | FALSE | 0 | 73.6054 | FALSE | FALSE | 0 |  | 73.7888 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.091688 | Normal | 73.9722 | -1.5499e-13 | Night | 202512 | 2025-12-09 | 1.5499e-13
2025-12-10 00:10 | 73.7888 | FALSE | FALSE | -0.11225 | -0.15236 | -0.14051 | -0.19006 | 0 |  |  | none | FALSE | 0 | 73.6765 | FALSE | FALSE | 0.0149 |  | 73.8029 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.063191 | Normal | 73.9293 | -0.22361 | Night | 202512 | 2025-12-10 | 0.22361
2025-12-10 00:25 | 73.7888 | FALSE | FALSE | -0.11225 | -0.15236 | -0.14051 | -0.19006 | 0 |  |  | none | FALSE | 0 | 73.6765 | FALSE | FALSE | 0.0149 |  | 73.8029 | 0 | 0 | 0 | 0.091688 | 0 | 0.063191 | Normal | 73.9293 | -0.22361 | Night | 202512 | 2025-12-10 | 0.22361
2025-12-10 00:40 | 73.7888 | FALSE | FALSE | -0.11225 | -0.15236 | -0.14051 | -0.19006 | 0 |  |  | none | FALSE | 0 | 73.6765 | FALSE | FALSE | 0.0149 |  | 73.8029 | 0 | 0 | 0 | 0.091688 | 0 | 0.063191 | Normal | 73.9293 | -0.22361 | Night | 202512 | 2025-12-10 | 0.22361
2025-12-10 00:55 | 73.7888 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.7888 | FALSE | FALSE | 0 |  | 73.7888 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0 | Normal | 73.7888 |  | Night | 202512 | 2025-12-10
2025-12-10 01:10 | 73.7888 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.7888 | FALSE | FALSE | 0 |  | 73.7888 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.7888 |  | Night | 202512 | 2025-12-10
2025-12-10 01:25 | 73.7888 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.7888 | FALSE | FALSE | 0 |  | 73.7888 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.7888 |  | Night | 202512 | 2025-12-10
2025-12-10 01:39 | 73.7888 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.7888 | FALSE | FALSE | 0 |  | 73.7888 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.7888 |  | Night | 202512 | 2025-12-10
2025-12-10 01:55 | 73.5062 | TRUE | FALSE | 0.14209 | 0.19293 | -0.39485 | -0.5343 | -0.2826 | 2025-12-10 05:09 | 2025-12-10 01:55 | lower | TRUE | 1 | 73.6483 | FALSE | FALSE | 0.3689 | 4.2485 | 73.7747 | 1 | -0.2826 | -0.01413 | 0.063191 | -4.2485 | 0.063191 | Extreme triggered | 73.9011 | -4.2485 | Night | 202512 | 2025-12-10 | 4.2485
2025-12-10 02:10 | 73.5062 | FALSE | FALSE | 0.080375 | 0.10923 | -0.4283 | -0.5793 | 0 |  | 2025-12-10 01:55 | lower | TRUE | 1 | 73.5866 | FALSE | FALSE | 0.3378 | 3.5863 | 73.7605 | 2 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.086982 | Extreme/elevated | 73.9345 | -2.924 | Night | 202512 | 2025-12-10 | 2.924
2025-12-10 02:25 | 73.5062 | FALSE | FALSE | 0.03315 | 0.045078 | -0.44727 | -0.6048 | 0 |  | 2025-12-10 01:55 | lower | TRUE | 1 | 73.5394 | FALSE | TRUE | 0.3547 | 3.1643 | 73.7464 | 3 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.10353 | Persistent | 73.9535 | -2.3202 | Night | 202512 | 2025-12-10 | 2.3202
2025-12-10 02:39 | 73.5062 | FALSE | FALSE | -0.0058732 | -0.0079907 | -0.45803 | -0.61926 | 0 |  | 2025-12-10 01:55 | none | FALSE | 1 | 73.5003 | FALSE | FALSE | 0.3871 | 2.8605 | 73.7323 | 4 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.11598 | Persistent | 73.9642 | -1.9494 | Night | 202512 | 2025-12-10 | 1.9494
2025-12-10 02:54 | 73.5062 | FALSE | FALSE | -0.039147 | -0.053285 | -0.46305 | -0.626 | 0 |  | 2025-12-10 01:55 | none | FALSE | 1 | 73.4671 | FALSE | FALSE | 0.4268 | 2.6261 | 73.7181 | 5 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.12555 | Persistent | 73.9692 | -1.6882 | Night | 202512 | 2025-12-10 | 1.6882
2025-12-10 03:09 | 73.2236 | TRUE | FALSE | 0.13444 | 0.18326 | -0.79814 | -1.0783 | -0.2826 |  | 2025-12-10 01:55 | lower | TRUE | 2 | 73.358 | TRUE | TRUE | 0.5873 | 2.6568 | 73.6899 | 6 | -0.2826 | -0.02826 | 0.086982 | -2.924 | 0.16593 | Persistent | 74.0217 | -2.8102 | Night | 202512 | 2025-12-10 | 2.8102
2025-12-10 03:24 | 73.2236 | FALSE | TRUE | 0.050115 | 0.068394 | -0.82595 | -1.1154 | 0 |  | 2025-12-10 01:55 | lower | TRUE | 2 | 73.2737 | FALSE | TRUE | 0.6077 | 2.5998 | 73.6616 | 7 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.19396 | Confirmed/Materialized Shift | 74.0495 | -2.2584 | Night | 202512 | 2025-12-10 | 2.2584
2025-12-10 03:39 | 73.2236 | FALSE | TRUE | -0.019304 | -0.02637 | -0.83884 | -1.1326 | 0 |  | 2025-12-10 01:55 | none | FALSE | 2 | 73.2043 | FALSE | FALSE | 0.5845 | 2.5136 | 73.6334 | 8 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21454 | Confirmed/Materialized Shift | 74.0624 | -1.91 | Night | 202512 | 2025-12-10 | 1.91
2025-12-10 03:54 | 73.2236 | FALSE | TRUE | -0.077844 | -0.10642 | -0.84086 | -1.1353 | 0 |  | 2025-12-10 01:55 | none | FALSE | 2 | 73.1458 | FALSE | FALSE | 0.5679 | 2.4189 | 73.6051 | 9 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22968 | Confirmed/Materialized Shift | 74.0645 | -1.6611 | Night | 202512 | 2025-12-10 | 1.6611
2025-12-10 04:09 | 73.2236 | FALSE | TRUE | -0.12756 | -0.17452 | -0.83406 | -1.1262 | 0 |  | 2025-12-10 01:55 | none | FALSE | 2 | 73.096 | FALSE | FALSE | 0.5551 | 2.3239 | 73.5768 | 10 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.24041 | Confirmed/Materialized Shift | 74.0577 | -1.4694 | Night | 202512 | 2025-12-10 | 1.4694
2025-12-10 04:24 | 73.2236 | FALSE | TRUE | -0.16961 | -0.23218 | -0.81959 | -1.1069 | 0 |  | 2025-12-10 01:55 | none | FALSE | 1 | 73.054 | FALSE | FALSE | 0.5162 | 2.2321 | 73.5486 | 11 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.2473 | Confirmed/Materialized Shift | 74.0432 | -1.3141 | Night | 202512 | 2025-12-10 | 1.3141
2025-12-10 04:39 | 73.2236 | FALSE | TRUE | -0.20463 | -0.28024 | -0.79809 | -1.0782 | 0 |  | 2025-12-10 01:55 | none | FALSE | 1 | 73.019 | FALSE | FALSE | 0.5075 | 2.1448 | 73.5203 | 12 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.25068 | Confirmed/Materialized Shift | 74.0217 | -1.1837 | Night | 202512 | 2025-12-10 | 1.1837
2025-12-10 04:54 | 73.2236 | FALSE | TRUE | -0.23289 | -0.31906 | -0.76983 | -1.0404 | 0 |  | 2025-12-10 01:55 | none | FALSE | 1 | 72.9907 | FALSE | FALSE | 0.5 | 2.0622 | 73.4921 | 13 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.25068 | Confirmed/Materialized Shift | 73.9934 | -1.071 | Night | 202512 | 2025-12-10 | 1.071
2025-12-10 05:09 | 73.2236 | FALSE | FALSE | -0.25439 | -0.34863 | -0.73481 | -0.99355 | 0 |  |  | none | FALSE | 1 | 72.9692 | FALSE | FALSE | 0.0933 |  | 73.4638 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.2473 | Persistence ends | 73.9584 | -0.97132 | Night | 202512 | 2025-12-10 | 0.97132
2025-12-10 05:24 | 72.941 | TRUE | FALSE | -0.041475 | -0.056893 | -1.0023 | -1.3555 | -0.2826 |  |  | none | FALSE | 2 | 72.8995 | TRUE | FALSE | 0.1799 |  | 73.4214 | 0 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.26095 | Normal | 73.9433 | -1.8411 | Night | 202512 | 2025-12-10 | 1.8411
2025-12-10 05:38 | 72.941 | FALSE | FALSE | -0.095809 | -0.13152 | -0.97187 | -1.3149 | 0 |  |  | none | FALSE | 1 | 72.8452 | FALSE | FALSE | 0.138 |  | 73.379 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.26692 | Normal | 73.9129 | -1.6411 | Night | 202512 | 2025-12-10 | 1.6411
2025-12-10 05:53 | 72.941 | FALSE | FALSE | -0.13583 | -0.18657 | -0.92711 | -1.2551 | 0 |  |  | none | FALSE | 1 | 72.8052 | FALSE | FALSE | 0.1278 |  | 73.3366 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.26574 | Normal | 73.8681 | -1.4888 | Night | 202512 | 2025-12-10 | 1.4888
2025-12-10 06:08 | 72.941 | FALSE | FALSE | -0.16135 | -0.22169 | -0.86785 | -1.1758 | 0 |  |  | none | FALSE | 1 | 72.7797 | FALSE | FALSE | 0.1201 |  | 73.2943 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.2573 | Normal | 73.8088 | -1.3729 | Night | 202512 | 2025-12-10 | 1.3729
2025-12-10 06:23 | 72.941 | FALSE | FALSE | -0.17083 | -0.23475 | -0.79255 | -1.0749 | 0 |  |  | none | FALSE | 1 | 72.7702 | FALSE | FALSE | 0.1146 |  | 73.2519 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.24084 | Normal | 73.7335 | -1.2907 | Night | 202512 | 2025-12-10 | 1.2907
2025-12-10 06:38 | 72.6584 | FALSE | FALSE | 0.055253 | 0.075987 | -1.0186 | -1.3826 | -0.2826 | 2025-12-10 08:15 | 2025-12-10 06:38 | lower | TRUE | 1 | 72.7137 | FALSE | FALSE | 0.2343 | 2.2294 | 73.1953 | 1 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.24084 | Extreme triggered | 73.677 | -2.2294 | Night | 202512 | 2025-12-10 | 2.2294
2025-12-10 06:53 | 72.6584 | FALSE | FALSE | -0.020045 | -0.027596 | -1.0091 | -1.3699 | 0 |  | 2025-12-10 06:38 | none | FALSE | 1 | 72.6384 | FALSE | FALSE | 0.271 | 2.0758 | 73.153 | 2 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.2573 | Extreme/elevated | 73.6675 | -1.9221 | Night | 202512 | 2025-12-10 | 1.9221
2025-12-10 07:08 | 72.6584 | FALSE | FALSE | -0.079312 | -0.10928 | -0.98363 | -1.3357 | 0 |  | 2025-12-10 06:38 | none | FALSE | 1 | 72.5791 | FALSE | FALSE | 0.3134 | 1.951 | 73.1106 | 3 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.26574 | Persistent | 73.642 | -1.7015 | Day | 202512 | 2025-12-10 | 1.7015
2025-12-10 07:23 | 72.6584 | FALSE | FALSE | -0.12407 | -0.17105 | -0.94361 | -1.282 | 0 |  | 2025-12-10 06:38 | none | FALSE | 1 | 72.5343 | FALSE | FALSE | 0.3595 | 1.8471 | 73.0682 | 4 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.26692 | Persistent | 73.602 | -1.5352 | Day | 202512 | 2025-12-10 | 1.5352
2025-12-10 07:30 | 72.6584 | FALSE | FALSE | -0.15451 | -0.21311 | -0.88927 | -1.2091 | 0 |  | 2025-12-10 06:38 | none | FALSE | 1 | 72.5039 | FALSE | FALSE | 0.4081 | 1.7592 | 73.0258 | 5 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.26095 | Persistent | 73.5477 | -1.4079 | Day | 202512 | 2025-12-10 | 1.4079
2025-12-10 07:45 | 72.3758 | FALSE | FALSE | 0.0464 | 0.064068 | -1.1405 | -1.5514 | -0.2826 |  | 2025-12-10 06:38 | lower | TRUE | 0 | 72.4222 | FALSE | TRUE | 0.4875 | 1.8276 | 72.9693 | 6 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.27353 | Persistent | 73.5163 | -2.1696 | Day | 202512 | 2025-12-10 | 2.1696
2025-12-10 08:00 | 72.6584 | TRUE | TRUE | -0.26753 | -0.36956 | -0.83273 | -1.1331 | 0.2826 |  | 2025-12-10 06:38 | none | FALSE | 1 | 72.3909 | FALSE | FALSE | 0.4971 | 1.7133 | 72.941 | 7 | 0.2826 | -0.02826 | 0.12638 | 2.4597 | 0.27506 | Confirmed/Materialized Shift | 73.4911 | -1.0274 | Day | 202512 | 2025-12-10 | 1.0274
2025-12-10 08:15 | 72.941 | TRUE | FALSE | -0.54797 | -0.75694 | -0.51971 | -0.70747 | 0.2826 |  |  | none | FALSE | 2 | 72.393 | TRUE | FALSE | 0.0607 |  | 72.9269 | 0 | 0.2826 | -0.01413 | 0.14424 | 2.0571 | 0.26692 | Persistence ends | 73.4607 | 0.052937 | Day | 202512 | 2025-12-10 | 0.052937
2025-12-10 08:30 | 72.941 | FALSE | FALSE | -0.54367 | -0.75095 | -0.48715 | -0.66344 | 0 |  |  | none | FALSE | 2 | 72.3973 | FALSE | FALSE | 0.0645 |  | 72.9127 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.25771 | Normal | 73.4282 | 0.10966 | Day | 202512 | 2025-12-10 | 0.10966
2025-12-10 08:45 | 73.2236 | FALSE | FALSE | -0.82627 | -1.1413 | -0.20455 | -0.27857 | 0.2826 |  |  | none | FALSE | 2 | 72.3973 | FALSE | FALSE | 0.1376 |  | 72.9127 | 0 | 0.2826 | 0 | 0.15881 | 1.7795 | 0.25771 | Normal | 73.4282 | 1.2063 | Day | 202512 | 2025-12-10 | 1.2063
2025-12-10 08:45 | 73.2236 | FALSE | FALSE | -0.82627 | -1.1413 | -0.20455 | -0.27857 | 0 |  |  | none | FALSE | 2 | 72.3973 | FALSE | FALSE | 0.1376 |  | 72.9127 | 0 | 0 | 0 | 0.15881 | 0 | 0.25771 | Normal | 73.4282 | 1.2063 | Day | 202512 | 2025-12-10 | 1.2063
2025-12-10 09:00 | 73.5062 | FALSE | FALSE | -1.1438 | -1.5806 | 0.014874 | 0.020239 | 0.2826 | 2025-12-10 11:31 | 2025-12-10 09:00 | upper | TRUE | 2 | 72.3624 | FALSE | FALSE | 0.2511 | 2.0527 | 72.9269 | 1 | 0.2826 | 0.01413 | 0.17092 | 1.5708 | 0.28223 | Extreme triggered | 73.4913 | 2.0527 | Day | 202512 | 2025-12-10 | 2.0527
2025-12-10 09:15 | 73.7888 | FALSE | FALSE | -1.5068 | -2.0846 | 0.16053 | 0.21803 | 0.2826 |  | 2025-12-10 09:00 | upper | TRUE | 2 | 72.282 | FALSE | FALSE | 0.3366 | 2.2648 | 72.9551 | 2 | 0.2826 | 0.02826 | 0.18107 | 1.4047 | 0.33657 | Extreme/elevated | 73.6283 | 2.477 | Day | 202512 | 2025-12-10 | 2.477
2025-12-10 09:30 | 73.5062 | FALSE | FALSE | -1.2448 | -1.7226 | -0.1709 | -0.23195 | -0.2826 |  | 2025-12-10 09:00 | none | FALSE | 2 | 72.2614 | FALSE | FALSE | 0.3297 | 2.0156 | 72.9693 | 3 | -0.2826 | 0.01413 | 0.19396 | -1.5299 | 0.35392 | Persistent | 73.6771 | 1.5171 | Day | 202512 | 2025-12-10 | 1.5171
2025-12-10 09:44 | 73.5062 | FALSE | FALSE | -1.2626 | -1.7477 | -0.21697 | -0.2943 | 0 |  | 2025-12-10 09:00 | none | FALSE | 2 | 72.2436 | FALSE | FALSE | 0.3799 | 1.8651 | 72.9834 | 4 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.36989 | Persistent | 73.7232 | 1.4134 | Day | 202512 | 2025-12-10 | 1.4134
2025-12-10 09:59 | 73.5062 | FALSE | FALSE | -1.2698 | -1.7579 | -0.28074 | -0.38047 | 0 |  | 2025-12-10 09:00 | none | FALSE | 2 | 72.2364 | FALSE | FALSE | 0.4279 | 1.7472 | 73.0117 | 5 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.38764 | Persistent | 73.7869 | 1.2758 | Day | 202512 | 2025-12-10 | 1.2758
2025-12-10 10:14 | 73.5062 | FALSE | FALSE | -1.2714 | -1.76 | -0.33879 | -0.45878 | 0 |  | 2025-12-10 09:00 | none | FALSE | 1 | 72.2348 | FALSE | FALSE | 0.4487 | 1.6491 | 73.0399 | 6 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.40254 | Persistent | 73.845 | 1.1584 | Day | 202512 | 2025-12-10 | 1.1584
2025-12-10 10:30 | 73.7888 | FALSE | TRUE | -1.5763 | -2.1829 | -0.16332 | -0.22085 | 0.2826 |  | 2025-12-10 09:00 | none | FALSE | 0 | 72.2125 | FALSE | FALSE | 0.5083 | 1.6455 | 73.0823 | 7 | 0.2826 | 0.04239 | 0.18957 | 1.2671 | 0.43491 | Confirmed/Materialized Shift | 73.9521 | 1.6245 | Day | 202512 | 2025-12-10 | 1.6245
2025-12-10 10:43 | 74.0714 | FALSE | TRUE | -1.9046 | -2.6392 | -0.039481 | -0.053273 | 0.2826 |  | 2025-12-10 09:00 | none | FALSE | 0 | 72.1668 | FALSE | FALSE | 0.5279 | 1.6797 | 73.1388 | 8 | 0.2826 | 0.05652 | 0.19665 | 1.1497 | 0.48603 | Confirmed/Materialized Shift | 74.1109 | 1.9188 | Day | 202512 | 2025-12-10 | 1.9188
2025-12-10 10:44 | 74.0714 | FALSE | TRUE | -1.9279 | -2.6723 | -0.17575 | -0.23671 | 0 |  | 2025-12-10 09:00 | none | FALSE | 0 | 72.1435 | FALSE | FALSE | 0.5111 | 1.6782 | 73.1953 | 9 | 0 | 0.05652 | 0.19665 | -0.28742 | 0.52591 | Confirmed/Materialized Shift | 74.2472 | 1.6658 | Day | 202512 | 2025-12-10 | 1.6658
2025-12-10 10:46 | 73.7888 | FALSE | TRUE | -1.5888 | -2.2005 | -0.51487 | -0.69293 | -0.2826 |  | 2025-12-10 09:00 | none | FALSE | 0 | 72.2 | FALSE | FALSE | 0.4681 | 1.6124 | 73.2519 | 10 | -0.2826 | 0.05652 | 0.19665 | -1.7245 | 0.52591 | Confirmed/Materialized Shift | 74.3037 | 1.021 | Day | 202512 | 2025-12-10 | 1.021
2025-12-10 11:01 | 74.0714 | FALSE | TRUE | -1.8225 | -2.5225 | -0.32468 | -0.43642 | 0.2826 |  | 2025-12-10 09:00 | none | FALSE | 0 | 72.2489 | FALSE | FALSE | 0.493 | 1.5927 | 73.3225 | 11 | 0.2826 | 0.07065 | 0.20244 | 1.047 | 0.53678 | Confirmed/Materialized Shift | 74.3961 | 1.3951 | Day | 202512 | 2025-12-10 | 1.3951
2025-12-10 11:16 | 74.0714 | FALSE | TRUE | -1.7538 | -2.4251 | -0.39728 | -0.53349 | 0 |  | 2025-12-10 09:00 | none | FALSE | 0 | 72.3176 | FALSE | FALSE | 0.4841 | 1.5651 | 73.3932 | 12 | 0 | 0.07065 | 0.20244 | -0.34899 | 0.53776 | Confirmed/Materialized Shift | 74.4687 | 1.2612 | Day | 202512 | 2025-12-10 | 1.2612
2025-12-10 11:31 | 73.7888 | FALSE | FALSE | -1.3699 | -1.8917 | -0.6917 | -0.9287 | -0.2826 |  |  | none | FALSE | 0 | 72.4189 | FALSE | FALSE | 0.0439 |  | 73.4497 | 0 | -0.2826 | 0.05652 | 0.21697 | -1.563 | 0.51541 | Persistence ends | 74.4805 | 0.65796 | Day | 202512 | 2025-12-10 | 0.65796
2025-12-10 11:44 | 73.5062 | FALSE | FALSE | -0.97532 | -1.3447 | -0.94706 | -1.272 | -0.2826 |  |  | none | FALSE | 0 | 72.5309 | FALSE | FALSE | 0.002 |  | 73.4921 | 0 | -0.2826 | 0.04239 | 0.22968 | -1.415 | 0.48059 | Normal | 74.4533 | 0.029401 | Day | 202512 | 2025-12-10 | 0.029401
2025-12-10 11:59 | 73.2236 | FALSE | FALSE | -0.50717 | -0.69746 | -1.1289 | -1.5183 | -0.2826 |  |  | none | FALSE | 0 | 72.7164 | FALSE | FALSE | 0.0507 |  | 73.5345 | 0 | -0.2826 | 0.04239 | 0.22968 | -1.415 | 0.40901 | Normal | 74.3525 | -0.76003 | Day | 202512 | 2025-12-10 | 0.76003
2025-12-10 12:14 | 73.2236 | FALSE | FALSE | -0.38515 | -0.52878 | -1.0634 | -1.4315 | 0 |  |  | none | FALSE | 0 | 72.8384 | FALSE | FALSE | 0.0624 |  | 73.5627 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.36214 | Normal | 74.287 | -0.93644 | Day | 202512 | 2025-12-10 | 0.93644
2025-12-10 12:29 | 73.2236 | FALSE | FALSE | -0.32981 | -0.45245 | -1.0363 | -1.3955 | 0 |  |  | none | FALSE | 0 | 72.8938 | FALSE | FALSE | 0.069 |  | 73.5768 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.34153 | Normal | 74.2599 | -1.0343 | Day | 202512 | 2025-12-10 | 1.0343
2025-12-10 12:43 | 73.2236 | FALSE | FALSE | -0.27049 | -0.37077 | -1.0053 | -1.3543 | 0 |  |  | none | FALSE | 0 | 72.9531 | FALSE | FALSE | 0.0768 |  | 73.591 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.31894 | Normal | 74.2289 | -1.1519 | Day | 202512 | 2025-12-10 | 1.1519
2025-12-10 12:58 | 73.2236 | FALSE | FALSE | -0.27049 | -0.37077 | -1.0053 | -1.3543 | 0 |  |  | none | FALSE | 0 | 72.9531 | FALSE | FALSE | 0.0768 |  | 73.591 | 0 | 0 | 0 | 0.20502 | 0 | 0.31894 | Normal | 74.2289 | -1.1519 | Day | 202512 | 2025-12-10 | 1.1519
2025-12-10 13:14 | 73.2236 | FALSE | FALSE | -0.27049 | -0.37077 | -1.0053 | -1.3543 | 0 |  |  | none | FALSE | 0 | 72.9531 | FALSE | FALSE | 0.0768 |  | 73.591 | 0 | 0 | 0 | 0.20502 | 0 | 0.31894 | Normal | 74.2289 | -1.1519 | Day | 202512 | 2025-12-10 | 1.1519
2025-12-10 13:29 | 73.2236 | FALSE | FALSE | -0.30473 | -0.41791 | -1.0112 | -1.3622 | 0 |  |  | none | FALSE | 0 | 72.9189 | FALSE | FALSE | 0.0716 |  | 73.5768 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.32899 | Normal | 74.2348 | -1.0737 | Day | 202512 | 2025-12-10 | 1.0737
2025-12-10 13:43 | 73.2236 | FALSE | FALSE | -0.34313 | -0.47082 | -0.99311 | -1.3381 | 0 |  |  | none | FALSE | 0 | 72.8805 | FALSE | FALSE | 0.0649 |  | 73.5486 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.33406 | Normal | 74.2167 | -0.97284 | Day | 202512 | 2025-12-10 | 0.97284
2025-12-10 13:58 | 73.5062 | FALSE | FALSE | -0.62573 | -0.85858 | -0.71051 | -0.95735 | 0.2826 |  |  | none | FALSE | 0 | 72.8805 | FALSE | FALSE | 0.0085 |  | 73.5486 | 0 | 0.2826 | 0 | 0.18338 | 1.5411 | 0.33406 | Normal | 74.2167 | -0.12689 | Day | 202512 | 2025-12-10 | 0.12689
2025-12-10 14:13 | 73.2236 | FALSE | FALSE | -0.37281 | -0.51175 | -0.99453 | -1.34 | -0.2826 |  |  | none | FALSE | 0 | 72.8508 | FALSE | FALSE | 0.0606 |  | 73.5345 | 0 | -0.2826 | -0.01413 | 0.19396 | -1.3842 | 0.34184 | Normal | 74.2181 | -0.90938 | Day | 202512 | 2025-12-10 | 0.90938
2025-12-10 14:28 | 73.2236 | FALSE | FALSE | -0.40094 | -0.55057 | -0.9944 | -1.3398 | 0 |  |  | none | FALSE | 0 | 72.8227 | FALSE | FALSE | 0.0567 |  | 73.5203 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.34883 | Normal | 74.218 | -0.85063 | Day | 202512 | 2025-12-10 | 0.85063
2025-12-10 14:43 | 73.2236 | FALSE | FALSE | -0.42761 | -0.58741 | -0.99281 | -1.3377 | 0 |  |  | none | FALSE | 0 | 72.796 | FALSE | FALSE | 0.0531 |  | 73.5062 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.3551 | Normal | 74.2164 | -0.79582 | Day | 202512 | 2025-12-10 | 0.79582
2025-12-10 14:58 | 73.2236 | FALSE | FALSE | -0.4535 | -0.62319 | -0.96218 | -1.297 | 0 |  |  | none | FALSE | 0 | 72.7701 | FALSE | FALSE | 0.0479 |  | 73.4779 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.35392 | Normal | 74.1858 | -0.71864 | Day | 202512 | 2025-12-10 | 0.71864
2025-12-10 15:13 | 73.2236 | FALSE | FALSE | -0.44603 | -0.61287 | -0.86993 | -1.1741 | 0 |  |  | none | FALSE | 0 | 72.7776 | FALSE | FALSE | 0.0429 |  | 73.4356 | 0 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.32899 | Normal | 74.0935 | -0.64424 | Day | 202512 | 2025-12-10 | 0.64424
2025-12-10 15:28 | 73.2236 | FALSE | FALSE | -0.42181 | -0.57939 | -0.76093 | -1.0285 | 0 |  |  | none | FALSE | 0 | 72.8018 | FALSE | FALSE | 0.0382 |  | 73.3932 | 0 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.29568 | Normal | 73.9845 | -0.57345 | Day | 202512 | 2025-12-10 | 0.57345
2025-12-10 15:43 | 73.2236 | FALSE | FALSE | -0.4239 | -0.58228 | -0.7065 | -0.95563 | 0 |  |  | none | FALSE | 0 | 72.7997 | FALSE | FALSE | 0.0333 |  | 73.3649 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.2826 | Normal | 73.9301 | -0.5 | Day | 202512 | 2025-12-10 | 0.5
2025-12-10 15:58 | 73.2236 | FALSE | FALSE | -0.36044 | -0.49469 | -0.55826 | -0.75664 | 0 |  |  | none | FALSE | 0 | 72.8632 | FALSE | FALSE | 0.0287 |  | 73.3225 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.22968 | Normal | 73.7819 | -0.43065 | Day | 202512 | 2025-12-10 | 0.43065
2025-12-10 16:13 | 73.2236 | FALSE | FALSE | -0.23916 | -0.32769 | -0.3522 | -0.47869 | 0 |  |  | none | FALSE | 0 | 72.9844 | FALSE | FALSE | 0.0255 |  | 73.2801 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.14784 | Normal | 73.5758 | -0.3823 | Day | 202512 | 2025-12-10 | 0.3823
2025-12-10 16:28 | 72.941 | FALSE | FALSE | 0.074022 | 0.10138 | -0.51944 | -0.7071 | -0.2826 | 2025-12-10 18:30 | 2025-12-10 16:28 | lower | TRUE | 0 | 73.015 | FALSE | FALSE | 0.2348 | 2.6647 | 73.2377 | 1 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.11135 | Extreme triggered | 73.4604 | -2.6647 | Day | 202512 | 2025-12-10 | 2.6647
2025-12-10 16:42 | 72.941 | FALSE | FALSE | 0.045762 | 0.062699 | -0.49118 | -0.66889 | 0 |  | 2025-12-10 16:28 | lower | TRUE | 0 | 72.9868 | FALSE | FALSE | 0.275 | 2.5378 | 73.2095 | 2 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.11135 | Extreme/elevated | 73.4322 | -2.411 | Day | 202512 | 2025-12-10 | 2.411
2025-12-10 16:57 | 72.6584 | TRUE | FALSE | 0.19096 | 0.26213 | -0.85466 | -1.1626 | -0.2826 |  | 2025-12-10 16:28 | lower | TRUE | 1 | 72.8494 | FALSE | TRUE | 0.4101 | 2.7422 | 73.1812 | 3 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.16593 | Persistent | 73.5131 | -3.1509 | Day | 202512 | 2025-12-10 | 3.1509
2025-12-10 17:12 | 72.3758 | FALSE | FALSE | 0.2744 | 0.3777 | -1.2516 | -1.7 | -0.2826 |  | 2025-12-10 16:28 | lower | TRUE | 1 | 72.6502 | FALSE | TRUE | 0.4654 | 2.8374 | 73.1388 | 4 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.24431 | Persistent | 73.6274 | -3.1232 | Day | 202512 | 2025-12-10 | 3.1232
2025-12-10 17:27 | 72.3758 | FALSE | FALSE | 0.12713 | 0.17535 | -1.3141 | -1.7833 | 0 |  | 2025-12-10 16:28 | lower | TRUE | 1 | 72.5029 | FALSE | TRUE | 0.4762 | 2.7556 | 73.0964 | 5 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.29675 | Persistent | 73.6899 | -2.4284 | Day | 202512 | 2025-12-10 | 2.4284
2025-12-10 17:42 | 72.095 | FALSE | FALSE | 0.20571 | 0.28452 | -1.6843 | -2.2829 | -0.2808 |  | 2025-12-10 16:28 | lower | TRUE | 1 | 72.3007 | FALSE | TRUE | 0.5419 | 2.7224 | 73.04 | 6 | -0.2808 | -0.05643 | 0.1477 | -1.5191 | 0.36965 | Persistent | 73.7793 | -2.5565 | Night | 202512 | 2025-12-10 | 2.5565
2025-12-10 17:57 | 72.095 | FALSE | TRUE | 0.043553 | 0.060374 | -1.7336 | -2.3481 | 0 |  | 2025-12-10 16:28 | lower | TRUE | 1 | 72.1386 | FALSE | TRUE | 0.5688 | 2.634 | 72.9836 | 7 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.42251 | Confirmed/Materialized Shift | 73.8286 | -2.1031 | Night | 202512 | 2025-12-10 | 2.1031
2025-12-10 18:12 | 72.095 | FALSE | TRUE | -0.092381 | -0.1283 | -1.7567 | -2.3786 | 0 |  | 2025-12-10 16:28 | none | FALSE | 1 | 72.0026 | FALSE | FALSE | 0.5486 | 2.5297 | 72.9271 | 8 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.46226 | Confirmed/Materialized Shift | 73.8517 | -1.8002 | Night | 202512 | 2025-12-10 | 1.8002
2025-12-10 18:27 | 72.3758 | FALSE | TRUE | -0.43586 | -0.60587 | -1.4538 | -1.9691 | 0.2808 |  | 2025-12-10 16:28 | none | FALSE | 1 | 71.9399 | FALSE | FALSE | 0.5004 | 2.3684 | 72.8847 | 9 | 0.2808 | -0.04239 | 0.1656 | 1.9516 | 0.4724 | Confirmed/Materialized Shift | 73.8296 | -1.0774 | Night | 202512 | 2025-12-10 | 1.0774
2025-12-10 18:30 | 72.3758 | FALSE | FALSE | -0.49024 | -0.68197 | -1.4234 | -1.9287 | 0 |  |  | none | FALSE | 1 | 71.8856 | FALSE | FALSE | 0.0936 |  | 72.8424 | 0 | 0 | -0.04239 | 0.1656 | 0.25597 | 0.4784 | Persistence ends | 73.7992 | -0.97525 | Night | 202512 | 2025-12-10 | 0.97525
2025-12-10 18:31 | 72.3758 | FALSE | FALSE | -0.51465 | -0.71618 | -1.3347 | -1.8108 | 0 |  |  | none | FALSE | 1 | 71.8611 | FALSE | FALSE | 0.0877 |  | 72.7858 | 0 | 0 | -0.05652 | 0.14748 | 0.38324 | 0.46235 | Normal | 73.7105 | -0.88687 | Night | 202512 | 2025-12-10 | 0.88687
2025-12-10 18:46 | 73.2236 | TRUE | FALSE | -1.3625 | -1.896 | -0.48693 | -0.6606 | 0.8478 |  |  | none | FALSE | 2 | 71.8611 | TRUE | FALSE | 0.1203 |  | 72.7858 | 0 | 0.8478 | 0 | 0.24236 | 3.4981 | 0.46235 | Normal | 73.7105 | 0.94682 | Night | 202512 | 2025-12-10 | 0.94682
2025-12-10 19:01 | 73.5062 | FALSE | FALSE | -1.667 | -2.3205 | -0.25456 | -0.34512 | 0.2826 |  |  | none | FALSE | 1 | 71.8392 | FALSE | FALSE | 0.1266 |  | 72.8 | 0 | 0.2826 | 0.01413 | 0.25046 | 1.0719 | 0.4804 | Normal | 73.7608 | 1.4701 | Night | 202512 | 2025-12-10 | 1.4701
2025-12-10 19:16 | 73.5062 | FALSE | FALSE | -1.6868 | -2.3487 | -0.30264 | -0.41003 | 0 |  |  | none | FALSE | 1 | 71.8194 | FALSE | FALSE | 0.1213 |  | 72.8141 | 0 | 0 | 0.01413 | 0.25046 | -0.056415 | 0.49737 | Normal | 73.8088 | 1.3915 | Night | 202512 | 2025-12-10 | 1.3915
2025-12-10 19:30 | 73.7888 | FALSE | FALSE | -2.0192 | -2.8135 | -0.12633 | -0.17092 | 0.2826 |  |  | none | FALSE | 1 | 71.7696 | FALSE | FALSE | 0.1462 |  | 72.8424 | 0 | 0.2826 | 0.02826 | 0.2575 | 0.98773 | 0.53639 | Normal | 73.9151 | 1.7645 | Night | 202512 | 2025-12-10 | 1.7645
2025-12-10 19:45 | 73.7888 | FALSE | FALSE | -2.0607 | -2.873 | -0.22439 | -0.30317 | 0 |  |  | none | FALSE | 1 | 71.7281 | FALSE | FALSE | 0.1357 |  | 72.8706 | 0 | 0 | 0.02826 | 0.2575 | -0.10975 | 0.57128 | Normal | 74.0132 | 1.6072 | Night | 202512 | 2025-12-10 | 1.6072
2025-12-10 20:00 | 73.7888 | FALSE | FALSE | -2.0955 | -2.9228 | -0.31563 | -0.42593 | 0 |  |  | none | FALSE | 1 | 71.6933 | FALSE | FALSE | 0.127 |  | 72.8989 | 0 | 0 | 0.02826 | 0.2575 | -0.10975 | 0.60278 | Normal | 74.1044 | 1.4764 | Night | 202512 | 2025-12-10 | 1.4764
2025-12-10 20:15 | 73.7888 | FALSE | FALSE | -2.1244 | -2.9644 | -0.40108 | -0.54062 | 0 |  |  | none | FALSE | 1 | 71.6644 | FALSE | FALSE | 0.1196 |  | 72.9271 | 0 | 0 | 0.02826 | 0.2575 | -0.10975 | 0.63137 | Normal | 74.1899 | 1.3647 | Night | 202512 | 2025-12-10 | 1.3647
2025-12-10 20:29 | 73.7888 | FALSE | FALSE | -2.1483 | -2.9987 | -0.4815 | -0.64831 | 0 |  |  | none | FALSE | 1 | 71.6405 | FALSE | FALSE | 0.1131 |  | 72.9554 | 0 | 0 | 0.02826 | 0.2575 | -0.10975 | 0.65745 | Normal | 74.2703 | 1.2676 | Night | 202512 | 2025-12-10 | 1.2676
2025-12-10 20:44 | 74.0714 | FALSE | FALSE | -2.4766 | -3.4592 | -0.32941 | -0.44275 | 0.2826 |  |  | none | FALSE | 1 | 71.5948 | FALSE | FALSE | 0.1306 |  | 72.9978 | 0 | 0.2826 | 0.04239 | 0.26355 | 0.91144 | 0.70151 | Normal | 74.4008 | 1.5304 | Night | 202512 | 2025-12-10 | 1.5304
2025-12-10 20:59 | 74.0714 | FALSE | FALSE | -2.4993 | -3.492 | -0.46513 | -0.62403 | 0 |  |  | none | FALSE | 1 | 71.5721 | FALSE | FALSE | 0.1201 |  | 73.0543 | 0 | 0 | 0.05652 | 0.25255 | -0.22379 | 0.74111 | Normal | 74.5365 | 1.3724 | Night | 202512 | 2025-12-10 | 1.3724
2025-12-10 21:14 | 74.0714 | FALSE | FALSE | -2.5093 | -3.5065 | -0.58818 | -0.78781 | 0 |  |  | none | FALSE | 0 | 71.5621 | FALSE | FALSE | 0.0827 |  | 73.1108 | 0 | 0 | 0.05652 | 0.25255 | -0.22379 | 0.77437 | Normal | 74.6596 | 1.2404 | Night | 202512 | 2025-12-10 | 1.2404
2025-12-10 21:29 | 74.0714 | FALSE | FALSE | -2.4801 | -3.4643 | -0.70029 | -0.93657 | 0 |  |  | none | FALSE | 0 | 71.5913 | FALSE | FALSE | 0.0746 |  | 73.1815 | 0 | 0 | 0.07065 | 0.24018 | -0.29415 | 0.7951 | Normal | 74.7717 | 1.1193 | Night | 202512 | 2025-12-10 | 1.1193
2025-12-10 21:44 | 74.0714 | FALSE | FALSE | -2.3953 | -3.3418 | -0.78501 | -1.0487 | 0 |  |  | none | FALSE | 0 | 71.6761 | FALSE | FALSE | 0.0675 |  | 73.2663 | 0 | 0 | 0.08478 | 0.22622 | -0.37478 | 0.79507 | Normal | 74.8564 | 1.0127 | Night | 202512 | 2025-12-10 | 1.0127
2025-12-10 21:59 | 74.0714 | FALSE | FALSE | -2.2913 | -3.1921 | -0.85058 | -1.1353 | 0 |  |  | none | FALSE | 0 | 71.7801 | FALSE | FALSE | 0.0611 |  | 73.351 | 0 | 0 | 0.08478 | 0.22622 | -0.37478 | 0.78547 | Normal | 74.922 | 0.91711 | Night | 202512 | 2025-12-10 | 0.91711
2025-12-10 22:14 | 74.0714 | FALSE | FALSE | -2.1061 | -2.9265 | -0.86299 | -1.1517 | 0 |  |  | none | FALSE | 0 | 71.9653 | FALSE | FALSE | 0.0558 |  | 73.4499 | 0 | 0 | 0.09882 | 0.2105 | -0.46945 | 0.74227 | Normal | 74.9344 | 0.83735 | Night | 202512 | 2025-12-10 | 0.83735
2025-12-10 22:29 | 73.7888 | FALSE | FALSE | -1.6001 | -2.2166 | -1.0916 | -1.4578 | -0.2826 |  |  | none | FALSE | 0 | 72.1887 | FALSE | FALSE | 0.0252 |  | 73.5345 | 0 | -0.2826 | 0.08469 | 0.22637 | -1.6225 | 0.67294 | Normal | 74.8804 | 0.37782 | Night | 202512 | 2025-12-10 | 0.37782
2025-12-10 22:44 | 73.7888 | FALSE | FALSE | -1.3351 | -1.8427 | -0.99599 | -1.3318 | 0 |  |  | none | FALSE | 0 | 72.4537 | FALSE | FALSE | 0.0194 |  | 73.6192 | 0 | 0 | 0.08469 | 0.22637 | -0.37412 | 0.58278 | Normal | 74.7848 | 0.29095 | Night | 202512 | 2025-12-10 | 0.29095
2025-12-10 22:59 | 73.7888 | FALSE | FALSE | -1.1079 | -1.5243 | -0.91007 | -1.2183 | 0 |  |  | none | FALSE | 0 | 72.6809 | FALSE | FALSE | 0.0131 |  | 73.6899 | 0 | 0 | 0.07065 | 0.22224 | -0.31791 | 0.50449 | Normal | 74.6989 | 0.19606 | Night | 202512 | 2025-12-10 | 0.19606
2025-12-10 23:14 | 73.7888 | FALSE | FALSE | -0.82547 | -1.1313 | -0.76895 | -1.0313 | 0 |  |  | none | FALSE | 0 | 72.9633 | FALSE | FALSE | 0.0047 |  | 73.7605 | 0 | 0 | 0.07065 | 0.22224 | -0.31791 | 0.3986 | Normal | 74.5577 | 0.070897 | Night | 202512 | 2025-12-10 | 0.070897
2025-12-10 23:28 | 73.7888 | FALSE | FALSE | -0.41696 | -0.56829 | -0.50174 | -0.67538 | 0 |  |  | none | FALSE | 0 | 73.3718 | FALSE | FALSE | 0.0123 |  | 73.8312 | 0 | 0 | 0.07065 | 0.22224 | -0.31791 | 0.22968 | Normal | 74.2905 | -0.18456 | Night | 202512 | 2025-12-10 | 0.18456
2025-12-10 23:43 | 73.7888 | FALSE | FALSE | -0.29032 | -0.39501 | -0.43162 | -0.58154 | 0 |  |  | none | FALSE | 0 | 73.4985 | FALSE | FALSE | 0.0261 |  | 73.8594 | 0 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.18049 | Normal | 74.2204 | -0.39144 | Night | 202512 | 2025-12-10 | 0.39144
2025-12-10 23:58 | 73.7888 | FALSE | FALSE | -0.23809 | -0.3237 | -0.40765 | -0.54941 | 0 |  |  | none | FALSE | 0 | 73.5507 | FALSE | FALSE | 0.035 |  | 73.8736 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.16143 | Normal | 74.1964 | -0.52517 | Night | 202512 | 2025-12-10 | 0.52517
2025-12-11 00:14 | 73.5062 | TRUE | FALSE | 0.044515 | 0.060523 | -0.69025 | -0.93029 | -0.2826 | 2025-12-11 08:16 | 2025-12-11 00:14 | lower | TRUE | 1 | 73.5507 | FALSE | FALSE | 0.2374 | 2.2757 | 73.8736 | 1 | -0.2826 | 0 | 0.12967 | -2.1794 | 0.16143 | Extreme triggered | 74.1964 | -2.2757 | Night | 202512 | 2025-12-11 | 2.2757
2025-12-11 00:28 | 73.5062 | FALSE | FALSE | -0.0077242 | -0.010509 | -0.71422 | -0.9623 | 0 |  | 2025-12-11 00:14 | none | FALSE | 1 | 73.4985 | FALSE | FALSE | 0.2733 | 2.1165 | 73.8594 | 2 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.18049 | Extreme/elevated | 74.2204 | -1.9572 | Night | 202512 | 2025-12-11 | 1.9572
2025-12-11 00:43 | 73.5062 | FALSE | FALSE | -0.054176 | -0.073757 | -0.73242 | -0.98657 | 0 |  | 2025-12-11 00:14 | none | FALSE | 1 | 73.452 | FALSE | FALSE | 0.315 | 1.9858 | 73.8453 | 3 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.19665 | Persistent | 74.2386 | -1.7245 | Night | 202512 | 2025-12-11 | 1.7245
2025-12-11 00:58 | 73.5062 | FALSE | FALSE | -0.096174 | -0.13101 | -0.74615 | -1.0049 | 0 |  | 2025-12-11 00:14 | none | FALSE | 1 | 73.41 | FALSE | FALSE | 0.36 | 1.8752 | 73.8312 | 4 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.21058 | Persistent | 74.2524 | -1.5433 | Night | 202512 | 2025-12-11 | 1.5433
2025-12-11 01:13 | 73.5062 | FALSE | FALSE | -0.13456 | -0.18339 | -0.75628 | -1.0184 | 0 |  | 2025-12-11 00:14 | none | FALSE | 1 | 73.3716 | FALSE | FALSE | 0.4073 | 1.7793 | 73.8171 | 5 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.22271 | Persistent | 74.2625 | -1.3958 | Night | 202512 | 2025-12-11 | 1.3958
2025-12-11 01:28 | 73.2236 | TRUE | FALSE | 0.046537 | 0.063514 | -1.0839 | -1.4586 | -0.2826 |  | 2025-12-11 00:14 | lower | TRUE | 2 | 73.2701 | TRUE | TRUE | 0.5453 | 1.846 | 73.7888 | 6 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.25933 | Persistent | 74.3075 | -2.1794 | Night | 202512 | 2025-12-11 | 2.1794
2025-12-11 01:43 | 73.2236 | FALSE | TRUE | -0.035657 | -0.048719 | -1.0813 | -1.4552 | 0 |  | 2025-12-11 00:14 | none | FALSE | 2 | 73.1879 | FALSE | FALSE | 0.582 | 1.8498 | 73.7464 | 7 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27923 | Confirmed/Materialized Shift | 74.3049 | -1.8723 | Night | 202512 | 2025-12-11 | 1.8723
2025-12-11 01:58 | 73.2236 | FALSE | TRUE | -0.10236 | -0.13998 | -1.0632 | -1.4312 | 0 |  | 2025-12-11 00:14 | none | FALSE | 2 | 73.1212 | FALSE | FALSE | 0.5671 | 1.8246 | 73.704 | 8 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.29139 | Confirmed/Materialized Shift | 74.2868 | -1.6487 | Night | 202512 | 2025-12-11 | 1.6487
2025-12-11 02:13 | 72.941 | FALSE | TRUE | 0.058171 | 0.079687 | -1.3548 | -1.8236 | -0.2826 |  | 2025-12-11 00:14 | lower | TRUE | 2 | 72.9992 | FALSE | TRUE | 0.6024 | 1.8641 | 73.6475 | 9 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.32416 | Confirmed/Materialized Shift | 74.2958 | -2.1794 | Night | 202512 | 2025-12-11 | 2.1794
2025-12-11 02:27 | 72.941 | FALSE | TRUE | -0.038593 | -0.052938 | -1.3386 | -1.802 | 0 |  | 2025-12-11 00:14 | none | FALSE | 2 | 72.9024 | FALSE | FALSE | 0.583 | 1.8664 | 73.591 | 10 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.34429 | Confirmed/Materialized Shift | 74.2796 | -1.8879 | Night | 202512 | 2025-12-11 | 1.8879
2025-12-11 02:43 | 72.6584 | FALSE | TRUE | 0.095365 | 0.13108 | -1.6285 | -2.1922 | -0.2826 |  | 2025-12-11 00:14 | lower | TRUE | 1 | 72.7538 | FALSE | TRUE | 0.5785 | 1.9012 | 73.5203 | 11 | -0.2826 | -0.07065 | 0.12555 | -1.6882 | 0.38328 | Confirmed/Materialized Shift | 74.2869 | -2.2488 | Night | 202512 | 2025-12-11 | 2.2488
2025-12-11 02:58 | 72.6584 | FALSE | TRUE | -0.020556 | -0.0283 | -1.6031 | -2.1587 | 0 |  | 2025-12-11 00:14 | none | FALSE | 1 | 72.6378 | FALSE | FALSE | 0.5585 | 1.9052 | 73.4497 | 12 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.40592 | Confirmed/Materialized Shift | 74.2615 | -1.9494 | Night | 202512 | 2025-12-11 | 1.9494
2025-12-11 03:13 | 72.3758 | FALSE | TRUE | 0.10016 | 0.13819 | -1.878 | -2.5292 | -0.2826 |  | 2025-12-11 00:14 | lower | TRUE | 1 | 72.476 | FALSE | TRUE | 0.5769 | 1.9298 | 73.3649 | 13 | -0.2826 | -0.08478 | 0.13287 | -1.4888 | 0.44447 | Confirmed/Materialized Shift | 74.2538 | -2.2253 | Night | 202512 | 2025-12-11 | 2.2253
2025-12-11 03:27 | 72.3758 | FALSE | TRUE | -0.049711 | -0.068732 | -1.8866 | -2.5405 | 0 |  | 2025-12-11 00:14 | none | FALSE | 1 | 72.3261 | FALSE | FALSE | 0.5551 | 1.9275 | 73.2943 | 14 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.48408 | Confirmed/Materialized Shift | 74.2624 | -1.8973 | Night | 202512 | 2025-12-11 | 1.8973
2025-12-11 03:42 | 72.3758 | FALSE | TRUE | -0.17319 | -0.23987 | -1.8688 | -2.5171 | 0 |  | 2025-12-11 00:14 | none | FALSE | 1 | 72.2026 | FALSE | FALSE | 0.5393 | 1.9097 | 73.2236 | 15 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.51049 | Confirmed/Materialized Shift | 74.2446 | -1.6607 | Night | 202512 | 2025-12-11 | 1.6607
2025-12-11 03:57 | 72.3758 | FALSE | TRUE | -0.27426 | -0.38038 | -1.8286 | -2.4642 | 0 |  | 2025-12-11 00:14 | none | FALSE | 0 | 72.1015 | FALSE | FALSE | 0.4986 | 1.8828 | 73.153 | 16 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.52571 | Confirmed/Materialized Shift | 74.2044 | -1.4783 | Night | 202512 | 2025-12-11 | 1.4783
2025-12-11 04:12 | 72.095 | FALSE | TRUE | -0.13389 | -0.18606 | -2.0804 | -2.8047 | -0.2808 |  | 2025-12-11 00:14 | none | FALSE | 0 | 71.9611 | FALSE | FALSE | 0.5172 | 1.8754 | 73.0683 | 17 | -0.2808 | -0.08469 | 0.13273 | -1.4775 | 0.55358 | Confirmed/Materialized Shift | 74.1754 | -1.7581 | Night | 202512 | 2025-12-11 | 1.7581
2025-12-11 04:27 | 72.095 | FALSE | TRUE | -0.24532 | -0.34143 | -2.0225 | -2.7287 | 0 |  | 2025-12-11 00:14 | none | FALSE | 0 | 71.8497 | FALSE | FALSE | 0.5045 | 1.8583 | 72.9836 | 18 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.56694 | Confirmed/Materialized Shift | 74.1175 | -1.5673 | Night | 202512 | 2025-12-11 | 1.5673
2025-12-11 04:42 | 72.095 | FALSE | TRUE | -0.3298 | -0.45955 | -1.9376 | -2.6172 | 0 |  | 2025-12-11 00:14 | none | FALSE | 0 | 71.7652 | FALSE | FALSE | 0.4945 | 1.8352 | 72.8989 | 19 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.56684 | Confirmed/Materialized Shift | 74.0326 | -1.4182 | Night | 202512 | 2025-12-11 | 1.4182
2025-12-11 04:57 | 72.095 | FALSE | TRUE | -0.38731 | -0.54012 | -1.8257 | -2.4698 | 0 |  | 2025-12-11 00:14 | none | FALSE | 0 | 71.7077 | FALSE | FALSE | 0.4867 | 1.8084 | 72.8142 | 20 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.55325 | Confirmed/Materialized Shift | 73.9207 | -1.2999 | Night | 202512 | 2025-12-11 | 1.2999
2025-12-11 05:12 | 71.8124 | FALSE | TRUE | -0.22509 | -0.31443 | -2.0593 | -2.7877 | -0.2826 |  | 2025-12-11 00:14 | none | FALSE | 0 | 71.5873 | FALSE | FALSE | 0.5071 | 1.7987 | 72.7295 | 21 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.5711 | Confirmed/Materialized Shift | 73.8717 | -1.6059 | Night | 202512 | 2025-12-11 | 1.6059
2025-12-11 05:27 | 71.8124 | FALSE | TRUE | -0.31845 | -0.44542 | -1.9833 | -2.6875 | 0 |  | 2025-12-11 00:14 | none | FALSE | 0 | 71.494 | FALSE | FALSE | 0.4964 | 1.7827 | 72.6448 | 22 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.57543 | Confirmed/Materialized Shift | 73.7957 | -1.4466 | Night | 202512 | 2025-12-11 | 1.4466
2025-12-11 05:42 | 71.5298 | FALSE | TRUE | -0.16232 | -0.22744 | -2.1947 | -2.9769 | -0.2826 |  | 2025-12-11 00:14 | none | FALSE | 0 | 71.3675 | FALSE | FALSE | 0.515 | 1.7802 | 72.546 | 23 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.58925 | Confirmed/Materialized Shift | 73.7245 | -1.7245 | Night | 202512 | 2025-12-11 | 1.7245
2025-12-11 05:57 | 71.5298 | FALSE | TRUE | -0.25355 | -0.35573 | -2.0883 | -2.8367 | 0 |  | 2025-12-11 00:14 | none | FALSE | 0 | 71.2762 | FALSE | FALSE | 0.5045 | 1.7713 | 72.4472 | 24 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.58546 | Confirmed/Materialized Shift | 73.6181 | -1.5669 | Night | 202512 | 2025-12-11 | 1.5669
2025-12-11 06:12 | 71.5298 | FALSE | TRUE | -0.30883 | -0.43363 | -1.9459 | -2.6484 | 0 |  | 2025-12-11 00:14 | none | FALSE | 0 | 71.221 | FALSE | FALSE | 0.4968 | 1.7586 | 72.3483 | 25 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.56369 | Confirmed/Materialized Shift | 73.4757 | -1.4521 | Night | 202512 | 2025-12-11 | 1.4521
2025-12-11 06:26 | 71.2472 | FALSE | TRUE | -0.14827 | -0.20854 | -2.1529 | -2.9331 | -0.2826 |  | 2025-12-11 00:14 | none | FALSE | 0 | 71.0989 | FALSE | FALSE | 0.5162 | 1.7579 | 72.2495 | 26 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.5753 | Confirmed/Materialized Shift | 73.4001 | -1.7423 | Night | 202512 | 2025-12-11 | 1.7423
2025-12-11 06:41 | 71.2472 | FALSE | TRUE | -0.23426 | -0.32988 | -2.0413 | -2.7853 | 0 |  | 2025-12-11 00:14 | none | FALSE | 0 | 71.0129 | FALSE | FALSE | 0.5059 | 1.7516 | 72.1507 | 27 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.56888 | Confirmed/Materialized Shift | 73.2885 | -1.5882 | Night | 202512 | 2025-12-11 | 1.5882
2025-12-11 06:56 | 71.2472 | FALSE | TRUE | -0.28293 | -0.3987 | -1.8923 | -2.5873 | 0 |  | 2025-12-11 00:14 | none | FALSE | 0 | 70.9643 | FALSE | FALSE | 0.4986 | 1.7419 | 72.0519 | 28 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.54381 | Confirmed/Materialized Shift | 73.1395 | -1.4797 | Night | 202512 | 2025-12-11 | 1.4797
2025-12-11 07:11 | 70.9646 | FALSE | TRUE | -0.11799 | -0.16655 | -2.0949 | -2.8674 | -0.2826 |  | 2025-12-11 00:14 | none | FALSE | 0 | 70.8466 | FALSE | FALSE | 0.5191 | 1.7435 | 71.9531 | 29 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.55323 | Confirmed/Materialized Shift | 73.0595 | -1.7867 | Day | 202512 | 2025-12-11 | 1.7867
2025-12-11 07:26 | 70.9646 | FALSE | TRUE | -0.19818 | -0.28004 | -1.9775 | -2.711 | 0 |  | 2025-12-11 00:14 | none | FALSE | 0 | 70.7664 | FALSE | FALSE | 0.509 | 1.7399 | 71.8542 | 30 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.54391 | Confirmed/Materialized Shift | 72.9421 | -1.6356 | Day | 202512 | 2025-12-11 | 1.6356
2025-12-11 07:30 | 70.9646 | FALSE | TRUE | -0.283 | -0.40039 | -1.8929 | -2.5981 | 0 |  | 2025-12-11 00:14 | none | FALSE | 0 | 70.6816 | FALSE | FALSE | 0.4987 | 1.7315 | 71.7696 | 31 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.54398 | Confirmed/Materialized Shift | 72.8575 | -1.4798 | Day | 202512 | 2025-12-11 | 1.4798
2025-12-11 07:45 | 70.9646 | FALSE | TRUE | -0.33971 | -0.481 | -1.7802 | -2.4472 | 0 |  | 2025-12-11 00:14 | none | FALSE | 0 | 70.6249 | FALSE | FALSE | 0.4906 | 1.7199 | 71.6849 | 32 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.52999 | Confirmed/Materialized Shift | 72.7448 | -1.359 | Day | 202512 | 2025-12-11 | 1.359
2025-12-11 08:00 | 70.9646 | FALSE | TRUE | -0.40447 | -0.57323 | -1.7039 | -2.3447 | 0 |  | 2025-12-11 00:14 | none | FALSE | 0 | 70.5601 | FALSE | FALSE | 0.4822 | 1.7051 | 71.6143 | 33 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.52709 | Confirmed/Materialized Shift | 72.6685 | -1.2326 | Day | 202512 | 2025-12-11 | 1.2326
2025-12-11 08:16 | 71.2472 | TRUE | FALSE | -0.69141 | -0.97995 | -1.3128 | -1.8092 | 0.2826 |  |  | none | FALSE | 1 | 70.5558 | FALSE | FALSE | 0.0699 |  | 71.5579 | 0 | 0.2826 | -0.05643 | 0.1477 | 2.2954 | 0.50105 | Persistence ends | 72.56 | -0.62006 | Day | 202512 | 2025-12-11 | 0.62006
2025-12-11 08:30 | 71.2472 | FALSE | FALSE | -0.67863 | -0.96166 | -1.1871 | -1.6389 | 0 |  |  | none | FALSE | 1 | 70.5686 | FALSE | FALSE | 0.0649 |  | 71.5015 | 0 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.46644 | Normal | 72.4343 | -0.54509 | Day | 202512 | 2025-12-11 | 0.54509
2025-12-11 08:30 | 71.2472 | FALSE | FALSE | -0.64451 | -0.91287 | -1.0401 | -1.4389 | 0 |  |  | none | FALSE | 1 | 70.6027 | FALSE | FALSE | 0.0599 |  | 71.445 | 0 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.42116 | Normal | 72.2873 | -0.4697 | Day | 202512 | 2025-12-11 | 0.4697
2025-12-11 08:45 | 71.5298 | FALSE | FALSE | -0.89963 | -1.2737 | -0.67355 | -0.93285 | 0.2826 |  |  | none | FALSE | 1 | 70.6302 | FALSE | FALSE | 0.0477 |  | 71.4168 | 0 | 0.2826 | -0.02826 | 0.15614 | 1.9909 | 0.3933 | Normal | 72.2034 | 0.28742 | Day | 202512 | 2025-12-11 | 0.28742
2025-12-11 09:00 | 71.5298 | FALSE | FALSE | -0.86325 | -1.2216 | -0.58065 | -0.80522 | 0 |  |  | none | FALSE | 1 | 70.6666 | FALSE | FALSE | 0.0547 |  | 71.3885 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.36097 | Normal | 72.1104 | 0.39144 | Day | 202512 | 2025-12-11 | 0.39144
2025-12-11 09:15 | 71.5298 | FALSE | FALSE | -0.81529 | -1.1529 | -0.47617 | -0.66129 | 0 |  |  | none | FALSE | 1 | 70.7145 | FALSE | FALSE | 0.0636 |  | 71.3602 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.32287 | Normal | 72.006 | 0.52517 | Day | 202512 | 2025-12-11 | 0.52517
2025-12-11 09:30 | 71.8124 | FALSE | FALSE | -1.0541 | -1.4897 | -0.12151 | -0.16892 | 0.2826 |  |  | none | FALSE | 1 | 70.7583 | FALSE | FALSE | 0.1343 |  | 71.3461 | 0 | 0.2826 | -0.01413 | 0.17092 | 1.7361 | 0.2939 | Normal | 71.9339 | 1.5866 | Day | 202512 | 2025-12-11 | 1.5866
2025-12-11 09:45 | 71.8124 | FALSE | FALSE | -1.0541 | -1.4897 | -0.12151 | -0.16892 | 0 |  |  | none | FALSE | 1 | 70.7583 | FALSE | FALSE | 0.1343 |  | 71.3461 | 0 | 0 | 0 | 0.15881 | 0 | 0.2939 | Normal | 71.9339 | 1.5866 | Day | 202512 | 2025-12-11 | 1.5866
2025-12-11 10:00 | 72.095 | FALSE | FALSE | -1.3805 | -1.9522 | 0.08903 | 0.12364 | 0.2826 | 2025-12-11 12:44 | 2025-12-11 10:00 | upper | TRUE | 1 | 70.7145 | FALSE | FALSE | 0.2374 | 2.2757 | 71.3602 | 1 | 0.2826 | 0.01413 | 0.17092 | 1.5708 | 0.32287 | Extreme triggered | 72.006 | 2.2757 | Day | 202512 | 2025-12-11 | 2.2757
2025-12-11 10:15 | 72.3758 | FALSE | FALSE | -1.761 | -2.4938 | 0.18554 | 0.25701 | 0.2808 |  | 2025-12-11 10:00 | upper | TRUE | 1 | 70.6148 | FALSE | FALSE | 0.3076 | 2.3734 | 71.4025 | 2 | 0.2808 | 0.0423 | 0.16579 | 1.4386 | 0.39386 | Extreme/elevated | 72.1903 | 2.4711 | Day | 202512 | 2025-12-11 | 2.4711
2025-12-11 10:29 | 72.6584 | FALSE | FALSE | -2.1668 | -3.0738 | 0.2321 | 0.32046 | 0.2826 |  | 2025-12-11 10:00 | upper | TRUE | 0 | 70.4916 | FALSE | TRUE | 0.3368 | 2.4089 | 71.459 | 3 | 0.2826 | 0.05643 | 0.17384 | 1.301 | 0.48367 | Persistent | 72.4263 | 2.4799 | Day | 202512 | 2025-12-11 | 2.4799
2025-12-11 10:44 | 72.941 | FALSE | FALSE | -2.5845 | -3.6735 | 0.23839 | 0.3279 | 0.2826 |  | 2025-12-11 10:00 | upper | TRUE | 0 | 70.3565 | FALSE | TRUE | 0.389 | 2.4083 | 71.5295 | 4 | 0.2826 | 0.07056 | 0.18038 | 1.1755 | 0.58654 | Persistent | 72.7026 | 2.4064 | Day | 202512 | 2025-12-11 | 2.4064
2025-12-11 10:59 | 73.2236 | FALSE | FALSE | -2.9818 | -4.245 | 0.20874 | 0.28589 | 0.2826 |  | 2025-12-11 10:00 | upper | TRUE | 0 | 70.2418 | FALSE | TRUE | 0.4391 | 2.3868 | 71.6283 | 5 | 0.2826 | 0.09882 | 0.16582 | 1.1083 | 0.69325 | Persistent | 73.0149 | 2.3011 | Day | 202512 | 2025-12-11 | 2.3011
2025-12-11 11:14 | 73.5062 | FALSE | FALSE | -3.3713 | -4.8069 | 0.15851 | 0.21611 | 0.2826 |  | 2025-12-11 10:00 | upper | TRUE | 0 | 70.1349 | FALSE | TRUE | 0.4893 | 2.3553 | 71.7413 | 6 | 0.2826 | 0.11295 | 0.16897 | 1.004 | 0.80319 | Persistent | 73.3477 | 2.1974 | Day | 202512 | 2025-12-11 | 2.1974
2025-12-11 11:29 | 73.2236 | TRUE | TRUE | -3.1012 | -4.4225 | -0.33423 | -0.45438 | -0.2826 |  | 2025-12-11 10:00 | none | FALSE | 1 | 70.1224 | FALSE | FALSE | 0.536 | 2.2489 | 71.8401 | 7 | -0.2826 | 0.09882 | 0.18948 | -2.013 | 0.85886 | Confirmed/Materialized Shift | 73.5578 | 1.6108 | Day | 202512 | 2025-12-11 | 1.6108
2025-12-11 11:44 | 73.2236 | FALSE | TRUE | -3.0421 | -4.3346 | -0.50102 | -0.67959 | 0 |  | 2025-12-11 10:00 | none | FALSE | 1 | 70.1815 | FALSE | FALSE | 0.5242 | 2.1471 | 71.9531 | 8 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.88578 | Confirmed/Materialized Shift | 73.7246 | 1.4344 | Day | 202512 | 2025-12-11 | 1.4344
2025-12-11 11:59 | 73.2236 | FALSE | TRUE | -2.9517 | -4.2004 | -0.63653 | -0.8618 | 0 |  | 2025-12-11 10:00 | none | FALSE | 1 | 70.2719 | FALSE | FALSE | 0.5146 | 2.0519 | 72.066 | 9 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.89705 | Confirmed/Materialized Shift | 73.8601 | 1.2904 | Day | 202512 | 2025-12-11 | 1.2904
2025-12-11 12:14 | 73.2236 | FALSE | TRUE | -2.8312 | -4.022 | -0.74194 | -1.0031 | 0 |  | 2025-12-11 10:00 | none | FALSE | 1 | 70.3924 | FALSE | FALSE | 0.5065 | 1.9637 | 72.179 | 10 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.89328 | Confirmed/Materialized Shift | 73.9655 | 1.1694 | Day | 202512 | 2025-12-11 | 1.1694
2025-12-11 12:29 | 73.2236 | FALSE | TRUE | -2.6802 | -3.7994 | -0.81685 | -1.1033 | 0 |  | 2025-12-11 10:00 | none | FALSE | 1 | 70.5434 | FALSE | FALSE | 0.4996 | 1.882 | 72.2919 | 11 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.87427 | Confirmed/Materialized Shift | 74.0405 | 1.0657 | Day | 202512 | 2025-12-11 | 1.0657
2025-12-11 12:44 | 73.2236 | FALSE | FALSE | -2.4967 | -3.53 | -0.85921 | -1.1598 | 0 |  |  | none | FALSE | 1 | 70.7269 | FALSE | FALSE | 0.0936 |  | 72.4049 | 0 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.83897 | Persistence ends | 74.0828 | 0.97587 | Day | 202512 | 2025-12-11 | 0.97587
2025-12-11 12:59 | 73.5062 | FALSE | FALSE | -2.6422 | -3.7285 | -0.6654 | -0.89711 | 0.2826 |  |  | none | FALSE | 1 | 70.864 | FALSE | FALSE | 0.1083 |  | 72.5178 | 0 | 0.2826 | 0.11295 | 0.16897 | 1.004 | 0.82689 | Normal | 74.1716 | 1.1953 | Day | 202512 | 2025-12-11 | 1.1953
2025-12-11 13:14 | 73.5062 | FALSE | FALSE | -2.4714 | -3.4791 | -0.72052 | -0.9707 | 0 |  |  | none | FALSE | 1 | 71.0348 | FALSE | FALSE | 0.1017 |  | 72.6308 | 0 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.79797 | Normal | 74.2267 | 1.0971 | Day | 202512 | 2025-12-11 | 1.0971
2025-12-11 13:28 | 73.5062 | FALSE | FALSE | -2.263 | -3.1765 | -0.73808 | -0.99412 | 0 |  |  | none | FALSE | 1 | 71.2432 | FALSE | FALSE | 0.0963 |  | 72.7437 | 0 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.75028 | Normal | 74.2443 | 1.0163 | Day | 202512 | 2025-12-11 | 1.0163
2025-12-11 13:43 | 73.7888 | FALSE | FALSE | -2.3873 | -3.3436 | -0.52309 | -0.70391 | 0.2826 |  |  | none | FALSE | 1 | 71.4015 | FALSE | FALSE | 0.114 |  | 72.8567 | 0 | 0.2826 | 0.11295 | 0.16897 | 1.004 | 0.72761 | Normal | 74.3119 | 1.2811 | Day | 202512 | 2025-12-11 | 1.2811
2025-12-11 13:59 | 73.5062 | TRUE | FALSE | -1.8904 | -2.6396 | -0.78896 | -1.0619 | -0.2826 |  |  | none | FALSE | 1 | 71.6158 | FALSE | FALSE | 0.0834 |  | 72.9555 | 0 | -0.2826 | 0.09882 | 0.18948 | -2.013 | 0.66983 | Normal | 74.2952 | 0.82216 | Day | 202512 | 2025-12-11 | 0.82216
2025-12-11 14:14 | 73.7888 | FALSE | FALSE | -1.9284 | -2.6835 | -0.48764 | -0.65652 | 0.2826 |  |  | none | FALSE | 1 | 71.8604 | FALSE | FALSE | 0.1081 |  | 73.0684 | 0 | 0.2826 | 0.11295 | 0.19224 | 0.88248 | 0.604 | Normal | 74.2764 | 1.1926 | Day | 202512 | 2025-12-11 | 1.1926
2025-12-11 14:28 | 73.7888 | FALSE | FALSE | -1.7148 | -2.3792 | -0.47174 | -0.63525 | 0 |  |  | none | FALSE | 1 | 72.074 | FALSE | FALSE | 0.1044 |  | 73.1673 | 0 | 0 | 0.09882 | 0.18948 | -0.52153 | 0.54664 | Normal | 74.2605 | 1.137 | Day | 202512 | 2025-12-11 | 1.137
2025-12-11 14:43 | 73.7888 | FALSE | FALSE | -1.4441 | -1.9962 | -0.3987 | -0.53743 | 0 |  |  | none | FALSE | 1 | 72.3447 | FALSE | FALSE | 0.1042 |  | 73.2661 | 0 | 0 | 0.09882 | 0.18948 | -0.52153 | 0.46071 | Normal | 74.1875 | 1.1346 | Day | 202512 | 2025-12-11 | 1.1346
2025-12-11 14:56 | 74.0714 | FALSE | FALSE | -1.5163 | -2.0898 | -0.10326 | -0.13922 | 0.2826 |  |  | none | FALSE | 1 | 72.5551 | FALSE | FALSE | 0.1449 |  | 73.3649 | 0 | 0.2826 | 0.09882 | 0.18948 | 0.96991 | 0.40488 | Normal | 74.1747 | 1.745 | Day | 202512 | 2025-12-11 | 1.745
2025-12-11 14:59 | 73.7888 | FALSE | FALSE | -1.0363 | -1.4244 | -0.32981 | -0.44497 | -0.2826 |  |  | none | FALSE | 1 | 72.7525 | FALSE | FALSE | 0.0975 |  | 73.4356 | 0 | -0.2826 | 0.07065 | 0.20244 | -1.745 | 0.34153 | Normal | 74.1186 | 1.0343 | Day | 202512 | 2025-12-11 | 1.0343
2025-12-11 15:14 | 73.2236 | TRUE | FALSE | -0.34759 | -0.47696 | -0.82801 | -1.1182 | -0.5652 |  |  | none | FALSE | 2 | 72.876 | TRUE | FALSE | 0.1116 |  | 73.4638 | 0 | -0.5652 | 0.02826 | 0.24084 | -2.4641 | 0.2939 | Normal | 74.0516 | -0.81732 | Day | 202512 | 2025-12-11 | 0.81732
2025-12-11 15:28 | 73.2236 | FALSE | FALSE | -0.29272 | -0.40137 | -0.8014 | -1.0826 | 0 |  |  | none | FALSE | 2 | 72.9309 | FALSE | FALSE | 0.1191 |  | 73.4779 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.27353 | Normal | 74.025 | -0.92984 | Day | 202512 | 2025-12-11 | 0.92984
2025-12-11 15:43 | 72.6584 | TRUE | FALSE | 0.14036 | 0.19281 | -1.4422 | -1.9463 | -0.5652 | 2025-12-11 16:50 | 2025-12-11 15:43 | lower | TRUE | 3 | 72.7988 | TRUE | FALSE | 0.3049 | 2.4313 | 73.4497 | 1 | -0.5652 | -0.02826 | 0.25771 | -2.0835 | 0.32546 | Extreme triggered | 74.1006 | -2.4313 | Day | 202512 | 2025-12-11 | 2.4313
2025-12-11 15:58 | 72.3758 | FALSE | FALSE | 0.20968 | 0.28887 | -1.825 | -2.4596 | -0.2826 |  | 2025-12-11 15:43 | lower | TRUE | 3 | 72.5855 | FALSE | FALSE | 0.3679 | 2.4752 | 73.3932 | 2 | -0.2826 | -0.05652 | 0.25277 | -0.89443 | 0.40384 | Extreme/elevated | 74.2008 | -2.5192 | Day | 202512 | 2025-12-11 | 2.5192
2025-12-11 16:13 | 72.3758 | FALSE | FALSE | 0.049425 | 0.068243 | -1.9005 | -2.5587 | 0 |  | 2025-12-11 15:43 | lower | TRUE | 2 | 72.4252 | FALSE | TRUE | 0.369 | 2.3524 | 73.3508 | 3 | 0 | -0.04239 | 0.2473 | 0.17141 | 0.46277 | Persistent | 74.2763 | -2.1068 | Day | 202512 | 2025-12-11 | 2.1068
2025-12-11 16:19 | 72.3758 | FALSE | FALSE | -0.090055 | -0.12458 | -1.9552 | -2.6304 | 0 |  | 2025-12-11 15:43 | none | FALSE | 2 | 72.2857 | FALSE | FALSE | 0.4073 | 2.2203 | 73.3084 | 4 | 0 | -0.04239 | 0.2473 | 0.17141 | 0.51132 | Persistent | 74.331 | -1.8239 | Day | 202512 | 2025-12-11 | 1.8239
2025-12-11 16:20 | 72.3758 | FALSE | FALSE | -0.21425 | -0.29691 | -1.9946 | -2.682 | 0 |  | 2025-12-11 15:43 | none | FALSE | 2 | 72.1615 | FALSE | FALSE | 0.4503 | 2.0986 | 73.266 | 5 | 0 | -0.04239 | 0.2473 | 0.17141 | 0.55222 | Persistent | 74.3704 | -1.612 | Day | 202512 | 2025-12-11 | 1.612
2025-12-11 16:35 | 72.6584 | FALSE | FALSE | -0.55811 | -0.77408 | -1.7168 | -2.3083 | 0.2826 |  | 2025-12-11 15:43 | none | FALSE | 2 | 72.1003 | FALSE | FALSE | 0.4679 | 1.9186 | 73.2377 | 6 | 0.2826 | -0.02826 | 0.25771 | 1.2063 | 0.56872 | Persistent | 74.3752 | -1.0187 | Day | 202512 | 2025-12-11 | 1.0187
2025-12-11 16:50 | 72.6584 | FALSE | FALSE | -0.61556 | -0.85444 | -1.7177 | -2.3095 | 0 |  |  | none | FALSE | 2 | 72.0428 | FALSE | FALSE | 0.1201 |  | 73.2095 | 0 | 0 | -0.02826 | 0.25771 | 0.10966 | 0.58332 | Persistence ends | 74.3761 | -0.94472 | Day | 202512 | 2025-12-11 | 0.94472
2025-12-11 17:05 | 72.6584 | FALSE | FALSE | -0.66948 | -0.92998 | -1.7151 | -2.3061 | 0 |  |  | none | FALSE | 2 | 71.9889 | FALSE | FALSE | 0.1156 |  | 73.1812 | 0 | 0 | -0.02826 | 0.25771 | 0.10966 | 0.59615 | Normal | 74.3735 | -0.87698 | Day | 202512 | 2025-12-11 | 0.87698
2025-12-11 17:19 | 72.6584 | FALSE | FALSE | -0.72345 | -1.0057 | -1.6843 | -2.2656 | 0 |  |  | none | FALSE | 1 | 71.935 | FALSE | FALSE | 0.0818 |  | 73.1388 | 0 | 0 | -0.04239 | 0.2473 | 0.17141 | 0.60193 | Normal | 74.3427 | -0.79813 | Day | 202512 | 2025-12-11 | 0.79813
2025-12-11 17:34 | 72.3758 | FALSE | FALSE | -0.53043 | -0.7383 | -1.9434 | -2.615 | -0.2826 |  |  | none | FALSE | 1 | 71.8454 | FALSE | FALSE | 0.1047 |  | 73.0823 | 0 | -0.2826 | -0.05652 | 0.25277 | -0.89443 | 0.61847 | Normal | 74.3192 | -1.1423 | Night | 202512 | 2025-12-11 | 1.1423
2025-12-11 17:49 | 72.3758 | FALSE | FALSE | -0.60851 | -0.8479 | -1.9085 | -2.5691 | 0 |  |  | none | FALSE | 0 | 71.7673 | FALSE | FALSE | 0.0689 |  | 73.0258 | 0 | 0 | -0.05652 | 0.25277 | 0.22361 | 0.62925 | Normal | 74.2843 | -1.0329 | Night | 202512 | 2025-12-11 | 1.0329
2025-12-11 18:04 | 72.3758 | FALSE | FALSE | -0.65726 | -0.91645 | -1.8159 | -2.4476 | 0 |  |  | none | FALSE | 0 | 71.7185 | FALSE | FALSE | 0.0625 |  | 72.9551 | 0 | 0 | -0.07065 | 0.24041 | 0.29388 | 0.6183 | Normal | 74.1917 | -0.93698 | Night | 202512 | 2025-12-11 | 0.93698
2025-12-11 18:19 | 72.095 | FALSE | FALSE | -0.47535 | -0.66371 | -2.0545 | -2.7707 | -0.2808 |  |  | none | FALSE | 0 | 71.6197 | FALSE | FALSE | 0.0832 |  | 72.8846 | 0 | -0.2808 | -0.07056 | 0.24032 | -0.87482 | 0.63246 | Normal | 74.1495 | -1.2484 | Night | 202512 | 2025-12-11 | 1.2484
2025-12-11 18:30 | 72.095 | FALSE | FALSE | -0.53162 | -0.74287 | -1.9414 | -2.6222 | 0 |  |  | none | FALSE | 0 | 71.5634 | FALSE | FALSE | 0.076 |  | 72.7999 | 0 | 0 | -0.08469 | 0.22637 | 0.37412 | 0.61825 | Normal | 74.0364 | -1.1401 | Night | 202512 | 2025-12-11 | 1.1401
2025-12-11 18:31 | 72.095 | FALSE | FALSE | -0.56195 | -0.78558 | -1.8023 | -2.439 | 0 |  |  | none | FALSE | 0 | 71.5331 | FALSE | FALSE | 0.07 |  | 72.7152 | 0 | 0 | -0.08469 | 0.22637 | 0.37412 | 0.59107 | Normal | 73.8973 | -1.0493 | Night | 202512 | 2025-12-11 | 1.0493
2025-12-11 18:46 | 72.941 | TRUE | FALSE | -1.3443 | -1.8776 | -0.80788 | -1.0955 | 0.846 |  |  | none | FALSE | 1 | 71.5967 | FALSE | FALSE | 0.0618 |  | 72.6728 | 0 | 0.846 | -0.04239 | 0.30752 | 2.8889 | 0.53804 | Normal | 73.7489 | 0.49847 | Night | 202512 | 2025-12-11 | 0.49847
2025-12-11 19:01 | 72.941 | FALSE | FALSE | -1.1895 | -1.6578 | -0.54006 | -0.73496 | 0 |  |  | none | FALSE | 1 | 71.7515 | FALSE | FALSE | 0.0786 |  | 72.6163 | 0 | 0 | -0.05652 | 0.29815 | 0.18957 | 0.43239 | Normal | 73.4811 | 0.75099 | Night | 202512 | 2025-12-11 | 0.75099
2025-12-11 19:16 | 72.941 | FALSE | FALSE | -1.0549 | -1.4674 | -0.32067 | -0.43771 | 0 |  |  | none | FALSE | 1 | 71.8861 | FALSE | FALSE | 0.0997 |  | 72.5739 | 0 | 0 | -0.04239 | 0.29354 | 0.14441 | 0.34389 | Normal | 73.2617 | 1.0675 | Night | 202512 | 2025-12-11 | 1.0675
2025-12-11 19:30 | 72.941 | FALSE | FALSE | -1.0229 | -1.4223 | -0.2604 | -0.35574 | 0 |  |  | none | FALSE | 1 | 71.9181 | FALSE | FALSE | 0.1078 |  | 72.5598 | 0 | 0 | -0.01413 | 0.26652 | 0.053017 | 0.32082 | Normal | 73.2014 | 1.1883 | Night | 202512 | 2025-12-11 | 1.1883
2025-12-11 19:45 | 72.941 | FALSE | FALSE | -0.98587 | -1.3701 | -0.19513 | -0.2668 | 0 |  |  | none | FALSE | 1 | 71.9551 | FALSE | FALSE | 0.1178 |  | 72.5456 | 0 | 0 | -0.01413 | 0.26652 | 0.053017 | 0.29525 | Normal | 73.1361 | 1.3391 | Night | 202512 | 2025-12-11 | 1.3391
2025-12-11 20:00 | 72.941 | FALSE | FALSE | -0.99612 | -1.3846 | -0.23364 | -0.31929 | 0 |  |  | none | FALSE | 1 | 71.9449 | FALSE | FALSE | 0.1112 |  | 72.5598 | 0 | 0 | 0.01413 | 0.23285 | -0.060683 | 0.30744 | Normal | 73.1746 | 1.24 | Night | 202512 | 2025-12-11 | 1.24
2025-12-11 20:15 | 72.941 | FALSE | FALSE | -0.984 | -1.3675 | -0.27804 | -0.37974 | 0 |  |  | none | FALSE | 1 | 71.957 | FALSE | FALSE | 0.1032 |  | 72.588 | 0 | 0 | 0.02826 | 0.22223 | -0.12717 | 0.31551 | Normal | 73.219 | 1.1188 | Night | 202512 | 2025-12-11 | 1.1188
2025-12-11 20:29 | 72.941 | FALSE | FALSE | -0.96626 | -1.3425 | -0.31682 | -0.43248 | 0 |  |  | none | FALSE | 1 | 71.9747 | FALSE | FALSE | 0.0961 |  | 72.6163 | 0 | 0 | 0.02826 | 0.22223 | -0.12717 | 0.32077 | Normal | 73.2578 | 1.0123 | Night | 202512 | 2025-12-11 | 1.0123
2025-12-11 20:44 | 72.6584 | FALSE | FALSE | -0.6596 | -0.91613 | -0.60362 | -0.82392 | -0.2826 |  |  | none | FALSE | 1 | 71.9988 | FALSE | FALSE | 0.0345 |  | 72.6304 | 0 | -0.2826 | 0.01413 | 0.23285 | -1.2743 | 0.31581 | Normal | 73.262 | 0.08863 | Night | 202512 | 2025-12-11 | 0.08863
2025-12-11 20:59 | 72.6584 | FALSE | FALSE | -0.63403 | -0.8803 | -0.60631 | -0.82756 | 0 |  |  | none | FALSE | 1 | 72.0244 | FALSE | FALSE | 0.0316 |  | 72.6445 | 0 | 0 | 0.01413 | 0.23285 | -0.060683 | 0.31009 | Normal | 73.2647 | 0.044697 | Night | 202512 | 2025-12-11 | 0.044697
2025-12-11 21:14 | 72.6584 | FALSE | FALSE | -0.63403 | -0.8803 | -0.60631 | -0.82756 | 0 |  |  | none | FALSE | 0 | 72.0244 | FALSE | FALSE | 0.003 |  | 72.6445 | 0 | 0 | 0 | 0.22411 | 0 | 0.31009 | Normal | 73.2647 | 0.044697 | Night | 202512 | 2025-12-11 | 0.044697
2025-12-11 21:29 | 72.6584 | FALSE | FALSE | -0.63403 | -0.8803 | -0.60631 | -0.82756 | 0 |  |  | none | FALSE | 0 | 72.0244 | FALSE | FALSE | 0.003 |  | 72.6445 | 0 | 0 | 0 | 0.22411 | 0 | 0.31009 | Normal | 73.2647 | 0.044697 | Night | 202512 | 2025-12-11 | 0.044697
2025-12-11 21:44 | 72.6584 | FALSE | FALSE | -0.63403 | -0.8803 | -0.60631 | -0.82756 | 0 |  |  | none | FALSE | 0 | 72.0244 | FALSE | FALSE | 0.003 |  | 72.6445 | 0 | 0 | 0 | 0.22411 | 0 | 0.31009 | Normal | 73.2647 | 0.044697 | Night | 202512 | 2025-12-11 | 0.044697
2025-12-11 21:59 | 72.3758 | FALSE | FALSE | -0.377 | -0.52362 | -0.88622 | -1.2097 | -0.2826 |  |  | none | FALSE | 0 | 71.9988 | FALSE | FALSE | 0.0537 |  | 72.6304 | 0 | -0.2826 | -0.01413 | 0.23285 | -1.153 | 0.31581 | Normal | 73.262 | -0.80622 | Night | 202512 | 2025-12-11 | 0.80622
2025-12-11 22:14 | 72.6584 | FALSE | FALSE | -0.63403 | -0.8803 | -0.60631 | -0.82756 | 0.2826 |  |  | none | FALSE | 0 | 72.0244 | FALSE | FALSE | 0.003 |  | 72.6445 | 0 | 0.2826 | 0.01413 | 0.23285 | 1.153 | 0.31009 | Normal | 73.2647 | 0.044697 | Night | 202512 | 2025-12-11 | 0.044697
2025-12-11 22:29 | 72.3758 | FALSE | FALSE | -0.35143 | -0.48793 | -0.88891 | -1.2133 | -0.2826 |  |  | none | FALSE | 0 | 72.0244 | FALSE | FALSE | 0.0578 |  | 72.6445 | 0 | -0.2826 | 0 | 0.24214 | -1.1671 | 0.31009 | Normal | 73.2647 | -0.86666 | Night | 202512 | 2025-12-11 | 0.86666
2025-12-11 22:44 | 72.3758 | FALSE | FALSE | -0.35143 | -0.48793 | -0.88891 | -1.2133 | 0 |  |  | none | FALSE | 0 | 72.0244 | FALSE | FALSE | 0.0578 |  | 72.6445 | 0 | 0 | 0 | 0.24214 | 0 | 0.31009 | Normal | 73.2647 | -0.86666 | Night | 202512 | 2025-12-11 | 0.86666
2025-12-11 22:59 | 72.3758 | FALSE | FALSE | -0.29636 | -0.41116 | -0.86192 | -1.1769 | 0 |  |  | none | FALSE | 0 | 72.0794 | FALSE | FALSE | 0.0651 |  | 72.6586 | 0 | 0 | 0.01404 | 0.23297 | -0.060265 | 0.28957 | Normal | 73.2377 | -0.97654 | Night | 202512 | 2025-12-11 | 0.97654
2025-12-11 23:14 | 72.3758 | FALSE | FALSE | -0.23661 | -0.32799 | -0.83025 | -1.1341 | 0 |  |  | none | FALSE | 0 | 72.1392 | FALSE | FALSE | 0.0742 |  | 72.6726 | 0 | 0 | 0.01404 | 0.23297 | -0.060265 | 0.26671 | Normal | 73.206 | -1.1129 | Night | 202512 | 2025-12-11 | 1.1129
2025-12-11 23:28 | 72.095 | FALSE | FALSE | 0.044192 | 0.061259 | -1.111 | -1.5177 | -0.2808 | 2025-12-12 08:00 | 2025-12-11 23:28 | lower | TRUE | 0 | 72.1392 | FALSE | FALSE | 0.2015 | 2.1657 | 72.6726 | 1 | -0.2808 | 0 | 0.24214 | -1.1597 | 0.26671 | Extreme triggered | 73.206 | -2.1657 | Night | 202512 | 2025-12-11 | 2.1657
2025-12-11 23:44 | 72.095 | FALSE | FALSE | -0.040952 | -0.056835 | -1.1116 | -1.5184 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 72.054 | FALSE | FALSE | 0.2381 | 2.0118 | 72.6303 | 2 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.28814 | Extreme/elevated | 73.2066 | -1.8579 | Night | 202512 | 2025-12-11 | 1.8579
2025-12-11 23:59 | 72.095 | FALSE | FALSE | -0.11077 | -0.15388 | -1.0968 | -1.4985 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 71.9842 | FALSE | FALSE | 0.2803 | 1.8855 | 72.588 | 3 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.3019 | Persistent | 73.1918 | -1.6331 | Night | 202512 | 2025-12-11 | 1.6331
2025-12-12 00:14 | 72.095 | FALSE | FALSE | -0.16732 | -0.23262 | -1.0688 | -1.4608 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 71.9277 | FALSE | FALSE | 0.3258 | 1.7788 | 72.5457 | 4 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.30902 | Persistent | 73.1638 | -1.4585 | Night | 202512 | 2025-12-12 | 1.4585
2025-12-12 00:28 | 71.8124 | FALSE | FALSE | 0.0069025 | 0.009611 | -1.3469 | -1.841 | -0.2826 |  | 2025-12-11 23:28 | lower | TRUE | 0 | 71.8193 | FALSE | TRUE | 0.4204 | 1.8272 | 72.4893 | 5 | -0.2826 | -0.05643 | 0.1477 | -1.5313 | 0.33499 | Persistent | 73.1593 | -2.0206 | Night | 202512 | 2025-12-12 | 2.0206
2025-12-12 00:43 | 71.8124 | FALSE | FALSE | -0.07881 | -0.10986 | -1.3197 | -1.8046 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 71.7336 | FALSE | FALSE | 0.4612 | 1.8184 | 72.4329 | 6 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.34963 | Persistent | 73.1321 | -1.7746 | Night | 202512 | 2025-12-12 | 1.7746
2025-12-12 00:58 | 71.8124 | FALSE | TRUE | -0.14467 | -0.20186 | -1.2727 | -1.7414 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 71.6677 | FALSE | FALSE | 0.5061 | 1.786 | 72.3764 | 7 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.35435 | Confirmed/Materialized Shift | 73.0851 | -1.5917 | Night | 202512 | 2025-12-12 | 1.5917
2025-12-12 01:13 | 71.5298 | FALSE | TRUE | 0.024343 | 0.034021 | -1.5278 | -2.0912 | -0.2826 |  | 2025-12-11 23:28 | lower | TRUE | 0 | 71.5541 | FALSE | TRUE | 0.5377 | 1.8209 | 72.3059 | 8 | -0.2826 | -0.07056 | 0.15534 | -1.365 | 0.37586 | Confirmed/Materialized Shift | 73.0576 | -2.0648 | Night | 202512 | 2025-12-12 | 2.0648
2025-12-12 01:28 | 71.5298 | FALSE | TRUE | -0.059998 | -0.083949 | -1.471 | -2.0151 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 71.4698 | FALSE | FALSE | 0.5229 | 1.8233 | 72.2353 | 9 | 0 | -0.07056 | 0.15534 | 0.45424 | 0.38275 | Confirmed/Materialized Shift | 73.0008 | -1.8432 | Night | 202512 | 2025-12-12 | 1.8432
2025-12-12 01:43 | 71.5298 | FALSE | TRUE | -0.15073 | -0.21117 | -1.4489 | -1.9854 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 71.3791 | FALSE | FALSE | 0.5082 | 1.8033 | 72.1789 | 10 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.39991 | Confirmed/Materialized Shift | 72.9787 | -1.6231 | Night | 202512 | 2025-12-12 | 1.6231
2025-12-12 01:58 | 71.5298 | FALSE | TRUE | -0.22379 | -0.31385 | -1.4091 | -1.9319 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 71.306 | FALSE | FALSE | 0.4968 | 1.7714 | 72.1225 | 11 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.40822 | Confirmed/Materialized Shift | 72.9389 | -1.4518 | Night | 202512 | 2025-12-12 | 1.4518
2025-12-12 02:13 | 71.5298 | FALSE | TRUE | -0.28026 | -0.39335 | -1.3527 | -1.856 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 71.2495 | FALSE | FALSE | 0.4876 | 1.7332 | 72.066 | 12 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.40824 | Confirmed/Materialized Shift | 72.8825 | -1.3135 | Night | 202512 | 2025-12-12 | 1.3135
2025-12-12 02:28 | 71.2472 | FALSE | TRUE | -0.096105 | -0.13507 | -1.5926 | -2.1865 | -0.2826 |  | 2025-12-11 23:28 | none | FALSE | 0 | 71.1511 | FALSE | FALSE | 0.5182 | 1.7362 | 71.9955 | 13 | -0.2826 | -0.07056 | 0.15534 | -1.365 | 0.42218 | Confirmed/Materialized Shift | 72.8398 | -1.7724 | Night | 202512 | 2025-12-12 | 1.7724
2025-12-12 02:43 | 71.2472 | FALSE | TRUE | -0.16926 | -0.23813 | -1.5247 | -2.0951 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 71.0779 | FALSE | FALSE | 0.5067 | 1.7265 | 71.9249 | 14 | 0 | -0.07056 | 0.15534 | 0.45424 | 0.42348 | Confirmed/Materialized Shift | 72.7719 | -1.6003 | Night | 202512 | 2025-12-12 | 1.6003
2025-12-12 02:58 | 71.2472 | FALSE | TRUE | -0.24926 | -0.35108 | -1.4918 | -2.0509 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 70.9979 | FALSE | FALSE | 0.4952 | 1.7066 | 71.8685 | 15 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.43526 | Confirmed/Materialized Shift | 72.739 | -1.4273 | Night | 202512 | 2025-12-12 | 1.4273
2025-12-12 03:13 | 71.2472 | FALSE | TRUE | -0.27799 | -0.39171 | -1.3794 | -1.8993 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 70.9692 | FALSE | FALSE | 0.4886 | 1.683 | 71.7979 | 16 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.41435 | Confirmed/Materialized Shift | 72.6266 | -1.3291 | Night | 202512 | 2025-12-12 | 1.3291
2025-12-12 03:27 | 70.9646 | FALSE | TRUE | -0.098451 | -0.13893 | -1.624 | -2.2372 | -0.2826 |  | 2025-12-11 23:28 | none | FALSE | 0 | 70.8661 | FALSE | FALSE | 0.5181 | 1.6882 | 71.7274 | 17 | -0.2826 | -0.07056 | 0.12539 | -1.6911 | 0.4306 | Confirmed/Materialized Shift | 72.5886 | -1.7714 | Night | 202512 | 2025-12-12 | 1.7714
2025-12-12 03:42 | 70.9646 | FALSE | TRUE | -0.17652 | -0.24937 | -1.5609 | -2.1522 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 70.7881 | FALSE | FALSE | 0.5062 | 1.6829 | 71.6568 | 18 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.43436 | Confirmed/Materialized Shift | 72.5255 | -1.5936 | Night | 202512 | 2025-12-12 | 1.5936
2025-12-12 03:57 | 70.9646 | FALSE | TRUE | -0.23027 | -0.32554 | -1.4735 | -2.0342 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 70.7343 | FALSE | FALSE | 0.4973 | 1.6712 | 71.5862 | 19 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.42595 | Confirmed/Materialized Shift | 72.4381 | -1.4594 | Night | 202512 | 2025-12-12 | 1.4594
2025-12-12 04:12 | 70.682 | FALSE | TRUE | -0.038608 | -0.054653 | -1.6777 | -2.3185 | -0.2826 |  | 2025-12-11 23:28 | none | FALSE | 0 | 70.6434 | FALSE | FALSE | 0.5273 | 1.6831 | 71.5015 | 20 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.42907 | Confirmed/Materialized Shift | 72.3597 | -1.91 | Night | 202512 | 2025-12-12 | 1.91
2025-12-12 04:27 | 70.682 | FALSE | TRUE | -0.13579 | -0.19248 | -1.6336 | -2.2589 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 70.5462 | FALSE | FALSE | 0.5129 | 1.6836 | 71.4309 | 21 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.44234 | Confirmed/Materialized Shift | 72.3156 | -1.693 | Night | 202512 | 2025-12-12 | 1.693
2025-12-12 04:42 | 70.682 | FALSE | TRUE | -0.20881 | -0.2963 | -1.5653 | -2.1666 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 70.4732 | FALSE | FALSE | 0.5019 | 1.6766 | 71.3602 | 22 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.44353 | Confirmed/Materialized Shift | 72.2473 | -1.5292 | Night | 202512 | 2025-12-12 | 1.5292
2025-12-12 04:57 | 70.682 | FALSE | TRUE | -0.25787 | -0.36617 | -1.4731 | -2.0415 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 70.4241 | FALSE | FALSE | 0.4936 | 1.6647 | 71.2896 | 23 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.43273 | Confirmed/Materialized Shift | 72.1551 | -1.4041 | Night | 202512 | 2025-12-12 | 1.4041
2025-12-12 05:12 | 70.3994 | FALSE | TRUE | -0.060054 | -0.085378 | -1.6709 | -2.3184 | -0.2826 |  | 2025-12-11 23:28 | none | FALSE | 0 | 70.3393 | FALSE | FALSE | 0.5241 | 1.6729 | 71.2048 | 24 | -0.2826 | -0.08478 | 0.13287 | -1.4888 | 0.43273 | Confirmed/Materialized Shift | 72.0703 | -1.8612 | Night | 202512 | 2025-12-12 | 1.8612
2025-12-12 05:27 | 70.3994 | FALSE | TRUE | -0.15229 | -0.21679 | -1.6218 | -2.2519 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 70.2471 | FALSE | FALSE | 0.5104 | 1.6722 | 71.1342 | 25 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.44353 | Confirmed/Materialized Shift | 72.0212 | -1.6566 | Night | 202512 | 2025-12-12 | 1.6566
2025-12-12 05:42 | 70.3994 | FALSE | TRUE | -0.22057 | -0.31429 | -1.5488 | -2.1526 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 70.1788 | FALSE | FALSE | 0.5001 | 1.6657 | 71.0635 | 26 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.44234 | Confirmed/Materialized Shift | 71.9482 | -1.5014 | Night | 202512 | 2025-12-12 | 1.5014
2025-12-12 05:57 | 70.3994 | FALSE | TRUE | -0.26469 | -0.3774 | -1.4516 | -2.0203 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 70.1347 | FALSE | FALSE | 0.4922 | 1.6552 | 70.9929 | 27 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.42907 | Confirmed/Materialized Shift | 71.851 | -1.3831 | Night | 202512 | 2025-12-12 | 1.3831
2025-12-12 06:12 | 70.1168 | FALSE | TRUE | -0.098073 | -0.14007 | -1.7089 | -2.3792 | -0.2826 |  | 2025-12-11 23:28 | none | FALSE | 0 | 70.0187 | FALSE | FALSE | 0.5189 | 1.6598 | 70.9222 | 28 | -0.2826 | -0.07065 | 0.12555 | -1.6882 | 0.45174 | Confirmed/Materialized Shift | 71.8257 | -1.7829 | Night | 202512 | 2025-12-12 | 1.7829
2025-12-12 06:26 | 70.1168 | FALSE | TRUE | -0.18942 | -0.27088 | -1.6589 | -2.3113 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 69.9274 | FALSE | FALSE | 0.506 | 1.6574 | 70.8516 | 29 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.46209 | Confirmed/Materialized Shift | 71.7757 | -1.5901 | Night | 202512 | 2025-12-12 | 1.5901
2025-12-12 06:41 | 70.1168 | FALSE | TRUE | -0.25779 | -0.36902 | -1.586 | -2.2119 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 69.859 | FALSE | FALSE | 0.496 | 1.6501 | 70.7809 | 30 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.46095 | Confirmed/Materialized Shift | 71.7028 | -1.4407 | Night | 202512 | 2025-12-12 | 1.4407
2025-12-12 06:56 | 70.1168 | FALSE | TRUE | -0.30302 | -0.43404 | -1.4899 | -2.0807 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 69.8138 | FALSE | FALSE | 0.4883 | 1.6396 | 70.7103 | 31 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.44824 | Confirmed/Materialized Shift | 71.6067 | -1.324 | Night | 202512 | 2025-12-12 | 1.324
2025-12-12 07:11 | 70.1168 | FALSE | TRUE | -0.323 | -0.4628 | -1.3686 | -1.9146 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 69.7938 | FALSE | FALSE | 0.4824 | 1.627 | 70.6396 | 32 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.42291 | Confirmed/Materialized Shift | 71.4854 | -1.2362 | Day | 202512 | 2025-12-12 | 1.2362
2025-12-12 07:26 | 69.836 | FALSE | TRUE | -0.13452 | -0.19299 | -1.6006 | -2.2406 | -0.2808 |  | 2025-12-11 23:28 | none | FALSE | 0 | 69.7015 | FALSE | FALSE | 0.5127 | 1.6289 | 70.5691 | 33 | -0.2808 | -0.07056 | 0.12539 | -1.6767 | 0.43378 | Confirmed/Materialized Shift | 71.4366 | -1.6899 | Day | 202512 | 2025-12-12 | 1.6899
2025-12-12 07:30 | 69.836 | FALSE | TRUE | -0.20239 | -0.29065 | -1.5274 | -2.1403 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 69.6336 | FALSE | FALSE | 0.5021 | 1.6261 | 70.4985 | 34 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.43244 | Confirmed/Materialized Shift | 71.3634 | -1.532 | Day | 202512 | 2025-12-12 | 1.532
2025-12-12 07:45 | 69.836 | FALSE | TRUE | -0.24559 | -0.35291 | -1.4295 | -2.0058 | 0 |  | 2025-12-11 23:28 | none | FALSE | 0 | 69.5904 | FALSE | FALSE | 0.4942 | 1.62 | 70.4279 | 35 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.41876 | Confirmed/Materialized Shift | 71.2655 | -1.4135 | Day | 202512 | 2025-12-12 | 1.4135
2025-12-12 08:00 | 70.1168 | TRUE | FALSE | -0.49843 | -0.71594 | -1.0076 | -1.4167 | 0.2808 |  |  | none | FALSE | 1 | 69.6184 | FALSE | FALSE | 0.0737 |  | 70.3714 | 0 | 0.2808 | -0.05652 | 0.14748 | 2.2872 | 0.37652 | Persistence ends | 71.1244 | -0.67622 | Day | 202512 | 2025-12-12 | 0.67622
2025-12-12 08:15 | 70.1168 | FALSE | FALSE | -0.49423 | -0.70987 | -0.91867 | -1.2933 | 0 |  |  | none | FALSE | 1 | 69.6226 | FALSE | FALSE | 0.0686 |  | 70.329 | 0 | 0 | -0.04239 | 0.13791 | 0.30738 | 0.35322 | Normal | 71.0355 | -0.60081 | Day | 202512 | 2025-12-12 | 0.60081
2025-12-12 08:30 | 70.3994 | FALSE | FALSE | -0.74028 | -1.0627 | -0.543 | -0.76541 | 0.2826 |  |  | none | FALSE | 1 | 69.6591 | FALSE | FALSE | 0.0491 |  | 70.3008 | 0 | 0.2826 | -0.02826 | 0.1558 | 1.9953 | 0.32082 | Normal | 70.9424 | 0.30746 | Day | 202512 | 2025-12-12 | 0.30746
2025-12-12 08:30 | 70.3994 | FALSE | FALSE | -0.69047 | -0.99051 | -0.43667 | -0.61646 | 0 |  |  | none | FALSE | 1 | 69.7089 | FALSE | FALSE | 0.0586 |  | 70.2725 | 0 | 0 | -0.02826 | 0.1558 | 0.18139 | 0.28179 | Normal | 70.8361 | 0.45034 | Day | 202512 | 2025-12-12 | 0.45034
2025-12-12 08:45 | 70.682 | FALSE | FALSE | -0.97307 | -1.3959 | -0.15407 | -0.21751 | 0.2826 |  |  | none | FALSE | 1 | 69.7089 | FALSE | FALSE | 0.1255 |  | 70.2725 | 0 | 0.2826 | 0 | 0.15847 | 1.7833 | 0.28179 | Normal | 70.8361 | 1.4532 | Day | 202512 | 2025-12-12 | 1.4532
2025-12-12 09:00 | 70.682 | FALSE | FALSE | -0.97307 | -1.3959 | -0.15407 | -0.21751 | 0 |  |  | none | FALSE | 1 | 69.7089 | FALSE | FALSE | 0.1255 |  | 70.2725 | 0 | 0 | 0 | 0.15847 | 0 | 0.28179 | Normal | 70.8361 | 1.4532 | Day | 202512 | 2025-12-12 | 1.4532
2025-12-12 09:15 | 70.9646 | FALSE | FALSE | -1.2963 | -1.8607 | 0.059654 | 0.084132 | 0.2826 | 2025-12-12 13:14 | 2025-12-12 09:15 | upper | TRUE | 1 | 69.6683 | FALSE | FALSE | 0.2319 | 2.193 | 70.2866 | 1 | 0.2826 | 0.01413 | 0.17061 | 1.5736 | 0.30916 | Extreme triggered | 70.9049 | 2.193 | Day | 202512 | 2025-12-12 | 2.193
2025-12-12 09:30 | 70.9646 | FALSE | FALSE | -1.3312 | -1.9117 | -0.0034923 | -0.0049209 | 0 |  | 2025-12-12 09:15 | none | FALSE | 1 | 69.6334 | FALSE | FALSE | 0.2755 | 2.0912 | 70.3008 | 2 | 0 | 0.01413 | 0.17061 | -0.082823 | 0.33367 | Extreme/elevated | 70.9681 | 1.9895 | Day | 202512 | 2025-12-12 | 1.9895
2025-12-12 09:45 | 71.5298 | TRUE | FALSE | -2.0373 | -2.9317 | 0.30774 | 0.43209 | 0.5652 |  | 2025-12-12 09:15 | upper | TRUE | 2 | 69.4925 | TRUE | TRUE | 0.4094 | 2.2981 | 70.3573 | 3 | 0.5652 | 0.05652 | 0.19638 | 2.5903 | 0.43239 | Persistent | 71.2221 | 2.7117 | Day | 202512 | 2025-12-12 | 2.7117
2025-12-12 10:00 | 71.8124 | FALSE | FALSE | -2.4672 | -3.5578 | 0.30178 | 0.42201 | 0.2826 |  | 2025-12-12 09:15 | upper | TRUE | 2 | 69.3452 | FALSE | TRUE | 0.4562 | 2.3629 | 70.4279 | 4 | 0.2826 | 0.07065 | 0.20218 | 1.0483 | 0.54134 | Persistent | 71.5106 | 2.5575 | Day | 202512 | 2025-12-12 | 2.5575
2025-12-12 10:15 | 72.3758 | TRUE | FALSE | -3.2382 | -4.6837 | 0.45991 | 0.63951 | 0.5634 |  | 2025-12-12 09:15 | upper | TRUE | 2 | 69.1376 | TRUE | TRUE | 0.5203 | 2.4228 | 70.5268 | 5 | 0.5634 | 0.09882 | 0.22925 | 2.0265 | 0.69457 | Persistent | 71.9159 | 2.6622 | Day | 202512 | 2025-12-12 | 2.6622
2025-12-12 10:29 | 72.6584 | FALSE | FALSE | -3.7007 | -5.3667 | 0.33668 | 0.46553 | 0.2826 |  | 2025-12-12 09:15 | upper | TRUE | 2 | 68.9577 | FALSE | TRUE | 0.56 | 2.419 | 70.6397 | 6 | 0.2826 | 0.11295 | 0.23154 | 0.73271 | 0.84101 | Persistent | 72.3217 | 2.4003 | Day | 202512 | 2025-12-12 | 2.4003
2025-12-12 10:44 | 72.941 | FALSE | TRUE | -4.1101 | -5.9713 | 0.21006 | 0.28882 | 0.2826 |  | 2025-12-12 09:15 | upper | TRUE | 2 | 68.8309 | FALSE | TRUE | 0.6048 | 2.3899 | 70.7809 | 7 | 0.2826 | 0.14121 | 0.21459 | 0.65888 | 0.97501 | Confirmed/Materialized Shift | 72.7309 | 2.2154 | Day | 202512 | 2025-12-12 | 2.2154
2025-12-12 10:59 | 73.2236 | FALSE | TRUE | -4.4929 | -6.5369 | 0.081831 | 0.11188 | 0.2826 |  | 2025-12-12 09:15 | upper | TRUE | 2 | 68.7307 | FALSE | TRUE | 0.5954 | 2.3505 | 70.9363 | 8 | 0.2826 | 0.15534 | 0.21411 | 0.59437 | 1.1028 | Confirmed/Materialized Shift | 73.1418 | 2.0742 | Day | 202512 | 2025-12-12 | 2.0742
2025-12-12 11:14 | 72.941 | FALSE | TRUE | -4.2056 | -6.1185 | -0.47849 | -0.65172 | -0.2826 |  | 2025-12-12 09:15 | none | FALSE | 2 | 68.7354 | FALSE | FALSE | 0.5632 | 2.2661 | 71.0775 | 9 | -0.2826 | 0.14121 | 0.23336 | -1.8161 | 1.171 | Confirmed/Materialized Shift | 73.4195 | 1.5914 | Day | 202512 | 2025-12-12 | 1.5914
2025-12-12 11:29 | 72.941 | FALSE | TRUE | -4.1591 | -6.0468 | -0.71446 | -0.97001 | 0 |  | 2025-12-12 09:15 | none | FALSE | 2 | 68.7819 | FALSE | FALSE | 0.5514 | 2.1809 | 71.2187 | 10 | 0 | 0.14121 | 0.23336 | -0.60512 | 1.2184 | Confirmed/Materialized Shift | 73.6555 | 1.4136 | Day | 202512 | 2025-12-12 | 1.4136
2025-12-12 11:44 | 73.2236 | FALSE | TRUE | -4.3847 | -6.3696 | -0.68557 | -0.92758 | 0.2826 |  | 2025-12-12 09:15 | none | FALSE | 2 | 68.8389 | FALSE | FALSE | 0.5544 | 2.1153 | 71.374 | 11 | 0.2826 | 0.15534 | 0.23291 | 0.54638 | 1.2676 | Confirmed/Materialized Shift | 73.9092 | 1.4592 | Day | 202512 | 2025-12-12 | 1.4592
2025-12-12 11:59 | 73.2236 | FALSE | TRUE | -4.2353 | -6.1391 | -0.87487 | -1.1807 | 0 |  | 2025-12-12 09:15 | none | FALSE | 2 | 68.9883 | FALSE | FALSE | 0.5448 | 2.0486 | 71.5434 | 12 | 0 | 0.16938 | 0.21284 | -0.79582 | 1.2775 | Confirmed/Materialized Shift | 74.0985 | 1.3152 | Day | 202512 | 2025-12-12 | 1.3152
2025-12-12 12:14 | 73.2236 | FALSE | TRUE | -4.0383 | -5.837 | -1.0167 | -1.3694 | 0 |  | 2025-12-12 09:15 | none | FALSE | 1 | 69.1853 | FALSE | FALSE | 0.5083 | 1.983 | 71.7128 | 13 | 0 | 0.16938 | 0.21284 | -0.79582 | 1.2637 | Confirmed/Materialized Shift | 74.2403 | 1.1955 | Day | 202512 | 2025-12-12 | 1.1955
2025-12-12 12:29 | 73.2236 | FALSE | TRUE | -3.7923 | -5.4619 | -1.1094 | -1.4924 | 0 |  | 2025-12-12 09:15 | none | FALSE | 1 | 69.4313 | FALSE | FALSE | 0.5016 | 1.9195 | 71.8821 | 14 | 0 | 0.16938 | 0.21284 | -0.79582 | 1.2254 | Confirmed/Materialized Shift | 74.333 | 1.0947 | Day | 202512 | 2025-12-12 | 1.0947
2025-12-12 12:44 | 73.5062 | FALSE | TRUE | -3.8597 | -5.5419 | -0.95056 | -1.2767 | 0.2826 |  | 2025-12-12 09:15 | none | FALSE | 0 | 69.6465 | FALSE | FALSE | 0.4806 | 1.8722 | 72.0516 | 15 | 0.2826 | 0.16947 | 0.21289 | 0.53141 | 1.2026 | Confirmed/Materialized Shift | 74.4568 | 1.2096 | Day | 202512 | 2025-12-12 | 1.2096
2025-12-12 12:59 | 73.7888 | FALSE | TRUE | -3.8967 | -5.5752 | -0.78949 | -1.0586 | 0.2826 |  | 2025-12-12 09:15 | none | FALSE | 0 | 69.8921 | FALSE | FALSE | 0.4884 | 1.8381 | 72.2352 | 16 | 0.2826 | 0.1836 | 0.21041 | 0.47051 | 1.1715 | Confirmed/Materialized Shift | 74.5783 | 1.3261 | Day | 202512 | 2025-12-12 | 1.3261
2025-12-12 13:14 | 73.5062 | FALSE | FALSE | -3.3559 | -4.7839 | -1.1247 | -1.507 | -0.2826 |  |  | none | FALSE | 0 | 70.1503 | FALSE | FALSE | 0.0664 |  | 72.3906 | 0 | -0.2826 | 0.15534 | 0.23314 | -1.8784 | 1.1202 | Persistence ends | 74.6309 | 0.99597 | Day | 202512 | 2025-12-12 | 0.99597
2025-12-12 13:28 | 73.7888 | FALSE | FALSE | -3.3442 | -4.7472 | -0.88664 | -1.1873 | 0.2826 |  |  | none | FALSE | 0 | 70.4446 | FALSE | FALSE | 0.0774 |  | 72.56 | 0 | 0.2826 | 0.16947 | 0.23179 | 0.48807 | 1.0577 | Normal | 74.6754 | 1.1617 | Day | 202512 | 2025-12-12 | 1.1617
2025-12-12 13:43 | 73.7888 | FALSE | FALSE | -3.0606 | -4.3272 | -0.9137 | -1.2231 | 0 |  |  | none | FALSE | 0 | 70.7282 | FALSE | FALSE | 0.072 |  | 72.7154 | 0 | 0 | 0.15534 | 0.23314 | -0.66629 | 0.99357 | Normal | 74.7025 | 1.0804 | Day | 202512 | 2025-12-12 | 1.0804
2025-12-12 13:43 | 73.7888 | FALSE | FALSE | -2.7123 | -3.816 | -0.87613 | -1.1734 | 0 |  |  | none | FALSE | 0 | 71.0765 | FALSE | FALSE | 0.0682 |  | 72.8707 | 0 | 0 | 0.15534 | 0.23314 | -0.66629 | 0.89711 | Normal | 74.6649 | 1.0234 | Day | 202512 | 2025-12-12 | 1.0234
2025-12-12 13:46 | 73.7888 | FALSE | FALSE | -2.3731 | -3.3229 | -0.81931 | -1.0982 | 0 |  |  | none | FALSE | 0 | 71.4157 | FALSE | FALSE | 0.0649 |  | 73.0119 | 0 | 0 | 0.14121 | 0.23359 | -0.60453 | 0.79809 | Normal | 74.6081 | 0.97342 | Day | 202512 | 2025-12-12 | 0.97342
2025-12-12 13:52 | 73.7888 | FALSE | FALSE | -1.9428 | -2.7041 | -0.67142 | -0.90172 | 0 |  |  | none | FALSE | 0 | 71.846 | FALSE | FALSE | 0.0648 |  | 73.1531 | 0 | 0 | 0.14121 | 0.23359 | -0.60453 | 0.65355 | Normal | 74.4602 | 0.97265 | Day | 202512 | 2025-12-12 | 0.97265
2025-12-12 13:52 | 73.7888 | FALSE | FALSE | -1.6113 | -2.2325 | -0.56589 | -0.76107 | 0 |  |  | none | FALSE | 0 | 72.1775 | FALSE | FALSE | 0.064 |  | 73.2661 | 0 | 0 | 0.11295 | 0.21286 | -0.53063 | 0.5443 | Normal | 74.3547 | 0.96034 | Day | 202512 | 2025-12-12 | 0.96034
2025-12-12 14:07 | 73.5062 | FALSE | FALSE | -1.0052 | -1.3865 | -0.69435 | -0.93578 | -0.2826 |  |  | none | FALSE | 0 | 72.501 | FALSE | FALSE | 0.0244 |  | 73.3508 | 0 | -0.2826 | 0.08469 | 0.22625 | -1.6234 | 0.42489 | Normal | 74.2006 | 0.36581 | Day | 202512 | 2025-12-12 | 0.36581
2025-12-12 14:22 | 73.2236 | FALSE | FALSE | -0.55006 | -0.75689 | -0.88918 | -1.1998 | -0.2826 |  |  | none | FALSE | 0 | 72.6735 | FALSE | FALSE | 0.0314 |  | 73.3932 | 0 | -0.2826 | 0.04239 | 0.21058 | -1.5433 | 0.35981 | Normal | 74.1128 | -0.47125 | Day | 202512 | 2025-12-12 | 0.47125
2025-12-12 14:37 | 72.941 | FALSE | FALSE | -0.20183 | -0.27748 | -1.1344 | -1.5314 | -0.2826 |  |  | none | FALSE | 0 | 72.7392 | FALSE | FALSE | 0.0931 |  | 73.4073 | 0 | -0.2826 | 0.01413 | 0.21454 | -1.3831 | 0.33406 | Normal | 74.0754 | -1.3958 | Day | 202512 | 2025-12-12 | 1.3958
2025-12-12 14:52 | 72.6584 | FALSE | FALSE | 0.015144 | 0.020839 | -1.4544 | -1.9624 | -0.2826 | 2025-12-12 15:52 | 2025-12-12 14:52 | lower | TRUE | 0 | 72.6735 | FALSE | FALSE | 0.1933 | 2.0421 | 73.3932 | 1 | -0.2826 | -0.01413 | 0.21454 | -1.2514 | 0.35981 | Extreme triggered | 74.1128 | -2.0421 | Day | 202512 | 2025-12-12 | 2.0421
2025-12-12 15:07 | 72.3758 | FALSE | FALSE | 0.12519 | 0.17267 | -1.8248 | -2.4592 | -0.2826 |  | 2025-12-12 14:52 | lower | TRUE | 0 | 72.501 | FALSE | FALSE | 0.2673 | 2.1684 | 73.3508 | 2 | -0.2826 | -0.04239 | 0.21058 | -1.1407 | 0.42489 | Extreme/elevated | 74.2006 | -2.2946 | Day | 202512 | 2025-12-12 | 2.2946
2025-12-12 15:22 | 72.3758 | FALSE | FALSE | 0.0067449 | 0.0093185 | -1.8867 | -2.5405 | 0 |  | 2025-12-12 14:52 | lower | TRUE | 0 | 72.3825 | FALSE | TRUE | 0.3057 | 2.117 | 73.3225 | 3 | 0 | -0.02826 | 0.20296 | 0.13924 | 0.46998 | Persistent | 74.2625 | -2.0144 | Day | 202512 | 2025-12-12 | 2.0144
2025-12-12 15:37 | 72.6584 | FALSE | FALSE | -0.32208 | -0.44525 | -1.622 | -2.1837 | 0.2826 |  | 2025-12-12 14:52 | none | FALSE | 0 | 72.3363 | FALSE | FALSE | 0.3177 | 1.9221 | 73.3084 | 4 | 0.2826 | -0.01413 | 0.21454 | 1.3831 | 0.48603 | Persistent | 74.2804 | -1.3373 | Day | 202512 | 2025-12-12 | 1.3373
2025-12-12 15:52 | 72.941 | FALSE | FALSE | -0.63212 | -0.8742 | -1.3386 | -1.8021 | 0.2826 |  |  | none | FALSE | 0 | 72.3089 | FALSE | FALSE | 0.0478 |  | 73.2943 | 0 | 0.2826 | -0.01413 | 0.21454 | 1.3831 | 0.49269 | Persistence ends | 74.2796 | -0.71699 | Day | 202512 | 2025-12-12 | 0.71699
2025-12-12 16:07 | 72.941 | FALSE | FALSE | -0.65855 | -0.91108 | -1.3368 | -1.7997 | 0 |  |  | none | FALSE | 0 | 72.2825 | FALSE | FALSE | 0.0453 |  | 73.2801 | 0 | 0 | -0.01413 | 0.21454 | 0.065863 | 0.49883 | Normal | 74.2778 | -0.67983 | Day | 202512 | 2025-12-12 | 0.67983
2025-12-12 16:22 | 72.941 | FALSE | FALSE | -0.68399 | -0.94661 | -1.334 | -1.796 | 0 |  |  | none | FALSE | 0 | 72.257 | FALSE | FALSE | 0.0429 |  | 73.266 | 0 | 0 | -0.01413 | 0.21454 | 0.065863 | 0.50449 | Normal | 74.275 | -0.6442 | Day | 202512 | 2025-12-12 | 0.6442
2025-12-12 16:37 | 72.941 | FALSE | FALSE | -0.70848 | -0.98083 | -1.3302 | -1.791 | 0 |  |  | none | FALSE | 0 | 72.2325 | FALSE | FALSE | 0.0407 |  | 73.2519 | 0 | 0 | -0.01413 | 0.21454 | 0.065863 | 0.50967 | Normal | 74.2712 | -0.60992 | Day | 202512 | 2025-12-12 | 0.60992
2025-12-12 16:51 | 72.941 | FALSE | FALSE | -0.73839 | -1.0227 | -1.3036 | -1.7558 | 0 |  |  | none | FALSE | 0 | 72.2026 | FALSE | FALSE | 0.0369 |  | 73.2236 | 0 | 0 | -0.02826 | 0.20296 | 0.13924 | 0.51049 | Normal | 74.2446 | -0.55358 | Day | 202512 | 2025-12-12 | 0.55358
2025-12-12 17:06 | 72.941 | FALSE | FALSE | -0.75197 | -1.0417 | -1.2324 | -1.6615 | 0 |  |  | none | FALSE | 0 | 72.189 | FALSE | FALSE | 0.0323 |  | 73.1812 | 0 | 0 | -0.04239 | 0.18957 | 0.22361 | 0.49609 | Normal | 74.1734 | -0.48421 | Day | 202512 | 2025-12-12 | 0.48421
2025-12-12 17:21 | 72.941 | FALSE | FALSE | -0.77342 | -1.0717 | -1.1973 | -1.615 | 0 |  |  | none | FALSE | 0 | 72.1676 | FALSE | FALSE | 0.0287 |  | 73.153 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.49269 | Normal | 74.1383 | -0.43019 | Day | 202512 | 2025-12-12 | 0.43019
2025-12-12 17:36 | 72.6584 | FALSE | FALSE | -0.52316 | -0.72525 | -1.3992 | -1.8894 | -0.2826 |  |  | none | FALSE | 0 | 72.1352 | FALSE | FALSE | 0.0608 |  | 73.0964 | 0 | -0.2826 | -0.05652 | 0.17396 | -1.2996 | 0.48059 | Normal | 74.0576 | -0.91143 | Night | 202512 | 2025-12-12 | 0.91143
2025-12-12 17:51 | 72.6584 | FALSE | FALSE | -0.54039 | -0.74932 | -1.3034 | -1.7623 | 0 |  |  | none | FALSE | 0 | 72.118 | FALSE | FALSE | 0.0552 |  | 73.0399 | 0 | 0 | -0.05652 | 0.17396 | 0.32489 | 0.46095 | Normal | 73.9618 | -0.82766 | Night | 202512 | 2025-12-12 | 0.82766
2025-12-12 18:06 | 72.6584 | FALSE | FALSE | -0.54047 | -0.74943 | -1.1905 | -1.612 | 0 |  |  | none | FALSE | 0 | 72.1179 | FALSE | FALSE | 0.0501 |  | 72.9834 | 0 | 0 | -0.05652 | 0.17396 | 0.32489 | 0.43273 | Normal | 73.8489 | -0.75102 | Night | 202512 | 2025-12-12 | 0.75102
2025-12-12 18:21 | 72.3758 | FALSE | FALSE | -0.28109 | -0.38988 | -1.355 | -1.8377 | -0.2826 |  |  | none | FALSE | 0 | 72.0947 | FALSE | FALSE | 0.0875 |  | 72.9127 | 0 | -0.2826 | -0.07065 | 0.18049 | -1.1743 | 0.40901 | Normal | 73.7308 | -1.3128 | Night | 202512 | 2025-12-12 | 1.3128
2025-12-12 18:36 | 72.3758 | FALSE | FALSE | -0.27349 | -0.3793 | -1.2061 | -1.6391 | 0 |  |  | none | FALSE | 0 | 72.1023 | FALSE | FALSE | 0.084 |  | 72.8421 | 0 | 0 | -0.07065 | 0.18049 | 0.39144 | 0.36989 | Normal | 73.5819 | -1.2606 | Night | 202512 | 2025-12-12 | 1.2606
2025-12-12 18:36 | 72.3758 | FALSE | FALSE | -0.22351 | -0.30977 | -1.0148 | -1.3827 | 0 |  |  | none | FALSE | 0 | 72.1523 | FALSE | FALSE | 0.0852 |  | 72.7714 | 0 | 0 | -0.07065 | 0.18049 | 0.39144 | 0.30957 | Normal | 73.3906 | -1.278 | Night | 202512 | 2025-12-12 | 1.278
2025-12-12 18:37 | 72.3758 | FALSE | FALSE | -0.19864 | -0.27521 | -0.87688 | -1.1971 | 0 |  |  | none | FALSE | 0 | 72.1772 | FALSE | FALSE | 0.0841 |  | 72.7149 | 0 | 0 | -0.05652 | 0.17396 | 0.32489 | 0.26888 | Normal | 73.2527 | -1.2612 | Night | 202512 | 2025-12-12 | 1.2612
2025-12-12 18:52 | 72.941 | TRUE | FALSE | -0.73481 | -1.0177 | -0.25439 | -0.34755 | 0.5652 |  |  | none | FALSE | 1 | 72.2062 | FALSE | FALSE | 0.0933 |  | 72.7008 | 0 | 0.5652 | -0.01413 | 0.21454 | 2.7004 | 0.2473 | Normal | 73.1954 | 0.97132 | Night | 202512 | 2025-12-12 | 0.97132
2025-12-12 19:07 | 73.2236 | FALSE | FALSE | -1.0464 | -1.4498 | -0.029081 | -0.0397 | 0.2826 |  |  | none | FALSE | 1 | 72.1772 | FALSE | FALSE | 0.1547 |  | 72.7149 | 0 | 0.2826 | 0.01413 | 0.21454 | 1.2514 | 0.26888 | Normal | 73.2527 | 1.8918 | Night | 202512 | 2025-12-12 | 1.8918
2025-12-12 19:22 | 73.2236 | FALSE | FALSE | -1.0632 | -1.4734 | -0.10236 | -0.13959 | 0 |  |  | none | FALSE | 1 | 72.1604 | FALSE | FALSE | 0.1385 |  | 72.7432 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.29139 | Normal | 73.326 | 1.6487 | Night | 202512 | 2025-12-12 | 1.6487
2025-12-12 19:36 | 73.2236 | FALSE | FALSE | -1.0315 | -1.4289 | -0.15547 | -0.21187 | 0 |  |  | none | FALSE | 1 | 72.1921 | FALSE | FALSE | 0.127 |  | 72.7856 | 0 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.29675 | Normal | 73.3791 | 1.4761 | Night | 202512 | 2025-12-12 | 1.4761
2025-12-12 19:51 | 72.941 | FALSE | FALSE | -0.69163 | -0.95728 | -0.43729 | -0.59593 | -0.2826 |  |  | none | FALSE | 1 | 72.2494 | FALSE | FALSE | 0.0586 |  | 72.8138 | 0 | -0.2826 | 0.02826 | 0.20296 | -1.5316 | 0.28223 | Normal | 73.3783 | 0.45059 | Night | 202512 | 2025-12-12 | 0.45059
2025-12-12 20:06 | 72.941 | FALSE | FALSE | -0.67526 | -0.93441 | -0.44918 | -0.61204 | 0 |  |  | none | FALSE | 1 | 72.2657 | FALSE | FALSE | 0.0554 |  | 72.828 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.28111 | Normal | 73.3902 | 0.40212 | Night | 202512 | 2025-12-12 | 0.40212
2025-12-12 20:21 | 72.941 | FALSE | FALSE | -0.67526 | -0.93441 | -0.44918 | -0.61204 | 0 |  |  | none | FALSE | 1 | 72.2657 | FALSE | FALSE | 0.0554 |  | 72.828 | 0 | 0 | 0 | 0.18338 | 0 | 0.28111 | Normal | 73.3902 | 0.40212 | Night | 202512 | 2025-12-12 | 0.40212
2025-12-12 20:35 | 72.941 | FALSE | FALSE | -0.67526 | -0.93441 | -0.44918 | -0.61204 | 0 |  |  | none | FALSE | 1 | 72.2657 | FALSE | FALSE | 0.0554 |  | 72.828 | 0 | 0 | 0 | 0.18338 | 0 | 0.28111 | Normal | 73.3902 | 0.40212 | Night | 202512 | 2025-12-12 | 0.40212
2025-12-12 20:51 | 72.941 | FALSE | FALSE | -0.67526 | -0.93441 | -0.44918 | -0.61204 | 0 |  |  | none | FALSE | 1 | 72.2657 | FALSE | FALSE | 0.0554 |  | 72.828 | 0 | 0 | 0 | 0.18338 | 0 | 0.28111 | Normal | 73.3902 | 0.40212 | Night | 202512 | 2025-12-12 | 0.40212
2025-12-12 21:06 | 72.6584 | FALSE | FALSE | -0.40903 | -0.56613 | -0.71989 | -0.98106 | -0.2826 |  |  | none | FALSE | 1 | 72.2494 | FALSE | FALSE | 0.0653 |  | 72.8138 | 0 | -0.2826 | -0.01413 | 0.19396 | -1.3842 | 0.28223 | Normal | 73.3783 | -0.55073 | Night | 202512 | 2025-12-12 | 0.55073
2025-12-12 21:21 | 72.6584 | FALSE | FALSE | -0.4239 | -0.58684 | -0.7065 | -0.96299 | 0 |  |  | none | FALSE | 0 | 72.2345 | FALSE | FALSE | 0.0333 |  | 72.7997 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.2826 | Normal | 73.3649 | -0.5 | Night | 202512 | 2025-12-12 | 0.5
2025-12-12 21:35 | 72.6584 | FALSE | FALSE | -0.43729 | -0.60548 | -0.69163 | -0.94291 | 0 |  |  | none | FALSE | 0 | 72.2211 | FALSE | FALSE | 0.03 |  | 72.7856 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.28223 | Normal | 73.35 | -0.45059 | Night | 202512 | 2025-12-12 | 0.45059
2025-12-12 21:50 | 72.6584 | FALSE | FALSE | -0.44918 | -0.62205 | -0.67526 | -0.9208 | 0 |  |  | none | FALSE | 0 | 72.2092 | FALSE | FALSE | 0.0268 |  | 72.7714 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.28111 | Normal | 73.3337 | -0.40212 | Night | 202512 | 2025-12-12 | 0.40212
2025-12-12 22:05 | 72.3758 | FALSE | FALSE | -0.20629 | -0.28584 | -0.96931 | -1.3216 | -0.2826 |  |  | none | FALSE | 0 | 72.1695 | FALSE | FALSE | 0.0865 |  | 72.7573 | 0 | -0.2826 | -0.01413 | 0.19396 | -1.3842 | 0.2939 | Normal | 73.3451 | -1.2981 | Night | 202512 | 2025-12-12 | 1.2981
2025-12-12 22:20 | 72.3758 | FALSE | FALSE | -0.24356 | -0.33766 | -0.97832 | -1.3337 | 0 |  |  | none | FALSE | 0 | 72.1322 | FALSE | FALSE | 0.0802 |  | 72.7432 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.30547 | Normal | 73.3541 | -1.2027 | Night | 202512 | 2025-12-12 | 1.2027
2025-12-12 22:35 | 72.3758 | FALSE | FALSE | -0.27866 | -0.38651 | -0.98516 | -1.3429 | 0 |  |  | none | FALSE | 0 | 72.0971 | FALSE | FALSE | 0.0745 |  | 72.7291 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.31596 | Normal | 73.361 | -1.118 | Night | 202512 | 2025-12-12 | 1.118
2025-12-12 22:50 | 72.3758 | FALSE | FALSE | -0.27866 | -0.38651 | -0.98516 | -1.3429 | 0 |  |  | none | FALSE | 0 | 72.0971 | FALSE | FALSE | 0.0745 |  | 72.7291 | 0 | 0 | 0 | 0.18338 | 0 | 0.31596 | Normal | 73.361 | -1.118 | Night | 202512 | 2025-12-12 | 1.118
2025-12-12 23:05 | 72.3758 | FALSE | FALSE | -0.27866 | -0.38651 | -0.98516 | -1.3429 | 0 |  |  | none | FALSE | 0 | 72.0971 | FALSE | FALSE | 0.0745 |  | 72.7291 | 0 | 0 | 0 | 0.18338 | 0 | 0.31596 | Normal | 73.361 | -1.118 | Night | 202512 | 2025-12-12 | 1.118
2025-12-12 23:20 | 72.3758 | FALSE | FALSE | -0.27866 | -0.38651 | -0.98516 | -1.3429 | 0 |  |  | none | FALSE | 0 | 72.0971 | FALSE | FALSE | 0.0745 |  | 72.7291 | 0 | 0 | 0 | 0.18338 | 0 | 0.31596 | Normal | 73.361 | -1.118 | Night | 202512 | 2025-12-12 | 1.118
2025-12-12 23:35 | 72.095 | FALSE | FALSE | -0.055896 | -0.077591 | -1.2959 | -1.7658 | -0.2808 |  |  | none | FALSE | 0 | 72.0391 | FALSE | FALSE | 0.1223 |  | 72.715 | 0 | -0.2808 | -0.01404 | 0.19383 | -1.3763 | 0.33795 | Normal | 73.3909 | -1.8346 | Night | 202512 | 2025-12-12 | 1.8346
2025-12-12 23:50 | 72.095 | FALSE | FALSE | -0.14305 | -0.19881 | -1.2985 | -1.7692 | 0 |  |  | none | FALSE | 0 | 71.952 | FALSE | FALSE | 0.1069 |  | 72.6727 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.36038 | Normal | 73.3935 | -1.6031 | Night | 202512 | 2025-12-12 | 1.6031
2025-12-13 00:05 | 72.095 | FALSE | FALSE | -0.19458 | -0.27063 | -1.2371 | -1.687 | 0 |  |  | none | FALSE | 0 | 71.9004 | FALSE | FALSE | 0.0971 |  | 72.6163 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.35793 | Normal | 73.3321 | -1.4564 | Night | 202512 | 2025-12-13 | 1.4564
2025-12-13 00:20 | 72.095 | FALSE | FALSE | -0.22696 | -0.31581 | -1.1567 | -1.579 | 0 |  |  | none | FALSE | 0 | 71.868 | FALSE | FALSE | 0.0896 |  | 72.5598 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.34591 | Normal | 73.2517 | -1.3439 | Night | 202512 | 2025-12-13 | 1.3439
2025-12-13 00:34 | 72.095 | FALSE | FALSE | -0.23806 | -0.3313 | -1.0549 | -1.4421 | 0 |  |  | none | FALSE | 0 | 71.8569 | FALSE | FALSE | 0.0842 |  | 72.5034 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.32324 | Normal | 73.1499 | -1.2635 | Night | 202512 | 2025-12-13 | 1.2635
2025-12-13 00:49 | 71.8124 | FALSE | FALSE | -0.047135 | -0.065679 | -1.3163 | -1.8 | -0.2826 |  |  | none | FALSE | 0 | 71.7653 | FALSE | FALSE | 0.1241 |  | 72.447 | 0 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.34086 | Normal | 73.1287 | -1.8617 | Night | 202512 | 2025-12-13 | 1.8617
2025-12-13 01:04 | 71.8124 | FALSE | FALSE | -0.11807 | -0.16469 | -1.2744 | -1.7437 | 0 |  |  | none | FALSE | 0 | 71.6943 | FALSE | FALSE | 0.1107 |  | 72.3906 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.34812 | Normal | 73.0868 | -1.6608 | Night | 202512 | 2025-12-13 | 1.6608
2025-12-13 01:19 | 71.8124 | FALSE | FALSE | -0.16959 | -0.23671 | -1.213 | -1.6611 | 0 |  |  | none | FALSE | 0 | 71.6428 | FALSE | FALSE | 0.1006 |  | 72.3341 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.34566 | Normal | 73.0254 | -1.5094 | Night | 202512 | 2025-12-13 | 1.5094
2025-12-13 01:34 | 71.8124 | FALSE | FALSE | -0.20125 | -0.28103 | -1.1318 | -1.5517 | 0 |  |  | none | FALSE | 0 | 71.6112 | FALSE | FALSE | 0.0931 |  | 72.2777 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.33327 | Normal | 72.9442 | -1.3962 | Night | 202512 | 2025-12-13 | 1.3962
2025-12-13 01:49 | 71.8124 | FALSE | FALSE | -0.21067 | -0.29423 | -1.0284 | -1.4119 | 0 |  |  | none | FALSE | 0 | 71.6017 | FALSE | FALSE | 0.088 |  | 72.2213 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.30977 | Normal | 72.8408 | -1.3199 | Night | 202512 | 2025-12-13 | 1.3199
2025-12-13 02:04 | 71.8124 | FALSE | FALSE | -0.24275 | -0.33917 | -0.97589 | -1.3407 | 0 |  |  | none | FALSE | 0 | 71.5697 | FALSE | FALSE | 0.0802 |  | 72.179 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.30466 | Normal | 72.7883 | -1.2032 | Night | 202512 | 2025-12-13 | 1.2032
2025-12-13 02:19 | 71.5298 | FALSE | FALSE | -0.038281 | -0.053546 | -1.2238 | -1.6821 | -0.2826 |  |  | none | FALSE | 0 | 71.4915 | FALSE | FALSE | 0.1252 |  | 72.1225 | 0 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.31551 | Normal | 72.7536 | -1.8787 | Night | 202512 | 2025-12-13 | 1.8787
2025-12-13 02:34 | 71.5298 | FALSE | FALSE | -0.094796 | -0.1327 | -1.1674 | -1.6059 | 0 |  |  | none | FALSE | 0 | 71.435 | FALSE | FALSE | 0.1133 |  | 72.0661 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.31555 | Normal | 72.6972 | -1.6996 | Night | 202512 | 2025-12-13 | 1.6996
2025-12-13 02:49 | 71.5298 | FALSE | FALSE | -0.1297 | -0.18165 | -1.0895 | -1.5002 | 0 |  |  | none | FALSE | 0 | 71.4001 | FALSE | FALSE | 0.105 |  | 72.0097 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.30479 | Normal | 72.6193 | -1.5745 | Night | 202512 | 2025-12-13 | 1.5745
2025-12-13 03:04 | 71.5298 | FALSE | FALSE | -0.18235 | -0.25558 | -1.0575 | -1.4569 | 0 |  |  | none | FALSE | 0 | 71.3475 | FALSE | FALSE | 0.0941 |  | 71.9674 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.30996 | Normal | 72.5873 | -1.4117 | Night | 202512 | 2025-12-13 | 1.4117
2025-12-13 03:19 | 71.2472 | FALSE | FALSE | -0.0033178 | -0.0046569 | -1.3308 | -1.8336 | -0.2826 |  |  | none | FALSE | 0 | 71.2439 | FALSE | FALSE | 0.1327 |  | 71.9109 | 0 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.33353 | Normal | 72.578 | -1.9901 | Night | 202512 | 2025-12-13 | 1.9901
2025-12-13 03:33 | 71.2472 | FALSE | FALSE | -0.084656 | -0.11896 | -1.2993 | -1.791 | 0 |  |  | none | FALSE | 0 | 71.1625 | FALSE | FALSE | 0.117 |  | 71.8545 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.34599 | Normal | 72.5465 | -1.7553 | Night | 202512 | 2025-12-13 | 1.7553
2025-12-13 03:48 | 71.2472 | FALSE | FALSE | -0.14615 | -0.20555 | -1.2479 | -1.7214 | 0 |  |  | none | FALSE | 0 | 71.101 | FALSE | FALSE | 0.1054 |  | 71.7981 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.34852 | Normal | 72.4951 | -1.5807 | Night | 202512 | 2025-12-13 | 1.5807
2025-12-13 04:03 | 71.2472 | FALSE | FALSE | -0.18824 | -0.26491 | -1.1772 | -1.6254 | 0 |  |  | none | FALSE | 0 | 71.059 | FALSE | FALSE | 0.0966 |  | 71.7417 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.34135 | Normal | 72.4244 | -1.4485 | Night | 202512 | 2025-12-13 | 1.4485
2025-12-13 04:18 | 71.2472 | FALSE | FALSE | -0.20965 | -0.29513 | -1.0857 | -1.501 | 0 |  |  | none | FALSE | 0 | 71.0375 | FALSE | FALSE | 0.0902 |  | 71.6852 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.32384 | Normal | 72.3329 | -1.3526 | Night | 202512 | 2025-12-13 | 1.3526
2025-12-13 04:33 | 71.2472 | FALSE | FALSE | -0.25009 | -0.35225 | -1.0414 | -1.4406 | 0 |  |  | none | FALSE | 0 | 70.9971 | FALSE | FALSE | 0.0817 |  | 71.6428 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.32287 | Normal | 72.2886 | -1.2254 | Night | 202512 | 2025-12-13 | 1.2254
2025-12-13 04:48 | 70.9646 | FALSE | FALSE | -0.054534 | -0.076906 | -1.298 | -1.7962 | -0.2826 |  |  | none | FALSE | 0 | 70.9101 | FALSE | FALSE | 0.1226 |  | 71.5863 | 0 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.33813 | Normal | 72.2626 | -1.8387 | Night | 202512 | 2025-12-13 | 1.8387
2025-12-13 05:03 | 70.9646 | FALSE | FALSE | -0.12093 | -0.1707 | -1.2513 | -1.7328 | 0 |  |  | none | FALSE | 0 | 70.8437 | FALSE | FALSE | 0.1098 |  | 71.5298 | 0 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.34306 | Normal | 72.2159 | -1.6475 | Night | 202512 | 2025-12-13 | 1.6475
2025-12-13 05:18 | 70.682 | FALSE | FALSE | 0.04652 | 0.065773 | -1.5078 | -2.0886 | -0.2826 | 2025-12-13 07:45 | 2025-12-13 05:18 | lower | TRUE | 0 | 70.7285 | FALSE | FALSE | 0.199 | 2.1273 | 71.4591 | 1 | -0.2826 | -0.07065 | 0.12555 | -1.6882 | 0.36531 | Extreme triggered | 72.1898 | -2.1273 | Night | 202512 | 2025-12-13 | 2.1273
2025-12-13 05:33 | 70.9646 | TRUE | FALSE | -0.25964 | -0.36722 | -1.1357 | -1.5752 | 0.2826 |  | 2025-12-13 05:18 | none | FALSE | 1 | 70.705 | FALSE | FALSE | 0.2266 | 1.6915 | 71.4026 | 2 | 0.2826 | -0.05652 | 0.14784 | 2.2938 | 0.34883 | Extreme/elevated | 72.1003 | -1.2557 | Night | 202512 | 2025-12-13 | 1.2557
2025-12-13 05:48 | 70.682 | FALSE | FALSE | -0.075667 | -0.10717 | -1.4039 | -1.9475 | -0.2826 |  | 2025-12-13 05:18 | none | FALSE | 1 | 70.6063 | FALSE | FALSE | 0.3197 | 1.7262 | 71.3461 | 3 | -0.2826 | -0.05652 | 0.14784 | -1.5292 | 0.36989 | Persistent | 72.0859 | -1.7954 | Night | 202512 | 2025-12-13 | 1.7954
2025-12-13 06:03 | 70.682 | FALSE | FALSE | -0.15458 | -0.21917 | -1.3698 | -1.9011 | 0 |  | 2025-12-13 05:18 | none | FALSE | 1 | 70.5274 | FALSE | FALSE | 0.3634 | 1.6932 | 71.2896 | 4 | 0 | -0.05652 | 0.14784 | 0.3823 | 0.38108 | Persistent | 72.0518 | -1.5944 | Night | 202512 | 2025-12-13 | 1.5944
2025-12-13 06:18 | 70.682 | FALSE | FALSE | -0.21549 | -0.30581 | -1.3176 | -1.8301 | 0 |  | 2025-12-13 05:18 | none | FALSE | 1 | 70.4665 | FALSE | FALSE | 0.4101 | 1.6421 | 71.2331 | 5 | 0 | -0.05652 | 0.14784 | 0.3823 | 0.38328 | Persistent | 71.9996 | -1.4378 | Night | 202512 | 2025-12-13 | 1.4378
2025-12-13 06:32 | 70.682 | FALSE | FALSE | -0.25874 | -0.36741 | -1.2478 | -1.7348 | 0 |  | 2025-12-13 05:18 | none | FALSE | 1 | 70.4233 | FALSE | FALSE | 0.459 | 1.5873 | 71.1766 | 6 | 0 | -0.05652 | 0.14784 | 0.3823 | 0.37665 | Persistent | 71.9298 | -1.313 | Night | 202512 | 2025-12-13 | 1.313
2025-12-13 06:47 | 70.682 | FALSE | TRUE | -0.28334 | -0.40247 | -1.1594 | -1.6138 | 0 |  | 2025-12-13 05:18 | none | FALSE | 1 | 70.3987 | FALSE | FALSE | 0.5095 | 1.534 | 71.12 | 7 | 0 | -0.05652 | 0.14784 | 0.3823 | 0.36068 | Confirmed/Materialized Shift | 71.8414 | -1.2144 | Night | 202512 | 2025-12-13 | 1.2144
2025-12-13 07:02 | 70.682 | FALSE | TRUE | -0.28661 | -0.40715 | -1.0496 | -1.4633 | 0 |  | 2025-12-13 05:18 | none | FALSE | 1 | 70.3954 | FALSE | FALSE | 0.5047 | 1.485 | 71.0635 | 8 | 0 | -0.05652 | 0.14784 | 0.3823 | 0.33406 | Confirmed/Materialized Shift | 71.7316 | -1.142 | Night | 202512 | 2025-12-13 | 1.142
2025-12-13 07:18 | 70.682 | FALSE | TRUE | -0.3118 | -0.44308 | -0.99004 | -1.3813 | 0 |  | 2025-12-13 05:18 | none | FALSE | 1 | 70.3702 | FALSE | FALSE | 0.498 | 1.4358 | 71.0211 | 9 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.32546 | Confirmed/Materialized Shift | 71.672 | -1.042 | Day | 202512 | 2025-12-13 | 1.042
2025-12-13 07:30 | 70.3994 | FALSE | TRUE | -0.095968 | -0.13651 | -1.2264 | -1.7122 | -0.2826 |  | 2025-12-13 05:18 | none | FALSE | 1 | 70.3034 | FALSE | FALSE | 0.5426 | 1.4632 | 70.9646 | 10 | -0.2826 | -0.05652 | 0.14784 | -1.5292 | 0.33058 | Confirmed/Materialized Shift | 71.6258 | -1.7097 | Day | 202512 | 2025-12-13 | 1.7097
2025-12-13 07:45 | 70.682 | FALSE | FALSE | -0.37553 | -0.53414 | -0.85595 | -1.1965 | 0.2826 |  |  | none | FALSE | 1 | 70.3065 | FALSE | FALSE | 0.0806 |  | 70.9222 | 0 | 0.2826 | -0.04239 | 0.16593 | 1.9586 | 0.30787 | Persistence ends | 71.538 | -0.78023 | Day | 202512 | 2025-12-13 | 0.78023
2025-12-13 08:00 | 70.3994 | FALSE | FALSE | -0.12151 | -0.1729 | -1.0541 | -1.4752 | -0.2826 |  |  | none | FALSE | 0 | 70.2779 | FALSE | FALSE | 0.1058 |  | 70.8657 | 0 | -0.2826 | -0.05652 | 0.17396 | -1.2996 | 0.2939 | Normal | 71.4535 | -1.5866 | Day | 202512 | 2025-12-13 | 1.5866
2025-12-13 08:15 | 70.3994 | FALSE | FALSE | -0.1703 | -0.2425 | -1.0181 | -1.4256 | 0 |  |  | none | FALSE | 0 | 70.2291 | FALSE | FALSE | 0.0951 |  | 70.8233 | 0 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.2971 | Normal | 71.4175 | -1.4268 | Day | 202512 | 2025-12-13 | 1.4268
2025-12-13 08:30 | 70.682 | FALSE | FALSE | -0.44918 | -0.63955 | -0.67526 | -0.94631 | 0.2826 |  |  | none | FALSE | 0 | 70.2328 | FALSE | FALSE | 0.0268 |  | 70.795 | 0 | 0.2826 | -0.02826 | 0.18107 | 1.7168 | 0.28111 | Normal | 71.3573 | -0.40212 | Day | 202512 | 2025-12-13 | 0.40212
2025-12-13 08:45 | 70.9646 | FALSE | FALSE | -0.71119 | -1.0123 | -0.34381 | -0.48215 | 0.2826 |  |  | none | FALSE | 0 | 70.2534 | FALSE | FALSE | 0.0464 |  | 70.7809 | 0 | 0.2826 | -0.01413 | 0.19396 | 1.5299 | 0.26375 | Normal | 71.3084 | 0.69645 | Day | 202512 | 2025-12-13 | 0.69645
2025-12-13 08:45 | 70.9646 | FALSE | FALSE | -0.68644 | -0.97674 | -0.2908 | -0.40811 | 0 |  |  | none | FALSE | 0 | 70.2782 | FALSE | FALSE | 0.054 |  | 70.7668 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.24431 | Normal | 71.2554 | 0.80971 | Day | 202512 | 2025-12-13 | 0.80971
2025-12-13 09:00 | 71.2472 | FALSE | FALSE | -0.96904 | -1.3789 | -0.0081981 | -0.011505 | 0.2826 |  |  | none | FALSE | 0 | 70.2782 | FALSE | FALSE | 0.1311 |  | 70.7668 | 0 | 0.2826 | 0 | 0.20502 | 1.3784 | 0.24431 | Normal | 71.2554 | 1.9664 | Day | 202512 | 2025-12-13 | 1.9664
2025-12-13 09:15 | 71.2472 | FALSE | FALSE | -0.96904 | -1.3789 | -0.0081981 | -0.011505 | 0 |  |  | none | FALSE | 0 | 70.2782 | FALSE | FALSE | 0.1311 |  | 70.7668 | 0 | 0 | 0 | 0.20502 | 0 | 0.24431 | Normal | 71.2554 | 1.9664 | Day | 202512 | 2025-12-13 | 1.9664
2025-12-13 09:30 | 71.5298 | FALSE | FALSE | -1.3261 | -1.889 | 0.14339 | 0.20087 | 0.2826 | 2025-12-13 13:43 | 2025-12-13 09:30 | upper | TRUE | 0 | 70.2037 | FALSE | FALSE | 0.2228 | 2.485 | 70.795 | 1 | 0.2826 | 0.02826 | 0.20296 | 1.2532 | 0.29568 | Extreme triggered | 71.3864 | 2.485 | Day | 202512 | 2025-12-13 | 2.485
2025-12-13 09:44 | 71.8124 | FALSE | FALSE | -1.7193 | -2.4528 | 0.23066 | 0.32223 | 0.2826 |  | 2025-12-13 09:30 | upper | TRUE | 0 | 70.0931 | FALSE | FALSE | 0.2889 | 2.5524 | 70.8374 | 2 | 0.2826 | 0.04239 | 0.21058 | 1.1407 | 0.37215 | Extreme/elevated | 71.5817 | 2.6198 | Day | 202512 | 2025-12-13 | 2.6198
2025-12-13 09:59 | 72.095 | FALSE | FALSE | -2.1147 | -3.0219 | 0.25911 | 0.36069 | 0.2826 |  | 2025-12-13 09:30 | upper | TRUE | 0 | 69.9803 | FALSE | TRUE | 0.342 | 2.5544 | 70.9081 | 3 | 0.2826 | 0.07065 | 0.20244 | 1.047 | 0.46391 | Persistent | 71.8359 | 2.5585 | Day | 202512 | 2025-12-13 | 2.5585
2025-12-13 10:14 | 72.6584 | TRUE | FALSE | -2.8801 | -4.1275 | 0.45116 | 0.62481 | 0.5634 |  | 2025-12-13 09:30 | upper | TRUE | 1 | 69.7783 | FALSE | TRUE | 0.44 | 2.6016 | 70.9928 | 4 | 0.5634 | 0.08469 | 0.22625 | 2.1158 | 0.60723 | Persistent | 72.2072 | 2.743 | Day | 202512 | 2025-12-13 | 2.743
2025-12-13 10:30 | 72.941 | FALSE | FALSE | -3.3185 | -4.7664 | 0.35205 | 0.485 | 0.2826 |  | 2025-12-13 09:30 | upper | TRUE | 1 | 69.6225 | FALSE | TRUE | 0.4793 | 2.5762 | 71.1057 | 5 | 0.2826 | 0.11295 | 0.21286 | 0.797 | 0.74161 | Persistent | 72.5889 | 2.4747 | Day | 202512 | 2025-12-13 | 2.4747
2025-12-13 10:44 | 73.2236 | FALSE | FALSE | -3.7339 | -5.3733 | 0.24768 | 0.3394 | 0.2826 |  | 2025-12-13 09:30 | upper | TRUE | 1 | 69.4897 | FALSE | TRUE | 0.5237 | 2.5275 | 71.2328 | 6 | 0.2826 | 0.12708 | 0.21434 | 0.72556 | 0.87156 | Persistent | 72.9759 | 2.2842 | Day | 202512 | 2025-12-13 | 2.2842
2025-12-13 10:59 | 73.2236 | FALSE | TRUE | -3.7979 | -5.4704 | -0.07044 | -0.096106 | 0 |  | 2025-12-13 09:30 | none | FALSE | 1 | 69.4257 | FALSE | FALSE | 0.557 | 2.4418 | 71.3599 | 7 | 0 | 0.12708 | 0.21434 | -0.59288 | 0.96708 | Confirmed/Materialized Shift | 73.294 | 1.9272 | Day | 202512 | 2025-12-13 | 1.9272
2025-12-13 11:14 | 72.941 | FALSE | TRUE | -3.4972 | -5.036 | -0.56082 | -0.76301 | -0.2826 |  | 2025-12-13 09:30 | none | FALSE | 1 | 69.4438 | FALSE | FALSE | 0.5251 | 2.3174 | 71.4728 | 8 | -0.2826 | 0.11295 | 0.23177 | -1.7067 | 1.0145 | Confirmed/Materialized Shift | 73.5018 | 1.4472 | Day | 202512 | 2025-12-13 | 1.4472
2025-12-13 11:29 | 72.941 | FALSE | TRUE | -3.4493 | -4.9636 | -0.73887 | -1.0028 | 0 |  | 2025-12-13 09:30 | none | FALSE | 1 | 69.4917 | FALSE | FALSE | 0.5149 | 2.2038 | 71.5858 | 9 | 0 | 0.11295 | 0.23177 | -0.48734 | 1.047 | Confirmed/Materialized Shift | 73.6799 | 1.2943 | Day | 202512 | 2025-12-13 | 1.2943
2025-12-13 11:44 | 72.941 | FALSE | TRUE | -3.3745 | -4.8507 | -0.88991 | -1.2053 | 0 |  | 2025-12-13 09:30 | none | FALSE | 1 | 69.5665 | FALSE | FALSE | 0.5063 | 2.0999 | 71.6987 | 10 | 0 | 0.11295 | 0.23177 | -0.48734 | 1.0661 | Confirmed/Materialized Shift | 73.8309 | 1.1653 | Day | 202512 | 2025-12-13 | 1.1653
2025-12-13 11:59 | 73.2236 | FALSE | TRUE | -3.5773 | -5.1363 | -0.78168 | -1.0563 | 0.2826 |  | 2025-12-13 09:30 | none | FALSE | 1 | 69.6463 | FALSE | FALSE | 0.5141 | 2.0256 | 71.8258 | 11 | 0.2826 | 0.12708 | 0.23313 | 0.66709 | 1.0897 | Confirmed/Materialized Shift | 74.0053 | 1.2827 | Day | 202512 | 2025-12-13 | 1.2827
2025-12-13 12:14 | 73.2236 | FALSE | TRUE | -3.4128 | -4.8886 | -0.8996 | -1.2137 | 0 |  | 2025-12-13 09:30 | none | FALSE | 1 | 69.8108 | FALSE | FALSE | 0.5063 | 1.9539 | 71.967 | 12 | 0 | 0.14121 | 0.21484 | -0.65728 | 1.0781 | Confirmed/Materialized Shift | 74.1232 | 1.1656 | Day | 202512 | 2025-12-13 | 1.1656
2025-12-13 12:29 | 73.5062 | FALSE | TRUE | -3.5697 | -5.1042 | -0.77373 | -1.0416 | 0.2826 |  | 2025-12-13 09:30 | none | FALSE | 1 | 69.9365 | FALSE | FALSE | 0.5144 | 1.9027 | 72.1082 | 13 | 0.2826 | 0.14121 | 0.21484 | 0.65812 | 1.0859 | Confirmed/Materialized Shift | 74.2799 | 1.2874 | Day | 202512 | 2025-12-13 | 1.2874
2025-12-13 12:43 | 73.5062 | FALSE | TRUE | -3.343 | -4.7645 | -0.85769 | -1.1534 | 0 |  | 2025-12-13 09:30 | none | FALSE | 0 | 70.1632 | FALSE | FALSE | 0.4789 | 1.8513 | 72.2636 | 14 | 0 | 0.15534 | 0.19376 | -0.80172 | 1.0502 | Confirmed/Materialized Shift | 74.3639 | 1.1833 | Day | 202512 | 2025-12-13 | 1.1833
2025-12-13 12:58 | 73.7888 | FALSE | TRUE | -3.3679 | -4.7825 | -0.65635 | -0.88165 | 0.2826 |  | 2025-12-13 09:30 | none | FALSE | 0 | 70.4209 | FALSE | FALSE | 0.4898 | 1.8177 | 72.433 | 15 | 0.2826 | 0.16947 | 0.19213 | 0.58882 | 1.0061 | Confirmed/Materialized Shift | 74.4451 | 1.3476 | Day | 202512 | 2025-12-13 | 1.3476
2025-12-13 13:14 | 73.7888 | FALSE | TRUE | -3.121 | -4.4164 | -0.72011 | -0.96648 | 0 |  | 2025-12-13 09:30 | none | FALSE | 0 | 70.6678 | FALSE | FALSE | 0.4833 | 1.7822 | 72.5884 | 16 | 0 | 0.15534 | 0.19376 | -0.80172 | 0.96027 | Confirmed/Materialized Shift | 74.5089 | 1.2501 | Day | 202512 | 2025-12-13 | 1.2501
2025-12-13 13:28 | 74.0714 | FALSE | TRUE | -3.1971 | -4.511 | -0.54175 | -0.72608 | 0.2826 |  | 2025-12-13 09:30 | none | FALSE | 0 | 70.8743 | FALSE | FALSE | 0.4947 | 1.761 | 72.7437 | 17 | 0.2826 | 0.15534 | 0.19376 | 0.6568 | 0.93472 | Confirmed/Materialized Shift | 74.6132 | 1.4204 | Day | 202512 | 2025-12-13 | 1.4204
2025-12-13 13:31 | 74.0714 | FALSE | TRUE | -2.9324 | -4.1221 | -0.58775 | -0.78724 | 0 |  | 2025-12-13 09:30 | none | FALSE | 0 | 71.139 | FALSE | FALSE | 0.4888 | 1.7371 | 72.8991 | 18 | 0 | 0.15534 | 0.19376 | -0.80172 | 0.88004 | Confirmed/Materialized Shift | 74.6591 | 1.3321 | Day | 202512 | 2025-12-13 | 1.3321
2025-12-13 13:43 | 73.7888 | FALSE | FALSE | -2.382 | -3.3358 | -0.85663 | -1.1476 | -0.2826 |  |  | none | FALSE | 0 | 71.4068 | FALSE | FALSE | 0.0628 |  | 73.0261 | 0 | -0.2826 | 0.12708 | 0.21434 | -1.9113 | 0.80965 | Persistence ends | 74.6454 | 0.94197 | Day | 202512 | 2025-12-13 | 0.94197
2025-12-13 13:58 | 73.2236 | TRUE | FALSE | -1.4854 | -2.0705 | -1.2881 | -1.7287 | -0.5652 |  |  | none | FALSE | 1 | 71.7382 | FALSE | FALSE | 0.0381 |  | 73.125 | 0 | -0.5652 | 0.09882 | 0.26358 | -2.5192 | 0.69336 | Normal | 74.5117 | 0.14226 | Day | 202512 | 2025-12-13 | 0.14226
2025-12-13 14:13 | 73.2236 | FALSE | FALSE | -1.1798 | -1.6376 | -1.1519 | -1.5487 | 0 |  |  | none | FALSE | 1 | 72.0438 | FALSE | FALSE | 0.0302 |  | 73.2096 | 0 | 0 | 0.08469 | 0.26077 | -0.32477 | 0.58291 | Normal | 74.3755 | 0.023932 | Day | 202512 | 2025-12-13 | 0.023932
2025-12-13 14:28 | 72.941 | FALSE | FALSE | -0.64955 | -0.89851 | -1.2997 | -1.7507 | -0.2826 |  |  | none | FALSE | 1 | 72.2915 | FALSE | FALSE | 0.073 |  | 73.2661 | 0 | -0.2826 | 0.05643 | 0.2687 | -1.2617 | 0.48731 | Normal | 74.2407 | -0.66709 | Day | 202512 | 2025-12-13 | 0.66709
2025-12-13 14:34 | 72.941 | FALSE | FALSE | -0.45475 | -0.62735 | -1.1895 | -1.6046 | 0 |  |  | none | FALSE | 1 | 72.4863 | FALSE | FALSE | 0.0882 |  | 73.3084 | 0 | 0 | 0.0423 | 0.26356 | -0.16049 | 0.41106 | Normal | 74.1305 | -0.89373 | Day | 202512 | 2025-12-13 | 0.89373
2025-12-13 14:34 | 72.941 | FALSE | FALSE | -0.40241 | -0.55475 | -1.1654 | -1.5726 | 0 |  |  | none | FALSE | 1 | 72.5386 | FALSE | FALSE | 0.0935 |  | 73.3225 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.39196 | Normal | 74.1064 | -0.97335 | Day | 202512 | 2025-12-13 | 0.97335
2025-12-13 14:35 | 72.941 | FALSE | FALSE | -0.40241 | -0.55475 | -1.1654 | -1.5726 | 0 |  |  | none | FALSE | 1 | 72.5386 | FALSE | FALSE | 0.0935 |  | 73.3225 | 0 | 0 | 0 | 0.22459 | 0 | 0.39196 | Normal | 74.1064 | -0.97335 | Day | 202512 | 2025-12-13 | 0.97335
2025-12-13 14:50 | 72.941 | FALSE | FALSE | -0.43403 | -0.59861 | -1.1688 | -1.5771 | 0 |  |  | none | FALSE | 1 | 72.507 | FALSE | FALSE | 0.0897 |  | 73.3084 | 0 | 0 | -0.01413 | 0.21454 | 0.065863 | 0.40071 | Normal | 74.1098 | -0.91683 | Day | 202512 | 2025-12-13 | 0.91683
2025-12-13 14:50 | 72.941 | FALSE | FALSE | -0.46426 | -0.64057 | -1.1708 | -1.5797 | 0 |  |  | none | FALSE | 1 | 72.4767 | FALSE | FALSE | 0.0862 |  | 73.2943 | 0 | 0 | -0.01413 | 0.21454 | 0.065863 | 0.40876 | Normal | 74.1118 | -0.86421 | Day | 202512 | 2025-12-13 | 0.86421
2025-12-13 15:05 | 72.941 | FALSE | FALSE | -0.46426 | -0.64057 | -1.1708 | -1.5797 | 0 |  |  | none | FALSE | 1 | 72.4767 | FALSE | FALSE | 0.0862 |  | 73.2943 | 0 | 0 | 0 | 0.20502 | 0 | 0.40876 | Normal | 74.1118 | -0.86421 | Day | 202512 | 2025-12-13 | 0.86421
2025-12-13 15:20 | 72.941 | FALSE | FALSE | -0.46426 | -0.64057 | -1.1708 | -1.5797 | 0 |  |  | none | FALSE | 1 | 72.4767 | FALSE | FALSE | 0.0862 |  | 73.2943 | 0 | 0 | 0 | 0.20502 | 0 | 0.40876 | Normal | 74.1118 | -0.86421 | Day | 202512 | 2025-12-13 | 0.86421
2025-12-13 15:35 | 72.6584 | FALSE | FALSE | -0.23053 | -0.31829 | -1.474 | -1.9883 | -0.2826 |  |  | none | FALSE | 0 | 72.4279 | FALSE | FALSE | 0.0973 |  | 73.2801 | 0 | -0.2826 | -0.01413 | 0.21454 | -1.2514 | 0.42613 | Normal | 74.1324 | -1.459 | Day | 202512 | 2025-12-13 | 1.459
2025-12-13 15:50 | 72.941 | FALSE | FALSE | -0.54047 | -0.74651 | -1.1905 | -1.6059 | 0.2826 |  |  | none | FALSE | 0 | 72.4005 | FALSE | FALSE | 0.0501 |  | 73.266 | 0 | 0.2826 | -0.01413 | 0.21454 | 1.3831 | 0.43273 | Normal | 74.1315 | -0.75102 | Day | 202512 | 2025-12-13 | 0.75102
2025-12-13 16:05 | 73.2236 | FALSE | FALSE | -0.82307 | -1.1368 | -0.90785 | -1.2247 | 0.2826 |  |  | none | FALSE | 0 | 72.4005 | FALSE | FALSE | 0.0065 |  | 73.266 | 0 | 0.2826 | 0 | 0.22459 | 1.2583 | 0.43273 | Normal | 74.1315 | -0.097959 | Day | 202512 | 2025-12-13 | 0.097959
2025-12-13 16:20 | 73.2236 | FALSE | FALSE | -0.82989 | -1.1464 | -0.88641 | -1.1961 | 0 |  |  | none | FALSE | 0 | 72.3937 | FALSE | FALSE | 0.0044 |  | 73.2519 | 0 | 0 | -0.01413 | 0.21454 | 0.065863 | 0.42907 | Normal | 74.11 | -0.065863 | Day | 202512 | 2025-12-13 | 0.065863
2025-12-13 16:35 | 73.2236 | FALSE | FALSE | -0.83565 | -1.1544 | -0.86391 | -1.1661 | 0 |  |  | none | FALSE | 0 | 72.3879 | FALSE | FALSE | 0.0022 |  | 73.2377 | 0 | 0 | -0.01413 | 0.21454 | 0.065863 | 0.42489 | Normal | 74.0875 | -0.033256 | Day | 202512 | 2025-12-13 | 0.033256
2025-12-13 16:49 | 73.2236 | FALSE | FALSE | -0.82337 | -1.1373 | -0.79511 | -1.0742 | 0 |  |  | none | FALSE | 0 | 72.4002 | FALSE | FALSE | 0.0023 |  | 73.2095 | 0 | 0 | -0.02826 | 0.20296 | 0.13924 | 0.40462 | Normal | 74.0187 | 0.034922 | Day | 202512 | 2025-12-13 | 0.034922
2025-12-13 17:04 | 73.2236 | FALSE | FALSE | -0.80456 | -1.111 | -0.71978 | -0.97341 | 0 |  |  | none | FALSE | 0 | 72.419 | FALSE | FALSE | 0.0074 |  | 73.1812 | 0 | 0 | -0.02826 | 0.20296 | 0.13924 | 0.38108 | Normal | 73.9434 | 0.11124 | Day | 202512 | 2025-12-13 | 0.11124
2025-12-13 17:19 | 73.2236 | FALSE | FALSE | -0.72265 | -0.99675 | -0.55309 | -0.74968 | 0 |  |  | none | FALSE | 0 | 72.5009 | FALSE | FALSE | 0.0177 |  | 73.1388 | 0 | 0 | -0.04239 | 0.18957 | 0.22361 | 0.31894 | Normal | 73.7767 | 0.26582 | Day | 202512 | 2025-12-13 | 0.26582
2025-12-13 17:34 | 73.2236 | FALSE | FALSE | -0.59379 | -0.81755 | -0.33945 | -0.46144 | 0 |  |  | none | FALSE | 0 | 72.6298 | FALSE | FALSE | 0.0363 |  | 73.0964 | 0 | 0 | -0.04239 | 0.18957 | 0.22361 | 0.23331 | Normal | 73.563 | 0.54507 | Night | 202512 | 2025-12-13 | 0.54507
2025-12-13 17:49 | 73.2236 | FALSE | FALSE | -0.49727 | -0.68375 | -0.18641 | -0.25392 | 0 |  |  | none | FALSE | 0 | 72.7263 | FALSE | FALSE | 0.0606 |  | 73.0682 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.17092 | Normal | 73.41 | 0.90938 | Night | 202512 | 2025-12-13 | 0.90938
2025-12-13 17:49 | 73.2236 | FALSE | FALSE | -0.49727 | -0.68375 | -0.18641 | -0.25392 | 0 |  |  | none | FALSE | 0 | 72.7263 | FALSE | FALSE | 0.0606 |  | 73.0682 | 0 | 0 | 0 | 0.12967 | 0 | 0.17092 | Normal | 73.41 | 0.90938 | Night | 202512 | 2025-12-13 | 0.90938
2025-12-13 17:50 | 73.2236 | FALSE | FALSE | -0.49727 | -0.68375 | -0.18641 | -0.25392 | 0 |  |  | none | FALSE | 0 | 72.7263 | FALSE | FALSE | 0.0606 |  | 73.0682 | 0 | 0 | 0 | 0.12967 | 0 | 0.17092 | Normal | 73.41 | 0.90938 | Night | 202512 | 2025-12-13 | 0.90938
2025-12-13 18:05 | 73.5062 | TRUE | FALSE | -0.79769 | -1.0971 | 0.021855 | 0.029741 | 0.2826 | 2025-12-13 19:19 | 2025-12-13 18:05 | upper | TRUE | 1 | 72.7085 | FALSE | FALSE | 0.2266 | 2.1127 | 73.0964 | 1 | 0.2826 | 0.02826 | 0.12638 | 2.0125 | 0.19396 | Extreme triggered | 73.4843 | 2.1127 | Night | 202512 | 2025-12-13 | 2.1127
2025-12-13 18:20 | 73.5062 | FALSE | FALSE | -0.80267 | -1.104 | -0.039654 | -0.053918 | 0 |  | 2025-12-13 18:05 | none | FALSE | 1 | 72.7035 | FALSE | FALSE | 0.2636 | 1.9622 | 73.1247 | 2 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.21058 | Extreme/elevated | 73.5459 | 1.8117 | Night | 202512 | 2025-12-13 | 1.8117
2025-12-13 18:35 | 73.5062 | FALSE | FALSE | -0.79772 | -1.0972 | -0.091222 | -0.12395 | 0 |  | 2025-12-13 18:05 | none | FALSE | 1 | 72.7085 | FALSE | FALSE | 0.306 | 1.838 | 73.153 | 3 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.22224 | Persistent | 73.5974 | 1.5895 | Night | 202512 | 2025-12-13 | 1.5895
2025-12-13 18:49 | 73.5062 | FALSE | FALSE | -0.78434 | -1.0786 | -0.13436 | -0.18246 | 0 |  | 2025-12-13 18:05 | none | FALSE | 1 | 72.7219 | FALSE | FALSE | 0.3515 | 1.7322 | 73.1812 | 4 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.22968 | Persistent | 73.6406 | 1.415 | Night | 202512 | 2025-12-13 | 1.415
2025-12-13 19:04 | 73.5062 | FALSE | FALSE | -0.76335 | -1.0494 | -0.16989 | -0.23059 | 0 |  | 2025-12-13 18:05 | none | FALSE | 1 | 72.7429 | FALSE | FALSE | 0.3991 | 1.6401 | 73.2095 | 5 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.23331 | Persistent | 73.6761 | 1.2718 | Night | 202512 | 2025-12-13 | 1.2718
2025-12-13 19:19 | 73.2236 | TRUE | FALSE | -0.44918 | -0.61722 | -0.44918 | -0.60969 | -0.2826 |  |  | none | FALSE | 2 | 72.7744 | TRUE | FALSE | 0.0571 |  | 73.2236 | 0 | -0.2826 | 0.01413 | 0.14424 | -2.0571 | 0.22459 | Persistence ends | 73.6728 | 0 | Night | 202512 | 2025-12-13 | 0
2025-12-13 19:34 | 73.5062 | FALSE | FALSE | -0.69976 | -0.96112 | -0.19108 | -0.25927 | 0.2826 |  |  | none | FALSE | 2 | 72.8064 | FALSE | FALSE | 0.1333 |  | 73.2519 | 0 | 0.2826 | 0.02826 | 0.15614 | 1.6289 | 0.22271 | Normal | 73.6973 | 1.142 | Night | 202512 | 2025-12-13 | 1.142
2025-12-13 19:48 | 73.5062 | FALSE | FALSE | -0.66002 | -0.90605 | -0.20786 | -0.28199 | 0 |  |  | none | FALSE | 2 | 72.8462 | FALSE | FALSE | 0.1266 |  | 73.2801 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.21697 | Normal | 73.7141 | 1.042 | Night | 202512 | 2025-12-13 | 1.042
2025-12-13 20:04 | 73.2236 | FALSE | FALSE | -0.23809 | -0.32621 | -0.40765 | -0.55363 | -0.2826 |  |  | none | FALSE | 2 | 72.9855 | FALSE | FALSE | 0.0922 |  | 73.3084 | 0 | -0.2826 | 0.02826 | 0.15614 | -1.9909 | 0.16143 | Normal | 73.6312 | -0.52517 | Night | 202512 | 2025-12-13 | 0.52517
2025-12-13 20:19 | 73.5062 | FALSE | FALSE | -0.45364 | -0.62098 | -0.11452 | -0.15556 | 0.2826 |  |  | none | FALSE | 2 | 73.0526 | FALSE | FALSE | 0.1367 |  | 73.3366 | 0 | 0.2826 | 0.02826 | 0.15614 | 1.6289 | 0.14204 | Normal | 73.6207 | 1.1937 | Night | 202512 | 2025-12-13 | 1.1937
2025-12-13 20:34 | 73.5062 | FALSE | FALSE | -0.44392 | -0.60759 | -0.13306 | -0.18069 | 0 |  |  | none | FALSE | 1 | 73.0623 | FALSE | FALSE | 0.1004 |  | 73.3508 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.14424 | Normal | 73.6393 | 1.0775 | Night | 202512 | 2025-12-13 | 1.0775
2025-12-13 20:48 | 73.5062 | FALSE | FALSE | -0.43124 | -0.59014 | -0.14864 | -0.20181 | 0 |  |  | none | FALSE | 1 | 73.075 | FALSE | FALSE | 0.0936 |  | 73.3649 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.14497 | Normal | 73.6548 | 0.97468 | Night | 202512 | 2025-12-13 | 0.97468
2025-12-13 21:03 | 73.5062 | FALSE | FALSE | -0.41566 | -0.56869 | -0.16132 | -0.21898 | 0 |  |  | none | FALSE | 1 | 73.0905 | FALSE | FALSE | 0.0873 |  | 73.379 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.14424 | Normal | 73.6675 | 0.88163 | Night | 202512 | 2025-12-13 | 0.88163
2025-12-13 21:18 | 73.7888 | FALSE | FALSE | -0.71336 | -0.9762 | 0.049657 | 0.067341 | 0.2826 | 2025-12-13 21:33 | 2025-12-13 21:18 | upper | TRUE | 1 | 73.0754 | FALSE | FALSE | 0.239 | 2.2993 | 73.4073 | 1 | 0.2826 | 0.02826 | 0.15614 | 1.6289 | 0.16593 | Extreme triggered | 73.7391 | 2.2993 | Night | 202512 | 2025-12-13 | 2.2993
2025-12-13 21:33 | 73.5062 | FALSE | FALSE | -0.40765 | -0.55767 | -0.23809 | -0.32285 | -0.2826 |  |  | none | FALSE | 1 | 73.0986 | FALSE | FALSE | 0.0636 |  | 73.4214 | 0 | -0.2826 | 0.01413 | 0.17092 | -1.7361 | 0.16143 | Persistence ends | 73.7443 | 0.52517 | Night | 202512 | 2025-12-13 | 0.52517
2025-12-13 21:48 | 73.5062 | FALSE | FALSE | -0.38158 | -0.52182 | -0.24028 | -0.32582 | 0 |  |  | none | FALSE | 0 | 73.1246 | FALSE | FALSE | 0.0303 |  | 73.4356 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.15546 | Normal | 73.7465 | 0.45445 | Night | 202512 | 2025-12-13 | 0.45445
2025-12-13 22:03 | 73.5062 | FALSE | FALSE | -0.3522 | -0.48145 | -0.23916 | -0.32431 | 0 |  |  | none | FALSE | 0 | 73.154 | FALSE | FALSE | 0.0255 |  | 73.4497 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.14784 | Normal | 73.7454 | 0.3823 | Night | 202512 | 2025-12-13 | 0.3823
2025-12-13 22:18 | 73.5062 | FALSE | FALSE | -0.31898 | -0.43584 | -0.2342 | -0.3176 | 0 |  |  | none | FALSE | 0 | 73.1872 | FALSE | FALSE | 0.0204 |  | 73.4638 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.13829 | Normal | 73.7404 | 0.30652 | Night | 202512 | 2025-12-13 | 0.30652
2025-12-13 22:33 | 73.5062 | FALSE | FALSE | -0.28103 | -0.38378 | -0.22451 | -0.30449 | 0 |  |  | none | FALSE | 0 | 73.2252 | FALSE | FALSE | 0.0149 |  | 73.4779 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.12638 | Normal | 73.7307 | 0.22361 | Night | 202512 | 2025-12-13 | 0.22361
2025-12-13 22:48 | 73.7888 | FALSE | FALSE | -0.54193 | -0.73987 | 0.023268 | 0.031544 | 0.2826 | 2025-12-13 23:03 | 2025-12-13 22:48 | upper | TRUE | 0 | 73.2469 | FALSE | FALSE | 0.2024 | 2.1794 | 73.5062 | 1 | 0.2826 | 0.02826 | 0.18107 | 1.4047 | 0.12967 | Extreme triggered | 73.7655 | 2.1794 | Night | 202512 | 2025-12-13 | 2.1794
2025-12-13 23:03 | 73.5062 | FALSE | FALSE | -0.25933 | -0.35405 | -0.25933 | -0.35156 | -0.2826 |  |  | none | FALSE | 0 | 73.2469 | FALSE | FALSE | 0 |  | 73.5062 | 0 | -0.2826 | 0 | 0.18338 | -1.5411 | 0.12967 | Persistence ends | 73.7655 | 0 | Night | 202512 | 2025-12-13 | 0
2025-12-13 23:18 | 73.5062 | FALSE | FALSE | -0.25933 | -0.35405 | -0.25933 | -0.35156 | 0 |  |  | none | FALSE | 0 | 73.2469 | FALSE | FALSE | 0 |  | 73.5062 | 0 | 0 | 0 | 0.18338 | 0 | 0.12967 | Normal | 73.7655 | 0 | Night | 202512 | 2025-12-13 | 0
2025-12-13 23:33 | 73.5062 | FALSE | FALSE | -0.25933 | -0.35405 | -0.25933 | -0.35156 | 0 |  |  | none | FALSE | 0 | 73.2469 | FALSE | FALSE | 0 |  | 73.5062 | 0 | 0 | 0 | 0.18338 | 0 | 0.12967 | Normal | 73.7655 | 0 | Night | 202512 | 2025-12-13 | 0
2025-12-13 23:47 | 73.7888 | FALSE | FALSE | -0.55696 | -0.76054 | -0.020018 | -0.027122 | 0.2826 |  |  | none | FALSE | 0 | 73.2318 | FALSE | FALSE | 0.1241 |  | 73.5203 | 0 | 0.2826 | 0.01413 | 0.19396 | 1.3842 | 0.14424 | Normal | 73.8088 | 1.8612 | Night | 202512 | 2025-12-13 | 1.8612
2025-12-14 00:02 | 73.7888 | FALSE | FALSE | -0.56662 | -0.77383 | -0.057937 | -0.078455 | 0 |  |  | none | FALSE | 0 | 73.2222 | FALSE | FALSE | 0.1086 |  | 73.5345 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.15614 | Normal | 73.8467 | 1.6289 | Night | 202512 | 2025-12-14 | 1.6289
2025-12-14 00:17 | 73.7888 | FALSE | FALSE | -0.52176 | -0.71214 | -0.069603 | -0.094239 | 0 |  |  | none | FALSE | 0 | 73.267 | FALSE | FALSE | 0.1019 |  | 73.5627 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.14784 | Normal | 73.8584 | 1.5292 | Night | 202512 | 2025-12-14 | 1.5292
2025-12-14 00:32 | 73.7888 | FALSE | FALSE | -0.52288 | -0.71367 | -0.098978 | -0.13396 | 0 |  |  | none | FALSE | 0 | 73.2659 | FALSE | FALSE | 0.0909 |  | 73.5768 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.15546 | Normal | 73.8878 | 1.3633 | Night | 202512 | 2025-12-14 | 1.3633
2025-12-14 00:47 | 73.5062 | FALSE | FALSE | -0.24028 | -0.32795 | -0.38158 | -0.51643 | -0.2826 |  |  | none | FALSE | 0 | 73.2659 | FALSE | FALSE | 0.0303 |  | 73.5768 | 0 | -0.2826 | 0 | 0.18338 | -1.5411 | 0.15546 | Normal | 73.8878 | -0.45445 | Night | 202512 | 2025-12-14 | 0.45445
2025-12-14 01:02 | 73.7888 | FALSE | FALSE | -0.46028 | -0.62769 | -0.092897 | -0.12574 | 0.2826 |  |  | none | FALSE | 0 | 73.3285 | FALSE | FALSE | 0.0886 |  | 73.6051 | 0 | 0.2826 | 0.02826 | 0.18107 | 1.4047 | 0.13829 | Normal | 73.8817 | 1.3283 | Night | 202512 | 2025-12-14 | 1.3283
2025-12-14 01:17 | 73.7888 | FALSE | FALSE | -0.45364 | -0.61859 | -0.11452 | -0.15496 | 0 |  |  | none | FALSE | 0 | 73.3352 | FALSE | FALSE | 0.0796 |  | 73.6192 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.14204 | Normal | 73.9033 | 1.1937 | Night | 202512 | 2025-12-14 | 1.1937
2025-12-14 01:32 | 73.5062 | FALSE | FALSE | -0.17104 | -0.23324 | -0.39712 | -0.53736 | -0.2826 |  |  | none | FALSE | 0 | 73.3352 | FALSE | FALSE | 0.0531 |  | 73.6192 | 0 | -0.2826 | 0 | 0.18338 | -1.5411 | 0.14204 | Normal | 73.9033 | -0.79582 | Night | 202512 | 2025-12-14 | 0.79582
2025-12-14 01:47 | 73.5062 | FALSE | FALSE | -0.17104 | -0.23324 | -0.39712 | -0.53736 | 0 |  |  | none | FALSE | 0 | 73.3352 | FALSE | FALSE | 0.0531 |  | 73.6192 | 0 | 0 | 0 | 0.18338 | 0 | 0.14204 | Normal | 73.9033 | -0.79582 | Night | 202512 | 2025-12-14 | 0.79582
2025-12-14 02:02 | 73.5062 | FALSE | FALSE | -0.17104 | -0.23324 | -0.39712 | -0.53736 | 0 |  |  | none | FALSE | 0 | 73.3352 | FALSE | FALSE | 0.0531 |  | 73.6192 | 0 | 0 | 0 | 0.18338 | 0 | 0.14204 | Normal | 73.9033 | -0.79582 | Night | 202512 | 2025-12-14 | 0.79582
2025-12-14 02:17 | 73.5062 | FALSE | FALSE | -0.17768 | -0.2423 | -0.3755 | -0.50824 | 0 |  |  | none | FALSE | 0 | 73.3285 | FALSE | FALSE | 0.0477 |  | 73.6051 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.13829 | Normal | 73.8817 | -0.71522 | Night | 202512 | 2025-12-14 | 0.71522
2025-12-14 02:32 | 73.5062 | FALSE | FALSE | -0.17768 | -0.2423 | -0.3755 | -0.50824 | 0 |  |  | none | FALSE | 0 | 73.3285 | FALSE | FALSE | 0.0477 |  | 73.6051 | 0 | 0 | 0 | 0.15881 | 0 | 0.13829 | Normal | 73.8817 | -0.71522 | Night | 202512 | 2025-12-14 | 0.71522
2025-12-14 02:46 | 73.5062 | FALSE | FALSE | -0.17768 | -0.2423 | -0.3755 | -0.50824 | 0 |  |  | none | FALSE | 0 | 73.3285 | FALSE | FALSE | 0.0477 |  | 73.6051 | 0 | 0 | 0 | 0.15881 | 0 | 0.13829 | Normal | 73.8817 | -0.71522 | Night | 202512 | 2025-12-14 | 0.71522
2025-12-14 03:01 | 73.5062 | FALSE | FALSE | -0.17768 | -0.2423 | -0.3755 | -0.50824 | 0 |  |  | none | FALSE | 0 | 73.3285 | FALSE | FALSE | 0.0477 |  | 73.6051 | 0 | 0 | 0 | 0.15881 | 0 | 0.13829 | Normal | 73.8817 | -0.71522 | Night | 202512 | 2025-12-14 | 0.71522
2025-12-14 03:16 | 73.5062 | FALSE | FALSE | -0.17768 | -0.2423 | -0.3755 | -0.50824 | 0 |  |  | none | FALSE | 0 | 73.3285 | FALSE | FALSE | 0.0477 |  | 73.6051 | 0 | 0 | 0 | 0.15881 | 0 | 0.13829 | Normal | 73.8817 | -0.71522 | Night | 202512 | 2025-12-14 | 0.71522
2025-12-14 03:31 | 73.5062 | FALSE | FALSE | -0.17768 | -0.2423 | -0.3755 | -0.50824 | 0 |  |  | none | FALSE | 0 | 73.3285 | FALSE | FALSE | 0.0477 |  | 73.6051 | 0 | 0 | 0 | 0.15881 | 0 | 0.13829 | Normal | 73.8817 | -0.71522 | Night | 202512 | 2025-12-14 | 0.71522
2025-12-14 03:46 | 73.5062 | FALSE | FALSE | -0.18096 | -0.24679 | -0.35052 | -0.47459 | 0 |  |  | none | FALSE | 0 | 73.3252 | FALSE | FALSE | 0.0425 |  | 73.591 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.13287 | Normal | 73.8567 | -0.63808 | Night | 202512 | 2025-12-14 | 0.63808
2025-12-14 04:01 | 73.5062 | FALSE | FALSE | -0.18096 | -0.24679 | -0.35052 | -0.47459 | 0 |  |  | none | FALSE | 0 | 73.3252 | FALSE | FALSE | 0.0425 |  | 73.591 | 0 | 0 | 0 | 0.12967 | 0 | 0.13287 | Normal | 73.8567 | -0.63808 | Night | 202512 | 2025-12-14 | 0.63808
2025-12-14 04:16 | 73.5062 | FALSE | FALSE | -0.18096 | -0.24679 | -0.35052 | -0.47459 | 0 |  |  | none | FALSE | 0 | 73.3252 | FALSE | FALSE | 0.0425 |  | 73.591 | 0 | 0 | 0 | 0.12967 | 0 | 0.13287 | Normal | 73.8567 | -0.63808 | Night | 202512 | 2025-12-14 | 0.63808
2025-12-14 04:31 | 73.5062 | FALSE | FALSE | -0.18096 | -0.24679 | -0.35052 | -0.47459 | 0 |  |  | none | FALSE | 0 | 73.3252 | FALSE | FALSE | 0.0425 |  | 73.591 | 0 | 0 | 0 | 0.12967 | 0 | 0.13287 | Normal | 73.8567 | -0.63808 | Night | 202512 | 2025-12-14 | 0.63808
2025-12-14 04:46 | 73.5062 | FALSE | FALSE | -0.18045 | -0.24609 | -0.32175 | -0.43581 | 0 |  |  | none | FALSE | 0 | 73.3258 | FALSE | FALSE | 0.0375 |  | 73.5768 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.12555 | Normal | 73.8279 | -0.56273 | Night | 202512 | 2025-12-14 | 0.56273
2025-12-14 05:01 | 73.5062 | FALSE | FALSE | -0.17543 | -0.23924 | -0.28847 | -0.39091 | 0 |  |  | none | FALSE | 0 | 73.3308 | FALSE | FALSE | 0.0325 |  | 73.5627 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.11598 | Normal | 73.7947 | -0.48734 | Night | 202512 | 2025-12-14 | 0.48734
2025-12-14 05:16 | 73.5062 | FALSE | FALSE | -0.16467 | -0.22452 | -0.24945 | -0.33821 | 0 |  |  | none | FALSE | 0 | 73.3415 | FALSE | FALSE | 0.0273 |  | 73.5486 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.10353 | Normal | 73.7556 | -0.40945 | Night | 202512 | 2025-12-14 | 0.40945
2025-12-14 05:31 | 73.5062 | FALSE | FALSE | -0.1457 | -0.19861 | -0.20222 | -0.27436 | 0 |  |  | none | FALSE | 0 | 73.3605 | FALSE | FALSE | 0.0217 |  | 73.5345 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.086982 | Normal | 73.7084 | -0.32489 | Night | 202512 | 2025-12-14 | 0.32489
2025-12-14 05:45 | 73.5062 | FALSE | FALSE | -0.1457 | -0.19861 | -0.20222 | -0.27436 | 0 |  |  | none | FALSE | 0 | 73.3605 | FALSE | FALSE | 0.0217 |  | 73.5345 | 0 | 0 | 0 | 0.091688 | 0 | 0.086982 | Normal | 73.7084 | -0.32489 | Night | 202512 | 2025-12-14 | 0.32489
2025-12-14 06:00 | 73.5062 | FALSE | FALSE | -0.11225 | -0.15295 | -0.14051 | -0.19079 | 0 |  |  | none | FALSE | 0 | 73.3939 | FALSE | FALSE | 0.0149 |  | 73.5203 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.063191 | Normal | 73.6467 | -0.22361 | Night | 202512 | 2025-12-14 | 0.22361
2025-12-14 06:16 | 73.5062 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.5062 | FALSE | FALSE | 0 |  | 73.5062 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0 | Normal | 73.5062 |  | Night | 202512 | 2025-12-14
2025-12-14 06:31 | 73.2236 | TRUE | FALSE | 0.14209 | 0.19367 | -0.39485 | -0.53635 | -0.2826 | 2025-12-14 07:00 | 2025-12-14 06:31 | lower | TRUE | 1 | 73.3657 | FALSE | FALSE | 0.3689 | 4.2485 | 73.4921 | 1 | -0.2826 | -0.01413 | 0.063191 | -4.2485 | 0.063191 | Extreme triggered | 73.6185 | -4.2485 | Night | 202512 | 2025-12-14 | 4.2485
2025-12-14 06:45 | 73.2236 | FALSE | FALSE | 0.080375 | 0.10965 | -0.4283 | -0.58153 | 0 |  | 2025-12-14 06:31 | lower | TRUE | 1 | 73.304 | FALSE | FALSE | 0.3378 | 3.5863 | 73.4779 | 2 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.086982 | Extreme/elevated | 73.6519 | -2.924 | Night | 202512 | 2025-12-14 | 2.924
2025-12-14 07:00 | 73.5062 | TRUE | FALSE | -0.20222 | -0.27587 | -0.1457 | -0.19783 | 0.2826 |  |  | none | FALSE | 2 | 73.304 | TRUE | FALSE | 0.0788 |  | 73.4779 | 0 | 0.2826 | 0 | 0.091688 | 3.0822 | 0.086982 | Persistence ends | 73.6519 | 0.32489 | Night | 202512 | 2025-12-14 | 0.32489
2025-12-14 07:15 | 73.2236 | TRUE | FALSE | 0.03315 | 0.045252 | -0.44727 | -0.60712 | -0.2826 | 2025-12-14 07:30 | 2025-12-14 07:15 | lower | TRUE | 3 | 73.2568 | TRUE | FALSE | 0.2975 | 2.3202 | 73.4638 | 1 | -0.2826 | -0.01413 | 0.11135 | -2.411 | 0.10353 | Extreme triggered | 73.6709 | -2.3202 | Day | 202512 | 2025-12-14 | 2.3202
2025-12-14 07:30 | 73.5062 | TRUE | FALSE | -0.24945 | -0.34051 | -0.16467 | -0.22352 | 0.2826 |  |  | none | FALSE | 4 | 73.2568 | TRUE | FALSE | 0.1416 |  | 73.4638 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.10353 | Persistence ends | 73.6709 | 0.40945 | Day | 202512 | 2025-12-14 | 0.40945
2025-12-14 07:45 | 73.2236 | FALSE | FALSE | -0.0058732 | -0.0080215 | -0.45803 | -0.62164 | -0.2826 |  |  | none | FALSE | 4 | 73.2177 | FALSE | FALSE | 0.2442 |  | 73.4497 | 0 | -0.2826 | -0.01413 | 0.14424 | -1.8612 | 0.11598 | Normal | 73.6816 | -1.9494 | Day | 202512 | 2025-12-14 | 1.9494
2025-12-14 08:00 | 73.2236 | FALSE | FALSE | -0.039147 | -0.05349 | -0.46305 | -0.6284 | 0 |  |  | none | FALSE | 4 | 73.1845 | FALSE | FALSE | 0.2268 |  | 73.4356 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.12555 | Normal | 73.6866 | -1.6882 | Day | 202512 | 2025-12-14 | 1.6882
2025-12-14 08:15 | 73.5062 | FALSE | FALSE | -0.32175 | -0.43964 | -0.18045 | -0.24488 | 0.2826 |  |  | none | FALSE | 4 | 73.1845 | FALSE | FALSE | 0.1518 |  | 73.4356 | 0 | 0.2826 | 0 | 0.15881 | 1.7795 | 0.12555 | Normal | 73.6866 | 0.56273 | Day | 202512 | 2025-12-14 | 0.56273
2025-12-14 08:30 | 73.5062 | FALSE | FALSE | -0.32175 | -0.43964 | -0.18045 | -0.24488 | 0 |  |  | none | FALSE | 4 | 73.1845 | FALSE | FALSE | 0.1518 |  | 73.4356 | 0 | 0 | 0 | 0.15881 | 0 | 0.12555 | Normal | 73.6866 | 0.56273 | Day | 202512 | 2025-12-14 | 0.56273
2025-12-14 08:45 | 73.5062 | FALSE | FALSE | -0.32175 | -0.43964 | -0.18045 | -0.24488 | 0 |  |  | none | FALSE | 4 | 73.1845 | FALSE | FALSE | 0.1518 |  | 73.4356 | 0 | 0 | 0 | 0.15881 | 0 | 0.12555 | Normal | 73.6866 | 0.56273 | Day | 202512 | 2025-12-14 | 0.56273
2025-12-14 08:45 | 73.5062 | FALSE | FALSE | -0.32175 | -0.43964 | -0.18045 | -0.24488 | 0 |  |  | none | FALSE | 3 | 73.1845 | FALSE | FALSE | 0.1232 |  | 73.4356 | 0 | 0 | 0 | 0.15881 | 0 | 0.12555 | Normal | 73.6866 | 0.56273 | Day | 202512 | 2025-12-14 | 0.56273
2025-12-14 09:00 | 73.5062 | FALSE | FALSE | -0.32175 | -0.43964 | -0.18045 | -0.24488 | 0 |  |  | none | FALSE | 3 | 73.1845 | FALSE | FALSE | 0.1232 |  | 73.4356 | 0 | 0 | 0 | 0.15881 | 0 | 0.12555 | Normal | 73.6866 | 0.56273 | Day | 202512 | 2025-12-14 | 0.56273
2025-12-14 09:15 | 73.5062 | FALSE | FALSE | -0.32175 | -0.43964 | -0.18045 | -0.24488 | 0 |  |  | none | FALSE | 2 | 73.1845 | FALSE | FALSE | 0.0947 |  | 73.4356 | 0 | 0 | 0 | 0.15881 | 0 | 0.12555 | Normal | 73.6866 | 0.56273 | Day | 202512 | 2025-12-14 | 0.56273
2025-12-14 09:30 | 73.5062 | FALSE | FALSE | -0.32175 | -0.43964 | -0.18045 | -0.24488 | 0 |  |  | none | FALSE | 1 | 73.1845 | FALSE | FALSE | 0.0661 |  | 73.4356 | 0 | 0 | 0 | 0.15881 | 0 | 0.12555 | Normal | 73.6866 | 0.56273 | Day | 202512 | 2025-12-14 | 0.56273
2025-12-14 09:45 | 73.7888 | FALSE | FALSE | -0.6348 | -0.86776 | 0.043437 | 0.058901 | 0.2826 | 2025-12-14 11:29 | 2025-12-14 09:45 | upper | TRUE | 0 | 73.154 | FALSE | FALSE | 0.2101 | 2.2938 | 73.4497 | 1 | 0.2826 | 0.01413 | 0.17092 | 1.5708 | 0.14784 | Extreme triggered | 73.7454 | 2.2938 | Day | 202512 | 2025-12-14 | 2.2938
2025-12-14 10:00 | 73.2236 | TRUE | FALSE | -0.098978 | -0.13535 | -0.52288 | -0.70902 | -0.5652 |  | 2025-12-14 09:45 | none | FALSE | 1 | 73.1246 | FALSE | FALSE | 0.2337 | 1.8286 | 73.4356 | 2 | -0.5652 | -0.01413 | 0.21454 | -2.5686 | 0.15546 | Extreme/elevated | 73.7465 | -1.3633 | Day | 202512 | 2025-12-14 | 1.3633
2025-12-14 10:15 | 72.3758 | TRUE | FALSE | 0.43877 | 0.60259 | -1.5677 | -2.1201 | -0.8478 |  | 2025-12-14 09:45 | lower | TRUE | 2 | 72.8146 | TRUE | TRUE | 0.4656 | 2.4039 | 73.379 | 3 | -0.8478 | -0.05652 | 0.28408 | -2.7854 | 0.28223 | Persistent | 73.9435 | -3.5547 | Day | 202512 | 2025-12-14 | 3.5547
2025-12-14 10:30 | 72.3758 | FALSE | FALSE | 0.23002 | 0.31681 | -1.6634 | -2.2466 | 0 |  | 2025-12-14 09:45 | lower | TRUE | 2 | 72.6058 | FALSE | TRUE | 0.4618 | 2.4634 | 73.3225 | 4 | 0 | -0.05652 | 0.28408 | 0.19896 | 0.35834 | Persistent | 74.0392 | -2.6419 | Day | 202512 | 2025-12-14 | 2.6419
2025-12-14 10:45 | 72.3758 | FALSE | FALSE | 0.064493 | 0.089029 | -1.7159 | -2.3159 | 0 |  | 2025-12-14 09:45 | lower | TRUE | 2 | 72.4403 | FALSE | TRUE | 0.4866 | 2.402 | 73.266 | 5 | 0 | -0.05652 | 0.28408 | 0.19896 | 0.41285 | Persistent | 74.0917 | -2.1562 | Day | 202512 | 2025-12-14 | 2.1562
2025-12-14 11:00 | 72.3758 | FALSE | FALSE | -0.073527 | -0.10169 | -1.7409 | -2.3488 | 0 |  | 2025-12-14 09:45 | none | FALSE | 2 | 72.3023 | FALSE | FALSE | 0.5225 | 2.308 | 73.2095 | 6 | 0 | -0.05652 | 0.28408 | 0.19896 | 0.4536 | Persistent | 74.1167 | -1.8379 | Day | 202512 | 2025-12-14 | 1.8379
2025-12-14 11:15 | 72.3758 | FALSE | TRUE | -0.18939 | -0.26236 | -1.772 | -2.3898 | 0 |  | 2025-12-14 09:45 | none | FALSE | 2 | 72.1864 | FALSE | FALSE | 0.5647 | 2.2088 | 73.1671 | 7 | 0 | -0.04239 | 0.27923 | 0.15181 | 0.49034 | Confirmed/Materialized Shift | 74.1478 | -1.6138 | Day | 202512 | 2025-12-14 | 1.6138
2025-12-14 11:29 | 72.6584 | FALSE | FALSE | -0.52564 | -0.72871 | -1.4865 | -2.0048 | 0.2826 |  |  | none | FALSE | 2 | 72.1328 | FALSE | FALSE | 0.1208 |  | 73.1388 | 0 | 0.2826 | -0.02826 | 0.28849 | 1.0775 | 0.50303 | Persistence ends | 74.1449 | -0.95505 | Day | 202512 | 2025-12-14 | 0.95505
2025-12-14 11:44 | 72.941 | FALSE | FALSE | -0.82473 | -1.1436 | -1.1639 | -1.5705 | 0.2826 |  |  | none | FALSE | 2 | 72.1163 | FALSE | FALSE | 0.0799 |  | 73.1106 | 0 | 0.2826 | -0.02826 | 0.28849 | 1.0775 | 0.49715 | Normal | 74.1049 | -0.34107 | Day | 202512 | 2025-12-14 | 0.34107
2025-12-14 11:59 | 73.2236 | FALSE | FALSE | -1.1073 | -1.5355 | -0.88125 | -1.1892 | 0.2826 |  |  | none | FALSE | 2 | 72.1163 | FALSE | FALSE | 0.0723 |  | 73.1106 | 0 | 0.2826 | 0 | 0.28994 | 0.97468 | 0.49715 | Normal | 74.1049 | 0.22738 | Day | 202512 | 2025-12-14 | 0.22738
2025-12-14 12:14 | 73.2236 | FALSE | FALSE | -1.1057 | -1.5332 | -0.85136 | -1.1493 | 0 |  |  | none | FALSE | 2 | 72.1179 | FALSE | FALSE | 0.0745 |  | 73.0964 | 0 | 0 | -0.01413 | 0.28223 | 0.050066 | 0.48926 | Normal | 74.075 | 0.25992 | Day | 202512 | 2025-12-14 | 0.25992
2025-12-14 12:29 | 73.2236 | FALSE | FALSE | -1.1057 | -1.5332 | -0.85136 | -1.1493 | 0 |  |  | none | FALSE | 1 | 72.1179 | FALSE | FALSE | 0.0459 |  | 73.0964 | 0 | 0 | 0 | 0.27506 | 0 | 0.48926 | Normal | 74.075 | 0.25992 | Day | 202512 | 2025-12-14 | 0.25992
2025-12-14 12:44 | 73.2236 | FALSE | FALSE | -1.1057 | -1.5332 | -0.85136 | -1.1493 | 0 |  |  | none | FALSE | 0 | 72.1179 | FALSE | FALSE | 0.0173 |  | 73.0964 | 0 | 0 | 0 | 0.27506 | 0 | 0.48926 | Normal | 74.075 | 0.25992 | Day | 202512 | 2025-12-14 | 0.25992
2025-12-14 12:59 | 73.2236 | FALSE | FALSE | -1.1029 | -1.5293 | -0.82033 | -1.1079 | 0 |  |  | none | FALSE | 0 | 72.1207 | FALSE | FALSE | 0.0196 |  | 73.0823 | 0 | 0 | -0.01413 | 0.26692 | 0.052937 | 0.48081 | Normal | 74.0439 | 0.29388 | Day | 202512 | 2025-12-14 | 0.29388
2025-12-14 13:14 | 73.5062 | FALSE | FALSE | -1.3855 | -1.9211 | -0.53773 | -0.72623 | 0.2826 |  |  | none | FALSE | 0 | 72.1207 | FALSE | FALSE | 0.0588 |  | 73.0823 | 0 | 0.2826 | 0 | 0.27506 | 1.0274 | 0.48081 | Normal | 74.0439 | 0.88163 | Day | 202512 | 2025-12-14 | 0.88163
2025-12-14 13:29 | 73.5062 | FALSE | FALSE | -1.3855 | -1.9211 | -0.53773 | -0.72623 | 0 |  |  | none | FALSE | 0 | 72.1207 | FALSE | FALSE | 0.0588 |  | 73.0823 | 0 | 0 | 0 | 0.27506 | 0 | 0.48081 | Normal | 74.0439 | 0.88163 | Day | 202512 | 2025-12-14 | 0.88163
2025-12-14 13:44 | 73.5062 | FALSE | FALSE | -1.3855 | -1.9211 | -0.53773 | -0.72623 | 0 |  |  | none | FALSE | 0 | 72.1207 | FALSE | FALSE | 0.0588 |  | 73.0823 | 0 | 0 | 0 | 0.27506 | 0 | 0.48081 | Normal | 74.0439 | 0.88163 | Day | 202512 | 2025-12-14 | 0.88163
2025-12-14 13:59 | 73.5062 | FALSE | FALSE | -1.3855 | -1.9211 | -0.53773 | -0.72623 | 0 |  |  | none | FALSE | 0 | 72.1207 | FALSE | FALSE | 0.0588 |  | 73.0823 | 0 | 0 | 0 | 0.27506 | 0 | 0.48081 | Normal | 74.0439 | 0.88163 | Day | 202512 | 2025-12-14 | 0.88163
2025-12-14 14:14 | 73.2236 | FALSE | FALSE | -1.099 | -1.5237 | -0.78811 | -1.0648 | -0.2826 |  |  | none | FALSE | 0 | 72.1246 | FALSE | FALSE | 0.022 |  | 73.0682 | 0 | -0.2826 | -0.01413 | 0.28223 | -0.95125 | 0.47177 | Normal | 74.0117 | 0.32946 | Day | 202512 | 2025-12-14 | 0.32946
2025-12-14 14:28 | 73.2236 | FALSE | FALSE | -1.0937 | -1.5164 | -0.75462 | -1.0201 | 0 |  |  | none | FALSE | 0 | 72.1299 | FALSE | FALSE | 0.0245 |  | 73.054 | 0 | 0 | -0.01413 | 0.28223 | 0.050066 | 0.46209 | Normal | 73.9782 | 0.36694 | Day | 202512 | 2025-12-14 | 0.36694
2025-12-14 14:43 | 73.2236 | FALSE | FALSE | -1.0599 | -1.4687 | -0.66424 | -0.89898 | 0 |  |  | none | FALSE | 0 | 72.1637 | FALSE | FALSE | 0.0306 |  | 73.0258 | 0 | 0 | -0.02826 | 0.27353 | 0.10332 | 0.43103 | Normal | 73.8878 | 0.45895 | Day | 202512 | 2025-12-14 | 0.45895
2025-12-14 14:59 | 73.2236 | FALSE | FALSE | -1.0599 | -1.4687 | -0.66424 | -0.89898 | 0 |  |  | none | FALSE | 0 | 72.1637 | FALSE | FALSE | 0.0306 |  | 73.0258 | 0 | 0 | 0 | 0.24258 | 0 | 0.43103 | Normal | 73.8878 | 0.45895 | Day | 202512 | 2025-12-14 | 0.45895
2025-12-14 15:14 | 73.2236 | FALSE | FALSE | -0.96467 | -1.335 | -0.65381 | -0.885 | 0 |  |  | none | FALSE | 0 | 72.2589 | FALSE | FALSE | 0.0256 |  | 73.0682 | 0 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.40462 | Normal | 73.8774 | 0.38414 | Day | 202512 | 2025-12-14 | 0.38414
2025-12-14 15:28 | 73.2236 | FALSE | FALSE | -0.85565 | -1.1824 | -0.62957 | -0.85247 | 0 |  |  | none | FALSE | 0 | 72.3679 | FALSE | FALSE | 0.0203 |  | 73.1106 | 0 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.37131 | Normal | 73.8532 | 0.30444 | Day | 202512 | 2025-12-14 | 0.30444
2025-12-14 15:43 | 73.2236 | FALSE | FALSE | -0.72863 | -1.0051 | -0.58733 | -0.79572 | 0 |  |  | none | FALSE | 0 | 72.495 | FALSE | FALSE | 0.0143 |  | 73.153 | 0 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.32899 | Normal | 73.8109 | 0.21475 | Day | 202512 | 2025-12-14 | 0.21475
2025-12-14 15:58 | 73.2236 | FALSE | FALSE | -0.57532 | -0.79193 | -0.5188 | -0.70353 | 0 |  |  | none | FALSE | 0 | 72.6483 | FALSE | FALSE | 0.0069 |  | 73.1953 | 0 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.27353 | Normal | 73.7424 | 0.10332 | Day | 202512 | 2025-12-14 | 0.10332
2025-12-14 16:13 | 73.2236 | FALSE | FALSE | -0.37379 | -0.51309 | -0.40205 | -0.54607 | 0 |  |  | none | FALSE | 0 | 72.8498 | FALSE | FALSE | 0.0049 |  | 73.2377 | 0 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.19396 | Normal | 73.6256 | -0.072851 | Day | 202512 | 2025-12-14 | 0.072851
2025-12-14 16:28 | 73.2236 | FALSE | FALSE | -0.2342 | -0.32086 | -0.31898 | -0.43373 | 0 |  |  | none | FALSE | 0 | 72.9894 | FALSE | FALSE | 0.0204 |  | 73.266 | 0 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.13829 | Normal | 73.5426 | -0.30652 | Day | 202512 | 2025-12-14 | 0.30652
2025-12-14 16:43 | 73.2236 | FALSE | FALSE | -0.17543 | -0.24016 | -0.28847 | -0.39242 | 0 |  |  | none | FALSE | 0 | 73.0482 | FALSE | FALSE | 0.0325 |  | 73.2801 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.11598 | Normal | 73.5121 | -0.48734 | Day | 202512 | 2025-12-14 | 0.48734
2025-12-14 16:58 | 73.2236 | FALSE | FALSE | -0.17543 | -0.24016 | -0.28847 | -0.39242 | 0 |  |  | none | FALSE | 0 | 73.0482 | FALSE | FALSE | 0.0325 |  | 73.2801 | 0 | 0 | 0 | 0.091688 | 0 | 0.11598 | Normal | 73.5121 | -0.48734 | Day | 202512 | 2025-12-14 | 0.48734
2025-12-14 17:13 | 72.941 | TRUE | FALSE | 0.048403 | 0.066316 | -0.60158 | -0.818 | -0.2826 | 2025-12-14 20:29 | 2025-12-14 17:13 | lower | TRUE | 1 | 72.9894 | FALSE | FALSE | 0.2424 | 2.35 | 73.266 | 1 | -0.2826 | -0.01413 | 0.11135 | -2.411 | 0.13829 | Extreme triggered | 73.5426 | -2.35 | Day | 202512 | 2025-12-14 | 2.35
2025-12-14 17:28 | 72.941 | FALSE | FALSE | -0.0014165 | -0.0019421 | -0.62314 | -0.84707 | 0 |  | 2025-12-14 17:13 | none | FALSE | 1 | 72.9396 | FALSE | FALSE | 0.2756 | 2.1705 | 73.2519 | 2 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.15614 | Extreme/elevated | 73.5641 | -1.9909 | Day | 202512 | 2025-12-14 | 1.9909
2025-12-14 17:30 | 72.941 | FALSE | FALSE | -0.045106 | -0.061877 | -0.63857 | -0.86786 | 0 |  | 2025-12-14 17:13 | none | FALSE | 1 | 72.8959 | FALSE | FALSE | 0.3157 | 2.0257 | 73.2377 | 3 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.17092 | Persistent | 73.5796 | -1.7361 | Day | 202512 | 2025-12-14 | 1.7361
2025-12-14 17:31 | 72.941 | FALSE | FALSE | -0.08415 | -0.1155 | -0.64935 | -0.88238 | 0 |  | 2025-12-14 17:13 | none | FALSE | 1 | 72.8568 | FALSE | FALSE | 0.3599 | 1.9045 | 73.2236 | 4 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.18338 | Persistent | 73.5904 | -1.5411 | Night | 202512 | 2025-12-14 | 1.5411
2025-12-14 17:46 | 72.941 | FALSE | FALSE | -0.1078 | -0.14801 | -0.61648 | -0.83809 | 0 |  | 2025-12-14 17:13 | none | FALSE | 1 | 72.8332 | FALSE | FALSE | 0.4079 | 1.8046 | 73.1953 | 5 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18107 | Persistent | 73.5575 | -1.4047 | Night | 202512 | 2025-12-14 | 1.4047
2025-12-14 18:01 | 73.5062 | TRUE | FALSE | -0.673 | -0.92402 | -0.051277 | -0.06971 | 0.5652 |  | 2025-12-14 17:13 | none | FALSE | 2 | 72.8332 | TRUE | FALSE | 0.5145 | 1.7899 | 73.1953 | 6 | 0.5652 | 0 | 0.15881 | 3.559 | 0.18107 | Persistent | 73.5575 | 1.7168 | Night | 202512 | 2025-12-14 | 1.7168
2025-12-14 18:16 | 73.7888 | FALSE | TRUE | -1.0084 | -1.3855 | 0.15026 | 0.20405 | 0.2826 |  | 2025-12-14 17:13 | upper | TRUE | 2 | 72.7804 | FALSE | TRUE | 0.6372 | 1.92 | 73.2095 | 7 | 0.2826 | 0.01413 | 0.17092 | 1.5708 | 0.21454 | Confirmed/Materialized Shift | 73.6385 | 2.7004 | Night | 202512 | 2025-12-14 | 2.7004
2025-12-14 18:30 | 74.0714 | FALSE | TRUE | -1.3981 | -1.9239 | 0.26921 | 0.36478 | 0.2826 |  | 2025-12-14 17:13 | upper | TRUE | 2 | 72.6733 | FALSE | TRUE | 0.6541 | 2.0492 | 73.2377 | 8 | 0.2826 | 0.02826 | 0.18107 | 1.4047 | 0.28223 | Confirmed/Materialized Shift | 73.8022 | 2.9539 | Night | 202512 | 2025-12-14 | 2.9539
2025-12-14 18:45 | 74.0714 | FALSE | TRUE | -1.4675 | -2.0213 | 0.11503 | 0.15553 | 0 |  | 2025-12-14 17:13 | upper | TRUE | 2 | 72.6039 | FALSE | TRUE | 0.6132 | 2.0816 | 73.2801 | 9 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.33813 | Confirmed/Materialized Shift | 73.9564 | 2.3402 | Night | 202512 | 2025-12-14 | 2.3402
2025-12-14 19:00 | 74.0714 | FALSE | TRUE | -1.5111 | -2.0825 | -0.013276 | -0.01792 | 0 |  | 2025-12-14 17:13 | none | FALSE | 2 | 72.5603 | FALSE | FALSE | 0.5882 | 2.0699 | 73.3225 | 10 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.38108 | Confirmed/Materialized Shift | 74.0847 | 1.9652 | Night | 202512 | 2025-12-14 | 1.9652
2025-12-14 19:15 | 74.0714 | FALSE | TRUE | -1.5368 | -2.1187 | -0.12377 | -0.16681 | 0 |  | 2025-12-14 17:13 | none | FALSE | 1 | 72.5346 | FALSE | FALSE | 0.542 | 2.0365 | 73.3649 | 11 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.41513 | Confirmed/Materialized Shift | 74.1952 | 1.7019 | Night | 202512 | 2025-12-14 | 1.7019
2025-12-14 19:29 | 74.0714 | FALSE | TRUE | -1.5488 | -2.1356 | -0.22057 | -0.29689 | 0 |  | 2025-12-14 17:13 | none | FALSE | 1 | 72.5226 | FALSE | FALSE | 0.5287 | 1.9919 | 73.4073 | 12 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.44234 | Confirmed/Materialized Shift | 74.292 | 1.5014 | Night | 202512 | 2025-12-14 | 1.5014
2025-12-14 19:44 | 74.0714 | FALSE | TRUE | -1.5495 | -2.1366 | -0.30609 | -0.41154 | 0 |  | 2025-12-14 17:13 | none | FALSE | 1 | 72.5219 | FALSE | FALSE | 0.5179 | 1.9417 | 73.4497 | 13 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.46391 | Confirmed/Materialized Shift | 74.3775 | 1.3402 | Night | 202512 | 2025-12-14 | 1.3402
2025-12-14 19:59 | 74.0714 | FALSE | TRUE | -1.5405 | -2.124 | -0.38186 | -0.51289 | 0 |  | 2025-12-14 17:13 | none | FALSE | 1 | 72.5309 | FALSE | FALSE | 0.5089 | 1.8891 | 73.4921 | 14 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.48059 | Confirmed/Materialized Shift | 74.4533 | 1.2054 | Night | 202512 | 2025-12-14 | 1.2054
2025-12-14 20:14 | 74.0714 | FALSE | TRUE | -1.5227 | -2.0989 | -0.44886 | -0.60233 | 0 |  | 2025-12-14 17:13 | none | FALSE | 1 | 72.5487 | FALSE | FALSE | 0.5012 | 1.8358 | 73.5345 | 15 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.4929 | Confirmed/Materialized Shift | 74.5203 | 1.0893 | Night | 202512 | 2025-12-14 | 1.0893
2025-12-14 20:29 | 74.0714 | FALSE | FALSE | -1.4968 | -2.0625 | -0.50774 | -0.68081 | 0 |  |  | none | FALSE | 0 | 72.5746 | FALSE | FALSE | 0.0658 |  | 73.5768 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.50115 | Persistence ends | 74.5791 | 0.98684 | Night | 202512 | 2025-12-14 | 0.98684
2025-12-14 20:44 | 74.0714 | FALSE | FALSE | -1.4632 | -2.0152 | -0.5589 | -0.74889 | 0 |  |  | none | FALSE | 0 | 72.6082 | FALSE | FALSE | 0.0596 |  | 73.6192 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.50553 | Normal | 74.6303 | 0.89443 | Night | 202512 | 2025-12-14 | 0.89443
2025-12-14 20:59 | 74.0714 | FALSE | FALSE | -1.4221 | -1.9575 | -0.60254 | -0.80689 | 0 |  |  | none | FALSE | 0 | 72.6493 | FALSE | FALSE | 0.054 |  | 73.6616 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.50615 | Normal | 74.6739 | 0.80958 | Night | 202512 | 2025-12-14 | 0.80958
2025-12-14 21:14 | 74.0714 | FALSE | FALSE | -1.3734 | -1.8892 | -0.63868 | -0.85488 | 0 |  |  | none | FALSE | 0 | 72.698 | FALSE | FALSE | 0.0487 |  | 73.704 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.50303 | Normal | 74.7101 | 0.73033 | Night | 202512 | 2025-12-14 | 0.73033
2025-12-14 21:29 | 74.0714 | FALSE | FALSE | -1.3172 | -1.8104 | -0.66719 | -0.89269 | 0 |  |  | none | FALSE | 0 | 72.7542 | FALSE | FALSE | 0.0437 |  | 73.7464 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.49609 | Normal | 74.7386 | 0.65511 | Night | 202512 | 2025-12-14 | 0.65511
2025-12-14 21:44 | 74.0714 | FALSE | FALSE | -1.194 | -1.6384 | -0.65707 | -0.87928 | 0 |  |  | none | FALSE | 0 | 72.8774 | FALSE | FALSE | 0.0387 |  | 73.8029 | 0 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.46277 | Normal | 74.7285 | 0.58013 | Night | 202512 | 2025-12-14 | 0.58013
2025-12-14 21:59 | 74.0714 | FALSE | FALSE | -1.0498 | -1.4376 | -0.62588 | -0.83788 | 0 |  |  | none | FALSE | 0 | 73.0216 | FALSE | FALSE | 0.0337 |  | 73.8594 | 0 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.41891 | Normal | 74.6973 | 0.50595 | Night | 202512 | 2025-12-14 | 0.50595
2025-12-14 22:14 | 74.0714 | FALSE | FALSE | -0.8768 | -1.1979 | -0.56594 | -0.75825 | 0 |  |  | none | FALSE | 0 | 73.1946 | FALSE | FALSE | 0.0287 |  | 73.916 | 0 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.36068 | Normal | 74.6373 | 0.43093 | Night | 202512 | 2025-12-14 | 0.43093
2025-12-14 22:28 | 74.0714 | FALSE | FALSE | -0.65738 | -0.89544 | -0.45956 | -0.6166 | 0 |  |  | none | FALSE | 0 | 73.414 | FALSE | FALSE | 0.0236 |  | 73.9725 | 0 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.27923 | Normal | 74.531 | 0.35422 | Night | 202512 | 2025-12-14 | 0.35422
2025-12-14 22:43 | 74.0714 | FALSE | FALSE | -0.31898 | -0.4325 | -0.2342 | -0.31518 | 0 |  |  | none | FALSE | 0 | 73.7524 | FALSE | FALSE | 0.0204 |  | 74.029 | 0 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.13829 | Normal | 74.3056 | 0.30652 | Night | 202512 | 2025-12-14 | 0.30652
2025-12-14 22:44 | 74.0714 | FALSE | FALSE | -0.14051 | -0.19006 | -0.11225 | -0.15132 | 0 |  |  | none | FALSE | 0 | 73.9309 | FALSE | FALSE | 0.0149 |  | 74.0573 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.063191 | Normal | 74.1837 | 0.22361 | Night | 202512 | 2025-12-14 | 0.22361
2025-12-14 22:59 | 74.0714 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.0714 | FALSE | FALSE | 0 |  | 74.0714 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0 | Normal | 74.0714 |  | Night | 202512 | 2025-12-14
2025-12-14 23:14 | 74.0714 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.0714 | FALSE | FALSE | 0 |  | 74.0714 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.0714 |  | Night | 202512 | 2025-12-14
2025-12-14 23:29 | 74.0714 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.0714 | FALSE | FALSE | 0 |  | 74.0714 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.0714 |  | Night | 202512 | 2025-12-14
2025-12-14 23:44 | 74.0714 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.0714 | FALSE | FALSE | 0 |  | 74.0714 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.0714 |  | Night | 202512 | 2025-12-14
2025-12-14 23:59 | 74.0714 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.0714 | FALSE | FALSE | 0 |  | 74.0714 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.0714 |  | Night | 202512 | 2025-12-14
2025-12-15 00:14 | 74.0714 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.0714 | FALSE | FALSE | 0 |  | 74.0714 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.0714 |  | Night | 202512 | 2025-12-15
2025-12-15 00:29 | 74.0714 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.0714 | FALSE | FALSE | 0 |  | 74.0714 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.0714 |  | Night | 202512 | 2025-12-15
2025-12-15 00:43 | 74.0714 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.0714 | FALSE | FALSE | 0 |  | 74.0714 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.0714 |  | Night | 202512 | 2025-12-15
2025-12-15 00:58 | 74.0714 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.0714 | FALSE | FALSE | 0 |  | 74.0714 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.0714 |  | Night | 202512 | 2025-12-15
2025-12-15 01:13 | 74.0714 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.0714 | FALSE | FALSE | 0 |  | 74.0714 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.0714 |  | Night | 202512 | 2025-12-15
2025-12-15 01:28 | 74.0714 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.0714 | FALSE | FALSE | 0 |  | 74.0714 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.0714 |  | Night | 202512 | 2025-12-15
2025-12-15 01:43 | 74.0714 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.0714 | FALSE | FALSE | 0 |  | 74.0714 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.0714 |  | Night | 202512 | 2025-12-15
2025-12-15 01:58 | 74.0714 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.0714 | FALSE | FALSE | 0 |  | 74.0714 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.0714 |  | Night | 202512 | 2025-12-15
2025-12-15 02:13 | 73.7888 | TRUE | FALSE | 0.14209 | 0.19219 | -0.39485 | -0.53226 | -0.2826 | 2025-12-15 05:27 | 2025-12-15 02:13 | lower | TRUE | 1 | 73.9309 | FALSE | FALSE | 0.3689 | 4.2485 | 74.0573 | 1 | -0.2826 | -0.01413 | 0.063191 | -4.2485 | 0.063191 | Extreme triggered | 74.1837 | -4.2485 | Night | 202512 | 2025-12-15 | 4.2485
2025-12-15 02:28 | 73.7888 | FALSE | FALSE | 0.080375 | 0.10881 | -0.4283 | -0.5771 | 0 |  | 2025-12-15 02:13 | lower | TRUE | 1 | 73.8692 | FALSE | FALSE | 0.3378 | 3.5863 | 74.0431 | 2 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.086982 | Extreme/elevated | 74.2171 | -2.924 | Night | 202512 | 2025-12-15 | 2.924
2025-12-15 02:43 | 73.7888 | FALSE | FALSE | 0.03315 | 0.044906 | -0.44727 | -0.6025 | 0 |  | 2025-12-15 02:13 | lower | TRUE | 1 | 73.822 | FALSE | TRUE | 0.3547 | 3.1643 | 74.029 | 3 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.10353 | Persistent | 74.2361 | -2.3202 | Night | 202512 | 2025-12-15 | 2.3202
2025-12-15 02:58 | 73.7888 | FALSE | FALSE | -0.0058732 | -0.0079601 | -0.45803 | -0.61691 | 0 |  | 2025-12-15 02:13 | none | FALSE | 1 | 73.7829 | FALSE | FALSE | 0.3871 | 2.8605 | 74.0149 | 4 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.11598 | Persistent | 74.2468 | -1.9494 | Night | 202512 | 2025-12-15 | 1.9494
2025-12-15 03:13 | 73.5062 | TRUE | FALSE | 0.15755 | 0.21388 | -0.80329 | -1.081 | -0.2826 |  | 2025-12-15 02:13 | lower | TRUE | 2 | 73.6638 | TRUE | TRUE | 0.5413 | 2.8836 | 73.9866 | 5 | -0.2826 | -0.02826 | 0.086982 | -2.924 | 0.16143 | Persistent | 74.3095 | -2.976 | Night | 202512 | 2025-12-15 | 2.976
2025-12-15 03:28 | 73.7888 | TRUE | FALSE | -0.14816 | -0.2012 | -0.51554 | -0.69383 | 0.2826 |  | 2025-12-15 02:13 | none | FALSE | 3 | 73.6406 | TRUE | FALSE | 0.5024 | 2.5875 | 73.9725 | 6 | 0.2826 | -0.01413 | 0.11135 | 2.6647 | 0.16593 | Persistent | 74.3043 | -1.1071 | Night | 202512 | 2025-12-15 | 1.1071
2025-12-15 03:42 | 73.5062 | TRUE | TRUE | 0.050115 | 0.068131 | -0.82595 | -1.1112 | -0.2826 |  | 2025-12-15 02:13 | lower | TRUE | 4 | 73.5563 | TRUE | TRUE | 0.6648 | 2.5405 | 73.9442 | 7 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.19396 | Confirmed/Materialized Shift | 74.3321 | -2.2584 | Night | 202512 | 2025-12-15 | 2.2584
2025-12-15 03:57 | 73.5062 | FALSE | TRUE | -0.019304 | -0.026269 | -0.83884 | -1.1283 | 0 |  | 2025-12-15 02:13 | none | FALSE | 4 | 73.4869 | FALSE | FALSE | 0.6416 | 2.4617 | 73.916 | 8 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21454 | Confirmed/Materialized Shift | 74.345 | -1.91 | Night | 202512 | 2025-12-15 | 1.91
2025-12-15 04:12 | 73.5062 | FALSE | TRUE | -0.077844 | -0.10601 | -0.84086 | -1.131 | 0 |  | 2025-12-15 02:13 | none | FALSE | 4 | 73.4284 | FALSE | FALSE | 0.625 | 2.3727 | 73.8877 | 9 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.22968 | Confirmed/Materialized Shift | 74.3471 | -1.6611 | Night | 202512 | 2025-12-15 | 1.6611
2025-12-15 04:27 | 73.5062 | FALSE | TRUE | -0.12756 | -0.17384 | -0.83406 | -1.122 | 0 |  | 2025-12-15 02:13 | none | FALSE | 4 | 73.3786 | FALSE | FALSE | 0.6122 | 2.2824 | 73.8594 | 10 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.24041 | Confirmed/Materialized Shift | 74.3403 | -1.4694 | Night | 202512 | 2025-12-15 | 1.4694
2025-12-15 04:42 | 73.5062 | FALSE | TRUE | -0.16961 | -0.23128 | -0.81959 | -1.1027 | 0 |  | 2025-12-15 02:13 | none | FALSE | 3 | 73.3366 | FALSE | FALSE | 0.5733 | 2.1944 | 73.8312 | 11 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.2473 | Confirmed/Materialized Shift | 74.3258 | -1.3141 | Night | 202512 | 2025-12-15 | 1.3141
2025-12-15 04:57 | 73.5062 | FALSE | TRUE | -0.20463 | -0.27916 | -0.79809 | -1.0741 | 0 |  | 2025-12-15 02:13 | none | FALSE | 3 | 73.3016 | FALSE | FALSE | 0.5646 | 2.1102 | 73.8029 | 12 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.25068 | Confirmed/Materialized Shift | 74.3043 | -1.1837 | Night | 202512 | 2025-12-15 | 1.1837
2025-12-15 05:12 | 73.5062 | FALSE | TRUE | -0.23289 | -0.31783 | -0.76983 | -1.0364 | 0 |  | 2025-12-15 02:13 | none | FALSE | 3 | 73.2733 | FALSE | FALSE | 0.5571 | 2.0302 | 73.7747 | 13 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.25068 | Confirmed/Materialized Shift | 74.276 | -1.071 | Night | 202512 | 2025-12-15 | 1.071
2025-12-15 05:27 | 73.5062 | FALSE | FALSE | -0.25439 | -0.34729 | -0.73481 | -0.98977 | 0 |  |  | none | FALSE | 3 | 73.2518 | FALSE | FALSE | 0.1505 |  | 73.7464 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.2473 | Persistence ends | 74.241 | -0.97132 | Night | 202512 | 2025-12-15 | 0.97132
2025-12-15 05:42 | 73.5062 | FALSE | FALSE | -0.26886 | -0.36711 | -0.69276 | -0.93366 | 0 |  |  | none | FALSE | 2 | 73.2373 | FALSE | FALSE | 0.1159 |  | 73.7181 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.24041 | Normal | 74.199 | -0.88163 | Night | 202512 | 2025-12-15 | 0.88163
2025-12-15 05:57 | 73.2236 | FALSE | FALSE | -0.046674 | -0.063783 | -0.95099 | -1.2821 | -0.2826 |  |  | none | FALSE | 1 | 73.1769 | FALSE | FALSE | 0.1494 |  | 73.6758 | 0 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.24942 | Normal | 74.1746 | -1.8129 | Night | 202512 | 2025-12-15 | 1.8129
2025-12-15 06:12 | 73.2236 | FALSE | FALSE | -0.091586 | -0.12523 | -0.91113 | -1.229 | 0 |  |  | none | FALSE | 0 | 73.132 | FALSE | FALSE | 0.109 |  | 73.6334 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.25068 | Normal | 74.1347 | -1.6346 | Night | 202512 | 2025-12-15 | 1.6346
2025-12-15 06:27 | 73.2236 | FALSE | FALSE | -0.12124 | -0.16585 | -0.856 | -1.1555 | 0 |  |  | none | FALSE | 0 | 73.1024 | FALSE | FALSE | 0.1003 |  | 73.591 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.24431 | Normal | 74.0796 | -1.5038 | Night | 202512 | 2025-12-15 | 1.5038
2025-12-15 06:41 | 73.2236 | FALSE | FALSE | -0.13436 | -0.18384 | -0.78434 | -1.0598 | 0 |  |  | none | FALSE | 0 | 73.0892 | FALSE | FALSE | 0.0943 |  | 73.5486 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.22968 | Normal | 74.0079 | -1.415 | Night | 202512 | 2025-12-15 | 1.415
2025-12-15 06:56 | 73.2236 | FALSE | FALSE | -0.12744 | -0.17434 | -0.69264 | -0.93706 | 0 |  |  | none | FALSE | 0 | 73.0962 | FALSE | FALSE | 0.0919 |  | 73.5062 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.20502 | Normal | 73.9162 | -1.3784 | Night | 202512 | 2025-12-15 | 1.3784
2025-12-15 07:11 | 73.2236 | FALSE | FALSE | -0.15158 | -0.20744 | -0.66026 | -0.89364 | 0 |  |  | none | FALSE | 0 | 73.072 | FALSE | FALSE | 0.0835 |  | 73.4779 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.20296 | Normal | 73.8839 | -1.2532 | Day | 202512 | 2025-12-15 | 1.2532
2025-12-15 07:26 | 73.2236 | FALSE | FALSE | -0.16722 | -0.22889 | -0.61938 | -0.83877 | 0 |  |  | none | FALSE | 0 | 73.0564 | FALSE | FALSE | 0.0766 |  | 73.4497 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.19665 | Normal | 73.843 | -1.1497 | Day | 202512 | 2025-12-15 | 1.1497
2025-12-15 07:30 | 73.2236 | FALSE | FALSE | -0.17349 | -0.23749 | -0.56913 | -0.77125 | 0 |  |  | none | FALSE | 0 | 73.0501 | FALSE | FALSE | 0.071 |  | 73.4214 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.18565 | Normal | 73.7927 | -1.0655 | Day | 202512 | 2025-12-15 | 1.0655
2025-12-15 07:45 | 73.2236 | FALSE | FALSE | -0.16857 | -0.23074 | -0.50769 | -0.68856 | 0 |  |  | none | FALSE | 0 | 73.055 | FALSE | FALSE | 0.0669 |  | 73.3932 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.16906 | Normal | 73.7313 | -1.0029 | Day | 202512 | 2025-12-15 | 1.0029
2025-12-15 08:00 | 73.2236 | FALSE | FALSE | -0.18641 | -0.25522 | -0.49727 | -0.67453 | 0 |  |  | none | FALSE | 0 | 73.0372 | FALSE | FALSE | 0.0606 |  | 73.379 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.17092 | Normal | 73.7209 | -0.90938 | Day | 202512 | 2025-12-15 | 0.90938
2025-12-15 08:15 | 73.2236 | FALSE | FALSE | -0.16132 | -0.2208 | -0.41566 | -0.56445 | 0 |  |  | none | FALSE | 0 | 73.0623 | FALSE | FALSE | 0.0588 |  | 73.3508 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.14424 | Normal | 73.6393 | -0.88163 | Day | 202512 | 2025-12-15 | 0.88163
2025-12-15 08:30 | 73.2236 | FALSE | FALSE | -0.17104 | -0.23414 | -0.39712 | -0.53942 | 0 |  |  | none | FALSE | 0 | 73.0526 | FALSE | FALSE | 0.0531 |  | 73.3366 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14204 | Normal | 73.6207 | -0.79582 | Day | 202512 | 2025-12-15 | 0.79582
2025-12-15 08:30 | 73.2236 | FALSE | FALSE | -0.17768 | -0.24324 | -0.3755 | -0.51019 | 0 |  |  | none | FALSE | 0 | 73.0459 | FALSE | FALSE | 0.0477 |  | 73.3225 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13829 | Normal | 73.5991 | -0.71522 | Day | 202512 | 2025-12-15 | 0.71522
2025-12-15 08:45 | 73.2236 | FALSE | FALSE | -0.18096 | -0.24774 | -0.35052 | -0.47641 | 0 |  |  | none | FALSE | 0 | 73.0426 | FALSE | FALSE | 0.0425 |  | 73.3084 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13287 | Normal | 73.5741 | -0.63808 | Day | 202512 | 2025-12-15 | 0.63808
2025-12-15 09:00 | 73.2236 | FALSE | FALSE | -0.18045 | -0.24704 | -0.32175 | -0.43748 | 0 |  |  | none | FALSE | 0 | 73.0432 | FALSE | FALSE | 0.0375 |  | 73.2943 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.12555 | Normal | 73.5453 | -0.56273 | Day | 202512 | 2025-12-15 | 0.56273
2025-12-15 09:15 | 73.2236 | FALSE | FALSE | -0.17543 | -0.24016 | -0.28847 | -0.39242 | 0 |  |  | none | FALSE | 0 | 73.0482 | FALSE | FALSE | 0.0325 |  | 73.2801 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.11598 | Normal | 73.5121 | -0.48734 | Day | 202512 | 2025-12-15 | 0.48734
2025-12-15 09:30 | 73.2236 | FALSE | FALSE | -0.16467 | -0.22539 | -0.24945 | -0.33951 | 0 |  |  | none | FALSE | 0 | 73.0589 | FALSE | FALSE | 0.0273 |  | 73.266 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.10353 | Normal | 73.473 | -0.40945 | Day | 202512 | 2025-12-15 | 0.40945
2025-12-15 09:45 | 73.2236 | FALSE | FALSE | -0.1457 | -0.19938 | -0.20222 | -0.27541 | 0 |  |  | none | FALSE | 0 | 73.0779 | FALSE | FALSE | 0.0217 |  | 73.2519 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.086982 | Normal | 73.4258 | -0.32489 | Day | 202512 | 2025-12-15 | 0.32489
2025-12-15 10:00 | 73.5062 | TRUE | FALSE | -0.4283 | -0.58609 | 0.080375 | 0.10946 | 0.2826 | 2025-12-15 11:20 | 2025-12-15 10:00 | upper | TRUE | 1 | 73.0779 | FALSE | FALSE | 0.2807 | 2.924 | 73.2519 | 1 | 0.2826 | 0 | 0.091688 | 3.0822 | 0.086982 | Extreme triggered | 73.4258 | 2.924 | Day | 202512 | 2025-12-15 | 2.924
2025-12-15 10:15 | 73.7888 | TRUE | FALSE | -0.7994 | -1.0952 | 0.24622 | 0.3348 | 0.2826 |  | 2025-12-15 10:00 | upper | TRUE | 2 | 72.9894 | TRUE | FALSE | 0.4235 | 3.3522 | 73.266 | 2 | 0.2826 | 0.01413 | 0.11135 | 2.411 | 0.13829 | Extreme/elevated | 73.5426 | 3.7804 | Day | 202512 | 2025-12-15 | 3.7804
2025-12-15 10:29 | 74.0714 | TRUE | FALSE | -1.2159 | -1.669 | 0.31012 | 0.42043 | 0.2826 |  | 2025-12-15 10:00 | upper | TRUE | 3 | 72.8555 | TRUE | TRUE | 0.4818 | 3.358 | 73.3084 | 3 | 0.2826 | 0.04239 | 0.10353 | 2.3202 | 0.22645 | Persistent | 73.7613 | 3.3695 | Day | 202512 | 2025-12-15 | 3.3695
2025-12-15 10:32 | 74.0714 | FALSE | FALSE | -1.2851 | -1.7656 | 0.15617 | 0.21129 | 0 |  | 2025-12-15 10:00 | upper | TRUE | 3 | 72.7863 | FALSE | TRUE | 0.4845 | 3.1568 | 73.3508 | 4 | 0 | 0.04239 | 0.10353 | -0.40945 | 0.28223 | Persistent | 73.9152 | 2.5534 | Day | 202512 | 2025-12-15 | 2.5534
2025-12-15 10:42 | 72.941 | TRUE | FALSE | -0.19573 | -0.26906 | -0.98701 | -1.3351 | -1.1304 |  | 2025-12-15 10:00 | none | FALSE | 4 | 72.7453 | TRUE | FALSE | 0.4892 | 2.7931 | 73.3366 | 5 | -1.1304 | -0.01413 | 0.28223 | -3.9552 | 0.29568 | Persistent | 73.928 | -1.3381 | Day | 202512 | 2025-12-15 | 1.3381
2025-12-15 10:50 | 71.8124 | TRUE | FALSE | 0.55081 | 0.76117 | -2.3566 | -3.1773 | -1.1286 |  | 2025-12-15 10:00 | lower | TRUE | 5 | 72.3632 | TRUE | TRUE | 0.7004 | 2.8642 | 73.2661 | 6 | -1.1286 | -0.07056 | 0.37638 | -2.8111 | 0.45144 | Persistent | 74.169 | -3.2201 | Day | 202512 | 2025-12-15 | 3.2201
2025-12-15 11:05 | 72.095 | FALSE | TRUE | 0.070565 | 0.097782 | -2.1587 | -2.9072 | 0.2826 |  | 2025-12-15 10:00 | lower | TRUE | 5 | 72.1656 | FALSE | TRUE | 0.6852 | 2.7601 | 73.2096 | 7 | 0.2826 | -0.05643 | 0.38439 | 0.882 | 0.52204 | Confirmed/Materialized Shift | 74.2537 | -2.1352 | Day | 202512 | 2025-12-15 | 2.1352
2025-12-15 11:20 | 72.941 | FALSE | FALSE | -0.7964 | -1.1039 | -1.3054 | -1.7582 | 0.846 |  |  | none | FALSE | 5 | 72.1446 | FALSE | FALSE | 0.1751 |  | 73.1955 | 0 | 0.846 | -0.01413 | 0.43424 | 1.9808 | 0.52546 | Persistence ends | 74.2464 | -0.48438 | Day | 202512 | 2025-12-15 | 0.48438
2025-12-15 11:32 | 73.2236 | FALSE | FALSE | -1.079 | -1.4956 | -1.0228 | -1.3776 | 0.2826 |  |  | none | FALSE | 5 | 72.1446 | FALSE | FALSE | 0.1464 |  | 73.1955 | 0 | 0.2826 | 0 | 0.43929 | 0.64331 | 0.52546 | Normal | 74.2464 | 0.053439 | Day | 202512 | 2025-12-15 | 0.053439
2025-12-15 11:47 | 73.7888 | FALSE | FALSE | -1.649 | -2.2858 | -0.51895 | -0.69838 | 0.5652 |  |  | none | FALSE | 5 | 72.1398 | FALSE | FALSE | 0.2124 |  | 73.2238 | 0 | 0.5652 | 0.02826 | 0.45711 | 1.1746 | 0.54199 | Normal | 74.3078 | 1.0425 | Day | 202512 | 2025-12-15 | 1.0425
2025-12-15 12:02 | 73.7888 | FALSE | FALSE | -1.6498 | -2.287 | -0.57627 | -0.77493 | 0 |  |  | none | FALSE | 4 | 72.139 | FALSE | FALSE | 0.1786 |  | 73.252 | 0 | 0 | 0.02826 | 0.45711 | -0.061823 | 0.55652 | Normal | 74.3651 | 0.9645 | Day | 202512 | 2025-12-15 | 0.9645
2025-12-15 12:17 | 73.5062 | FALSE | FALSE | -1.3587 | -1.8832 | -0.87865 | -1.1812 | -0.2826 |  |  | none | FALSE | 3 | 72.1475 | FALSE | FALSE | 0.1143 |  | 73.2662 | 0 | -0.2826 | 0.01413 | 0.46237 | -0.64176 | 0.55934 | Normal | 74.3848 | 0.42913 | Day | 202512 | 2025-12-15 | 0.42913
2025-12-15 12:32 | 73.5062 | FALSE | FALSE | -1.3494 | -1.8702 | -0.89764 | -1.2064 | 0 |  |  | none | FALSE | 2 | 72.1568 | FALSE | FALSE | 0.084 |  | 73.2803 | 0 | 0 | 0.01413 | 0.46237 | -0.03056 | 0.56177 | Normal | 74.4038 | 0.40212 | Day | 202512 | 2025-12-15 | 0.40212
2025-12-15 12:47 | 73.2236 | FALSE | FALSE | -1.0668 | -1.4785 | -1.1802 | -1.5863 | -0.2826 |  |  | none | FALSE | 2 | 72.1568 | FALSE | FALSE | 0.0639 |  | 73.2803 | 0 | -0.2826 | 0 | 0.46712 | -0.60499 | 0.56177 | Normal | 74.4038 | -0.10093 | Day | 202512 | 2025-12-15 | 0.10093
2025-12-15 13:02 | 73.2236 | FALSE | FALSE | -1.0668 | -1.4785 | -1.1802 | -1.5863 | 0 |  |  | none | FALSE | 1 | 72.1568 | FALSE | FALSE | 0.0353 |  | 73.2803 | 0 | 0 | 0 | 0.46712 | 0 | 0.56177 | Normal | 74.4038 | -0.10093 | Day | 202512 | 2025-12-15 | 0.10093
2025-12-15 13:17 | 73.2236 | FALSE | FALSE | -1.0668 | -1.4785 | -1.1802 | -1.5863 | 0 |  |  | none | FALSE | 0 | 72.1568 | FALSE | FALSE | 0.0067 |  | 73.2803 | 0 | 0 | 0 | 0.46712 | 0 | 0.56177 | Normal | 74.4038 | -0.10093 | Day | 202512 | 2025-12-15 | 0.10093
2025-12-15 13:31 | 73.2236 | FALSE | FALSE | -1.0668 | -1.4785 | -1.1802 | -1.5863 | 0 |  |  | none | FALSE | 0 | 72.1568 | FALSE | FALSE | 0.0067 |  | 73.2803 | 0 | 0 | 0 | 0.46712 | 0 | 0.56177 | Normal | 74.4038 | -0.10093 | Day | 202512 | 2025-12-15 | 0.10093
2025-12-15 13:46 | 73.2236 | FALSE | FALSE | -1.0668 | -1.4785 | -1.1802 | -1.5863 | 0 |  |  | none | FALSE | 0 | 72.1568 | FALSE | FALSE | 0.0067 |  | 73.2803 | 0 | 0 | 0 | 0.46712 | 0 | 0.56177 | Normal | 74.4038 | -0.10093 | Day | 202512 | 2025-12-15 | 0.10093
2025-12-15 14:01 | 73.2236 | FALSE | FALSE | -1.0668 | -1.4785 | -1.1802 | -1.5863 | 0 |  |  | none | FALSE | 0 | 72.1568 | FALSE | FALSE | 0.0067 |  | 73.2803 | 0 | 0 | 0 | 0.46712 | 0 | 0.56177 | Normal | 74.4038 | -0.10093 | Day | 202512 | 2025-12-15 | 0.10093
2025-12-15 14:16 | 73.2236 | FALSE | FALSE | -1.0668 | -1.4785 | -1.1802 | -1.5863 | 0 |  |  | none | FALSE | 0 | 72.1568 | FALSE | FALSE | 0.0067 |  | 73.2803 | 0 | 0 | 0 | 0.46712 | 0 | 0.56177 | Normal | 74.4038 | -0.10093 | Day | 202512 | 2025-12-15 | 0.10093
2025-12-15 14:31 | 73.2236 | FALSE | FALSE | -1.0761 | -1.4915 | -1.1612 | -1.5611 | 0 |  |  | none | FALSE | 0 | 72.1475 | FALSE | FALSE | 0.0051 |  | 73.2662 | 0 | 0 | -0.01413 | 0.46237 | 0.03056 | 0.55934 | Normal | 74.3848 | -0.076108 | Day | 202512 | 2025-12-15 | 0.076108
2025-12-15 14:46 | 73.2236 | FALSE | FALSE | -1.077 | -1.4928 | -1.1056 | -1.4875 | 0 |  |  | none | FALSE | 0 | 72.1466 | FALSE | FALSE | 0.0017 |  | 73.2379 | 0 | 0 | -0.02826 | 0.45711 | 0.061823 | 0.54565 | Normal | 74.3292 | -0.026225 | Day | 202512 | 2025-12-15 | 0.026225
2025-12-15 15:01 | 72.941 | FALSE | FALSE | -0.78421 | -1.0868 | -1.265 | -1.7047 | -0.2826 |  |  | none | FALSE | 0 | 72.1568 | FALSE | FALSE | 0.0313 |  | 73.1814 | 0 | -0.2826 | -0.05652 | 0.45434 | -0.4976 | 0.5123 | Normal | 74.206 | -0.46924 | Day | 202512 | 2025-12-15 | 0.46924
2025-12-15 15:16 | 73.2236 | FALSE | FALSE | -1.0205 | -1.4133 | -0.85127 | -1.1492 | 0.2826 |  |  | none | FALSE | 0 | 72.2031 | FALSE | FALSE | 0.0121 |  | 73.139 | 0 | 0.2826 | -0.04239 | 0.46055 | 0.70566 | 0.46793 | Normal | 74.0749 | 0.18079 | Day | 202512 | 2025-12-15 | 0.18079
2025-12-15 15:31 | 72.941 | FALSE | FALSE | -0.73787 | -1.0219 | -1.1339 | -1.5307 | -0.2826 |  |  | none | FALSE | 0 | 72.2031 | FALSE | FALSE | 0.0282 |  | 73.139 | 0 | -0.2826 | 0 | 0.38852 | -0.72738 | 0.46793 | Normal | 74.0749 | -0.42314 | Day | 202512 | 2025-12-15 | 0.42314
2025-12-15 15:46 | 72.941 | FALSE | FALSE | -0.45282 | -0.62468 | -0.96168 | -1.3013 | 0 |  |  | none | FALSE | 0 | 72.4882 | FALSE | FALSE | 0.048 |  | 73.1954 | 0 | 0 | 0.05643 | 0.28382 | -0.19882 | 0.35362 | Normal | 73.9027 | -0.71949 | Day | 202512 | 2025-12-15 | 0.71949
2025-12-15 16:01 | 72.941 | FALSE | FALSE | -0.20463 | -0.28133 | -0.79809 | -1.0823 | 0 |  |  | none | FALSE | 0 | 72.7364 | FALSE | FALSE | 0.0789 |  | 73.2377 | 0 | 0 | 0.0423 | 0.27896 | -0.15163 | 0.25068 | Normal | 73.7391 | -1.1837 | Day | 202512 | 2025-12-15 | 1.1837
2025-12-15 16:16 | 72.941 | FALSE | FALSE | -0.20463 | -0.28133 | -0.79809 | -1.0823 | 0 |  |  | none | FALSE | 0 | 72.7364 | FALSE | FALSE | 0.0789 |  | 73.2377 | 0 | 0 | 0 | 0.20502 | 0 | 0.25068 | Normal | 73.7391 | -1.1837 | Day | 202512 | 2025-12-15 | 1.1837
2025-12-15 16:30 | 72.941 | FALSE | FALSE | -0.23606 | -0.32469 | -0.80126 | -1.0866 | 0 |  |  | none | FALSE | 0 | 72.7049 | FALSE | FALSE | 0.0726 |  | 73.2236 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.25933 | Normal | 73.7423 | -1.0897 | Day | 202512 | 2025-12-15 | 1.0897
2025-12-15 16:45 | 72.941 | FALSE | FALSE | -0.21914 | -0.30135 | -0.69956 | -0.94997 | 0 |  |  | none | FALSE | 0 | 72.7219 | FALSE | FALSE | 0.0697 |  | 73.1812 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.22968 | Normal | 73.6406 | -1.0459 | Day | 202512 | 2025-12-15 | 1.0459
2025-12-15 17:00 | 72.6584 | FALSE | FALSE | 0.045126 | 0.062068 | -0.88745 | -1.2067 | -0.2826 | 2025-12-15 19:01 | 2025-12-15 17:00 | lower | TRUE | 0 | 72.7035 | FALSE | FALSE | 0.2048 | 2.2143 | 73.1247 | 1 | -0.2826 | -0.05652 | 0.14784 | -1.5292 | 0.21058 | Extreme triggered | 73.5459 | -2.2143 | Day | 202512 | 2025-12-15 | 2.2143
2025-12-15 17:15 | 72.6584 | FALSE | FALSE | -0.0061527 | -0.0084687 | -0.85395 | -1.1616 | 0 |  | 2025-12-15 17:00 | none | FALSE | 0 | 72.6522 | FALSE | FALSE | 0.2457 | 2.0928 | 73.0823 | 2 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.21503 | Extreme/elevated | 73.5124 | -1.9714 | Day | 202512 | 2025-12-15 | 1.9714
2025-12-15 17:30 | 72.6584 | FALSE | FALSE | -0.039654 | -0.054606 | -0.80267 | -1.0927 | 0 |  | 2025-12-15 17:00 | none | FALSE | 0 | 72.6187 | FALSE | FALSE | 0.2922 | 1.9991 | 73.0399 | 3 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.21058 | Persistent | 73.4611 | -1.8117 | Day | 202512 | 2025-12-15 | 1.8117
2025-12-15 17:45 | 72.3758 | FALSE | FALSE | 0.11619 | 0.16028 | -1.1273 | -1.5336 | -0.2826 |  | 2025-12-15 17:00 | lower | TRUE | 0 | 72.492 | FALSE | TRUE | 0.3925 | 2.1143 | 72.9975 | 4 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.25277 | Persistent | 73.5031 | -2.4597 | Night | 202512 | 2025-12-15 | 2.4597
2025-12-15 18:00 | 72.3758 | FALSE | FALSE | 0.014874 | 0.020547 | -1.1438 | -1.5558 | 0 |  | 2025-12-15 17:00 | lower | TRUE | 0 | 72.3907 | FALSE | TRUE | 0.4226 | 2.1019 | 72.9551 | 5 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.28223 | Persistent | 73.5196 | -2.0527 | Night | 202512 | 2025-12-15 | 2.0527
2025-12-15 18:15 | 72.3758 | FALSE | FALSE | -0.068476 | -0.094701 | -1.1424 | -1.5538 | 0 |  | 2025-12-15 17:00 | none | FALSE | 0 | 72.3073 | FALSE | FALSE | 0.4611 | 2.0473 | 72.9127 | 6 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.30271 | Persistent | 73.5182 | -1.7738 | Night | 202512 | 2025-12-15 | 1.7738
2025-12-15 18:30 | 72.3758 | FALSE | TRUE | -0.13736 | -0.19015 | -1.1265 | -1.5326 | 0 |  | 2025-12-15 17:00 | none | FALSE | 0 | 72.2384 | FALSE | FALSE | 0.5043 | 1.9784 | 72.8704 | 7 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.31596 | Confirmed/Materialized Shift | 73.5023 | -1.5652 | Night | 202512 | 2025-12-15 | 1.5652
2025-12-15 18:30 | 72.3758 | FALSE | TRUE | -0.19357 | -0.26817 | -1.0979 | -1.4943 | 0 |  | 2025-12-15 17:00 | none | FALSE | 0 | 72.1822 | FALSE | FALSE | 0.4934 | 1.9062 | 72.828 | 8 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.32287 | Confirmed/Materialized Shift | 73.4737 | -1.4005 | Night | 202512 | 2025-12-15 | 1.4005
2025-12-15 18:31 | 72.3758 | FALSE | TRUE | -0.23791 | -0.3298 | -1.0575 | -1.44 | 0 |  | 2025-12-15 17:00 | none | FALSE | 0 | 72.1379 | FALSE | FALSE | 0.4844 | 1.835 | 72.7856 | 9 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.32384 | Confirmed/Materialized Shift | 73.4333 | -1.2653 | Night | 202512 | 2025-12-15 | 1.2653
2025-12-15 18:46 | 72.3758 | FALSE | TRUE | -0.27049 | -0.37513 | -1.0053 | -1.3699 | 0 |  | 2025-12-15 17:00 | none | FALSE | 0 | 72.1053 | FALSE | FALSE | 0.4768 | 1.7666 | 72.7432 | 10 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.31894 | Confirmed/Materialized Shift | 73.3811 | -1.1519 | Night | 202512 | 2025-12-15 | 1.1519
2025-12-15 19:01 | 72.6584 | FALSE | FALSE | -0.54051 | -0.74948 | -0.65355 | -0.89146 | 0.2826 |  |  | none | FALSE | 0 | 72.1179 | FALSE | FALSE | 0.0126 |  | 72.7149 | 0 | 0.2826 | -0.02826 | 0.15614 | 1.9909 | 0.29851 | Persistence ends | 73.3119 | -0.18934 | Night | 202512 | 2025-12-15 | 0.18934
2025-12-15 19:16 | 72.941 | FALSE | FALSE | -0.79868 | -1.1071 | -0.31826 | -0.43443 | 0.2826 |  |  | none | FALSE | 0 | 72.1423 | FALSE | FALSE | 0.0573 |  | 72.7008 | 0 | 0.2826 | -0.01413 | 0.17092 | 1.7361 | 0.27923 | Normal | 73.2593 | 0.86025 | Night | 202512 | 2025-12-15 | 0.86025
2025-12-15 19:30 | 73.2236 | FALSE | FALSE | -1.1057 | -1.5332 | -0.088346 | -0.12051 | 0.2826 |  |  | none | FALSE | 0 | 72.1179 | FALSE | FALSE | 0.1136 |  | 72.7149 | 0 | 0.2826 | 0.01413 | 0.17092 | 1.5708 | 0.29851 | Normal | 73.3119 | 1.704 | Night | 202512 | 2025-12-15 | 1.704
2025-12-15 19:45 | 73.2236 | FALSE | FALSE | -1.1057 | -1.5332 | -0.088346 | -0.12051 | 0 |  |  | none | FALSE | 0 | 72.1179 | FALSE | FALSE | 0.1136 |  | 72.7149 | 0 | 0 | 0 | 0.15881 | 0 | 0.29851 | Normal | 73.3119 | 1.704 | Night | 202512 | 2025-12-15 | 1.704
2025-12-15 20:00 | 73.2236 | FALSE | FALSE | -1.1265 | -1.5624 | -0.13736 | -0.18724 | 0 |  |  | none | FALSE | 0 | 72.0971 | FALSE | FALSE | 0.1043 |  | 72.7291 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.31596 | Normal | 73.361 | 1.5652 | Night | 202512 | 2025-12-15 | 1.5652
2025-12-15 20:15 | 73.2236 | FALSE | FALSE | -1.1441 | -1.5873 | -0.18329 | -0.24969 | 0 |  |  | none | FALSE | 0 | 72.0795 | FALSE | FALSE | 0.0965 |  | 72.7432 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.33185 | Normal | 73.4069 | 1.4477 | Night | 202512 | 2025-12-15 | 1.4477
2025-12-15 20:29 | 73.2236 | FALSE | FALSE | -1.1591 | -1.6085 | -0.22654 | -0.30843 | 0 |  |  | none | FALSE | 0 | 72.0645 | FALSE | FALSE | 0.0897 |  | 72.7573 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.34642 | Normal | 73.4501 | 1.346 | Night | 202512 | 2025-12-15 | 1.346
2025-12-15 20:44 | 72.941 | FALSE | FALSE | -0.87652 | -1.2163 | -0.50914 | -0.69318 | -0.2826 |  |  | none | FALSE | 0 | 72.0645 | FALSE | FALSE | 0.0354 |  | 72.7573 | 0 | -0.2826 | 0 | 0.15881 | -1.7795 | 0.34642 | Normal | 73.4501 | 0.53026 | Night | 202512 | 2025-12-15 | 0.53026
2025-12-15 20:59 | 72.941 | FALSE | FALSE | -0.87652 | -1.2163 | -0.50914 | -0.69318 | 0 |  |  | none | FALSE | 0 | 72.0645 | FALSE | FALSE | 0.0354 |  | 72.7573 | 0 | 0 | 0 | 0.15881 | 0 | 0.34642 | Normal | 73.4501 | 0.53026 | Night | 202512 | 2025-12-15 | 0.53026
2025-12-15 21:14 | 72.941 | FALSE | FALSE | -0.87652 | -1.2163 | -0.50914 | -0.69318 | 0 |  |  | none | FALSE | 0 | 72.0645 | FALSE | FALSE | 0.0354 |  | 72.7573 | 0 | 0 | 0 | 0.15881 | 0 | 0.34642 | Normal | 73.4501 | 0.53026 | Night | 202512 | 2025-12-15 | 0.53026
2025-12-15 21:29 | 72.941 | FALSE | FALSE | -0.86542 | -1.2007 | -0.5263 | -0.71637 | 0 |  |  | none | FALSE | 0 | 72.0756 | FALSE | FALSE | 0.0325 |  | 72.7714 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.34793 | Normal | 73.4673 | 0.48734 | Night | 202512 | 2025-12-15 | 0.48734
2025-12-15 21:44 | 72.941 | FALSE | FALSE | -0.8531 | -1.1834 | -0.54224 | -0.73791 | 0 |  |  | none | FALSE | 0 | 72.0879 | FALSE | FALSE | 0.0297 |  | 72.7856 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.34883 | Normal | 73.4832 | 0.44557 | Night | 202512 | 2025-12-15 | 0.44557
2025-12-15 21:59 | 72.941 | FALSE | FALSE | -0.83957 | -1.1644 | -0.55697 | -0.75781 | 0 |  |  | none | FALSE | 0 | 72.1014 | FALSE | FALSE | 0.027 |  | 72.7997 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.34914 | Normal | 73.498 | 0.40471 | Night | 202512 | 2025-12-15 | 0.40471
2025-12-15 22:14 | 72.6584 | TRUE | FALSE | -0.51771 | -0.71764 | -0.82857 | -1.1275 | -0.2826 |  |  | none | FALSE | 1 | 72.1407 | FALSE | FALSE | 0.0594 |  | 72.8138 | 0 | -0.2826 | 0.01413 | 0.14424 | -2.0571 | 0.33657 | Normal | 73.487 | -0.46181 | Night | 202512 | 2025-12-15 | 0.46181
2025-12-15 22:29 | 72.941 | FALSE | FALSE | -0.74138 | -1.0268 | -0.54356 | -0.73969 | 0.2826 |  |  | none | FALSE | 1 | 72.1996 | FALSE | FALSE | 0.0491 |  | 72.8421 | 0 | 0.2826 | 0.02826 | 0.15614 | 1.6289 | 0.32123 | Normal | 73.4846 | 0.30791 | Night | 202512 | 2025-12-15 | 0.30791
2025-12-15 22:44 | 72.6584 | FALSE | FALSE | -0.41312 | -0.57184 | -0.80876 | -1.1009 | -0.2826 |  |  | none | FALSE | 1 | 72.2453 | FALSE | FALSE | 0.0717 |  | 72.8562 | 0 | -0.2826 | 0.01413 | 0.17092 | -1.7361 | 0.30547 | Normal | 73.4672 | -0.64759 | Night | 202512 | 2025-12-15 | 0.64759
2025-12-15 22:59 | 72.6584 | FALSE | FALSE | -0.3643 | -0.50391 | -0.7882 | -1.0732 | 0 |  |  | none | FALSE | 1 | 72.2941 | FALSE | FALSE | 0.0776 |  | 72.8704 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.28812 | Normal | 73.4466 | -0.73562 | Night | 202512 | 2025-12-15 | 0.73562
2025-12-15 23:14 | 72.6584 | FALSE | FALSE | -0.31168 | -0.43082 | -0.76384 | -1.0403 | 0 |  |  | none | FALSE | 1 | 72.3467 | FALSE | FALSE | 0.0846 |  | 72.8845 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.26888 | Normal | 73.4222 | -0.84082 | Night | 202512 | 2025-12-15 | 0.84082
2025-12-15 23:28 | 72.6584 | FALSE | FALSE | -0.25439 | -0.35135 | -0.73481 | -1.0012 | 0 |  |  | none | FALSE | 1 | 72.404 | FALSE | FALSE | 0.0933 |  | 72.8986 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.2473 | Normal | 73.3932 | -0.97132 | Night | 202512 | 2025-12-15 | 0.97132
2025-12-15 23:43 | 72.6584 | FALSE | FALSE | -0.19108 | -0.26367 | -0.69976 | -0.95389 | 0 |  |  | none | FALSE | 1 | 72.4673 | FALSE | FALSE | 0.1047 |  | 72.9127 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.22271 | Normal | 73.3582 | -1.142 | Night | 202512 | 2025-12-15 | 1.142
2025-12-15 23:58 | 72.3758 | FALSE | FALSE | 0.028207 | 0.038958 | -1.0174 | -1.3862 | -0.2826 | 2025-12-16 01:58 | 2025-12-15 23:58 | lower | TRUE | 1 | 72.404 | FALSE | FALSE | 0.2267 | 2.1141 | 72.8986 | 1 | -0.2826 | -0.01413 | 0.17092 | -1.5708 | 0.2473 | Extreme triggered | 73.3932 | -2.1141 | Night | 202512 | 2025-12-15 | 2.1141
2025-12-16 00:14 | 72.3758 | FALSE | FALSE | -0.051742 | -0.071541 | -1.0408 | -1.4177 | 0 |  | 2025-12-15 23:58 | none | FALSE | 1 | 72.3241 | FALSE | FALSE | 0.2636 | 1.9623 | 72.8704 | 2 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.27315 | Extreme/elevated | 73.4166 | -1.8106 | Night | 202512 | 2025-12-16 | 1.8106
2025-12-16 00:28 | 72.3758 | FALSE | FALSE | -0.11006 | -0.1523 | -1.0144 | -1.3822 | 0 |  | 2025-12-15 23:58 | none | FALSE | 1 | 72.2657 | FALSE | FALSE | 0.3072 | 1.8444 | 72.828 | 3 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.28111 | Persistent | 73.3902 | -1.6085 | Night | 202512 | 2025-12-16 | 1.6085
2025-12-16 00:43 | 72.3758 | FALSE | FALSE | -0.15469 | -0.21418 | -0.97423 | -1.3282 | 0 |  | 2025-12-15 23:58 | none | FALSE | 0 | 72.2211 | FALSE | FALSE | 0.3254 | 1.7463 | 72.7856 | 4 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.28223 | Persistent | 73.35 | -1.4519 | Night | 202512 | 2025-12-16 | 1.4519
2025-12-16 00:58 | 72.3758 | FALSE | FALSE | -0.18579 | -0.25737 | -0.92055 | -1.2559 | 0 |  | 2025-12-15 23:58 | none | FALSE | 0 | 72.19 | FALSE | FALSE | 0.3743 | 1.6627 | 72.7432 | 5 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.27659 | Persistent | 73.2964 | -1.3283 | Night | 202512 | 2025-12-16 | 1.3283
2025-12-16 01:13 | 72.3758 | FALSE | FALSE | -0.20251 | -0.28059 | -0.85249 | -1.1642 | 0 |  | 2025-12-15 23:58 | none | FALSE | 0 | 72.1733 | FALSE | FALSE | 0.425 | 1.5909 | 72.7008 | 6 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.26375 | Persistent | 73.2283 | -1.2322 | Night | 202512 | 2025-12-16 | 1.2322
2025-12-16 01:28 | 72.3758 | FALSE | TRUE | -0.20256 | -0.28066 | -0.76776 | -1.0497 | 0 |  | 2025-12-15 23:58 | none | FALSE | 0 | 72.1732 | FALSE | FALSE | 0.4777 | 1.5301 | 72.6584 | 7 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.24258 | Confirmed/Materialized Shift | 73.1436 | -1.165 | Night | 202512 | 2025-12-16 | 1.165
2025-12-16 01:43 | 72.3758 | FALSE | TRUE | -0.22735 | -0.31511 | -0.73603 | -1.0067 | 0 |  | 2025-12-15 23:58 | none | FALSE | 0 | 72.1485 | FALSE | FALSE | 0.4704 | 1.4708 | 72.6301 | 8 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.24084 | Confirmed/Materialized Shift | 73.1118 | -1.056 | Night | 202512 | 2025-12-16 | 1.056
2025-12-16 01:58 | 72.3758 | FALSE | FALSE | -0.24502 | -0.33969 | -0.69718 | -0.95409 | 0 |  |  | none | FALSE | 0 | 72.1308 | FALSE | FALSE | 0.064 |  | 72.6019 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.23555 | Persistence ends | 73.073 | -0.9598 | Night | 202512 | 2025-12-16 | 0.9598
2025-12-16 02:13 | 72.3758 | FALSE | FALSE | -0.25508 | -0.35369 | -0.65072 | -0.89108 | 0 |  |  | none | FALSE | 0 | 72.1207 | FALSE | FALSE | 0.0582 |  | 72.5736 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.22645 | Normal | 73.0265 | -0.87356 | Night | 202512 | 2025-12-16 | 0.87356
2025-12-16 02:28 | 72.3758 | FALSE | FALSE | -0.25657 | -0.35575 | -0.59569 | -0.81633 | 0 |  |  | none | FALSE | 0 | 72.1192 | FALSE | FALSE | 0.0531 |  | 72.5454 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21306 | Normal | 72.9715 | -0.79582 | Night | 202512 | 2025-12-16 | 0.79582
2025-12-16 02:43 | 72.3758 | FALSE | FALSE | -0.2477 | -0.34341 | -0.5303 | -0.72737 | 0 |  |  | none | FALSE | 0 | 72.1281 | FALSE | FALSE | 0.0484 |  | 72.5171 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.1945 | Normal | 72.9061 | -0.72648 | Night | 202512 | 2025-12-16 | 0.72648
2025-12-16 02:58 | 72.095 | FALSE | FALSE | 0.001033 | 0.0014328 | -0.75857 | -1.0412 | -0.2808 | 2025-12-16 05:12 | 2025-12-16 02:58 | lower | TRUE | 0 | 72.096 | FALSE | FALSE | 0.1908 | 2.0055 | 72.4748 | 1 | -0.2808 | -0.0423 | 0.13813 | -1.7266 | 0.18938 | Extreme triggered | 72.8536 | -2.0055 | Night | 202512 | 2025-12-16 | 2.0055
2025-12-16 03:13 | 72.095 | FALSE | FALSE | -0.052591 | -0.073 | -0.75585 | -1.0375 | 0 |  | 2025-12-16 02:58 | none | FALSE | 0 | 72.0424 | FALSE | FALSE | 0.2303 | 1.8726 | 72.4466 | 2 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.20211 | Extreme/elevated | 72.8509 | -1.7398 | Night | 202512 | 2025-12-16 | 1.7398
2025-12-16 03:27 | 72.095 | FALSE | FALSE | -0.051832 | -0.071946 | -0.67049 | -0.92144 | 0 |  | 2025-12-16 02:58 | none | FALSE | 0 | 72.0432 | FALSE | FALSE | 0.2856 | 1.8194 | 72.4043 | 3 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.18058 | Persistent | 72.7655 | -1.713 | Night | 202512 | 2025-12-16 | 1.713
2025-12-16 03:42 | 72.095 | FALSE | FALSE | -0.084423 | -0.11724 | -0.64674 | -0.8891 | 0 |  | 2025-12-16 02:58 | none | FALSE | 0 | 72.0106 | FALSE | FALSE | 0.3311 | 1.7491 | 72.3762 | 4 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.18279 | Persistent | 72.7417 | -1.5381 | Night | 202512 | 2025-12-16 | 1.5381
2025-12-16 03:57 | 72.095 | FALSE | FALSE | -0.10782 | -0.14977 | -0.6138 | -0.84419 | 0 |  | 2025-12-16 02:58 | none | FALSE | 0 | 71.9872 | FALSE | FALSE | 0.3792 | 1.6797 | 72.348 | 5 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.1804 | Persistent | 72.7088 | -1.4024 | Night | 202512 | 2025-12-16 | 1.4024
2025-12-16 04:12 | 72.095 | FALSE | FALSE | -0.12163 | -0.169 | -0.57127 | -0.78616 | 0 |  | 2025-12-16 02:58 | none | FALSE | 0 | 71.9734 | FALSE | FALSE | 0.4294 | 1.6161 | 72.3198 | 6 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.17323 | Persistent | 72.6663 | -1.2978 | Night | 202512 | 2025-12-16 | 1.2978
2025-12-16 04:27 | 72.095 | FALSE | TRUE | -0.12459 | -0.17311 | -0.51789 | -0.71322 | 0 |  | 2025-12-16 02:58 | none | FALSE | 0 | 71.9704 | FALSE | FALSE | 0.4816 | 1.5601 | 72.2917 | 7 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.16062 | Confirmed/Materialized Shift | 72.6129 | -1.2243 | Night | 202512 | 2025-12-16 | 1.2243
2025-12-16 04:42 | 72.095 | FALSE | TRUE | -0.11379 | -0.15809 | -0.45075 | -0.62134 | 0 |  | 2025-12-16 02:58 | none | FALSE | 0 | 71.9812 | FALSE | FALSE | 0.4796 | 1.5143 | 72.2635 | 8 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.14114 | Confirmed/Materialized Shift | 72.5458 | -1.1937 | Night | 202512 | 2025-12-16 | 1.1937
2025-12-16 04:57 | 71.8124 | TRUE | TRUE | 0.081563 | 0.11345 | -0.76426 | -1.053 | -0.2826 |  | 2025-12-16 02:58 | lower | TRUE | 1 | 71.894 | FALSE | TRUE | 0.5938 | 1.6214 | 72.2353 | 9 | -0.2826 | -0.02817 | 0.086706 | -2.9344 | 0.17067 | Confirmed/Materialized Shift | 72.5767 | -2.4779 | Night | 202512 | 2025-12-16 | 2.4779
2025-12-16 05:12 | 72.095 | TRUE | FALSE | -0.21384 | -0.2975 | -0.46638 | -0.64274 | 0.2826 |  |  | none | FALSE | 2 | 71.8812 | TRUE | FALSE | 0.1066 |  | 72.2213 | 0 | 0.2826 | -0.01404 | 0.11113 | 2.6694 | 0.17006 | Persistence ends | 72.5614 | -0.74252 | Night | 202512 | 2025-12-16 | 0.74252
2025-12-16 05:27 | 72.095 | FALSE | FALSE | -0.22419 | -0.31193 | -0.44865 | -0.61845 | 0 |  |  | none | FALSE | 2 | 71.8708 | FALSE | FALSE | 0.1016 |  | 72.2072 | 0 | 0 | -0.01404 | 0.11113 | 0.12634 | 0.16821 | Normal | 72.5436 | -0.66721 | Night | 202512 | 2025-12-16 | 0.66721
2025-12-16 05:42 | 71.8124 | TRUE | FALSE | -0.003032 | -0.0042223 | -0.73635 | -1.015 | -0.2826 |  |  | none | FALSE | 3 | 71.8094 | TRUE | FALSE | 0.218 |  | 72.1791 | 0 | -0.2826 | -0.02817 | 0.12619 | -2.0162 | 0.18485 | Normal | 72.5488 | -1.9836 | Night | 202512 | 2025-12-16 | 1.9836
2025-12-16 05:57 | 71.8124 | FALSE | FALSE | -0.053282 | -0.074251 | -0.73026 | -1.0067 | 0 |  |  | none | FALSE | 3 | 71.7591 | FALSE | FALSE | 0.2009 |  | 72.1509 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.19589 | Normal | 72.5427 | -1.728 | Night | 202512 | 2025-12-16 | 1.728
2025-12-16 06:12 | 71.8124 | FALSE | FALSE | -0.094174 | -0.13131 | -0.71481 | -0.98558 | 0 |  |  | none | FALSE | 3 | 71.7182 | FALSE | FALSE | 0.188 |  | 72.1227 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.20225 | Normal | 72.5272 | -1.5344 | Night | 202512 | 2025-12-16 | 1.5344
2025-12-16 06:26 | 71.8124 | FALSE | FALSE | -0.12658 | -0.17658 | -0.69088 | -0.9529 | 0 |  |  | none | FALSE | 3 | 71.6858 | FALSE | FALSE | 0.1778 |  | 72.0945 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.20437 | Normal | 72.5033 | -1.3806 | Night | 202512 | 2025-12-16 | 1.3806
2025-12-16 06:41 | 71.8124 | FALSE | FALSE | -0.15078 | -0.2104 | -0.65874 | -0.90897 | 0 |  |  | none | FALSE | 3 | 71.6616 | FALSE | FALSE | 0.1694 |  | 72.0664 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.20238 | Normal | 72.4711 | -1.255 | Night | 202512 | 2025-12-16 | 1.255
2025-12-16 06:56 | 71.8124 | FALSE | FALSE | -0.16651 | -0.2324 | -0.61813 | -0.85341 | 0 |  |  | none | FALSE | 3 | 71.6459 | FALSE | FALSE | 0.1625 |  | 72.0382 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.19616 | Normal | 72.4305 | -1.1512 | Night | 202512 | 2025-12-16 | 1.1512
2025-12-16 07:11 | 71.8124 | FALSE | FALSE | -0.17292 | -0.24137 | -0.5682 | -0.78501 | 0 |  |  | none | FALSE | 3 | 71.6395 | FALSE | FALSE | 0.1568 |  | 72.01 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.18528 | Normal | 72.3806 | -1.0667 | Day | 202512 | 2025-12-16 | 1.0667
2025-12-16 07:26 | 71.8124 | FALSE | FALSE | -0.16821 | -0.23479 | -0.50715 | -0.70127 | 0 |  |  | none | FALSE | 2 | 71.6442 | FALSE | FALSE | 0.1241 |  | 71.9819 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.16884 | Normal | 72.3196 | -1.0037 | Day | 202512 | 2025-12-16 | 1.0037
2025-12-16 07:30 | 71.5298 | FALSE | FALSE | 0.067934 | 0.094883 | -0.75161 | -1.0398 | -0.2826 | 2025-12-16 12:12 | 2025-12-16 07:30 | lower | TRUE | 1 | 71.5977 | FALSE | FALSE | 0.2455 | 2.3975 | 71.9396 | 1 | -0.2826 | -0.0423 | 0.13813 | -1.7397 | 0.17092 | Extreme triggered | 72.2814 | -2.3975 | Day | 202512 | 2025-12-16 | 2.3975
2025-12-16 07:45 | 71.5298 | FALSE | FALSE | 0.0023623 | 0.0033024 | -0.76066 | -1.0522 | 0 |  | 2025-12-16 07:30 | lower | TRUE | 1 | 71.5322 | FALSE | FALSE | 0.277 | 2.205 | 71.9113 | 2 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.18957 | Extreme/elevated | 72.2905 | -2.0125 | Day | 202512 | 2025-12-16 | 2.0125
2025-12-16 08:00 | 71.5298 | FALSE | FALSE | -0.051631 | -0.072234 | -0.75813 | -1.0488 | 0 |  | 2025-12-16 07:30 | none | FALSE | 0 | 71.4782 | FALSE | FALSE | 0.2878 | 2.0516 | 71.883 | 3 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.20244 | Persistent | 72.2879 | -1.745 | Day | 202512 | 2025-12-16 | 1.745
2025-12-16 08:30 | 72.095 | TRUE | FALSE | -0.61683 | -0.86296 | -0.19293 | -0.26689 | 0.5652 |  | 2025-12-16 07:30 | none | FALSE | 1 | 71.4782 | FALSE | FALSE | 0.3269 | 1.8005 | 71.883 | 4 | 0.5652 | 0 | 0.18338 | 3.0822 | 0.20244 | Persistent | 72.2879 | 1.047 | Day | 202512 | 2025-12-16 | 1.047
2025-12-16 08:30 | 72.095 | FALSE | FALSE | -0.61683 | -0.86296 | -0.19293 | -0.26689 | 0 |  | 2025-12-16 07:30 | none | FALSE | 1 | 71.4782 | FALSE | FALSE | 0.3841 | 1.6498 | 71.883 | 5 | 0 | 0 | 0.18338 | 0 | 0.20244 | Persistent | 72.2879 | 1.047 | Day | 202512 | 2025-12-16 | 1.047
2025-12-16 08:45 | 72.095 | FALSE | FALSE | -0.61683 | -0.86296 | -0.19293 | -0.26689 | 0 |  | 2025-12-16 07:30 | none | FALSE | 1 | 71.4782 | FALSE | FALSE | 0.4412 | 1.5493 | 71.883 | 6 | 0 | 0 | 0.18338 | 0 | 0.20244 | Persistent | 72.2879 | 1.047 | Day | 202512 | 2025-12-16 | 1.047
2025-12-16 09:00 | 72.3758 | FALSE | TRUE | -0.93121 | -1.3034 | 0.026208 | 0.036225 | 0.2808 |  | 2025-12-16 07:30 | upper | TRUE | 1 | 71.4446 | FALSE | TRUE | 0.5696 | 1.6302 | 71.8971 | 7 | 0.2808 | 0.01404 | 0.19383 | 1.3763 | 0.22625 | Confirmed/Materialized Shift | 72.3496 | 2.1158 | Day | 202512 | 2025-12-16 | 2.1158
2025-12-16 09:15 | 72.6584 | FALSE | TRUE | -1.2946 | -1.814 | 0.17172 | 0.2369 | 0.2826 |  | 2025-12-16 07:30 | upper | TRUE | 1 | 71.3638 | FALSE | TRUE | 0.6027 | 1.7529 | 71.9253 | 8 | 0.2826 | 0.02817 | 0.20284 | 1.2543 | 0.28071 | Confirmed/Materialized Shift | 72.4867 | 2.6117 | Day | 202512 | 2025-12-16 | 2.6117
2025-12-16 09:30 | 72.941 | FALSE | TRUE | -1.6937 | -2.3772 | 0.25316 | 0.34829 | 0.2826 |  | 2025-12-16 07:30 | upper | TRUE | 1 | 71.2473 | FALSE | TRUE | 0.6088 | 1.8585 | 71.9676 | 9 | 0.2826 | 0.0423 | 0.21047 | 1.1417 | 0.36014 | Confirmed/Materialized Shift | 72.6878 | 2.703 | Day | 202512 | 2025-12-16 | 2.703
2025-12-16 09:45 | 73.2236 | FALSE | TRUE | -2.0937 | -2.9435 | 0.27724 | 0.38006 | 0.2826 |  | 2025-12-16 07:30 | upper | TRUE | 1 | 71.1299 | FALSE | TRUE | 0.6026 | 1.9337 | 72.0381 | 10 | 0.2826 | 0.07056 | 0.20234 | 1.0479 | 0.45412 | Confirmed/Materialized Shift | 72.9464 | 2.6105 | Day | 202512 | 2025-12-16 | 2.6105
2025-12-16 10:00 | 73.2236 | FALSE | TRUE | -2.181 | -3.07 | 0.077063 | 0.10535 | 0 |  | 2025-12-16 07:30 | upper | TRUE | 1 | 71.0426 | FALSE | TRUE | 0.5717 | 1.953 | 72.0945 | 11 | 0 | 0.05643 | 0.19654 | -0.28712 | 0.52599 | Confirmed/Materialized Shift | 73.1465 | 2.1465 | Day | 202512 | 2025-12-16 | 2.1465
2025-12-16 10:15 | 73.2236 | FALSE | TRUE | -2.2395 | -3.1549 | -0.094272 | -0.12858 | 0 |  | 2025-12-16 07:30 | none | FALSE | 1 | 70.9841 | FALSE | FALSE | 0.5511 | 1.9435 | 72.151 | 12 | 0 | 0.05643 | 0.19654 | -0.28712 | 0.58345 | Confirmed/Materialized Shift | 73.3179 | 1.8384 | Day | 202512 | 2025-12-16 | 1.8384
2025-12-16 10:29 | 73.2236 | FALSE | TRUE | -2.2506 | -3.171 | -0.24644 | -0.33543 | 0 |  | 2025-12-16 07:30 | none | FALSE | 1 | 70.973 | FALSE | FALSE | 0.5356 | 1.9175 | 72.2215 | 13 | 0 | 0.07056 | 0.18038 | -0.39118 | 0.62425 | Confirmed/Materialized Shift | 73.47 | 1.6052 | Day | 202512 | 2025-12-16 | 1.6052
2025-12-16 10:44 | 73.5062 | FALSE | TRUE | -2.5567 | -3.6036 | -0.15677 | -0.21283 | 0.2826 |  | 2025-12-16 07:30 | none | FALSE | 0 | 70.9495 | FALSE | FALSE | 0.5179 | 1.9069 | 72.3062 | 14 | 0.2826 | 0.08469 | 0.18555 | 1.0666 | 0.67837 | Confirmed/Materialized Shift | 73.663 | 1.7689 | Day | 202512 | 2025-12-16 | 1.7689
2025-12-16 10:59 | 73.5062 | FALSE | TRUE | -2.5514 | -3.5958 | -0.32081 | -0.43454 | 0 |  | 2025-12-16 07:30 | none | FALSE | 0 | 70.9548 | FALSE | FALSE | 0.5035 | 1.8833 | 72.3909 | 15 | 0 | 0.08469 | 0.18555 | -0.45642 | 0.71805 | Confirmed/Materialized Shift | 73.827 | 1.5532 | Day | 202512 | 2025-12-16 | 1.5532
2025-12-16 11:15 | 73.5062 | FALSE | TRUE | -2.5218 | -3.5525 | -0.46057 | -0.62267 | 0 |  | 2025-12-16 07:30 | none | FALSE | 0 | 70.9844 | FALSE | FALSE | 0.4922 | 1.852 | 72.4756 | 16 | 0 | 0.08469 | 0.18555 | -0.45642 | 0.74558 | Confirmed/Materialized Shift | 73.9668 | 1.3823 | Day | 202512 | 2025-12-16 | 1.3823
2025-12-16 11:29 | 73.7888 | FALSE | TRUE | -2.7805 | -3.9158 | -0.3518 | -0.4745 | 0.2826 |  | 2025-12-16 07:30 | none | FALSE | 0 | 71.0083 | FALSE | FALSE | 0.5034 | 1.8342 | 72.5744 | 17 | 0.2826 | 0.09882 | 0.18948 | 0.96991 | 0.78309 | Confirmed/Materialized Shift | 74.1406 | 1.5508 | Day | 202512 | 2025-12-16 | 1.5508
2025-12-16 11:39 | 73.7888 | FALSE | TRUE | -2.728 | -3.839 | -0.4969 | -0.6689 | 0 |  | 2025-12-16 07:30 | none | FALSE | 0 | 71.0608 | FALSE | FALSE | 0.4922 | 1.8092 | 72.6732 | 18 | 0 | 0.09882 | 0.18948 | -0.52153 | 0.80622 | Confirmed/Materialized Shift | 74.2857 | 1.3837 | Day | 202512 | 2025-12-16 | 1.3837
2025-12-16 11:39 | 73.7888 | FALSE | TRUE | -2.6492 | -3.7239 | -0.6157 | -0.82751 | 0 |  | 2025-12-16 07:30 | none | FALSE | 0 | 71.1396 | FALSE | FALSE | 0.483 | 1.7796 | 72.7721 | 19 | 0 | 0.09882 | 0.18948 | -0.52153 | 0.81622 | Confirmed/Materialized Shift | 74.4045 | 1.2457 | Day | 202512 | 2025-12-16 | 1.2457
2025-12-16 11:42 | 73.7888 | FALSE | TRUE | -2.545 | -3.5723 | -0.70919 | -0.95196 | 0 |  | 2025-12-16 07:30 | none | FALSE | 0 | 71.2438 | FALSE | FALSE | 0.4752 | 1.747 | 72.8709 | 20 | 0 | 0.09882 | 0.18948 | -0.52153 | 0.81355 | Confirmed/Materialized Shift | 74.498 | 1.1283 | Day | 202512 | 2025-12-16 | 1.1283
2025-12-16 11:57 | 73.7888 | FALSE | TRUE | -2.3517 | -3.292 | -0.74181 | -0.99531 | 0 |  | 2025-12-16 07:30 | none | FALSE | 0 | 71.4371 | FALSE | FALSE | 0.4694 | 1.7134 | 72.9838 | 21 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.77338 | Confirmed/Materialized Shift | 74.5306 | 1.0408 | Day | 202512 | 2025-12-16 | 1.0408
2025-12-16 12:12 | 73.2236 | TRUE | FALSE | -1.5441 | -2.1541 | -1.2339 | -1.6572 | -0.5652 |  |  | none | FALSE | 1 | 71.6795 | FALSE | FALSE | 0.0435 |  | 73.0685 | 0 | -0.5652 | 0.08469 | 0.22637 | -2.8709 | 0.6945 | Persistence ends | 74.4575 | 0.22328 | Day | 202512 | 2025-12-16 | 0.22328
2025-12-16 12:27 | 72.6584 | TRUE | FALSE | -0.73878 | -1.0272 | -1.6719 | -2.2493 | -0.5652 |  |  | none | FALSE | 2 | 71.9196 | TRUE | FALSE | 0.1088 |  | 73.125 | 0 | -0.5652 | 0.05643 | 0.2688 | -2.3126 | 0.60267 | Normal | 74.3303 | -0.77416 | Day | 202512 | 2025-12-16 | 0.77416
2025-12-16 12:39 | 72.3758 | FALSE | FALSE | -0.39733 | -0.55202 | -1.9237 | -2.5892 | -0.2826 |  |  | none | FALSE | 2 | 71.9785 | FALSE | FALSE | 0.1448 |  | 73.139 | 0 | -0.2826 | 0.01404 | 0.25058 | -1.1838 | 0.58027 | Normal | 74.2995 | -1.3153 | Day | 202512 | 2025-12-16 | 1.3153
2025-12-16 12:54 | 72.3758 | FALSE | FALSE | -0.33594 | -0.46633 | -1.8904 | -2.5455 | 0 |  |  | none | FALSE | 2 | 72.0399 | FALSE | FALSE | 0.1502 |  | 73.153 | 0 | 0 | 0.01404 | 0.25058 | -0.056031 | 0.55659 | Normal | 74.2662 | -1.3964 | Day | 202512 | 2025-12-16 | 1.3964
2025-12-16 13:09 | 72.095 | FALSE | FALSE | -0.055141 | -0.076542 | -2.1712 | -2.9236 | -0.2808 |  |  | none | FALSE | 2 | 72.0399 | FALSE | FALSE | 0.1839 |  | 73.153 | 0 | -0.2808 | 0 | 0.25913 | -1.0836 | 0.55659 | Normal | 74.2662 | -1.9009 | Day | 202512 | 2025-12-16 | 1.9009
2025-12-16 13:24 | 71.8124 | FALSE | FALSE | 0.09303 | 0.12938 | -2.5319 | -3.4057 | -0.2826 | 2025-12-16 13:38 | 2025-12-16 13:24 | lower | TRUE | 2 | 71.9054 | FALSE | FALSE | 0.2578 | 2.1526 | 73.1249 | 1 | -0.2826 | -0.02817 | 0.25761 | -0.98765 | 0.60972 | Extreme triggered | 74.3443 | -2.1526 | Day | 202512 | 2025-12-16 | 2.1526
2025-12-16 13:27 | 71.8124 | FALSE | FALSE | -0.070105 | -0.097718 | -2.6104 | -3.5076 | 0 |  | 2025-12-16 13:24 | none | FALSE | 2 | 71.7423 | FALSE | FALSE | 0.2978 | 2.024 | 73.0826 | 2 | 0 | -0.0423 | 0.24721 | 0.17111 | 0.67014 | Extreme/elevated | 74.4228 | -1.8954 | Day | 202512 | 2025-12-16 | 1.8954
2025-12-16 13:38 | 72.3758 | TRUE | FALSE | -0.69769 | -0.97336 | -2.0547 | -2.7606 | 0.5634 |  |  | none | FALSE | 3 | 71.6781 | TRUE | FALSE | 0.1515 |  | 73.0543 | 0 | 0.5634 | -0.02826 | 0.27324 | 2.1654 | 0.6881 | Persistence ends | 74.4305 | -0.98606 | Day | 202512 | 2025-12-16 | 0.98606
2025-12-16 13:53 | 72.6584 | FALSE | FALSE | -1.0171 | -1.4197 | -1.7524 | -2.355 | 0.2826 |  |  | none | FALSE | 3 | 71.6413 | FALSE | FALSE | 0.1211 |  | 73.026 | 0 | 0.2826 | -0.02826 | 0.27324 | 1.1377 | 0.69237 | Normal | 74.4108 | -0.531 | Day | 202512 | 2025-12-16 | 0.531
2025-12-16 14:08 | 72.941 | FALSE | FALSE | -1.3111 | -1.8304 | -1.4529 | -1.953 | 0.2826 |  |  | none | FALSE | 3 | 71.6299 | FALSE | FALSE | 0.0926 |  | 73.0119 | 0 | 0.2826 | -0.01413 | 0.28194 | 1.0524 | 0.69101 | Normal | 74.3939 | -0.10263 | Day | 202512 | 2025-12-16 | 0.10263
2025-12-16 14:23 | 72.941 | FALSE | FALSE | -1.3219 | -1.8457 | -1.4355 | -1.93 | 0 |  |  | none | FALSE | 2 | 71.6191 | FALSE | FALSE | 0.0626 |  | 72.9978 | 0 | 0 | -0.01413 | 0.28194 | 0.050116 | 0.68934 | Normal | 74.3765 | -0.082383 | Day | 202512 | 2025-12-16 | 0.082383
2025-12-16 14:38 | 72.941 | FALSE | FALSE | -1.3321 | -1.8602 | -1.4174 | -1.9062 | 0 |  |  | none | FALSE | 1 | 71.6089 | FALSE | FALSE | 0.0327 |  | 72.9837 | 0 | 0 | -0.01413 | 0.28194 | 0.050116 | 0.68736 | Normal | 74.3584 | -0.062063 | Day | 202512 | 2025-12-16 | 0.062063
2025-12-16 14:53 | 72.941 | FALSE | FALSE | -1.3382 | -1.8689 | -1.367 | -1.8396 | 0 |  |  | none | FALSE | 1 | 71.6028 | FALSE | FALSE | 0.03 |  | 72.9554 | 0 | 0 | -0.02826 | 0.27324 | 0.10343 | 0.67628 | Normal | 74.308 | -0.021293 | Day | 202512 | 2025-12-16 | 0.021293
2025-12-16 15:08 | 73.2236 | FALSE | FALSE | -1.6164 | -2.2574 | -1.0518 | -1.4161 | 0.2826 |  |  | none | FALSE | 1 | 71.6072 | FALSE | FALSE | 0.0568 |  | 72.9413 | 0 | 0.2826 | -0.01413 | 0.28194 | 1.0524 | 0.66705 | Normal | 74.2754 | 0.42325 | Day | 202512 | 2025-12-16 | 0.42325
2025-12-16 15:23 | 73.2236 | FALSE | FALSE | -1.6112 | -2.2499 | -1.0183 | -1.3716 | 0 |  |  | none | FALSE | 1 | 71.6124 | FALSE | FALSE | 0.0586 |  | 72.9271 | 0 | 0 | -0.01413 | 0.28194 | 0.050116 | 0.65738 | Normal | 74.2419 | 0.45097 | Day | 202512 | 2025-12-16 | 0.45097
2025-12-16 15:38 | 73.2236 | FALSE | FALSE | -1.5847 | -2.212 | -0.93521 | -1.2611 | 0 |  |  | none | FALSE | 1 | 71.6389 | FALSE | FALSE | 0.0629 |  | 72.8989 | 0 | 0 | -0.02826 | 0.27324 | 0.10343 | 0.62997 | Normal | 74.1588 | 0.51546 | Day | 202512 | 2025-12-16 | 0.51546
2025-12-16 15:53 | 73.2236 | FALSE | FALSE | -1.5528 | -2.1666 | -0.84683 | -1.1433 | 0 |  |  | none | FALSE | 1 | 71.6708 | FALSE | FALSE | 0.0678 |  | 72.8706 | 0 | 0 | -0.02826 | 0.27324 | 0.10343 | 0.5999 | Normal | 74.0704 | 0.58839 | Day | 202512 | 2025-12-16 | 0.58839
2025-12-16 16:08 | 73.2236 | FALSE | FALSE | -1.5148 | -2.1124 | -0.7523 | -1.017 | 0 |  |  | none | FALSE | 0 | 71.7088 | FALSE | FALSE | 0.0448 |  | 72.8424 | 0 | 0 | -0.02826 | 0.27324 | 0.10343 | 0.56677 | Normal | 73.9759 | 0.67265 | Day | 202512 | 2025-12-16 | 0.67265
2025-12-16 16:23 | 73.2236 | FALSE | FALSE | -1.4695 | -2.048 | -0.65049 | -0.88054 | 0 |  |  | none | FALSE | 0 | 71.7541 | FALSE | FALSE | 0.0515 |  | 72.8141 | 0 | 0 | -0.02826 | 0.27324 | 0.10343 | 0.53 | Normal | 73.8741 | 0.77265 | Day | 202512 | 2025-12-16 | 0.77265
2025-12-16 16:37 | 73.2236 | FALSE | FALSE | -1.4153 | -1.9709 | -0.53974 | -0.73172 | 0 |  |  | none | FALSE | 0 | 71.8083 | FALSE | FALSE | 0.0597 |  | 72.7858 | 0 | 0 | -0.02826 | 0.27324 | 0.10343 | 0.48875 | Normal | 73.7633 | 0.89567 | Day | 202512 | 2025-12-16 | 0.89567
2025-12-16 16:52 | 73.2236 | FALSE | FALSE | -1.4153 | -1.9709 | -0.53974 | -0.73172 | 0 |  |  | none | FALSE | 0 | 71.8083 | FALSE | FALSE | 0.0597 |  | 72.7858 | 0 | 0 | 0 | 0.24225 | 0 | 0.48875 | Normal | 73.7633 | 0.89567 | Day | 202512 | 2025-12-16 | 0.89567
2025-12-16 17:07 | 73.2236 | FALSE | FALSE | -1.404 | -1.9549 | -0.58502 | -0.79262 | 0 |  |  | none | FALSE | 0 | 71.8196 | FALSE | FALSE | 0.0549 |  | 72.8141 | 0 | 0 | 0.02826 | 0.20256 | -0.13951 | 0.49726 | Normal | 73.8086 | 0.82351 | Day | 202512 | 2025-12-16 | 0.82351
2025-12-16 17:22 | 73.2236 | FALSE | FALSE | -1.3552 | -1.8857 | -0.621 | -0.84096 | 0 |  |  | none | FALSE | 0 | 71.8684 | FALSE | FALSE | 0.0495 |  | 72.8565 | 0 | 0 | 0.04239 | 0.18915 | -0.22411 | 0.49406 | Normal | 73.8446 | 0.74305 | Day | 202512 | 2025-12-16 | 0.74305
2025-12-16 17:37 | 73.2236 | FALSE | FALSE | -1.2986 | -1.8056 | -0.6492 | -0.87881 | 0 |  |  | none | FALSE | 0 | 71.925 | FALSE | FALSE | 0.0445 |  | 72.8989 | 0 | 0 | 0.04239 | 0.18915 | -0.22411 | 0.48696 | Normal | 73.8728 | 0.66683 | Night | 202512 | 2025-12-16 | 0.66683
2025-12-16 17:52 | 72.941 | FALSE | FALSE | -0.89722 | -1.2454 | -0.89758 | -1.2156 | -0.2826 |  |  | none | FALSE | 0 | 72.0438 | FALSE | FALSE | 0 |  | 72.9412 | 0 | -0.2826 | 0.0423 | 0.18931 | -1.7162 | 0.4487 | Normal | 73.8386 | -0.00040116 | Night | 202512 | 2025-12-16 | 0.00040116
2025-12-16 18:07 | 72.941 | FALSE | FALSE | -0.66704 | -0.92294 | -0.78026 | -1.0584 | 0 |  |  | none | FALSE | 0 | 72.274 | FALSE | FALSE | 0.0104 |  | 72.9976 | 0 | 0 | 0.05643 | 0.17369 | -0.32489 | 0.36183 | Normal | 73.7213 | -0.15646 | Night | 202512 | 2025-12-16 | 0.15646
2025-12-16 18:22 | 72.941 | FALSE | FALSE | -0.35087 | -0.48335 | -0.57695 | -0.78477 | 0 |  |  | none | FALSE | 0 | 72.5901 | FALSE | FALSE | 0.0325 |  | 73.054 | 0 | 0 | 0.05643 | 0.17369 | -0.32489 | 0.23195 | Normal | 73.5179 | -0.48734 | Night | 202512 | 2025-12-16 | 0.48734
2025-12-16 18:30 | 72.6584 | TRUE | FALSE | 0.021855 | 0.03007 | -0.79769 | -1.0859 | -0.2826 | 2025-12-16 19:01 | 2025-12-16 18:30 | lower | TRUE | 1 | 72.6803 | FALSE | FALSE | 0.2266 | 2.1127 | 73.0682 | 1 | -0.2826 | 0.01413 | 0.14424 | -2.0571 | 0.19396 | Extreme triggered | 73.4561 | -2.1127 | Night | 202512 | 2025-12-16 | 2.1127
2025-12-16 18:31 | 72.6584 | FALSE | FALSE | 0.021855 | 0.03007 | -0.79769 | -1.0859 | 0 |  | 2025-12-16 18:30 | lower | TRUE | 1 | 72.6803 | FALSE | FALSE | 0.2837 | 2.1127 | 73.0682 | 2 | 0 | 0 | 0.12967 | 0 | 0.19396 | Extreme/elevated | 73.4561 | -2.1127 | Night | 202512 | 2025-12-16 | 2.1127
2025-12-16 18:46 | 72.6584 | FALSE | FALSE | -0.030485 | -0.041975 | -0.82177 | -1.1183 | 0 |  | 2025-12-16 18:30 | none | FALSE | 1 | 72.6279 | FALSE | FALSE | 0.3238 | 2.0274 | 73.054 | 3 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.21306 | Persistent | 73.4802 | -1.8569 | Night | 202512 | 2025-12-16 | 1.8569
2025-12-16 19:01 | 73.2236 | TRUE | FALSE | -0.5845 | -0.80467 | -0.27364 | -0.37232 | 0.5652 |  |  | none | FALSE | 2 | 72.6391 | TRUE | FALSE | 0.1054 |  | 73.0682 | 0 | 0.5652 | 0.01413 | 0.17092 | 3.2242 | 0.21454 | Persistence ends | 73.4972 | 0.72449 | Night | 202512 | 2025-12-16 | 0.72449
2025-12-16 19:16 | 73.5062 | FALSE | FALSE | -0.87639 | -1.2066 | -0.056847 | -0.077276 | 0.2826 |  |  | none | FALSE | 2 | 72.6298 | FALSE | FALSE | 0.1742 |  | 73.0964 | 0 | 0.2826 | 0.02826 | 0.18107 | 1.4047 | 0.23331 | Normal | 73.563 | 1.7563 | Night | 202512 | 2025-12-16 | 1.7563
2025-12-16 19:30 | 73.5062 | FALSE | FALSE | -0.87611 | -1.2063 | -0.11309 | -0.15362 | 0 |  |  | none | FALSE | 2 | 72.6301 | FALSE | FALSE | 0.16 |  | 73.1247 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.2473 | Normal | 73.6193 | 1.5427 | Night | 202512 | 2025-12-16 | 1.5427
2025-12-16 19:45 | 73.7888 | FALSE | FALSE | -1.2121 | -1.6701 | 0.059603 | 0.08084 | 0.2826 | 2025-12-16 20:15 | 2025-12-16 19:45 | upper | TRUE | 2 | 72.5767 | FALSE | FALSE | 0.2614 | 2.2069 | 73.153 | 1 | 0.2826 | 0.02826 | 0.18107 | 1.4047 | 0.28812 | Extreme triggered | 73.7292 | 2.2069 | Night | 202512 | 2025-12-16 | 2.2069
2025-12-16 20:00 | 73.7888 | FALSE | FALSE | -1.2501 | -1.7233 | -0.034877 | -0.047244 | 0 |  | 2025-12-16 19:45 | none | FALSE | 2 | 72.5387 | FALSE | FALSE | 0.2975 | 2.0491 | 73.1812 | 2 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.32123 | Extreme/elevated | 73.8237 | 1.8914 | Night | 202512 | 2025-12-16 | 1.8914
2025-12-16 20:15 | 73.5062 | FALSE | FALSE | -0.96948 | -1.3365 | -0.34776 | -0.47088 | -0.2826 |  |  | none | FALSE | 2 | 72.5367 | FALSE | FALSE | 0.1201 |  | 73.1953 | 0 | -0.2826 | 0.01413 | 0.19396 | -1.5299 | 0.32931 | Persistence ends | 73.854 | 0.94397 | Night | 202512 | 2025-12-16 | 0.94397
2025-12-16 20:29 | 73.5062 | FALSE | FALSE | -0.96987 | -1.3371 | -0.37641 | -0.50947 | 0 |  |  | none | FALSE | 2 | 72.5363 | FALSE | FALSE | 0.1159 |  | 73.2095 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.33657 | Normal | 73.8826 | 0.88163 | Night | 202512 | 2025-12-16 | 0.88163
2025-12-16 20:44 | 73.5062 | FALSE | FALSE | -0.96873 | -1.3355 | -0.40353 | -0.54597 | 0 |  |  | none | FALSE | 1 | 72.5375 | FALSE | FALSE | 0.0835 |  | 73.2236 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.34306 | Normal | 73.9097 | 0.82375 | Night | 202512 | 2025-12-16 | 0.82375
2025-12-16 20:59 | 73.5062 | FALSE | FALSE | -0.96614 | -1.3319 | -0.4292 | -0.58051 | 0 |  |  | none | FALSE | 1 | 72.5401 | FALSE | FALSE | 0.0799 |  | 73.2377 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.34883 | Normal | 73.9354 | 0.76962 | Night | 202512 | 2025-12-16 | 0.76962
2025-12-16 21:14 | 73.5062 | FALSE | FALSE | -0.96218 | -1.3263 | -0.4535 | -0.61317 | 0 |  |  | none | FALSE | 1 | 72.544 | FALSE | FALSE | 0.0765 |  | 73.2519 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.35392 | Normal | 73.9597 | 0.71864 | Night | 202512 | 2025-12-16 | 0.71864
2025-12-16 21:29 | 73.5062 | FALSE | FALSE | -0.9569 | -1.319 | -0.47648 | -0.64404 | 0 |  |  | none | FALSE | 0 | 72.5493 | FALSE | FALSE | 0.0447 |  | 73.266 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.35834 | Normal | 73.9827 | 0.67033 | Night | 202512 | 2025-12-16 | 0.67033
2025-12-16 21:44 | 73.5062 | FALSE | FALSE | -0.95035 | -1.3098 | -0.49819 | -0.67319 | 0 |  |  | none | FALSE | 0 | 72.5558 | FALSE | FALSE | 0.0416 |  | 73.2801 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.36214 | Normal | 74.0044 | 0.62429 | Night | 202512 | 2025-12-16 | 0.62429
2025-12-16 21:59 | 73.5062 | FALSE | FALSE | -0.94258 | -1.299 | -0.51868 | -0.70068 | 0 |  |  | none | FALSE | 0 | 72.5636 | FALSE | FALSE | 0.0387 |  | 73.2943 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.36531 | Normal | 74.0249 | 0.58018 | Night | 202512 | 2025-12-16 | 0.58018
2025-12-16 22:14 | 73.5062 | FALSE | FALSE | -0.93361 | -1.2864 | -0.53797 | -0.72655 | 0 |  |  | none | FALSE | 0 | 72.5726 | FALSE | FALSE | 0.0358 |  | 73.3084 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.36789 | Normal | 74.0442 | 0.53771 | Night | 202512 | 2025-12-16 | 0.53771
2025-12-16 22:29 | 73.5062 | FALSE | FALSE | -0.88918 | -1.2245 | -0.55006 | -0.74275 | 0 |  |  | none | FALSE | 0 | 72.617 | FALSE | FALSE | 0.0314 |  | 73.3366 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.35981 | Normal | 74.0563 | 0.47125 | Night | 202512 | 2025-12-16 | 0.47125
2025-12-16 22:44 | 73.5062 | FALSE | FALSE | -0.83957 | -1.1554 | -0.55697 | -0.75202 | 0 |  |  | none | FALSE | 0 | 72.6666 | FALSE | FALSE | 0.027 |  | 73.3649 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.34914 | Normal | 74.0632 | 0.40471 | Night | 202512 | 2025-12-16 | 0.40471
2025-12-16 22:59 | 73.5062 | FALSE | FALSE | -0.7843 | -1.0785 | -0.55822 | -0.7537 | 0 |  |  | none | FALSE | 0 | 72.7219 | FALSE | FALSE | 0.0225 |  | 73.3932 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.33563 | Normal | 74.0644 | 0.3368 | Night | 202512 | 2025-12-16 | 0.3368
2025-12-16 23:14 | 73.5062 | FALSE | FALSE | -0.6469 | -0.88787 | -0.5056 | -0.68313 | 0 |  |  | none | FALSE | 0 | 72.8593 | FALSE | FALSE | 0.0163 |  | 73.4356 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.28812 | Normal | 74.0118 | 0.24521 | Night | 202512 | 2025-12-16 | 0.24521
2025-12-16 23:28 | 73.5062 | FALSE | FALSE | -0.47368 | -0.64858 | -0.41716 | -0.56431 | 0 |  |  | none | FALSE | 0 | 73.0325 | FALSE | FALSE | 0.0085 |  | 73.4779 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.22271 | Normal | 73.9234 | 0.12689 | Night | 202512 | 2025-12-16 | 0.12689
2025-12-16 23:43 | 73.5062 | FALSE | FALSE | -0.20858 | -0.28456 | -0.23684 | -0.32117 | 0 |  |  | none | FALSE | 0 | 73.2976 | FALSE | FALSE | 0.0085 |  | 73.5203 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.11135 | Normal | 73.743 | -0.12689 | Night | 202512 | 2025-12-16 | 0.12689
2025-12-16 23:59 | 73.5062 | FALSE | FALSE | -0.1457 | -0.19861 | -0.20222 | -0.27436 | 0 |  |  | none | FALSE | 0 | 73.3605 | FALSE | FALSE | 0.0217 |  | 73.5345 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.086982 | Normal | 73.7084 | -0.32489 | Night | 202512 | 2025-12-16 | 0.32489
2025-12-17 00:14 | 73.5062 | FALSE | FALSE | -0.1457 | -0.19861 | -0.20222 | -0.27436 | 0 |  |  | none | FALSE | 0 | 73.3605 | FALSE | FALSE | 0.0217 |  | 73.5345 | 0 | 0 | 0 | 0.091688 | 0 | 0.086982 | Normal | 73.7084 | -0.32489 | Night | 202512 | 2025-12-17 | 0.32489
2025-12-17 00:28 | 73.5062 | FALSE | FALSE | -0.1457 | -0.19861 | -0.20222 | -0.27436 | 0 |  |  | none | FALSE | 0 | 73.3605 | FALSE | FALSE | 0.0217 |  | 73.5345 | 0 | 0 | 0 | 0.091688 | 0 | 0.086982 | Normal | 73.7084 | -0.32489 | Night | 202512 | 2025-12-17 | 0.32489
2025-12-17 00:43 | 73.5062 | FALSE | FALSE | -0.11225 | -0.15295 | -0.14051 | -0.19079 | 0 |  |  | none | FALSE | 0 | 73.3939 | FALSE | FALSE | 0.0149 |  | 73.5203 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.063191 | Normal | 73.6467 | -0.22361 | Night | 202512 | 2025-12-17 | 0.22361
2025-12-17 00:58 | 73.5062 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.5062 | FALSE | FALSE | 0 |  | 73.5062 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0 | Normal | 73.5062 |  | Night | 202512 | 2025-12-17
2025-12-17 01:13 | 73.5062 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.5062 | FALSE | FALSE | 0 |  | 73.5062 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.5062 |  | Night | 202512 | 2025-12-17
2025-12-17 01:28 | 73.5062 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.5062 | FALSE | FALSE | 0 |  | 73.5062 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.5062 |  | Night | 202512 | 2025-12-17
2025-12-17 01:43 | 73.2236 | TRUE | FALSE | 0.14209 | 0.19367 | -0.39485 | -0.53635 | -0.2826 | 2025-12-17 03:57 | 2025-12-17 01:43 | lower | TRUE | 1 | 73.3657 | FALSE | FALSE | 0.3689 | 4.2485 | 73.4921 | 1 | -0.2826 | -0.01413 | 0.063191 | -4.2485 | 0.063191 | Extreme triggered | 73.6185 | -4.2485 | Night | 202512 | 2025-12-17 | 4.2485
2025-12-17 01:58 | 73.2236 | FALSE | FALSE | 0.080375 | 0.10965 | -0.4283 | -0.58153 | 0 |  | 2025-12-17 01:43 | lower | TRUE | 1 | 73.304 | FALSE | FALSE | 0.3378 | 3.5863 | 73.4779 | 2 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.086982 | Extreme/elevated | 73.6519 | -2.924 | Night | 202512 | 2025-12-17 | 2.924
2025-12-17 02:13 | 73.2236 | FALSE | FALSE | 0.03315 | 0.045252 | -0.44727 | -0.60712 | 0 |  | 2025-12-17 01:43 | lower | TRUE | 1 | 73.2568 | FALSE | TRUE | 0.3547 | 3.1643 | 73.4638 | 3 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.10353 | Persistent | 73.6709 | -2.3202 | Night | 202512 | 2025-12-17 | 2.3202
2025-12-17 02:28 | 73.2236 | FALSE | FALSE | -0.0058732 | -0.0080215 | -0.45803 | -0.62164 | 0 |  | 2025-12-17 01:43 | none | FALSE | 1 | 73.2177 | FALSE | FALSE | 0.3871 | 2.8605 | 73.4497 | 4 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.11598 | Persistent | 73.6816 | -1.9494 | Night | 202512 | 2025-12-17 | 1.9494
2025-12-17 02:43 | 73.2236 | FALSE | FALSE | -0.039147 | -0.05349 | -0.46305 | -0.6284 | 0 |  | 2025-12-17 01:43 | none | FALSE | 1 | 73.1845 | FALSE | FALSE | 0.4268 | 2.6261 | 73.4356 | 5 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.12555 | Persistent | 73.6866 | -1.6882 | Night | 202512 | 2025-12-17 | 1.6882
2025-12-17 02:58 | 73.2236 | FALSE | FALSE | -0.067916 | -0.092837 | -0.46356 | -0.62909 | 0 |  | 2025-12-17 01:43 | none | FALSE | 1 | 73.1557 | FALSE | FALSE | 0.4707 | 2.4365 | 73.4214 | 6 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13287 | Persistent | 73.6872 | -1.4888 | Night | 202512 | 2025-12-17 | 1.4888
2025-12-17 03:13 | 73.2236 | FALSE | TRUE | -0.092897 | -0.12703 | -0.46028 | -0.62466 | 0 |  | 2025-12-17 01:43 | none | FALSE | 1 | 73.1307 | FALSE | FALSE | 0.5171 | 2.2782 | 73.4073 | 7 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13829 | Confirmed/Materialized Shift | 73.6839 | -1.3283 | Night | 202512 | 2025-12-17 | 1.3283
2025-12-17 03:27 | 73.2236 | FALSE | TRUE | -0.11452 | -0.15665 | -0.45364 | -0.61572 | 0 |  | 2025-12-17 01:43 | none | FALSE | 1 | 73.1091 | FALSE | FALSE | 0.5082 | 2.1426 | 73.3932 | 8 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14204 | Confirmed/Materialized Shift | 73.6772 | -1.1937 | Night | 202512 | 2025-12-17 | 1.1937
2025-12-17 03:42 | 73.2236 | FALSE | TRUE | -0.13306 | -0.18205 | -0.44392 | -0.6026 | 0 |  | 2025-12-17 01:43 | none | FALSE | 1 | 73.0905 | FALSE | FALSE | 0.5004 | 2.0243 | 73.379 | 9 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14424 | Confirmed/Materialized Shift | 73.6675 | -1.0775 | Night | 202512 | 2025-12-17 | 1.0775
2025-12-17 03:57 | 73.2236 | FALSE | FALSE | -0.14864 | -0.20341 | -0.43124 | -0.58549 | 0 |  |  | none | FALSE | 1 | 73.075 | FALSE | FALSE | 0.0936 |  | 73.3649 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14497 | Persistence ends | 73.6548 | -0.97468 | Night | 202512 | 2025-12-17 | 0.97468
2025-12-17 04:12 | 73.2236 | FALSE | FALSE | -0.16132 | -0.2208 | -0.41566 | -0.56445 | 0 |  |  | none | FALSE | 0 | 73.0623 | FALSE | FALSE | 0.0588 |  | 73.3508 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14424 | Normal | 73.6393 | -0.88163 | Night | 202512 | 2025-12-17 | 0.88163
2025-12-17 04:27 | 73.2236 | FALSE | FALSE | -0.17104 | -0.23414 | -0.39712 | -0.53942 | 0 |  |  | none | FALSE | 0 | 73.0526 | FALSE | FALSE | 0.0531 |  | 73.3366 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14204 | Normal | 73.6207 | -0.79582 | Night | 202512 | 2025-12-17 | 0.79582
2025-12-17 04:42 | 72.941 | TRUE | FALSE | 0.044515 | 0.060991 | -0.69025 | -0.93744 | -0.2826 | 2025-12-17 06:26 | 2025-12-17 04:42 | lower | TRUE | 1 | 72.9855 | FALSE | FALSE | 0.2374 | 2.2757 | 73.3084 | 1 | -0.2826 | -0.02826 | 0.086982 | -2.924 | 0.16143 | Extreme triggered | 73.6312 | -2.2757 | Night | 202512 | 2025-12-17 | 2.2757
2025-12-17 04:57 | 72.941 | FALSE | FALSE | -0.0088098 | -0.012079 | -0.68705 | -0.93314 | 0 |  | 2025-12-17 04:42 | none | FALSE | 1 | 72.9322 | FALSE | FALSE | 0.2728 | 2.1126 | 73.2801 | 2 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.17396 | Extreme/elevated | 73.628 | -1.9494 | Night | 202512 | 2025-12-17 | 1.9494
2025-12-17 05:12 | 72.941 | FALSE | FALSE | -0.051277 | -0.070348 | -0.673 | -0.91422 | 0 |  | 2025-12-17 04:42 | none | FALSE | 1 | 72.8897 | FALSE | FALSE | 0.3145 | 1.9806 | 73.2519 | 3 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18107 | Persistent | 73.614 | -1.7168 | Night | 202512 | 2025-12-17 | 1.7168
2025-12-17 05:27 | 72.941 | FALSE | FALSE | -0.08415 | -0.1155 | -0.64935 | -0.88238 | 0 |  | 2025-12-17 04:42 | none | FALSE | 1 | 72.8568 | FALSE | FALSE | 0.3599 | 1.8708 | 73.2236 | 4 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18338 | Persistent | 73.5904 | -1.5411 | Night | 202512 | 2025-12-17 | 1.5411
2025-12-17 05:42 | 72.941 | FALSE | FALSE | -0.1078 | -0.14801 | -0.61648 | -0.83809 | 0 |  | 2025-12-17 04:42 | none | FALSE | 1 | 72.8332 | FALSE | FALSE | 0.4079 | 1.7775 | 73.1953 | 5 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18107 | Persistent | 73.5575 | -1.4047 | Night | 202512 | 2025-12-17 | 1.4047
2025-12-17 05:57 | 72.941 | FALSE | FALSE | -0.12185 | -0.16733 | -0.57401 | -0.78081 | 0 |  | 2025-12-17 04:42 | none | FALSE | 1 | 72.8192 | FALSE | FALSE | 0.4581 | 1.6979 | 73.1671 | 6 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.17396 | Persistent | 73.515 | -1.2996 | Night | 202512 | 2025-12-17 | 1.2996
2025-12-17 06:12 | 72.6584 | TRUE | TRUE | 0.087142 | 0.11979 | -0.84544 | -1.1502 | -0.2826 |  | 2025-12-17 04:42 | lower | TRUE | 2 | 72.7455 | TRUE | TRUE | 0.6211 | 1.8067 | 73.1247 | 7 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.18957 | Confirmed/Materialized Shift | 73.5038 | -2.4597 | Night | 202512 | 2025-12-17 | 2.4597
2025-12-17 06:26 | 72.941 | TRUE | FALSE | -0.18641 | -0.25621 | -0.49727 | -0.67712 | 0.2826 |  |  | none | FALSE | 3 | 72.7546 | TRUE | FALSE | 0.1463 |  | 73.0964 | 0 | 0.2826 | -0.02826 | 0.12638 | 2.4597 | 0.17092 | Persistence ends | 73.4383 | -0.90938 | Night | 202512 | 2025-12-17 | 0.90938
2025-12-17 06:41 | 72.941 | FALSE | FALSE | -0.20176 | -0.27738 | -0.48436 | -0.65967 | 0 |  |  | none | FALSE | 3 | 72.7392 | FALSE | FALSE | 0.1406 |  | 73.0823 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.17153 | Normal | 73.4254 | -0.82375 | Night | 202512 | 2025-12-17 | 0.82375
2025-12-17 06:56 | 72.6584 | TRUE | FALSE | 0.010989 | 0.015122 | -0.78029 | -1.0625 | -0.2826 | 2025-12-17 08:45 | 2025-12-17 06:56 | lower | TRUE | 4 | 72.6694 | TRUE | FALSE | 0.3086 | 2.0571 | 73.054 | 1 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.19233 | Extreme triggered | 73.4387 | -2.0571 | Night | 202512 | 2025-12-17 | 2.0571
2025-12-17 07:11 | 72.6584 | FALSE | FALSE | -0.046739 | -0.064369 | -0.7815 | -1.0641 | 0 |  | 2025-12-17 06:56 | none | FALSE | 3 | 72.6117 | FALSE | FALSE | 0.3183 | 1.9157 | 73.0258 | 2 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.20706 | Extreme/elevated | 73.4399 | -1.7743 | Day | 202512 | 2025-12-17 | 1.7743
2025-12-17 07:26 | 72.6584 | FALSE | FALSE | -0.094825 | -0.13068 | -0.77306 | -1.0528 | 0 |  | 2025-12-17 06:56 | none | FALSE | 3 | 72.5636 | FALSE | FALSE | 0.3613 | 1.7981 | 72.9975 | 3 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21697 | Persistent | 73.4315 | -1.563 | Day | 202512 | 2025-12-17 | 1.563
2025-12-17 07:30 | 72.3758 | FALSE | FALSE | 0.077974 | 0.10762 | -1.0807 | -1.4712 | -0.2826 |  | 2025-12-17 06:56 | lower | TRUE | 3 | 72.4538 | FALSE | TRUE | 0.4684 | 1.9264 | 72.9551 | 4 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.25068 | Persistent | 73.4565 | -2.3111 | Day | 202512 | 2025-12-17 | 2.3111
2025-12-17 07:45 | 72.3758 | FALSE | FALSE | -0.01012 | -0.013985 | -1.084 | -1.4756 | 0 |  | 2025-12-17 06:56 | none | FALSE | 3 | 72.3657 | FALSE | FALSE | 0.5023 | 1.9337 | 72.9127 | 5 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.27353 | Persistent | 73.4598 | -1.963 | Day | 202512 | 2025-12-17 | 1.963
2025-12-17 08:00 | 72.3758 | FALSE | FALSE | -0.081697 | -0.11301 | -1.0708 | -1.4579 | 0 |  | 2025-12-17 06:56 | none | FALSE | 3 | 72.2941 | FALSE | FALSE | 0.543 | 1.8975 | 72.8704 | 6 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.28812 | Persistent | 73.4466 | -1.7165 | Day | 202512 | 2025-12-17 | 1.7165
2025-12-17 08:16 | 72.3758 | FALSE | TRUE | -0.13921 | -0.19271 | -1.0435 | -1.4213 | 0 |  | 2025-12-17 06:56 | none | FALSE | 3 | 72.2366 | FALSE | FALSE | 0.5877 | 1.8449 | 72.828 | 7 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.29568 | Confirmed/Materialized Shift | 73.4193 | -1.5292 | Day | 202512 | 2025-12-17 | 1.5292
2025-12-17 08:30 | 72.3758 | FALSE | TRUE | -0.18373 | -0.2545 | -1.0033 | -1.3672 | 0 |  | 2025-12-17 06:56 | none | FALSE | 2 | 72.1921 | FALSE | FALSE | 0.5492 | 1.7869 | 72.7856 | 8 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.29675 | Confirmed/Materialized Shift | 73.3791 | -1.3809 | Day | 202512 | 2025-12-17 | 1.3809
2025-12-17 08:30 | 72.3758 | FALSE | TRUE | -0.2154 | -0.29849 | -0.95016 | -1.2958 | 0 |  | 2025-12-17 06:56 | none | FALSE | 1 | 72.1604 | FALSE | FALSE | 0.5126 | 1.7284 | 72.7432 | 9 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.29139 | Confirmed/Materialized Shift | 73.326 | -1.2608 | Day | 202512 | 2025-12-17 | 1.2608
2025-12-17 08:45 | 72.6584 | FALSE | FALSE | -0.48124 | -0.66675 | -0.59428 | -0.81128 | 0.2826 |  |  | none | FALSE | 1 | 72.1772 | FALSE | FALSE | 0.0426 |  | 72.7149 | 0 | 0.2826 | -0.02826 | 0.15614 | 1.9909 | 0.26888 | Persistence ends | 73.2527 | -0.2102 | Day | 202512 | 2025-12-17 | 0.2102
2025-12-17 09:00 | 72.6584 | FALSE | FALSE | -0.45343 | -0.62797 | -0.50995 | -0.69695 | 0 |  |  | none | FALSE | 0 | 72.205 | FALSE | FALSE | 0.0078 |  | 72.6867 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.24084 | Normal | 73.1683 | -0.11734 | Day | 202512 | 2025-12-17 | 0.11734
2025-12-17 09:15 | 72.941 | FALSE | FALSE | -0.73603 | -1.0194 | -0.22735 | -0.31072 | 0.2826 |  |  | none | FALSE | 0 | 72.205 | FALSE | FALSE | 0.0704 |  | 72.6867 | 0 | 0.2826 | 0 | 0.15881 | 1.7795 | 0.24084 | Normal | 73.1683 | 1.056 | Day | 202512 | 2025-12-17 | 1.056
2025-12-17 09:30 | 72.941 | FALSE | FALSE | -0.73603 | -1.0194 | -0.22735 | -0.31072 | 0 |  |  | none | FALSE | 0 | 72.205 | FALSE | FALSE | 0.0704 |  | 72.6867 | 0 | 0 | 0 | 0.15881 | 0 | 0.24084 | Normal | 73.1683 | 1.056 | Day | 202512 | 2025-12-17 | 1.056
2025-12-17 09:45 | 73.2236 | FALSE | FALSE | -1.0503 | -1.4553 | -0.0046923 | -0.0064078 | 0.2826 |  |  | none | FALSE | 0 | 72.1733 | FALSE | FALSE | 0.1321 |  | 72.7008 | 0 | 0.2826 | 0.01413 | 0.17092 | 1.5708 | 0.26375 | Normal | 73.2283 | 1.9822 | Day | 202512 | 2025-12-17 | 1.9822
2025-12-17 10:00 | 73.5062 | FALSE | FALSE | -1.4091 | -1.9544 | 0.14524 | 0.19798 | 0.2826 | 2025-12-17 11:44 | 2025-12-17 10:00 | upper | TRUE | 0 | 72.0971 | FALSE | FALSE | 0.2211 | 2.4597 | 72.7291 | 1 | 0.2826 | 0.02826 | 0.18107 | 1.4047 | 0.31596 | Extreme triggered | 73.361 | 2.4597 | Day | 202512 | 2025-12-17 | 2.4597
2025-12-17 10:15 | 73.5062 | FALSE | FALSE | -1.4656 | -2.0344 | 0.032201 | 0.043826 | 0 |  | 2025-12-17 10:00 | upper | TRUE | 0 | 72.0406 | FALSE | FALSE | 0.2536 | 2.2748 | 72.7573 | 2 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.35834 | Extreme/elevated | 73.474 | 2.0899 | Day | 202512 | 2025-12-17 | 2.0899
2025-12-17 10:29 | 73.5062 | FALSE | FALSE | -1.5088 | -2.0957 | -0.067563 | -0.09183 | 0 |  | 2025-12-17 10:00 | none | FALSE | 0 | 71.9974 | FALSE | FALSE | 0.2933 | 2.126 | 72.7856 | 3 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.3941 | Persistent | 73.5738 | 1.8286 | Day | 202512 | 2025-12-17 | 1.8286
2025-12-17 10:44 | 73.5062 | FALSE | FALSE | -1.5265 | -2.1208 | -0.17006 | -0.23081 | 0 |  | 2025-12-17 10:00 | none | FALSE | 0 | 71.9797 | FALSE | FALSE | 0.3352 | 1.9943 | 72.828 | 4 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.42415 | Persistent | 73.6763 | 1.5991 | Day | 202512 | 2025-12-17 | 1.5991
2025-12-17 10:59 | 73.7888 | FALSE | FALSE | -1.8691 | -2.5989 | -0.032187 | -0.043601 | 0.2826 |  | 2025-12-17 10:00 | none | FALSE | 0 | 71.9197 | FALSE | FALSE | 0.4145 | 1.9819 | 72.8704 | 5 | 0.2826 | 0.04239 | 0.16593 | 1.4477 | 0.47532 | Persistent | 73.821 | 1.9323 | Day | 202512 | 2025-12-17 | 1.9323
2025-12-17 11:14 | 73.7888 | FALSE | FALSE | -1.9118 | -2.6598 | -0.15964 | -0.21589 | 0 |  | 2025-12-17 10:00 | none | FALSE | 0 | 71.877 | FALSE | FALSE | 0.4556 | 1.9335 | 72.9127 | 6 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.51785 | Persistent | 73.9484 | 1.6917 | Day | 202512 | 2025-12-17 | 1.6917
2025-12-17 11:29 | 73.7888 | FALSE | TRUE | -1.9183 | -2.6691 | -0.27918 | -0.37693 | 0 |  | 2025-12-17 10:00 | none | FALSE | 0 | 71.8705 | FALSE | FALSE | 0.4995 | 1.8704 | 72.9693 | 7 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.54936 | Confirmed/Materialized Shift | 74.068 | 1.4918 | Day | 202512 | 2025-12-17 | 1.4918
2025-12-17 11:44 | 73.2236 | TRUE | FALSE | -1.3202 | -1.8361 | -0.86804 | -1.1716 | -0.5652 |  |  | none | FALSE | 1 | 71.9034 | FALSE | FALSE | 0.0561 |  | 72.9975 | 0 | -0.5652 | 0.02826 | 0.20296 | -2.924 | 0.54706 | Persistence ends | 74.0916 | 0.41326 | Day | 202512 | 2025-12-17 | 0.41326
2025-12-17 11:59 | 73.2236 | FALSE | FALSE | -1.2842 | -1.7852 | -0.88859 | -1.199 | 0 |  |  | none | FALSE | 1 | 71.9394 | FALSE | FALSE | 0.0528 |  | 73.0258 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.54321 | Normal | 74.1122 | 0.36417 | Day | 202512 | 2025-12-17 | 0.36417
2025-12-17 12:14 | 72.941 | FALSE | FALSE | -0.93075 | -1.2925 | -1.1568 | -1.5612 | -0.2826 |  |  | none | FALSE | 1 | 72.0103 | FALSE | FALSE | 0.043 |  | 73.054 | 0 | -0.2826 | 0.02826 | 0.20296 | -1.5316 | 0.52189 | Normal | 74.0978 | -0.2166 | Day | 202512 | 2025-12-17 | 0.2166
2025-12-17 12:29 | 72.941 | FALSE | FALSE | -0.85468 | -1.1856 | -1.1373 | -1.5352 | 0 |  |  | none | FALSE | 1 | 72.0863 | FALSE | FALSE | 0.0475 |  | 73.0823 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.49799 | Normal | 74.0783 | -0.28374 | Day | 202512 | 2025-12-17 | 0.28374
2025-12-17 12:44 | 72.941 | FALSE | FALSE | -0.77264 | -1.0706 | -1.1118 | -1.5013 | 0 |  |  | none | FALSE | 1 | 72.1684 | FALSE | FALSE | 0.0526 |  | 73.1106 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.4711 | Normal | 74.0528 | -0.35992 | Day | 202512 | 2025-12-17 | 0.35992
2025-12-17 12:59 | 72.6584 | FALSE | FALSE | -0.43719 | -0.60535 | -1.3698 | -1.8503 | -0.2826 |  |  | none | FALSE | 1 | 72.2212 | FALSE | FALSE | 0.0974 |  | 73.1247 | 0 | -0.2826 | 0.01413 | 0.21454 | -1.3831 | 0.45174 | Normal | 74.0282 | -1.0322 | Day | 202512 | 2025-12-17 | 1.0322
2025-12-17 13:14 | 72.941 | FALSE | FALSE | -0.62588 | -0.86548 | -1.0498 | -1.4188 | 0.2826 |  |  | none | FALSE | 1 | 72.3151 | FALSE | FALSE | 0.0623 |  | 73.153 | 0 | 0.2826 | 0.02826 | 0.22271 | 1.142 | 0.41891 | Normal | 73.9908 | -0.50595 | Day | 202512 | 2025-12-17 | 0.50595
2025-12-17 13:28 | 73.2236 | FALSE | FALSE | -0.78211 | -1.0796 | -0.72559 | -0.9812 | 0.2826 |  |  | none | FALSE | 1 | 72.4415 | FALSE | FALSE | 0.0336 |  | 73.1953 | 0 | 0.2826 | 0.04239 | 0.22968 | 1.0459 | 0.37692 | Normal | 73.9492 | 0.074975 | Day | 202512 | 2025-12-17 | 0.074975
2025-12-17 13:43 | 73.7888 | TRUE | FALSE | -1.2908 | -1.7804 | -0.21691 | -0.2931 | 0.5652 |  |  | none | FALSE | 2 | 72.498 | TRUE | FALSE | 0.1521 |  | 73.2519 | 0 | 0.5652 | 0.05652 | 0.25277 | 2.0125 | 0.37692 | Normal | 74.0057 | 1.4245 | Day | 202512 | 2025-12-17 | 1.4245
2025-12-17 13:52 | 74.0714 | FALSE | FALSE | -1.5328 | -2.1131 | -0.035025 | -0.047263 | 0.2826 |  |  | none | FALSE | 2 | 72.5386 | FALSE | FALSE | 0.1845 |  | 73.3225 | 0 | 0.2826 | 0.07065 | 0.2573 | 0.82375 | 0.39196 | Normal | 74.1064 | 1.9106 | Day | 202512 | 2025-12-17 | 1.9106
2025-12-17 13:55 | 74.0714 | FALSE | FALSE | -1.5221 | -2.0981 | -0.13739 | -0.18514 | 0 |  |  | none | FALSE | 1 | 72.5493 | FALSE | FALSE | 0.1398 |  | 73.379 | 0 | 0 | 0.05652 | 0.25277 | -0.22361 | 0.41488 | Normal | 74.2088 | 1.6688 | Day | 202512 | 2025-12-17 | 1.6688
2025-12-17 14:10 | 73.7888 | FALSE | FALSE | -1.1895 | -1.6385 | -0.45475 | -0.61251 | -0.2826 |  |  | none | FALSE | 1 | 72.5993 | FALSE | FALSE | 0.0882 |  | 73.4214 | 0 | -0.2826 | 0.04239 | 0.26375 | -1.2322 | 0.41106 | Normal | 74.2435 | 0.89373 | Day | 202512 | 2025-12-17 | 0.89373
2025-12-17 14:25 | 73.5062 | FALSE | FALSE | -0.88816 | -1.2231 | -0.74686 | -1.0058 | -0.2826 |  |  | none | FALSE | 1 | 72.618 | FALSE | FALSE | 0.0401 |  | 73.4356 | 0 | -0.2826 | 0.01413 | 0.26692 | -1.1117 | 0.40876 | Normal | 74.2531 | 0.17284 | Day | 202512 | 2025-12-17 | 0.17284
2025-12-17 14:28 | 73.5062 | FALSE | FALSE | -0.88816 | -1.2231 | -0.74686 | -1.0058 | 0 |  |  | none | FALSE | 1 | 72.618 | FALSE | FALSE | 0.0401 |  | 73.4356 | 0 | 0 | 0 | 0.25933 | 0 | 0.40876 | Normal | 74.2531 | 0.17284 | Day | 202512 | 2025-12-17 | 0.17284
2025-12-17 14:43 | 73.5062 | FALSE | FALSE | -0.88816 | -1.2231 | -0.74686 | -1.0058 | 0 |  |  | none | FALSE | 1 | 72.618 | FALSE | FALSE | 0.0401 |  | 73.4356 | 0 | 0 | 0 | 0.25933 | 0 | 0.40876 | Normal | 74.2531 | 0.17284 | Day | 202512 | 2025-12-17 | 0.17284
2025-12-17 14:58 | 73.2236 | FALSE | FALSE | -0.62431 | -0.85993 | -1.0199 | -1.3738 | -0.2826 |  |  | none | FALSE | 1 | 72.5993 | FALSE | FALSE | 0.0607 |  | 73.4214 | 0 | -0.2826 | -0.01413 | 0.26692 | -1.0058 | 0.41106 | Normal | 74.2435 | -0.48124 | Day | 202512 | 2025-12-17 | 0.48124
2025-12-17 15:13 | 73.2236 | FALSE | FALSE | -0.64201 | -0.88453 | -1.0094 | -1.3598 | 0 |  |  | none | FALSE | 1 | 72.5816 | FALSE | FALSE | 0.0582 |  | 73.4073 | 0 | 0 | -0.01413 | 0.26692 | 0.052937 | 0.41285 | Normal | 74.233 | -0.44493 | Day | 202512 | 2025-12-17 | 0.44493
2025-12-17 15:28 | 73.2236 | FALSE | FALSE | -0.65381 | -0.90094 | -0.96467 | -1.3003 | 0 |  |  | none | FALSE | 1 | 72.5698 | FALSE | FALSE | 0.0542 |  | 73.379 | 0 | 0 | -0.02826 | 0.25771 | 0.10966 | 0.40462 | Normal | 74.1883 | -0.38414 | Day | 202512 | 2025-12-17 | 0.38414
2025-12-17 15:43 | 73.2236 | FALSE | FALSE | -0.66102 | -0.91097 | -0.91536 | -1.2347 | 0 |  |  | none | FALSE | 0 | 72.5626 | FALSE | FALSE | 0.0215 |  | 73.3508 | 0 | 0 | -0.02826 | 0.25771 | 0.10966 | 0.3941 | Normal | 74.139 | -0.32269 | Day | 202512 | 2025-12-17 | 0.32269
2025-12-17 15:58 | 72.941 | FALSE | FALSE | -0.41277 | -0.56912 | -1.1475 | -1.5489 | -0.2826 |  |  | none | FALSE | 0 | 72.5282 | FALSE | FALSE | 0.0628 |  | 73.3084 | 0 | -0.2826 | -0.04239 | 0.26375 | -0.91074 | 0.39008 | Normal | 74.0885 | -0.94182 | Day | 202512 | 2025-12-17 | 0.94182
2025-12-17 16:13 | 72.6584 | FALSE | FALSE | -0.21057 | -0.29065 | -1.454 | -1.9619 | -0.2826 |  |  | none | FALSE | 0 | 72.4478 | FALSE | FALSE | 0.0996 |  | 73.2801 | 0 | -0.2826 | -0.02826 | 0.24084 | -1.056 | 0.41614 | Normal | 74.1124 | -1.494 | Day | 202512 | 2025-12-17 | 1.494
2025-12-17 16:28 | 72.3758 | FALSE | FALSE | -0.063615 | -0.087972 | -1.7875 | -2.4102 | -0.2826 |  |  | none | FALSE | 0 | 72.3122 | FALSE | FALSE | 0.1242 |  | 73.2377 | 0 | -0.2826 | -0.04239 | 0.2473 | -0.97132 | 0.46277 | Normal | 74.1633 | -1.8625 | Day | 202512 | 2025-12-17 | 1.8625
2025-12-17 16:43 | 72.3758 | FALSE | FALSE | -0.16189 | -0.22418 | -1.8292 | -2.4651 | 0 |  |  | none | FALSE | 0 | 72.2139 | FALSE | FALSE | 0.1117 |  | 73.2095 | 0 | 0 | -0.02826 | 0.24084 | 0.11734 | 0.49778 | Normal | 74.205 | -1.6748 | Day | 202512 | 2025-12-17 | 1.6748
2025-12-17 16:58 | 72.3758 | FALSE | FALSE | -0.25238 | -0.34993 | -1.8632 | -2.5097 | 0 |  |  | none | FALSE | 0 | 72.1234 | FALSE | FALSE | 0.1015 |  | 73.1812 | 0 | 0 | -0.02826 | 0.24084 | 0.11734 | 0.52889 | Normal | 74.239 | -1.5228 | Day | 202512 | 2025-12-17 | 1.5228
2025-12-17 17:13 | 72.3758 | FALSE | FALSE | -0.33639 | -0.46695 | -1.8907 | -2.5458 | 0 |  |  | none | FALSE | 0 | 72.0394 | FALSE | FALSE | 0.0931 |  | 73.153 | 0 | 0 | -0.02826 | 0.24084 | 0.11734 | 0.55677 | Normal | 74.2665 | -1.3958 | Day | 202512 | 2025-12-17 | 1.3958
2025-12-17 17:27 | 72.6584 | FALSE | FALSE | -0.61899 | -0.85924 | -1.6081 | -2.1653 | 0.2826 |  |  | none | FALSE | 0 | 72.0394 | FALSE | FALSE | 0.0592 |  | 73.153 | 0 | 0.2826 | 0 | 0.24258 | 1.165 | 0.55677 | Normal | 74.2665 | -0.88825 | Day | 202512 | 2025-12-17 | 0.88825
2025-12-17 17:42 | 72.941 | FALSE | FALSE | -0.90159 | -1.2515 | -1.3255 | -1.7848 | 0.2826 |  |  | none | FALSE | 0 | 72.0394 | FALSE | FALSE | 0.0254 |  | 73.153 | 0 | 0.2826 | 0 | 0.24258 | 1.165 | 0.55677 | Normal | 74.2665 | -0.38068 | Night | 202512 | 2025-12-17 | 0.38068
2025-12-17 17:57 | 72.941 | FALSE | FALSE | -0.91911 | -1.2762 | -1.3148 | -1.7706 | 0 |  |  | none | FALSE | 0 | 72.0219 | FALSE | FALSE | 0.0236 |  | 73.1388 | 0 | 0 | -0.01413 | 0.23331 | 0.060564 | 0.55847 | Normal | 74.2558 | -0.35422 | Night | 202512 | 2025-12-17 | 0.35422
2025-12-17 18:12 | 72.941 | FALSE | FALSE | -0.92126 | -1.2792 | -1.2321 | -1.6611 | 0 |  |  | none | FALSE | 0 | 72.0197 | FALSE | FALSE | 0.0192 |  | 73.0964 | 0 | 0 | -0.04239 | 0.18957 | 0.22361 | 0.53835 | Normal | 74.1731 | -0.28872 | Night | 202512 | 2025-12-17 | 0.28872
2025-12-17 18:27 | 72.941 | FALSE | FALSE | -0.87617 | -1.2158 | -1.074 | -1.451 | 0 |  |  | none | FALSE | 0 | 72.0648 | FALSE | FALSE | 0.0135 |  | 73.0399 | 0 | 0 | -0.05652 | 0.17396 | 0.32489 | 0.48754 | Normal | 74.015 | -0.20288 | Night | 202512 | 2025-12-17 | 0.20288
2025-12-17 18:42 | 72.941 | FALSE | FALSE | -0.80342 | -1.1137 | -0.8882 | -1.2031 | 0 |  |  | none | FALSE | 0 | 72.1376 | FALSE | FALSE | 0.0067 |  | 72.9834 | 0 | 0 | -0.05652 | 0.17396 | 0.32489 | 0.42291 | Normal | 73.8292 | -0.10023 | Night | 202512 | 2025-12-17 | 0.10023
2025-12-17 18:42 | 72.941 | FALSE | FALSE | -0.75607 | -1.0474 | -0.75607 | -1.0259 | 0 |  |  | none | FALSE | 0 | 72.1849 | FALSE | FALSE | 0 |  | 72.941 | 0 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.37804 | Normal | 73.6971 | 0 | Night | 202512 | 2025-12-17 | 0
2025-12-17 18:43 | 72.941 | FALSE | FALSE | -0.7361 | -1.0195 | -0.67958 | -0.92308 | 0 |  |  | none | FALSE | 0 | 72.2049 | FALSE | FALSE | 0.0053 |  | 72.9127 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.35392 | Normal | 73.6206 | 0.079849 | Night | 202512 | 2025-12-17 | 0.079849
2025-12-17 18:58 | 73.2236 | FALSE | FALSE | -0.99311 | -1.3749 | -0.34313 | -0.46643 | 0.2826 |  |  | none | FALSE | 0 | 72.2305 | FALSE | FALSE | 0.0649 |  | 72.8986 | 0 | 0.2826 | -0.01413 | 0.17092 | 1.7361 | 0.33406 | Normal | 73.5667 | 0.97284 | Night | 202512 | 2025-12-17 | 0.97284
2025-12-17 19:13 | 73.5062 | FALSE | FALSE | -1.2757 | -1.7662 | -0.060535 | -0.082286 | 0.2826 |  |  | none | FALSE | 0 | 72.2305 | FALSE | FALSE | 0.1213 |  | 72.8986 | 0 | 0.2826 | 0 | 0.18338 | 1.5411 | 0.33406 | Normal | 73.5667 | 1.8188 | Night | 202512 | 2025-12-17 | 1.8188
2025-12-17 19:28 | 73.5062 | FALSE | FALSE | -1.3013 | -1.8022 | -0.11438 | -0.15536 | 0 |  |  | none | FALSE | 0 | 72.2049 | FALSE | FALSE | 0.1118 |  | 72.9127 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.35392 | Normal | 73.6206 | 1.6768 | Night | 202512 | 2025-12-17 | 1.6768
2025-12-17 19:42 | 73.5062 | FALSE | FALSE | -1.3236 | -1.8337 | -0.16498 | -0.22394 | 0 |  |  | none | FALSE | 0 | 72.1826 | FALSE | FALSE | 0.1038 |  | 72.9269 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.37215 | Normal | 73.6712 | 1.5567 | Night | 202512 | 2025-12-17 | 1.5567
2025-12-17 19:57 | 73.7888 | FALSE | FALSE | -1.6634 | -2.3063 | 0.0039104 | 0.0052997 | 0.2826 | 2025-12-17 22:56 | 2025-12-17 19:57 | upper | TRUE | 0 | 72.1254 | FALSE | FALSE | 0.1911 | 2.0094 | 72.9551 | 1 | 0.2826 | 0.02826 | 0.18107 | 1.4047 | 0.41488 | Extreme triggered | 73.7849 | 2.0094 | Night | 202512 | 2025-12-17 | 2.0094
2025-12-17 20:12 | 73.7888 | FALSE | FALSE | -1.7089 | -2.3708 | -0.098073 | -0.13273 | 0 |  | 2025-12-17 19:57 | none | FALSE | 0 | 72.0799 | FALSE | FALSE | 0.2331 | 1.8962 | 72.9834 | 2 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.45174 | Extreme/elevated | 73.8869 | 1.7829 | Night | 202512 | 2025-12-17 | 1.7829
2025-12-17 20:27 | 73.7888 | FALSE | FALSE | -1.7351 | -2.408 | -0.20904 | -0.2825 | 0 |  | 2025-12-17 19:57 | none | FALSE | 0 | 72.0537 | FALSE | FALSE | 0.2761 | 1.7874 | 73.0258 | 3 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.48603 | Persistent | 73.9978 | 1.5699 | Night | 202512 | 2025-12-17 | 1.5699
2025-12-17 20:41 | 73.7888 | FALSE | FALSE | -1.7192 | -2.3855 | -0.30622 | -0.41328 | 0 |  | 2025-12-17 19:57 | none | FALSE | 0 | 72.0696 | FALSE | FALSE | 0.3216 | 1.6894 | 73.0823 | 4 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.50636 | Persistent | 74.095 | 1.3952 | Night | 202512 | 2025-12-17 | 1.3952
2025-12-17 20:56 | 73.7888 | FALSE | FALSE | -1.6381 | -2.2704 | -0.36644 | -0.49416 | 0 |  | 2025-12-17 19:57 | none | FALSE | 0 | 72.1507 | FALSE | FALSE | 0.3703 | 1.6053 | 73.153 | 5 | 0 | 0.07065 | 0.12555 | -0.56273 | 0.50115 | Persistent | 74.1552 | 1.2688 | Night | 202512 | 2025-12-17 | 1.2688
2025-12-17 21:11 | 73.7888 | FALSE | FALSE | -1.5355 | -2.1252 | -0.40513 | -0.54604 | 0 |  | 2025-12-17 19:57 | none | FALSE | 0 | 72.2533 | FALSE | FALSE | 0.4205 | 1.5319 | 73.2236 | 6 | 0 | 0.07065 | 0.12555 | -0.56273 | 0.48516 | Persistent | 74.1939 | 1.165 | Night | 202512 | 2025-12-17 | 1.165
2025-12-17 21:26 | 74.0714 | FALSE | TRUE | -1.7176 | -2.3739 | -0.19159 | -0.25799 | 0.2826 |  | 2025-12-17 19:57 | none | FALSE | 0 | 72.3538 | FALSE | FALSE | 0.5066 | 1.5414 | 73.3084 | 7 | 0.2826 | 0.08478 | 0.13287 | 1.4888 | 0.4773 | Confirmed/Materialized Shift | 74.263 | 1.5986 | Night | 202512 | 2025-12-17 | 1.5986
2025-12-17 21:41 | 74.0714 | FALSE | TRUE | -1.584 | -2.1853 | -0.22757 | -0.30628 | 0 |  | 2025-12-17 19:57 | none | FALSE | 0 | 72.4874 | FALSE | FALSE | 0.4998 | 1.5359 | 73.3932 | 8 | 0 | 0.08478 | 0.13287 | -0.63808 | 0.4529 | Confirmed/Materialized Shift | 74.299 | 1.4975 | Night | 202512 | 2025-12-17 | 1.4975
2025-12-17 21:56 | 74.0714 | FALSE | TRUE | -1.4923 | -2.0561 | -0.27709 | -0.37269 | 0 |  | 2025-12-17 19:57 | none | FALSE | 0 | 72.5791 | FALSE | FALSE | 0.4916 | 1.5179 | 73.4638 | 9 | 0 | 0.07065 | 0.12555 | -0.56273 | 0.44234 | Confirmed/Materialized Shift | 74.3485 | 1.3736 | Night | 202512 | 2025-12-17 | 1.3736
2025-12-17 22:11 | 74.0714 | FALSE | TRUE | -1.4395 | -1.982 | -0.3374 | -0.45344 | 0 |  | 2025-12-17 19:57 | none | FALSE | 0 | 72.6319 | FALSE | FALSE | 0.4827 | 1.4901 | 73.5203 | 10 | 0 | 0.05652 | 0.11598 | -0.48734 | 0.44424 | Confirmed/Materialized Shift | 74.4088 | 1.2405 | Night | 202512 | 2025-12-17 | 1.2405
2025-12-17 22:26 | 74.0714 | FALSE | TRUE | -1.3716 | -1.8867 | -0.38249 | -0.51373 | 0 |  | 2025-12-17 19:57 | none | FALSE | 0 | 72.6998 | FALSE | FALSE | 0.4752 | 1.4572 | 73.5768 | 11 | 0 | 0.05652 | 0.11598 | -0.48734 | 0.43852 | Confirmed/Materialized Shift | 74.4539 | 1.1278 | Night | 202512 | 2025-12-17 | 1.1278
2025-12-17 22:41 | 74.0714 | FALSE | TRUE | -1.2878 | -1.7694 | -0.41175 | -0.55281 | 0 |  | 2025-12-17 19:57 | none | FALSE | 0 | 72.7836 | FALSE | FALSE | 0.4687 | 1.4217 | 73.6334 | 12 | 0 | 0.05652 | 0.11598 | -0.48734 | 0.42489 | Confirmed/Materialized Shift | 74.4832 | 1.0309 | Night | 202512 | 2025-12-17 | 1.0309
2025-12-17 22:56 | 74.0714 | FALSE | FALSE | -1.1866 | -1.628 | -0.42357 | -0.56859 | 0 |  |  | none | FALSE | 0 | 72.8848 | FALSE | FALSE | 0.0632 |  | 73.6899 | 0 | 0 | 0.05652 | 0.11598 | -0.48734 | 0.40254 | Persistence ends | 74.495 | 0.94776 | Night | 202512 | 2025-12-17 | 0.94776
2025-12-17 23:11 | 74.0714 | FALSE | FALSE | -1.0648 | -1.4585 | -0.41479 | -0.55686 | 0 |  |  | none | FALSE | 0 | 73.0066 | FALSE | FALSE | 0.0586 |  | 73.7464 | 0 | 0 | 0.05652 | 0.11598 | -0.48734 | 0.36989 | Normal | 74.4862 | 0.87862 | Night | 202512 | 2025-12-17 | 0.87862
2025-12-17 23:26 | 74.0714 | FALSE | FALSE | -0.91615 | -1.2523 | -0.37921 | -0.50934 | 0 |  |  | none | FALSE | 0 | 73.1552 | FALSE | FALSE | 0.0553 |  | 73.8029 | 0 | 0 | 0.05652 | 0.11598 | -0.48734 | 0.32384 | Normal | 74.4506 | 0.82902 | Night | 202512 | 2025-12-17 | 0.82902
2025-12-17 23:40 | 74.0714 | FALSE | FALSE | -0.72655 | -0.99059 | -0.30265 | -0.40692 | 0 |  |  | none | FALSE | 0 | 73.3449 | FALSE | FALSE | 0.0549 |  | 73.8594 | 0 | 0 | 0.05652 | 0.11598 | -0.48734 | 0.2573 | Normal | 74.374 | 0.82375 | Night | 202512 | 2025-12-17 | 0.82375
2025-12-17 23:55 | 74.0714 | FALSE | FALSE | -0.59569 | -0.81072 | -0.25657 | -0.34518 | 0 |  |  | none | FALSE | 0 | 73.4757 | FALSE | FALSE | 0.0531 |  | 73.9018 | 0 | 0 | 0.04239 | 0.10353 | -0.40945 | 0.21306 | Normal | 74.328 | 0.79582 | Night | 202512 | 2025-12-17 | 0.79582
2025-12-18 00:10 | 74.0714 | FALSE | FALSE | -0.5303 | -0.72109 | -0.2477 | -0.33329 | 0 |  |  | none | FALSE | 0 | 73.5411 | FALSE | FALSE | 0.0484 |  | 73.9301 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.1945 | Normal | 74.3191 | 0.72648 | Night | 202512 | 2025-12-18 | 0.72648
2025-12-18 00:26 | 74.0714 | FALSE | FALSE | -0.45117 | -0.61283 | -0.22509 | -0.30296 | 0 |  |  | none | FALSE | 0 | 73.6202 | FALSE | FALSE | 0.0446 |  | 73.9584 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.16906 | Normal | 74.2965 | 0.66862 | Night | 202512 | 2025-12-18 | 0.66862
2025-12-18 00:40 | 74.0714 | FALSE | FALSE | -0.35052 | -0.47546 | -0.18096 | -0.2437 | 0 |  |  | none | FALSE | 0 | 73.7209 | FALSE | FALSE | 0.0425 |  | 73.9866 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.13287 | Normal | 74.2524 | 0.63808 | Night | 202512 | 2025-12-18 | 0.63808
2025-12-18 00:55 | 74.0714 | FALSE | FALSE | -0.32175 | -0.43627 | -0.18045 | -0.24302 | 0 |  |  | none | FALSE | 0 | 73.7497 | FALSE | FALSE | 0.0375 |  | 74.0007 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.12555 | Normal | 74.2518 | 0.56273 | Night | 202512 | 2025-12-18 | 0.56273
2025-12-18 01:10 | 74.0714 | FALSE | FALSE | -0.28847 | -0.39098 | -0.17543 | -0.23628 | 0 |  |  | none | FALSE | 0 | 73.7829 | FALSE | FALSE | 0.0325 |  | 74.0149 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.11598 | Normal | 74.2468 | 0.48734 | Night | 202512 | 2025-12-18 | 0.48734
2025-12-18 01:25 | 74.0714 | FALSE | FALSE | -0.24945 | -0.33791 | -0.16467 | -0.22182 | 0 |  |  | none | FALSE | 0 | 73.822 | FALSE | FALSE | 0.0273 |  | 74.029 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.10353 | Normal | 74.2361 | 0.40945 | Night | 202512 | 2025-12-18 | 0.40945
2025-12-18 01:40 | 74.0714 | FALSE | FALSE | -0.20222 | -0.27376 | -0.1457 | -0.19632 | 0 |  |  | none | FALSE | 0 | 73.8692 | FALSE | FALSE | 0.0217 |  | 74.0431 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.086982 | Normal | 74.2171 | 0.32489 | Night | 202512 | 2025-12-18 | 0.32489
2025-12-18 01:55 | 74.0714 | FALSE | FALSE | -0.14051 | -0.19006 | -0.11225 | -0.15132 | 0 |  |  | none | FALSE | 0 | 73.9309 | FALSE | FALSE | 0.0149 |  | 74.0573 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.063191 | Normal | 74.1837 | 0.22361 | Night | 202512 | 2025-12-18 | 0.22361
2025-12-18 02:10 | 73.7888 | TRUE | FALSE | 0.14209 | 0.19219 | -0.39485 | -0.53226 | -0.2826 | 2025-12-18 02:25 | 2025-12-18 02:10 | lower | TRUE | 1 | 73.9309 | FALSE | FALSE | 0.3689 | 4.2485 | 74.0573 | 1 | -0.2826 | 0 | 0.091688 | -3.0822 | 0.063191 | Extreme triggered | 74.1837 | -4.2485 | Night | 202512 | 2025-12-18 | 4.2485
2025-12-18 02:25 | 74.0714 | TRUE | FALSE | -0.14051 | -0.19006 | -0.11225 | -0.15132 | 0.2826 |  |  | none | FALSE | 2 | 73.9309 | TRUE | FALSE | 0.072 |  | 74.0573 | 0 | 0.2826 | 0 | 0.091688 | 3.0822 | 0.063191 | Persistence ends | 74.1837 | 0.22361 | Night | 202512 | 2025-12-18 | 0.22361
2025-12-18 02:39 | 73.7888 | TRUE | FALSE | 0.080375 | 0.10881 | -0.4283 | -0.5771 | -0.2826 | 2025-12-18 04:39 | 2025-12-18 02:39 | lower | TRUE | 3 | 73.8692 | TRUE | FALSE | 0.3378 | 2.924 | 74.0431 | 1 | -0.2826 | -0.01413 | 0.11135 | -2.411 | 0.086982 | Extreme triggered | 74.2171 | -2.924 | Night | 202512 | 2025-12-18 | 2.924
2025-12-18 02:54 | 73.7888 | FALSE | FALSE | 0.03315 | 0.044906 | -0.44727 | -0.6025 | 0 |  | 2025-12-18 02:39 | lower | TRUE | 3 | 73.822 | FALSE | FALSE | 0.3547 | 2.6221 | 74.029 | 2 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.10353 | Extreme/elevated | 74.2361 | -2.3202 | Night | 202512 | 2025-12-18 | 2.3202
2025-12-18 03:10 | 73.7888 | FALSE | FALSE | -0.0058732 | -0.0079601 | -0.45803 | -0.61691 | 0 |  | 2025-12-18 02:39 | none | FALSE | 3 | 73.7829 | FALSE | FALSE | 0.3871 | 2.3979 | 74.0149 | 3 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.11598 | Persistent | 74.2468 | -1.9494 | Night | 202512 | 2025-12-18 | 1.9494
2025-12-18 03:25 | 73.7888 | FALSE | FALSE | -0.039147 | -0.053081 | -0.46305 | -0.62362 | 0 |  | 2025-12-18 02:39 | none | FALSE | 3 | 73.7497 | FALSE | FALSE | 0.4268 | 2.2204 | 74.0007 | 4 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.12555 | Persistent | 74.2518 | -1.6882 | Night | 202512 | 2025-12-18 | 1.6882
2025-12-18 03:39 | 73.7888 | FALSE | FALSE | -0.067916 | -0.092126 | -0.46356 | -0.6243 | 0 |  | 2025-12-18 02:39 | none | FALSE | 3 | 73.7209 | FALSE | FALSE | 0.4707 | 2.0741 | 73.9866 | 5 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13287 | Persistent | 74.2524 | -1.4888 | Night | 202512 | 2025-12-18 | 1.4888
2025-12-18 03:54 | 73.7888 | FALSE | FALSE | -0.092897 | -0.12605 | -0.46028 | -0.61991 | 0 |  | 2025-12-18 02:39 | none | FALSE | 3 | 73.6959 | FALSE | FALSE | 0.5171 | 1.9498 | 73.9725 | 6 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13829 | Persistent | 74.2491 | -1.3283 | Night | 202512 | 2025-12-18 | 1.3283
2025-12-18 04:09 | 73.7888 | FALSE | TRUE | -0.11452 | -0.15545 | -0.45364 | -0.61103 | 0 |  | 2025-12-18 02:39 | none | FALSE | 3 | 73.6743 | FALSE | FALSE | 0.5653 | 1.8418 | 73.9584 | 7 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14204 | Confirmed/Materialized Shift | 74.2424 | -1.1937 | Night | 202512 | 2025-12-18 | 1.1937
2025-12-18 04:24 | 73.7888 | FALSE | TRUE | -0.13306 | -0.18065 | -0.44392 | -0.59801 | 0 |  | 2025-12-18 02:39 | none | FALSE | 3 | 73.6557 | FALSE | FALSE | 0.5576 | 1.7463 | 73.9442 | 8 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14424 | Confirmed/Materialized Shift | 74.2327 | -1.0775 | Night | 202512 | 2025-12-18 | 1.0775
2025-12-18 04:39 | 73.7888 | FALSE | FALSE | -0.14864 | -0.20185 | -0.43124 | -0.58103 | 0 |  |  | none | FALSE | 2 | 73.6402 | FALSE | FALSE | 0.1221 |  | 73.9301 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14497 | Persistence ends | 74.22 | -0.97468 | Night | 202512 | 2025-12-18 | 0.97468
2025-12-18 04:54 | 73.7888 | FALSE | FALSE | -0.16132 | -0.2191 | -0.41566 | -0.56015 | 0 |  |  | none | FALSE | 1 | 73.6275 | FALSE | FALSE | 0.0873 |  | 73.916 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14424 | Normal | 74.2045 | -0.88163 | Night | 202512 | 2025-12-18 | 0.88163
2025-12-18 05:09 | 73.7888 | FALSE | FALSE | -0.17104 | -0.23234 | -0.39712 | -0.53531 | 0 |  |  | none | FALSE | 0 | 73.6178 | FALSE | FALSE | 0.0531 |  | 73.9018 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14204 | Normal | 74.1859 | -0.79582 | Night | 202512 | 2025-12-18 | 0.79582
2025-12-18 05:24 | 73.7888 | FALSE | FALSE | -0.17768 | -0.24137 | -0.3755 | -0.5063 | 0 |  |  | none | FALSE | 0 | 73.6111 | FALSE | FALSE | 0.0477 |  | 73.8877 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13829 | Normal | 74.1643 | -0.71522 | Night | 202512 | 2025-12-18 | 0.71522
2025-12-18 05:39 | 73.7888 | FALSE | FALSE | -0.18096 | -0.24584 | -0.35052 | -0.47278 | 0 |  |  | none | FALSE | 0 | 73.6078 | FALSE | FALSE | 0.0425 |  | 73.8736 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13287 | Normal | 74.1393 | -0.63808 | Night | 202512 | 2025-12-18 | 0.63808
2025-12-18 05:54 | 73.7888 | FALSE | FALSE | -0.18045 | -0.24514 | -0.32175 | -0.43414 | 0 |  |  | none | FALSE | 0 | 73.6084 | FALSE | FALSE | 0.0375 |  | 73.8594 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.12555 | Normal | 74.1105 | -0.56273 | Night | 202512 | 2025-12-18 | 0.56273
2025-12-18 06:09 | 73.7888 | FALSE | FALSE | -0.17543 | -0.23832 | -0.28847 | -0.38942 | 0 |  |  | none | FALSE | 0 | 73.6134 | FALSE | FALSE | 0.0325 |  | 73.8453 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.11598 | Normal | 74.0773 | -0.48734 | Night | 202512 | 2025-12-18 | 0.48734
2025-12-18 06:24 | 73.7888 | FALSE | FALSE | -0.16467 | -0.22366 | -0.24945 | -0.33692 | 0 |  |  | none | FALSE | 0 | 73.6241 | FALSE | FALSE | 0.0273 |  | 73.8312 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.10353 | Normal | 74.0382 | -0.40945 | Night | 202512 | 2025-12-18 | 0.40945
2025-12-18 06:38 | 73.7888 | FALSE | FALSE | -0.1457 | -0.19785 | -0.20222 | -0.27331 | 0 |  |  | none | FALSE | 0 | 73.6431 | FALSE | FALSE | 0.0217 |  | 73.8171 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.086982 | Normal | 73.991 | -0.32489 | Night | 202512 | 2025-12-18 | 0.32489
2025-12-18 06:53 | 73.7888 | FALSE | FALSE | -0.11225 | -0.15236 | -0.14051 | -0.19006 | 0 |  |  | none | FALSE | 0 | 73.6765 | FALSE | FALSE | 0.0149 |  | 73.8029 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.063191 | Normal | 73.9293 | -0.22361 | Night | 202512 | 2025-12-18 | 0.22361
2025-12-18 07:08 | 73.7888 | FALSE | FALSE | -0.11225 | -0.15236 | -0.14051 | -0.19006 | 0 |  |  | none | FALSE | 0 | 73.6765 | FALSE | FALSE | 0.0149 |  | 73.8029 | 0 | 0 | 0 | 0.091688 | 0 | 0.063191 | Normal | 73.9293 | -0.22361 | Day | 202512 | 2025-12-18 | 0.22361
2025-12-18 07:23 | 73.7888 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.7888 | FALSE | FALSE | 0 |  | 73.7888 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0 | Normal | 73.7888 |  | Day | 202512 | 2025-12-18
2025-12-18 07:30 | 73.7888 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.7888 | FALSE | FALSE | 0 |  | 73.7888 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.7888 |  | Day | 202512 | 2025-12-18
2025-12-18 07:45 | 73.7888 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.7888 | FALSE | FALSE | 0 |  | 73.7888 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.7888 |  | Day | 202512 | 2025-12-18
2025-12-18 08:00 | 73.7888 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.7888 | FALSE | FALSE | 0 |  | 73.7888 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.7888 |  | Day | 202512 | 2025-12-18
2025-12-18 08:15 | 73.7888 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.7888 | FALSE | FALSE | 0 |  | 73.7888 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.7888 |  | Day | 202512 | 2025-12-18
2025-12-18 08:30 | 73.7888 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.7888 | FALSE | FALSE | 0 |  | 73.7888 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.7888 |  | Day | 202512 | 2025-12-18
2025-12-18 08:30 | 73.7888 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.7888 | FALSE | FALSE | 0 |  | 73.7888 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.7888 |  | Day | 202512 | 2025-12-18
2025-12-18 08:31 | 74.0714 | TRUE | FALSE | -0.39485 | -0.53593 | 0.14209 | 0.19219 | 0.2826 | 2025-12-18 08:34 | 2025-12-18 08:31 | upper | TRUE | 1 | 73.6765 | FALSE | FALSE | 0.3689 | 4.2485 | 73.8029 | 1 | 0.2826 | 0.01413 | 0.063191 | 4.2485 | 0.063191 | Extreme triggered | 73.9293 | 4.2485 | Day | 202512 | 2025-12-18 | 4.2485
2025-12-18 08:34 | 73.7888 | TRUE | FALSE | -0.11225 | -0.15236 | -0.14051 | -0.19006 | -0.2826 |  |  | none | FALSE | 2 | 73.6765 | TRUE | FALSE | 0.072 |  | 73.8029 | 0 | -0.2826 | 0 | 0.091688 | -3.0822 | 0.063191 | Persistence ends | 73.9293 | -0.22361 | Day | 202512 | 2025-12-18 | 0.22361
2025-12-18 08:49 | 73.5062 | TRUE | FALSE | 0.099225 | 0.13481 | -0.46598 | -0.62993 | -0.2826 | 2025-12-18 10:44 | 2025-12-18 08:49 | lower | TRUE | 3 | 73.6054 | TRUE | FALSE | 0.3483 | 3.0822 | 73.7888 | 1 | -0.2826 | -0.01413 | 0.11135 | -2.411 | 0.091688 | Extreme triggered | 73.9722 | -3.0822 | Day | 202512 | 2025-12-18 | 3.0822
2025-12-18 09:04 | 73.2236 | TRUE | FALSE | 0.22466 | 0.30588 | -0.84922 | -1.1465 | -0.2826 |  | 2025-12-18 08:49 | lower | TRUE | 4 | 73.4483 | TRUE | FALSE | 0.4578 | 3.2605 | 73.7605 | 2 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.15614 | Extreme/elevated | 74.0728 | -3.4389 | Day | 202512 | 2025-12-18 | 3.4389
2025-12-18 09:19 | 72.6584 | TRUE | FALSE | 0.46284 | 0.63298 | -1.6284 | -2.192 | -0.5652 |  | 2025-12-18 08:49 | lower | TRUE | 5 | 73.1212 | TRUE | TRUE | 0.5535 | 3.3698 | 73.704 | 3 | -0.5652 | -0.05652 | 0.17396 | -2.924 | 0.29139 | Persistent | 74.2868 | -3.5884 | Day | 202512 | 2025-12-18 | 3.5884
2025-12-18 09:30 | 72.3758 | FALSE | FALSE | 0.42781 | 0.58762 | -2.0873 | -2.8032 | -0.2826 |  | 2025-12-18 08:49 | lower | TRUE | 5 | 72.8036 | FALSE | TRUE | 0.5735 | 3.2852 | 73.6334 | 4 | -0.2826 | -0.07065 | 0.18049 | -1.1743 | 0.41488 | Persistent | 74.4631 | -3.0312 | Day | 202512 | 2025-12-18 | 3.0312
2025-12-18 09:45 | 72.3758 | FALSE | FALSE | 0.18925 | 0.2608 | -2.1846 | -2.93 | 0 |  | 2025-12-18 08:49 | lower | TRUE | 5 | 72.5651 | FALSE | TRUE | 0.5872 | 3.104 | 73.5627 | 5 | 0 | -0.07065 | 0.18049 | 0.39144 | 0.49883 | Persistent | 74.5604 | -2.3794 | Day | 202512 | 2025-12-18 | 2.3794
2025-12-18 10:00 | 72.095 | FALSE | FALSE | 0.19648 | 0.27179 | -2.5696 | -3.4415 | -0.2808 |  | 2025-12-18 08:49 | lower | TRUE | 5 | 72.2915 | FALSE | TRUE | 0.6411 | 2.9752 | 73.478 | 6 | -0.2808 | -0.08469 | 0.18555 | -1.0569 | 0.59327 | Persistent | 74.6646 | -2.3312 | Day | 202512 | 2025-12-18 | 2.3312
2025-12-18 10:15 | 72.3758 | FALSE | TRUE | -0.24212 | -0.33566 | -2.3053 | -3.0868 | 0.2808 |  | 2025-12-18 08:49 | none | FALSE | 5 | 72.1337 | FALSE | FALSE | 0.6508 | 2.7816 | 73.4074 | 7 | 0.2808 | -0.07065 | 0.20218 | 1.7383 | 0.63685 | Confirmed/Materialized Shift | 74.6811 | -1.6198 | Day | 202512 | 2025-12-18 | 1.6198
2025-12-18 10:29 | 72.6584 | FALSE | TRUE | -0.60998 | -0.84662 | -1.9949 | -2.6722 | 0.2826 |  | 2025-12-18 08:49 | none | FALSE | 5 | 72.0484 | FALSE | FALSE | 0.6137 | 2.5668 | 73.3509 | 8 | 0.2826 | -0.05652 | 0.21673 | 1.5647 | 0.65122 | Confirmed/Materialized Shift | 74.6533 | -1.0633 | Day | 202512 | 2025-12-18 | 1.0633
2025-12-18 10:44 | 72.6584 | FALSE | FALSE | -0.68446 | -0.95099 | -1.9563 | -2.6219 | 0 |  |  | none | FALSE | 4 | 71.9739 | FALSE | FALSE | 0.1785 |  | 73.2943 | 0 | 0 | -0.05652 | 0.21673 | 0.26079 | 0.6602 | Persistence ends | 74.6147 | -0.96325 | Day | 202512 | 2025-12-18 | 0.96325
2025-12-18 10:59 | 72.3758 | FALSE | FALSE | -0.51174 | -0.7121 | -2.2075 | -2.9598 | -0.2826 |  |  | none | FALSE | 3 | 71.8641 | FALSE | FALSE | 0.1689 |  | 73.2237 | 0 | -0.2826 | -0.07065 | 0.222 | -0.95475 | 0.67982 | Normal | 74.5833 | -1.2472 | Day | 202512 | 2025-12-18 | 1.2472
2025-12-18 11:14 | 72.3758 | FALSE | FALSE | -0.6054 | -0.84353 | -2.1599 | -2.8978 | 0 |  |  | none | FALSE | 2 | 71.7704 | FALSE | FALSE | 0.1321 |  | 73.153 | 0 | 0 | -0.07065 | 0.222 | 0.31825 | 0.69132 | Normal | 74.5357 | -1.1243 | Day | 202512 | 2025-12-18 | 1.1243
2025-12-18 11:29 | 72.095 | FALSE | FALSE | -0.45216 | -0.63113 | -2.3989 | -3.2202 | -0.2808 |  |  | none | FALSE | 1 | 71.6428 | FALSE | FALSE | 0.1196 |  | 73.0683 | 0 | -0.2808 | -0.08469 | 0.22613 | -0.86723 | 0.71276 | Normal | 74.4939 | -1.3656 | Day | 202512 | 2025-12-18 | 1.3656
2025-12-18 11:44 | 72.095 | FALSE | FALSE | -0.55774 | -0.77964 | -2.3351 | -3.1372 | 0 |  |  | none | FALSE | 0 | 71.5373 | FALSE | FALSE | 0.0819 |  | 72.9837 | 0 | 0 | -0.08469 | 0.22613 | 0.37451 | 0.7232 | Normal | 74.4301 | -1.2288 | Day | 202512 | 2025-12-18 | 1.2288
2025-12-18 11:59 | 72.3758 | FALSE | FALSE | -0.88137 | -1.2328 | -1.9558 | -2.6312 | 0.2808 |  |  | none | FALSE | 0 | 71.4944 | FALSE | FALSE | 0.0505 |  | 72.913 | 0 | 0.2808 | -0.07065 | 0.23996 | 1.4646 | 0.70929 | Normal | 74.3316 | -0.75739 | Day | 202512 | 2025-12-18 | 0.75739
2025-12-18 12:14 | 72.3758 | FALSE | FALSE | -0.90844 | -1.2711 | -1.8416 | -2.4813 | 0 |  |  | none | FALSE | 0 | 71.4674 | FALSE | FALSE | 0.0452 |  | 72.8424 | 0 | 0 | -0.07065 | 0.23996 | 0.29442 | 0.6875 | Normal | 74.2174 | -0.67863 | Day | 202512 | 2025-12-18 | 0.67863
2025-12-18 12:29 | 72.3758 | FALSE | FALSE | -0.91819 | -1.2849 | -1.71 | -2.3081 | 0 |  |  | none | FALSE | 0 | 71.4576 | FALSE | FALSE | 0.0402 |  | 72.7717 | 0 | 0 | -0.07065 | 0.23996 | 0.29442 | 0.65705 | Normal | 74.0858 | -0.60256 | Day | 202512 | 2025-12-18 | 0.60256
2025-12-18 12:44 | 72.6584 | FALSE | FALSE | -1.1673 | -1.6328 | -1.2809 | -1.7323 | 0.2826 |  |  | none | FALSE | 0 | 71.4911 | FALSE | FALSE | 0.0062 |  | 72.7152 | 0 | 0.2826 | -0.05652 | 0.25234 | 1.3439 | 0.61203 | Normal | 73.9393 | -0.092789 | Day | 202512 | 2025-12-18 | 0.092789
2025-12-18 12:59 | 72.941 | FALSE | FALSE | -1.3902 | -1.9429 | -0.85378 | -1.157 | 0.2826 |  |  | none | FALSE | 0 | 71.5508 | FALSE | FALSE | 0.0319 |  | 72.6728 | 0 | 0.2826 | -0.04239 | 0.26335 | 1.2341 | 0.56099 | Normal | 73.7948 | 0.47808 | Day | 202512 | 2025-12-18 | 0.47808
2025-12-18 13:14 | 72.941 | FALSE | FALSE | -1.246 | -1.7379 | -0.59654 | -0.81121 | 0 |  |  | none | FALSE | 0 | 71.695 | FALSE | FALSE | 0.047 |  | 72.6163 | 0 | 0 | -0.05652 | 0.25234 | 0.22398 | 0.46063 | Normal | 73.5375 | 0.70495 | Day | 202512 | 2025-12-18 | 0.70495
2025-12-18 13:28 | 73.2236 | FALSE | FALSE | -1.4316 | -1.994 | -0.16039 | -0.21857 | 0.2826 |  |  | none | FALSE | 0 | 71.792 | FALSE | FALSE | 0.1065 |  | 72.588 | 0 | 0.2826 | -0.02826 | 0.25729 | 1.2082 | 0.39799 | Normal | 73.384 | 1.597 | Day | 202512 | 2025-12-18 | 1.597
2025-12-18 13:44 | 73.2236 | FALSE | FALSE | -1.3848 | -1.9276 | -0.085338 | -0.11641 | 0 |  |  | none | FALSE | 0 | 71.8388 | FALSE | FALSE | 0.1179 |  | 72.5739 | 0 | 0 | -0.01413 | 0.25025 | 0.056463 | 0.36752 | Normal | 73.3089 | 1.7678 | Day | 202512 | 2025-12-18 | 1.7678
2025-12-18 13:59 | 73.2236 | FALSE | FALSE | -1.3848 | -1.9276 | -0.085338 | -0.11641 | 0 |  |  | none | FALSE | 0 | 71.8388 | FALSE | FALSE | 0.1179 |  | 72.5739 | 0 | 0 | 0 | 0.24214 | 0 | 0.36752 | Normal | 73.3089 | 1.7678 | Day | 202512 | 2025-12-18 | 1.7678
2025-12-18 14:14 | 73.5062 | FALSE | FALSE | -1.735 | -2.4175 | 0.044807 | 0.060995 | 0.2826 | 2025-12-18 15:28 | 2025-12-18 14:14 | upper | TRUE | 0 | 71.7712 | FALSE | FALSE | 0.1975 | 2.106 | 72.6163 | 1 | 0.2826 | 0.04239 | 0.21007 | 1.1435 | 0.42256 | Extreme triggered | 73.4614 | 2.106 | Day | 202512 | 2025-12-18 | 2.106
2025-12-18 14:28 | 73.2236 | FALSE | FALSE | -1.4436 | -2.0112 | -0.31378 | -0.42669 | -0.2826 |  | 2025-12-18 14:14 | none | FALSE | 0 | 71.78 | FALSE | FALSE | 0.2 | 1.6959 | 72.6587 | 2 | -0.2826 | 0.04239 | 0.21007 | -1.547 | 0.43935 | Extreme/elevated | 73.5374 | 1.2858 | Day | 202512 | 2025-12-18 | 1.2858
2025-12-18 14:43 | 73.2236 | FALSE | FALSE | -1.4253 | -1.9851 | -0.38018 | -0.51652 | 0 |  | 2025-12-18 14:14 | none | FALSE | 0 | 71.7983 | FALSE | FALSE | 0.2486 | 1.5165 | 72.7011 | 3 | 0 | 0.04239 | 0.21007 | -0.20179 | 0.45136 | Persistent | 73.6038 | 1.1577 | Day | 202512 | 2025-12-18 | 1.1577
2025-12-18 14:58 | 73.2236 | FALSE | FALSE | -1.3502 | -1.8786 | -0.418 | -0.56761 | 0 |  | 2025-12-18 14:14 | none | FALSE | 0 | 71.8734 | FALSE | FALSE | 0.2989 | 1.401 | 72.7575 | 4 | 0 | 0.05643 | 0.19627 | -0.28752 | 0.44205 | Persistent | 73.6416 | 1.0544 | Day | 202512 | 2025-12-18 | 1.0544
2025-12-18 15:13 | 73.5062 | FALSE | FALSE | -1.6171 | -2.2495 | -0.23277 | -0.31566 | 0.2826 |  | 2025-12-18 14:14 | none | FALSE | 0 | 71.8891 | FALSE | FALSE | 0.3855 | 1.4201 | 72.814 | 5 | 0.2826 | 0.05652 | 0.19638 | 1.1513 | 0.46248 | Persistent | 73.739 | 1.4967 | Day | 202512 | 2025-12-18 | 1.4967
2025-12-18 15:28 | 73.2236 | FALSE | FALSE | -1.3207 | -1.8368 | -0.55803 | -0.75633 | -0.2826 |  |  | none | FALSE | 0 | 71.9029 | FALSE | FALSE | 0.0541 |  | 72.8423 | 0 | -0.2826 | 0.02826 | 0.2027 | -1.5336 | 0.46968 | Persistence ends | 73.7816 | 0.81189 | Day | 202512 | 2025-12-18 | 0.81189
2025-12-18 15:43 | 73.2236 | FALSE | FALSE | -1.3031 | -1.8118 | -0.59695 | -0.80865 | 0 |  |  | none | FALSE | 0 | 71.9205 | FALSE | FALSE | 0.0496 |  | 72.8705 | 0 | 0 | 0.02826 | 0.2027 | -0.13942 | 0.47501 | Normal | 73.8205 | 0.74329 | Day | 202512 | 2025-12-18 | 0.74329
2025-12-18 15:58 | 73.2236 | FALSE | FALSE | -1.2432 | -1.7272 | -0.62189 | -0.84215 | 0 |  |  | none | FALSE | 0 | 71.9804 | FALSE | FALSE | 0.0444 |  | 72.9129 | 0 | 0 | 0.04239 | 0.18929 | -0.22394 | 0.46628 | Normal | 73.8455 | 0.66629 | Day | 202512 | 2025-12-18 | 0.66629
2025-12-18 16:13 | 73.2236 | FALSE | FALSE | -1.1748 | -1.6305 | -0.63819 | -0.86403 | 0 |  |  | none | FALSE | 0 | 72.0488 | FALSE | FALSE | 0.0395 |  | 72.9553 | 0 | 0 | 0.04239 | 0.18929 | -0.22394 | 0.45324 | Normal | 73.8618 | 0.59194 | Day | 202512 | 2025-12-18 | 0.59194
2025-12-18 16:28 | 73.2236 | FALSE | FALSE | -1.0289 | -1.4252 | -0.60523 | -0.81977 | 0 |  |  | none | FALSE | 0 | 72.1947 | FALSE | FALSE | 0.0346 |  | 73.0117 | 0 | 0 | 0.05643 | 0.17384 | -0.3246 | 0.40854 | Normal | 73.8288 | 0.51857 | Day | 202512 | 2025-12-18 | 0.51857
2025-12-18 16:43 | 73.2236 | FALSE | FALSE | -0.8531 | -1.1788 | -0.54224 | -0.73508 | 0 |  |  | none | FALSE | 0 | 72.3705 | FALSE | FALSE | 0.0297 |  | 73.0682 | 0 | 0 | 0.05643 | 0.17384 | -0.3246 | 0.34883 | Normal | 73.7658 | 0.44557 | Day | 202512 | 2025-12-18 | 0.44557
2025-12-18 16:58 | 73.2236 | FALSE | FALSE | -0.73219 | -1.01 | -0.50611 | -0.68643 | 0 |  |  | none | FALSE | 0 | 72.4914 | FALSE | FALSE | 0.0243 |  | 73.1106 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.30957 | Normal | 73.7297 | 0.36515 | Day | 202512 | 2025-12-18 | 0.36515
2025-12-18 17:13 | 72.941 | FALSE | FALSE | -0.32407 | -0.44628 | -0.71971 | -0.97707 | -0.2826 |  |  | none | FALSE | 0 | 72.6169 | FALSE | FALSE | 0.0505 |  | 73.1388 | 0 | -0.2826 | 0.02826 | 0.18107 | -1.7168 | 0.26095 | Normal | 73.6607 | -0.75808 | Day | 202512 | 2025-12-18 | 0.75808
2025-12-18 17:27 | 72.941 | FALSE | FALSE | -0.16722 | -0.22977 | -0.61938 | -0.842 | 0 |  |  | none | FALSE | 0 | 72.7738 | FALSE | FALSE | 0.0766 |  | 73.1671 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.19665 | Normal | 73.5604 | -1.1497 | Day | 202512 | 2025-12-18 | 1.1497
2025-12-18 17:42 | 72.6584 | FALSE | FALSE | 0.11538 | 0.15855 | -0.90198 | -1.2262 | -0.2826 | 2025-12-18 18:46 | 2025-12-18 17:42 | lower | TRUE | 0 | 72.7738 | FALSE | FALSE | 0.2296 | 2.5868 | 73.1671 | 1 | -0.2826 | 0 | 0.18338 | -1.5411 | 0.19665 | Extreme triggered | 73.5604 | -2.5868 | Night | 202512 | 2025-12-18 | 2.5868
2025-12-18 17:57 | 72.6584 | FALSE | FALSE | 0.050078 | 0.068875 | -0.93902 | -1.2759 | 0 |  | 2025-12-18 17:42 | lower | TRUE | 0 | 72.7085 | FALSE | FALSE | 0.2626 | 2.406 | 73.153 | 2 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.22224 | Extreme/elevated | 73.5974 | -2.2253 | Night | 202512 | 2025-12-18 | 2.2253
2025-12-18 18:12 | 72.6584 | FALSE | FALSE | -0.0081981 | -0.011284 | -0.96904 | -1.3161 | 0 |  | 2025-12-18 17:42 | none | FALSE | 0 | 72.6502 | FALSE | FALSE | 0.3025 | 2.2595 | 73.1388 | 3 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.24431 | Persistent | 73.6274 | -1.9664 | Night | 202512 | 2025-12-18 | 1.9664
2025-12-18 18:27 | 72.3758 | FALSE | FALSE | 0.12713 | 0.17535 | -1.3141 | -1.7833 | -0.2826 |  | 2025-12-18 17:42 | lower | TRUE | 0 | 72.5029 | FALSE | TRUE | 0.3905 | 2.3017 | 73.0964 | 4 | -0.2826 | -0.04239 | 0.16593 | -1.4477 | 0.29675 | Persistent | 73.6899 | -2.4284 | Night | 202512 | 2025-12-18 | 2.4284
2025-12-18 18:30 | 72.6584 | FALSE | FALSE | -0.21141 | -0.29181 | -1.0309 | -1.399 | 0.2826 |  | 2025-12-18 17:42 | none | FALSE | 0 | 72.447 | FALSE | FALSE | 0.3737 | 2.1053 | 73.0682 | 5 | 0.2826 | -0.02826 | 0.18107 | 1.7168 | 0.31059 | Persistent | 73.6893 | -1.3193 | Night | 202512 | 2025-12-18 | 1.3193
2025-12-18 18:31 | 72.3758 | FALSE | FALSE | -0.038593 | -0.053351 | -1.3386 | -1.8159 | -0.2826 |  | 2025-12-18 17:42 | none | FALSE | 0 | 72.3372 | FALSE | FALSE | 0.4687 | 2.069 | 73.0258 | 6 | -0.2826 | -0.04239 | 0.18957 | -1.2671 | 0.34429 | Persistent | 73.7144 | -1.8879 | Night | 202512 | 2025-12-18 | 1.8879
2025-12-18 18:46 | 72.941 | TRUE | FALSE | -0.5944 | -0.8216 | -0.70744 | -0.96056 | 0.5652 |  |  | none | FALSE | 1 | 72.3466 | FALSE | FALSE | 0.0401 |  | 72.9975 | 0 | 0.5652 | -0.02826 | 0.22271 | 2.6647 | 0.32546 | Persistence ends | 73.6484 | -0.17366 | Night | 202512 | 2025-12-18 | 0.17366
2025-12-18 19:01 | 73.2236 | FALSE | FALSE | -0.877 | -1.2122 | -0.42484 | -0.57684 | 0.2826 |  |  | none | FALSE | 1 | 72.3466 | FALSE | FALSE | 0.0749 |  | 72.9975 | 0 | 0.2826 | 0 | 0.22459 | 1.2583 | 0.32546 | Normal | 73.6484 | 0.69465 | Night | 202512 | 2025-12-18 | 0.69465
2025-12-18 19:16 | 73.5062 | FALSE | FALSE | -1.1776 | -1.6281 | -0.18851 | -0.25579 | 0.2826 |  |  | none | FALSE | 1 | 72.3286 | FALSE | FALSE | 0.1251 |  | 73.0117 | 0 | 0.2826 | 0.01413 | 0.23331 | 1.1507 | 0.34153 | Normal | 73.6947 | 1.448 | Night | 202512 | 2025-12-18 | 1.448
2025-12-18 19:30 | 73.5062 | FALSE | FALSE | -1.193 | -1.6498 | -0.23215 | -0.31483 | 0 |  |  | none | FALSE | 1 | 72.3132 | FALSE | FALSE | 0.1185 |  | 73.0258 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.35629 | Normal | 73.7384 | 1.3484 | Night | 202512 | 2025-12-18 | 1.3484
2025-12-18 19:45 | 73.5062 | FALSE | FALSE | -1.193 | -1.6498 | -0.23215 | -0.31483 | 0 |  |  | none | FALSE | 1 | 72.3132 | FALSE | FALSE | 0.1185 |  | 73.0258 | 0 | 0 | 0 | 0.22459 | 0 | 0.35629 | Normal | 73.7384 | 1.3484 | Night | 202512 | 2025-12-18 | 1.3484
2025-12-18 20:00 | 73.7888 | FALSE | FALSE | -1.5214 | -2.1052 | -0.051832 | -0.070194 | 0.2826 |  |  | none | FALSE | 1 | 72.2674 | FALSE | FALSE | 0.1531 |  | 73.054 | 0 | 0.2826 | 0.02826 | 0.22271 | 1.142 | 0.3933 | Normal | 73.8406 | 1.8682 | Night | 202512 | 2025-12-18 | 1.8682
2025-12-18 20:15 | 73.7888 | FALSE | FALSE | -1.5568 | -2.1552 | -0.14378 | -0.19447 | 0 |  |  | none | FALSE | 1 | 72.232 | FALSE | FALSE | 0.1394 |  | 73.0823 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.42514 | Normal | 73.9326 | 1.6618 | Night | 202512 | 2025-12-18 | 1.6618
2025-12-18 20:29 | 73.7888 | FALSE | FALSE | -1.584 | -2.1938 | -0.22757 | -0.30745 | 0 |  |  | none | FALSE | 1 | 72.2048 | FALSE | FALSE | 0.1284 |  | 73.1106 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.4529 | Normal | 74.0164 | 1.4975 | Night | 202512 | 2025-12-18 | 1.4975
2025-12-18 20:44 | 73.7888 | FALSE | FALSE | -1.6046 | -2.2229 | -0.30463 | -0.41114 | 0 |  |  | none | FALSE | 1 | 72.1842 | FALSE | FALSE | 0.1194 |  | 73.1388 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.4773 | Normal | 74.0934 | 1.3618 | Night | 202512 | 2025-12-18 | 1.3618
2025-12-18 20:59 | 73.7888 | FALSE | FALSE | -1.6194 | -2.2439 | -0.37595 | -0.50691 | 0 |  |  | none | FALSE | 1 | 72.1694 | FALSE | FALSE | 0.1117 |  | 73.1671 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.49883 | Normal | 74.1647 | 1.2463 | Night | 202512 | 2025-12-18 | 1.2463
2025-12-18 21:14 | 74.0714 | FALSE | FALSE | -1.9386 | -2.6876 | -0.21476 | -0.2891 | 0.2826 |  |  | none | FALSE | 0 | 72.1328 | FALSE | FALSE | 0.1067 |  | 73.2095 | 0 | 0.2826 | 0.04239 | 0.22968 | 1.0459 | 0.53835 | Normal | 74.2862 | 1.6011 | Night | 202512 | 2025-12-18 | 1.6011
2025-12-18 21:29 | 74.0714 | FALSE | FALSE | -1.9632 | -2.7226 | -0.32417 | -0.43574 | 0 |  |  | none | FALSE | 0 | 72.1082 | FALSE | FALSE | 0.0955 |  | 73.2519 | 0 | 0 | 0.04239 | 0.22968 | -0.18456 | 0.57185 | Normal | 74.3956 | 1.4331 | Night | 202512 | 2025-12-18 | 1.4331
2025-12-18 21:44 | 74.0714 | FALSE | FALSE | -1.9528 | -2.7078 | -0.4268 | -0.5729 | 0 |  |  | none | FALSE | 0 | 72.1186 | FALSE | FALSE | 0.0855 |  | 73.3084 | 0 | 0 | 0.05652 | 0.21697 | -0.26049 | 0.59491 | Normal | 74.4982 | 1.2826 | Night | 202512 | 2025-12-18 | 1.2826
2025-12-18 21:59 | 74.0714 | FALSE | FALSE | -1.9298 | -2.675 | -0.51676 | -0.69282 | 0 |  |  | none | FALSE | 0 | 72.1416 | FALSE | FALSE | 0.077 |  | 73.3649 | 0 | 0 | 0.05652 | 0.21697 | -0.26049 | 0.61163 | Normal | 74.5882 | 1.1551 | Night | 202512 | 2025-12-18 | 1.1551
2025-12-18 22:14 | 74.0714 | FALSE | FALSE | -1.8505 | -2.5623 | -0.57879 | -0.77534 | 0 |  |  | none | FALSE | 0 | 72.2209 | FALSE | FALSE | 0.0698 |  | 73.4356 | 0 | 0 | 0.07065 | 0.20244 | -0.34899 | 0.60732 | Normal | 74.6502 | 1.047 | Night | 202512 | 2025-12-18 | 1.047
2025-12-18 22:29 | 74.3522 | FALSE | FALSE | -2.0546 | -2.8419 | -0.3907 | -0.52273 | 0.2808 |  |  | none | FALSE | 0 | 72.2976 | FALSE | FALSE | 0.0907 |  | 73.5202 | 0 | 0.2808 | 0.08469 | 0.20697 | 0.94753 | 0.61133 | Normal | 74.7429 | 1.3609 | Night | 202512 | 2025-12-18 | 1.3609
2025-12-18 22:44 | 74.3522 | FALSE | FALSE | -1.9531 | -2.6977 | -0.45857 | -0.61297 | 0 |  |  | none | FALSE | 0 | 72.3991 | FALSE | FALSE | 0.0826 |  | 73.6049 | 0 | 0 | 0.08469 | 0.20697 | -0.40919 | 0.60292 | Normal | 74.8108 | 1.2394 | Night | 202512 | 2025-12-18 | 1.2394
2025-12-18 22:59 | 74.3522 | FALSE | FALSE | -1.7496 | -2.4098 | -0.45266 | -0.60512 | 0 |  |  | none | FALSE | 0 | 72.6026 | FALSE | FALSE | 0.0785 |  | 73.7037 | 0 | 0 | 0.09882 | 0.18948 | -0.52153 | 0.55055 | Normal | 74.8049 | 1.1778 | Night | 202512 | 2025-12-18 | 1.1778
2025-12-18 23:14 | 74.3522 | FALSE | FALSE | -1.5839 | -2.1766 | -0.45639 | -0.61008 | 0 |  |  | none | FALSE | 0 | 72.7683 | FALSE | FALSE | 0.0737 |  | 73.7884 | 0 | 0 | 0.08469 | 0.18555 | -0.45642 | 0.51008 | Normal | 74.8086 | 1.1052 | Night | 202512 | 2025-12-18 | 1.1052
2025-12-18 23:28 | 74.6348 | FALSE | FALSE | -1.5806 | -2.1636 | -0.11375 | -0.15218 | 0.2826 |  |  | none | FALSE | 0 | 73.0542 | FALSE | FALSE | 0.1154 |  | 73.9014 | 0 | 0.2826 | 0.11295 | 0.16897 | 1.004 | 0.42358 | Normal | 74.7486 | 1.7315 | Night | 202512 | 2025-12-18 | 1.7315
2025-12-18 23:43 | 74.6348 | FALSE | FALSE | -1.4275 | -1.95 | -0.13009 | -0.174 | 0 |  |  | none | FALSE | 0 | 73.2073 | FALSE | FALSE | 0.1111 |  | 73.9861 | 0 | 0 | 0.08469 | 0.13273 | -0.63807 | 0.3894 | Normal | 74.7649 | 1.6659 | Night | 202512 | 2025-12-18 | 1.6659
2025-12-18 23:59 | 74.6348 | FALSE | FALSE | -1.321 | -1.8018 | -0.16466 | -0.22014 | 0 |  |  | none | FALSE | 0 | 73.3138 | FALSE | FALSE | 0.1038 |  | 74.0566 | 0 | 0 | 0.07056 | 0.12539 | -0.56273 | 0.37141 | Normal | 74.7995 | 1.5567 | Night | 202512 | 2025-12-18 | 1.5567
2025-12-19 00:14 | 74.6348 | FALSE | FALSE | -1.2599 | -1.7171 | -0.21648 | -0.28922 | 0 |  |  | none | FALSE | 0 | 73.3749 | FALSE | FALSE | 0.0942 |  | 74.1131 | 0 | 0 | 0.05643 | 0.11579 | -0.48734 | 0.36911 | Normal | 74.8513 | 1.4135 | Night | 202512 | 2025-12-19 | 1.4135
2025-12-19 00:28 | 74.6348 | FALSE | FALSE | -1.1804 | -1.6069 | -0.24977 | -0.33354 | 0 |  |  | none | FALSE | 0 | 73.4544 | FALSE | FALSE | 0.0868 |  | 74.1695 | 0 | 0 | 0.05643 | 0.11579 | -0.48734 | 0.35753 | Normal | 74.8846 | 1.3014 | Night | 202512 | 2025-12-19 | 1.3014
2025-12-19 00:43 | 74.6348 | FALSE | FALSE | -1.0803 | -1.4688 | -0.2626 | -0.35061 | 0 |  |  | none | FALSE | 0 | 73.5545 | FALSE | FALSE | 0.0812 |  | 74.2259 | 0 | 0 | 0.05643 | 0.11579 | -0.48734 | 0.33573 | Normal | 74.8974 | 1.2178 | Night | 202512 | 2025-12-19 | 1.2178
2025-12-19 00:58 | 74.6348 | FALSE | FALSE | -1.0286 | -1.3975 | -0.29547 | -0.39433 | 0 |  |  | none | FALSE | 0 | 73.6062 | FALSE | FALSE | 0.0738 |  | 74.2682 | 0 | 0 | 0.0423 | 0.10331 | -0.40945 | 0.33102 | Normal | 74.9303 | 1.1074 | Night | 202512 | 2025-12-19 | 1.1074
2025-12-19 01:13 | 74.6348 | FALSE | FALSE | -0.9651 | -1.31 | -0.31656 | -0.42236 | 0 |  |  | none | FALSE | 0 | 73.6697 | FALSE | FALSE | 0.0675 |  | 74.3105 | 0 | 0 | 0.0423 | 0.10331 | -0.40945 | 0.32042 | Normal | 74.9514 | 1.012 | Night | 202512 | 2025-12-19 | 1.012
2025-12-19 01:28 | 74.6348 | FALSE | FALSE | -0.88857 | -1.2049 | -0.32463 | -0.43308 | 0 |  |  | none | FALSE | 0 | 73.7462 | FALSE | FALSE | 0.062 |  | 74.3528 | 0 | 0 | 0.0423 | 0.10331 | -0.40945 | 0.3033 | Normal | 74.9594 | 0.92967 | Night | 202512 | 2025-12-19 | 0.92967
2025-12-19 01:43 | 74.6348 | FALSE | FALSE | -0.79662 | -1.0789 | -0.31728 | -0.42331 | 0 |  |  | none | FALSE | 0 | 73.8382 | FALSE | FALSE | 0.0574 |  | 74.3951 | 0 | 0 | 0.0423 | 0.10331 | -0.40945 | 0.27848 | Normal | 74.9521 | 0.86065 | Night | 202512 | 2025-12-19 | 0.86065
2025-12-19 01:58 | 74.6348 | FALSE | FALSE | -0.68456 | -0.92571 | -0.28982 | -0.38682 | 0 |  |  | none | FALSE | 0 | 73.9502 | FALSE | FALSE | 0.054 |  | 74.4374 | 0 | 0 | 0.0423 | 0.10331 | -0.40945 | 0.2436 | Normal | 74.9246 | 0.81023 | Night | 202512 | 2025-12-19 | 0.81023
2025-12-19 02:13 | 74.6348 | FALSE | FALSE | -0.63181 | -0.85377 | -0.29341 | -0.39159 | 0 |  |  | none | FALSE | 0 | 74.003 | FALSE | FALSE | 0.0488 |  | 74.4656 | 0 | 0 | 0.02817 | 0.086706 | -0.32489 | 0.23131 | Normal | 74.9282 | 0.7315 | Night | 202512 | 2025-12-19 | 0.7315
2025-12-19 02:28 | 74.6348 | FALSE | FALSE | -0.56996 | -0.76955 | -0.2879 | -0.38427 | 0 |  |  | none | FALSE | 0 | 74.0648 | FALSE | FALSE | 0.0438 |  | 74.4938 | 0 | 0 | 0.02817 | 0.086706 | -0.32489 | 0.21447 | Normal | 74.9227 | 0.65759 | Night | 202512 | 2025-12-19 | 0.65759
2025-12-19 02:43 | 74.6348 | FALSE | FALSE | -0.49662 | -0.66986 | -0.2709 | -0.36166 | 0 |  |  | none | FALSE | 0 | 74.1382 | FALSE | FALSE | 0.0392 |  | 74.5219 | 0 | 0 | 0.02817 | 0.086706 | -0.32489 | 0.19188 | Normal | 74.9057 | 0.58818 | Night | 202512 | 2025-12-19 | 0.58818
2025-12-19 02:58 | 74.6348 | FALSE | FALSE | -0.40699 | -0.5483 | -0.23761 | -0.31736 | 0 |  |  | none | FALSE | 0 | 74.2278 | FALSE | FALSE | 0.035 |  | 74.5501 | 0 | 0 | 0.02817 | 0.086706 | -0.32489 | 0.16115 | Normal | 74.8724 | 0.52553 | Night | 202512 | 2025-12-19 | 0.52553
2025-12-19 03:13 | 74.6348 | FALSE | FALSE | -0.28847 | -0.38801 | -0.17543 | -0.2345 | 0 |  |  | none | FALSE | 0 | 74.3463 | FALSE | FALSE | 0.0325 |  | 74.5783 | 0 | 0 | 0.02817 | 0.086706 | -0.32489 | 0.11598 | Normal | 74.8102 | 0.48734 | Night | 202512 | 2025-12-19 | 0.48734
2025-12-19 03:27 | 74.6348 | FALSE | FALSE | -0.24945 | -0.33535 | -0.16467 | -0.22015 | 0 |  |  | none | FALSE | 0 | 74.3854 | FALSE | FALSE | 0.0273 |  | 74.5924 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.10353 | Normal | 74.7995 | 0.40945 | Night | 202512 | 2025-12-19 | 0.40945
2025-12-19 03:42 | 74.6348 | FALSE | FALSE | -0.20222 | -0.27169 | -0.1457 | -0.19484 | 0 |  |  | none | FALSE | 0 | 74.4326 | FALSE | FALSE | 0.0217 |  | 74.6065 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.086982 | Normal | 74.7805 | 0.32489 | Night | 202512 | 2025-12-19 | 0.32489
2025-12-19 03:57 | 74.6348 | FALSE | FALSE | -0.14051 | -0.18862 | -0.11225 | -0.15018 | 0 |  |  | none | FALSE | 0 | 74.4943 | FALSE | FALSE | 0.0149 |  | 74.6207 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.063191 | Normal | 74.7471 | 0.22361 | Night | 202512 | 2025-12-19 | 0.22361
2025-12-19 04:12 | 74.6348 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.6348 | FALSE | FALSE | 0 |  | 74.6348 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0 | Normal | 74.6348 |  | Night | 202512 | 2025-12-19
2025-12-19 04:27 | 74.6348 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.6348 | FALSE | FALSE | 0 |  | 74.6348 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.6348 |  | Night | 202512 | 2025-12-19
2025-12-19 04:42 | 74.6348 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.6348 | FALSE | FALSE | 0 |  | 74.6348 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.6348 |  | Night | 202512 | 2025-12-19
2025-12-19 04:57 | 74.6348 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.6348 | FALSE | FALSE | 0 |  | 74.6348 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.6348 |  | Night | 202512 | 2025-12-19
2025-12-19 05:12 | 74.6348 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.6348 | FALSE | FALSE | 0 |  | 74.6348 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.6348 |  | Night | 202512 | 2025-12-19
2025-12-19 05:27 | 74.6348 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.6348 | FALSE | FALSE | 0 |  | 74.6348 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.6348 |  | Night | 202512 | 2025-12-19
2025-12-19 05:42 | 74.6348 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.6348 | FALSE | FALSE | 0 |  | 74.6348 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.6348 |  | Night | 202512 | 2025-12-19
2025-12-19 05:57 | 74.6348 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.6348 | FALSE | FALSE | 0 |  | 74.6348 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.6348 |  | Night | 202512 | 2025-12-19
2025-12-19 06:12 | 74.6348 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.6348 | FALSE | FALSE | 0 |  | 74.6348 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.6348 |  | Night | 202512 | 2025-12-19
2025-12-19 06:26 | 74.6348 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.6348 | FALSE | FALSE | 0 |  | 74.6348 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.6348 |  | Night | 202512 | 2025-12-19
2025-12-19 06:41 | 74.6348 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.6348 | FALSE | FALSE | 0 |  | 74.6348 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.6348 |  | Night | 202512 | 2025-12-19
2025-12-19 06:56 | 74.6348 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.6348 | FALSE | FALSE | 0 |  | 74.6348 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.6348 |  | Night | 202512 | 2025-12-19
2025-12-19 07:11 | 74.3522 | TRUE | FALSE | 0.14209 | 0.19074 | -0.39485 | -0.52825 | -0.2826 | 2025-12-19 07:26 | 2025-12-19 07:11 | lower | TRUE | 1 | 74.4943 | FALSE | FALSE | 0.3689 | 4.2485 | 74.6207 | 1 | -0.2826 | -0.01413 | 0.063191 | -4.2485 | 0.063191 | Extreme triggered | 74.7471 | -4.2485 | Day | 202512 | 2025-12-19 | 4.2485
2025-12-19 07:26 | 74.6348 | TRUE | FALSE | -0.14051 | -0.18862 | -0.11225 | -0.15018 | 0.2826 |  |  | none | FALSE | 2 | 74.4943 | TRUE | FALSE | 0.072 |  | 74.6207 | 0 | 0.2826 | 0 | 0.091688 | 3.0822 | 0.063191 | Persistence ends | 74.7471 | 0.22361 | Day | 202512 | 2025-12-19 | 0.22361
2025-12-19 07:30 | 74.6348 | FALSE | FALSE | -0.14051 | -0.18862 | -0.11225 | -0.15018 | 0 |  |  | none | FALSE | 2 | 74.4943 | FALSE | FALSE | 0.072 |  | 74.6207 | 0 | 0 | 0 | 0.091688 | 0 | 0.063191 | Normal | 74.7471 | 0.22361 | Day | 202512 | 2025-12-19 | 0.22361
2025-12-19 07:45 | 74.6348 | FALSE | FALSE | -0.14051 | -0.18862 | -0.11225 | -0.15018 | 0 |  |  | none | FALSE | 2 | 74.4943 | FALSE | FALSE | 0.072 |  | 74.6207 | 0 | 0 | 0 | 0.091688 | 0 | 0.063191 | Normal | 74.7471 | 0.22361 | Day | 202512 | 2025-12-19 | 0.22361
2025-12-19 08:00 | 74.3522 | TRUE | FALSE | 0.080375 | 0.10798 | -0.4283 | -0.57275 | -0.2826 | 2025-12-19 08:30 | 2025-12-19 08:00 | lower | TRUE | 3 | 74.4326 | TRUE | FALSE | 0.3378 | 2.924 | 74.6065 | 1 | -0.2826 | -0.01413 | 0.11135 | -2.411 | 0.086982 | Extreme triggered | 74.7805 | -2.924 | Day | 202512 | 2025-12-19 | 2.924
2025-12-19 08:16 | 74.3522 | FALSE | FALSE | 0.03315 | 0.044566 | -0.44727 | -0.59796 | 0 |  | 2025-12-19 08:00 | lower | TRUE | 3 | 74.3854 | FALSE | FALSE | 0.3547 | 2.6221 | 74.5924 | 2 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.10353 | Extreme/elevated | 74.7995 | -2.3202 | Day | 202512 | 2025-12-19 | 2.3202
2025-12-19 08:30 | 74.3522 | FALSE | FALSE | -0.0058732 | -0.0078998 | -0.45803 | -0.61226 | 0 |  | 2025-12-19 08:00 | none | FALSE | 3 | 74.3463 | FALSE | FALSE | 0.3871 | 2.3979 | 74.5783 | 3 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.11598 | Persistent | 74.8102 | -1.9494 | Day | 202512 | 2025-12-19 | 1.9494
2025-12-19 08:30 | 74.6348 | TRUE | FALSE | -0.28847 | -0.38801 | -0.17543 | -0.2345 | 0.2826 |  |  | none | FALSE | 4 | 74.3463 | TRUE | FALSE | 0.1468 |  | 74.5783 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.11598 | Persistence ends | 74.8102 | 0.48734 | Day | 202512 | 2025-12-19 | 0.48734
2025-12-19 08:33 | 74.3522 | FALSE | FALSE | -0.039147 | -0.052678 | -0.46305 | -0.61892 | -0.2826 |  |  | none | FALSE | 4 | 74.3131 | FALSE | FALSE | 0.2268 |  | 74.5641 | 0 | -0.2826 | -0.01413 | 0.14424 | -1.8612 | 0.12555 | Normal | 74.8152 | -1.6882 | Day | 202512 | 2025-12-19 | 1.6882
2025-12-19 08:48 | 74.0714 | FALSE | FALSE | 0.13326 | 0.17958 | -0.7959 | -1.0631 | -0.2808 | 2025-12-19 10:44 | 2025-12-19 08:48 | lower | TRUE | 4 | 74.2047 | FALSE | FALSE | 0.3584 | 2.8044 | 74.536 | 1 | -0.2808 | -0.02817 | 0.15598 | -1.6196 | 0.16566 | Extreme triggered | 74.8673 | -2.8044 | Day | 202512 | 2025-12-19 | 2.8044
2025-12-19 09:02 | 72.941 | TRUE | FALSE | 0.72729 | 0.98725 | -2.2933 | -3.0482 | -1.1304 |  | 2025-12-19 08:48 | lower | TRUE | 4 | 73.6683 | TRUE | FALSE | 0.4858 | 3.3311 | 74.4513 | 2 | -1.1304 | -0.08469 | 0.29132 | -3.5895 | 0.3915 | Extreme/elevated | 75.2343 | -3.8577 | Day | 202512 | 2025-12-19 | 3.8577
2025-12-19 09:17 | 72.095 | TRUE | FALSE | 0.92279 | 1.2638 | -3.5358 | -4.6751 | -0.846 |  | 2025-12-19 08:48 | lower | TRUE | 4 | 73.0178 | TRUE | TRUE | 0.5132 | 3.3582 | 74.3243 | 3 | -0.846 | -0.12699 | 0.33632 | -2.1379 | 0.65325 | Persistent | 75.6308 | -3.4126 | Day | 202512 | 2025-12-19 | 3.4126
2025-12-19 09:30 | 72.095 | FALSE | FALSE | 0.46982 | 0.64744 | -3.7348 | -4.9252 | 0 |  | 2025-12-19 08:48 | lower | TRUE | 4 | 72.5648 | FALSE | TRUE | 0.5146 | 3.1626 | 74.1973 | 4 | 0 | -0.12699 | 0.33632 | 0.37758 | 0.81625 | Persistent | 75.8298 | -2.5756 | Day | 202512 | 2025-12-19 | 2.5756
2025-12-19 09:45 | 72.095 | FALSE | FALSE | 0.10789 | 0.14942 | -3.8428 | -5.0604 | 0 |  | 2025-12-19 08:48 | lower | TRUE | 4 | 72.2029 | FALSE | TRUE | 0.541 | 2.9532 | 74.0703 | 5 | 0 | -0.12699 | 0.33632 | 0.37758 | 0.93372 | Persistent | 75.9378 | -2.1155 | Day | 202512 | 2025-12-19 | 2.1155
2025-12-19 10:00 | 72.3758 | FALSE | FALSE | -0.41117 | -0.57135 | -3.5743 | -4.7061 | 0.2808 |  | 2025-12-19 08:48 | none | FALSE | 3 | 71.9646 | FALSE | FALSE | 0.5344 | 2.7255 | 73.9574 | 6 | 0.2808 | -0.11295 | 0.34758 | 1.1328 | 0.99637 | Persistent | 75.9501 | -1.5873 | Day | 202512 | 2025-12-19 | 1.5873
2025-12-19 10:15 | 72.3758 | FALSE | TRUE | -0.61639 | -0.85897 | -3.5536 | -4.6802 | 0 |  | 2025-12-19 08:48 | none | FALSE | 3 | 71.7594 | FALSE | FALSE | 0.5796 | 2.5374 | 73.8444 | 7 | 0 | -0.11295 | 0.34758 | 0.32496 | 1.0425 | Confirmed/Materialized Shift | 75.9294 | -1.4087 | Day | 202512 | 2025-12-19 | 1.4087
2025-12-19 10:29 | 72.6584 | FALSE | TRUE | -1.0272 | -1.434 | -3.2016 | -4.2204 | 0.2826 |  | 2025-12-19 08:48 | none | FALSE | 3 | 71.6312 | FALSE | FALSE | 0.5543 | 2.3488 | 73.7456 | 8 | 0.2826 | -0.09882 | 0.358 | 1.0654 | 1.0572 | Confirmed/Materialized Shift | 75.86 | -1.0284 | Day | 202512 | 2025-12-19 | 1.0284
2025-12-19 10:44 | 72.941 | FALSE | FALSE | -1.3802 | -1.9287 | -2.82 | -3.7222 | 0.2826 |  |  | none | FALSE | 2 | 71.5608 | FALSE | FALSE | 0.1028 |  | 73.6609 | 0 | 0.2826 | -0.08469 | 0.36755 | 0.99928 | 1.05 | Persistence ends | 75.761 | -0.6856 | Day | 202512 | 2025-12-19 | 0.6856
2025-12-19 10:59 | 72.941 | FALSE | FALSE | -1.4359 | -2.0081 | -2.7064 | -3.5776 | 0 |  |  | none | FALSE | 2 | 71.5051 | FALSE | FALSE | 0.098 |  | 73.5762 | 0 | 0 | -0.08469 | 0.36755 | 0.23042 | 1.0356 | Normal | 75.6474 | -0.6134 | Day | 202512 | 2025-12-19 | 0.6134
2025-12-19 11:15 | 73.2236 | FALSE | FALSE | -1.7326 | -2.4236 | -2.2967 | -3.0412 | 0.2826 |  |  | none | FALSE | 2 | 71.491 | FALSE | FALSE | 0.0758 |  | 73.5057 | 0 | 0.2826 | -0.07056 | 0.37631 | 0.93849 | 1.0073 | Normal | 75.5203 | -0.28 | Day | 202512 | 2025-12-19 | 0.28
2025-12-19 11:29 | 73.5062 | FALSE | FALSE | -2.0178 | -2.8226 | -1.9321 | -2.5612 | 0.2826 |  |  | none | FALSE | 1 | 71.4884 | FALSE | FALSE | 0.0315 |  | 73.4634 | 0 | 0.2826 | -0.0423 | 0.38074 | 0.85333 | 0.98749 | Normal | 75.4383 | 0.043383 | Day | 202512 | 2025-12-19 | 0.043383
2025-12-19 11:44 | 73.2236 | FALSE | FALSE | -1.7289 | -2.4182 | -2.0673 | -2.7458 | -0.2826 |  |  | none | FALSE | 0 | 71.4947 | FALSE | FALSE | 0.0119 |  | 73.3928 | 0 | -0.2826 | -0.07056 | 0.37631 | -0.56347 | 0.94905 | Normal | 75.2909 | -0.17828 | Day | 202512 | 2025-12-19 | 0.17828
2025-12-19 11:59 | 73.2236 | FALSE | FALSE | -1.7078 | -2.388 | -1.905 | -2.5357 | 0 |  |  | none | FALSE | 0 | 71.5158 | FALSE | FALSE | 0.0073 |  | 73.3222 | 0 | 0 | -0.07056 | 0.37631 | 0.18751 | 0.9032 | Normal | 75.1286 | -0.10921 | Day | 202512 | 2025-12-19 | 0.10921
2025-12-19 12:14 | 73.2236 | FALSE | FALSE | -1.6694 | -2.3331 | -1.7256 | -2.3023 | 0 |  |  | none | FALSE | 0 | 71.5542 | FALSE | FALSE | 0.0022 |  | 73.2517 | 0 | 0 | -0.07056 | 0.37631 | 0.18751 | 0.84875 | Normal | 74.9492 | -0.033084 | Day | 202512 | 2025-12-19 | 0.033084
2025-12-19 12:29 | 73.2236 | FALSE | FALSE | -1.6449 | -2.298 | -1.5882 | -2.1229 | 0 |  |  | none | FALSE | 0 | 71.5787 | FALSE | FALSE | 0.0023 |  | 73.1953 | 0 | 0 | -0.05643 | 0.37322 | 0.1512 | 0.80828 | Normal | 74.8118 | 0.035074 | Day | 202512 | 2025-12-19 | 0.035074
2025-12-19 12:44 | 73.2236 | FALSE | FALSE | -1.6074 | -2.2444 | -1.4378 | -1.9258 | 0 |  |  | none | FALSE | 0 | 71.6162 | FALSE | FALSE | 0.0074 |  | 73.1388 | 0 | 0 | -0.05643 | 0.37322 | 0.1512 | 0.76129 | Normal | 74.6614 | 0.11136 | Day | 202512 | 2025-12-19 | 0.11136
2025-12-19 12:59 | 73.2236 | FALSE | FALSE | -1.5541 | -2.1685 | -1.2717 | -1.7071 | 0 |  |  | none | FALSE | 0 | 71.6695 | FALSE | FALSE | 0.0133 |  | 73.0824 | 0 | 0 | -0.05643 | 0.37322 | 0.1512 | 0.70647 | Normal | 74.4953 | 0.19988 | Day | 202512 | 2025-12-19 | 0.19988
2025-12-19 13:14 | 73.2236 | FALSE | FALSE | -1.4251 | -1.9849 | -1.0016 | -1.3494 | 0 |  |  | none | FALSE | 0 | 71.7985 | FALSE | FALSE | 0.0233 |  | 73.0118 | 0 | 0 | -0.07056 | 0.36497 | 0.19333 | 0.60668 | Normal | 74.2252 | 0.34906 | Day | 202512 | 2025-12-19 | 0.34906
2025-12-19 13:28 | 73.2236 | FALSE | FALSE | -1.3123 | -1.8248 | -0.77586 | -1.0485 | 0 |  |  | none | FALSE | 0 | 71.9113 | FALSE | FALSE | 0.0343 |  | 72.9554 | 0 | 0 | -0.05643 | 0.36178 | 0.15598 | 0.52203 | Normal | 73.9995 | 0.51376 | Day | 202512 | 2025-12-19 | 0.51376
2025-12-19 13:43 | 73.2236 | FALSE | FALSE | -1.2246 | -1.7009 | -0.60343 | -0.81736 | 0 |  |  | none | FALSE | 0 | 71.999 | FALSE | FALSE | 0.0453 |  | 72.913 | 0 | 0 | -0.04239 | 0.35805 | 0.11839 | 0.45701 | Normal | 73.827 | 0.67961 | Day | 202512 | 2025-12-19 | 0.67961
2025-12-19 13:59 | 73.2236 | FALSE | FALSE | -1.221 | -1.6957 | -0.62806 | -0.85044 | 0 |  |  | none | FALSE | 0 | 72.0026 | FALSE | FALSE | 0.0428 |  | 72.9271 | 0 | 0 | 0.01413 | 0.25025 | -0.056463 | 0.46226 | Normal | 73.8517 | 0.64133 | Day | 202512 | 2025-12-19 | 0.64133
2025-12-19 14:14 | 73.2236 | FALSE | FALSE | -1.085 | -1.5041 | -0.60499 | -0.81945 | 0 |  |  | none | FALSE | 0 | 72.1386 | FALSE | FALSE | 0.0379 |  | 72.9836 | 0 | 0 | 0.05643 | 0.1477 | -0.38207 | 0.42251 | Normal | 73.8286 | 0.56811 | Day | 202512 | 2025-12-19 | 0.56811
2025-12-19 14:28 | 72.941 | FALSE | FALSE | -0.65044 | -0.89976 | -0.82018 | -1.1119 | -0.2826 |  |  | none | FALSE | 0 | 72.2906 | FALSE | FALSE | 0.0154 |  | 73.0259 | 0 | -0.2826 | 0.0423 | 0.16579 | -1.9597 | 0.36765 | Normal | 73.7612 | -0.23084 | Day | 202512 | 2025-12-19 | 0.23084
2025-12-19 14:43 | 72.941 | FALSE | FALSE | -0.46633 | -0.64343 | -0.72067 | -0.97835 | 0 |  |  | none | FALSE | 0 | 72.4747 | FALSE | FALSE | 0.0286 |  | 73.0682 | 0 | 0 | 0.0423 | 0.16579 | -0.25514 | 0.29675 | Normal | 73.6617 | -0.42855 | Day | 202512 | 2025-12-19 | 0.42855
2025-12-19 14:58 | 72.941 | FALSE | FALSE | -0.34593 | -0.47651 | -0.65679 | -0.8924 | 0 |  |  | none | FALSE | 0 | 72.5951 | FALSE | FALSE | 0.0413 |  | 73.0964 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.25068 | Normal | 73.5978 | -0.62004 | Day | 202512 | 2025-12-19 | 0.62004
2025-12-19 15:13 | 72.941 | FALSE | FALSE | -0.19546 | -0.26869 | -0.56284 | -0.76573 | 0 |  |  | none | FALSE | 0 | 72.7455 | FALSE | FALSE | 0.0646 |  | 73.1247 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.18957 | Normal | 73.5038 | -0.96896 | Day | 202512 | 2025-12-19 | 0.96896
2025-12-19 15:28 | 72.941 | FALSE | FALSE | -0.12505 | -0.17173 | -0.52069 | -0.70878 | 0 |  |  | none | FALSE | 0 | 72.816 | FALSE | FALSE | 0.0817 |  | 73.1388 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.16143 | Normal | 73.4617 | -1.2254 | Day | 202512 | 2025-12-19 | 1.2254
2025-12-19 15:43 | 72.941 | FALSE | FALSE | -0.12505 | -0.17173 | -0.52069 | -0.70878 | 0 |  |  | none | FALSE | 0 | 72.816 | FALSE | FALSE | 0.0817 |  | 73.1388 | 0 | 0 | 0 | 0.12967 | 0 | 0.16143 | Normal | 73.4617 | -1.2254 | Day | 202512 | 2025-12-19 | 1.2254
2025-12-19 15:58 | 72.6584 | FALSE | FALSE | 0.087142 | 0.11979 | -0.84544 | -1.1502 | -0.2826 | 2025-12-19 17:42 | 2025-12-19 15:58 | lower | TRUE | 0 | 72.7455 | FALSE | FALSE | 0.2211 | 2.4597 | 73.1247 | 1 | -0.2826 | -0.01413 | 0.14424 | -1.8612 | 0.18957 | Extreme triggered | 73.5038 | -2.4597 | Day | 202512 | 2025-12-19 | 2.4597
2025-12-19 16:13 | 72.6584 | FALSE | FALSE | 0.0089558 | 0.012324 | -0.8671 | -1.1793 | 0 |  | 2025-12-19 15:58 | lower | TRUE | 0 | 72.6674 | FALSE | FALSE | 0.2504 | 2.2507 | 73.0964 | 2 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21454 | Extreme/elevated | 73.5255 | -2.0417 | Day | 202512 | 2025-12-19 | 2.0417
2025-12-19 16:27 | 72.6584 | FALSE | FALSE | -0.030485 | -0.041975 | -0.82177 | -1.1183 | 0 |  | 2025-12-19 15:58 | none | FALSE | 0 | 72.6279 | FALSE | FALSE | 0.2952 | 2.1194 | 73.054 | 3 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.21306 | Persistent | 73.4802 | -1.8569 | Day | 202512 | 2025-12-19 | 1.8569
2025-12-19 16:43 | 72.3758 | TRUE | FALSE | 0.12125 | 0.16725 | -1.1504 | -1.5647 | -0.2826 |  | 2025-12-19 15:58 | lower | TRUE | 1 | 72.4971 | FALSE | TRUE | 0.4219 | 2.2074 | 73.0117 | 4 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.2573 | Persistent | 73.5262 | -2.4713 | Day | 202512 | 2025-12-19 | 2.4713
2025-12-19 16:58 | 72.095 | FALSE | FALSE | 0.21304 | 0.29463 | -1.5074 | -2.048 | -0.2808 |  | 2025-12-19 15:58 | lower | TRUE | 1 | 72.308 | FALSE | TRUE | 0.4915 | 2.2976 | 72.9552 | 5 | -0.2808 | -0.05643 | 0.11579 | -1.9377 | 0.32359 | Persistent | 73.6024 | -2.6584 | Day | 202512 | 2025-12-19 | 2.6584
2025-12-19 17:13 | 72.095 | FALSE | FALSE | 0.064838 | 0.089853 | -1.5427 | -2.095 | 0 |  | 2025-12-19 15:58 | lower | TRUE | 1 | 72.1598 | FALSE | TRUE | 0.5165 | 2.2772 | 72.8988 | 6 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.36948 | Persistent | 73.6377 | -2.1755 | Day | 202512 | 2025-12-19 | 2.1755
2025-12-19 17:27 | 72.3758 | TRUE | TRUE | -0.27693 | -0.3841 | -1.2381 | -1.6819 | 0.2808 |  | 2025-12-19 15:58 | none | FALSE | 2 | 72.0989 | TRUE | FALSE | 0.5417 | 2.1332 | 72.8564 | 7 | 0.2808 | -0.04239 | 0.13791 | 2.3435 | 0.37877 | Confirmed/Materialized Shift | 73.6139 | -1.2689 | Day | 202512 | 2025-12-19 | 1.2689
2025-12-19 17:42 | 72.941 | TRUE | FALSE | -0.83774 | -1.1619 | -0.64028 | -0.87017 | 0.5652 |  |  | none | FALSE | 3 | 72.1033 | TRUE | FALSE | 0.1035 |  | 72.8423 | 0 | 0.5652 | -0.01413 | 0.19368 | 2.9911 | 0.36951 | Persistence ends | 73.5813 | 0.2672 | Night | 202512 | 2025-12-19 | 0.2672
2025-12-19 17:57 | 72.941 | FALSE | FALSE | -0.8317 | -1.1534 | -0.60598 | -0.82394 | 0 |  |  | none | FALSE | 3 | 72.1093 | FALSE | FALSE | 0.1066 |  | 72.8281 | 0 | 0 | -0.01413 | 0.19368 | 0.072955 | 0.35942 | Normal | 73.547 | 0.314 | Night | 202512 | 2025-12-19 | 0.314
2025-12-19 18:12 | 73.2236 | FALSE | FALSE | -1.1143 | -1.5453 | -0.32338 | -0.4397 | 0.2826 |  |  | none | FALSE | 3 | 72.1093 | FALSE | FALSE | 0.1591 |  | 72.8281 | 0 | 0.2826 | 0 | 0.20476 | 1.3802 | 0.35942 | Normal | 73.547 | 1.1003 | Night | 202512 | 2025-12-19 | 1.1003
2025-12-19 18:27 | 73.2236 | FALSE | FALSE | -1.1143 | -1.5453 | -0.32338 | -0.4397 | 0 |  |  | none | FALSE | 3 | 72.1093 | FALSE | FALSE | 0.1591 |  | 72.8281 | 0 | 0 | 0 | 0.20476 | 0 | 0.35942 | Normal | 73.547 | 1.1003 | Night | 202512 | 2025-12-19 | 1.1003
2025-12-19 18:30 | 73.2236 | FALSE | FALSE | -1.1143 | -1.5453 | -0.32338 | -0.4397 | 0 |  |  | none | FALSE | 3 | 72.1093 | FALSE | FALSE | 0.1591 |  | 72.8281 | 0 | 0 | 0 | 0.20476 | 0 | 0.35942 | Normal | 73.547 | 1.1003 | Night | 202512 | 2025-12-19 | 1.1003
2025-12-19 18:31 | 73.2236 | FALSE | FALSE | -1.1143 | -1.5453 | -0.32338 | -0.4397 | 0 |  |  | none | FALSE | 3 | 72.1093 | FALSE | FALSE | 0.1591 |  | 72.8281 | 0 | 0 | 0 | 0.20476 | 0 | 0.35942 | Normal | 73.547 | 1.1003 | Night | 202512 | 2025-12-19 | 1.1003
2025-12-19 18:46 | 73.7888 | TRUE | FALSE | -1.7538 | -2.4347 | 0.11098 | 0.15062 | 0.5652 | 2025-12-19 20:59 | 2025-12-19 18:46 | upper | TRUE | 3 | 72.035 | TRUE | FALSE | 0.2942 | 2.2702 | 72.8564 | 1 | 0.5652 | 0.02826 | 0.24062 | 2.2315 | 0.41071 | Extreme triggered | 73.6778 | 2.2702 | Night | 202512 | 2025-12-19 | 2.2702
2025-12-19 19:01 | 73.7888 | FALSE | FALSE | -1.8113 | -2.5164 | -0.031233 | -0.042309 | 0 |  | 2025-12-19 18:46 | none | FALSE | 3 | 71.9775 | FALSE | FALSE | 0.3288 | 2.1012 | 72.8988 | 2 | 0 | 0.04239 | 0.22944 | -0.18475 | 0.46062 | Extreme/elevated | 73.82 | 1.9322 | Night | 202512 | 2025-12-19 | 1.9322
2025-12-19 19:16 | 74.0714 | FALSE | FALSE | -2.1764 | -3.0272 | 0.055741 | 0.07531 | 0.2826 |  | 2025-12-19 18:46 | upper | TRUE | 3 | 71.895 | FALSE | TRUE | 0.3975 | 2.1025 | 72.9553 | 3 | 0.2826 | 0.05652 | 0.23532 | 0.96072 | 0.53017 | Persistent | 74.0157 | 2.1051 | Night | 202512 | 2025-12-19 | 2.1051
2025-12-19 19:30 | 74.0714 | FALSE | FALSE | -2.2314 | -3.106 | -0.11222 | -0.15127 | 0 |  | 2025-12-19 18:46 | none | FALSE | 2 | 71.84 | FALSE | FALSE | 0.4063 | 2.029 | 73.0118 | 4 | 0 | 0.05652 | 0.23532 | -0.24018 | 0.58589 | Persistent | 74.1836 | 1.8085 | Night | 202512 | 2025-12-19 | 1.8085
2025-12-19 19:45 | 74.0714 | FALSE | FALSE | -2.266 | -3.1557 | -0.25986 | -0.3496 | 0 |  | 2025-12-19 18:46 | none | FALSE | 1 | 71.8054 | FALSE | FALSE | 0.4202 | 1.9409 | 73.0683 | 5 | 0 | 0.05652 | 0.23532 | -0.24018 | 0.63145 | Persistent | 74.3313 | 1.5885 | Night | 202512 | 2025-12-19 | 1.5885
2025-12-19 20:00 | 74.0714 | FALSE | FALSE | -2.2844 | -3.1822 | -0.39134 | -0.52555 | 0 |  | 2025-12-19 18:46 | none | FALSE | 1 | 71.787 | FALSE | FALSE | 0.4658 | 1.8532 | 73.1249 | 6 | 0 | 0.05652 | 0.23532 | -0.24018 | 0.66893 | Persistent | 74.4627 | 1.415 | Night | 202512 | 2025-12-19 | 1.415
2025-12-19 20:15 | 74.0714 | FALSE | TRUE | -2.2893 | -3.1892 | -0.50925 | -0.68282 | 0 |  | 2025-12-19 18:46 | none | FALSE | 1 | 71.7821 | FALSE | FALSE | 0.5134 | 1.7702 | 73.1814 | 7 | 0 | 0.05652 | 0.23532 | -0.24018 | 0.69963 | Confirmed/Materialized Shift | 74.5807 | 1.2721 | Night | 202512 | 2025-12-19 | 1.2721
2025-12-19 20:29 | 74.0714 | FALSE | TRUE | -2.2498 | -3.1325 | -0.61106 | -0.81821 | 0 |  | 2025-12-19 18:46 | none | FALSE | 1 | 71.8216 | FALSE | FALSE | 0.5049 | 1.6922 | 73.252 | 8 | 0 | 0.07065 | 0.222 | -0.31825 | 0.71521 | Confirmed/Materialized Shift | 74.6825 | 1.1456 | Night | 202512 | 2025-12-19 | 1.1456
2025-12-19 20:44 | 74.0714 | FALSE | TRUE | -2.1952 | -3.0541 | -0.69774 | -0.9332 | 0 |  | 2025-12-19 18:46 | none | FALSE | 1 | 71.8762 | FALSE | FALSE | 0.4976 | 1.6192 | 73.3227 | 9 | 0 | 0.07065 | 0.222 | -0.31825 | 0.72323 | Confirmed/Materialized Shift | 74.7691 | 1.0352 | Night | 202512 | 2025-12-19 | 1.0352
2025-12-19 20:59 | 74.0714 | FALSE | FALSE | -2.1259 | -2.9549 | -0.76981 | -1.0286 | 0 |  |  | none | FALSE | 1 | 71.9455 | FALSE | FALSE | 0.091 |  | 73.3933 | 0 | 0 | 0.07065 | 0.222 | -0.31825 | 0.72393 | Persistence ends | 74.8412 | 0.93663 | Night | 202512 | 2025-12-19 | 0.93663
2025-12-19 21:14 | 74.3522 | FALSE | FALSE | -2.2851 | -3.1708 | -0.56502 | -0.75419 | 0.2808 |  |  | none | FALSE | 0 | 72.0671 | FALSE | FALSE | 0.0805 |  | 73.4922 | 0 | 0.2808 | 0.09882 | 0.21025 | 0.86556 | 0.71253 | Normal | 74.9172 | 1.207 | Night | 202512 | 2025-12-19 | 1.207
2025-12-19 21:29 | 74.3522 | FALSE | FALSE | -2.0594 | -2.8487 | -0.56504 | -0.75422 | 0 |  |  | none | FALSE | 0 | 72.2928 | FALSE | FALSE | 0.0759 |  | 73.605 | 0 | 0 | 0.11286 | 0.19216 | -0.58733 | 0.65611 | Normal | 74.9172 | 1.1388 | Night | 202512 | 2025-12-19 | 1.1388
2025-12-19 21:44 | 74.3522 | FALSE | FALSE | -1.777 | -2.4485 | -0.50839 | -0.67911 | 0 |  |  | none | FALSE | 0 | 72.5752 | FALSE | FALSE | 0.074 |  | 73.7179 | 0 | 0 | 0.11286 | 0.19216 | -0.58733 | 0.57135 | Normal | 74.8606 | 1.1102 | Night | 202512 | 2025-12-19 | 1.1102
2025-12-19 21:59 | 74.3522 | FALSE | FALSE | -1.5205 | -2.0877 | -0.44948 | -0.60089 | 0 |  |  | none | FALSE | 0 | 72.8317 | FALSE | FALSE | 0.0725 |  | 73.8167 | 0 | 0 | 0.09882 | 0.18948 | -0.52153 | 0.49249 | Normal | 74.8017 | 1.0873 | Night | 202512 | 2025-12-19 | 1.0873
2025-12-19 22:14 | 74.3522 | FALSE | FALSE | -1.3859 | -1.8994 | -0.45601 | -0.60957 | 0 |  |  | none | FALSE | 0 | 72.9663 | FALSE | FALSE | 0.0673 |  | 73.8873 | 0 | 0 | 0.07056 | 0.15534 | -0.45424 | 0.46047 | Normal | 74.8082 | 1.0097 | Night | 202512 | 2025-12-19 | 1.0097
2025-12-19 22:29 | 74.3522 | FALSE | FALSE | -1.2215 | -1.6703 | -0.43277 | -0.57869 | 0 |  |  | none | FALSE | 0 | 73.1307 | FALSE | FALSE | 0.0636 |  | 73.9578 | 0 | 0 | 0.07056 | 0.15534 | -0.45424 | 0.41358 | Normal | 74.785 | 0.95358 | Night | 202512 | 2025-12-19 | 0.95358
2025-12-19 22:44 | 74.3522 | FALSE | FALSE | -1.1061 | -1.5101 | -0.43018 | -0.57525 | 0 |  |  | none | FALSE | 0 | 73.2461 | FALSE | FALSE | 0.0587 |  | 74.0143 | 0 | 0 | 0.05643 | 0.1477 | -0.38207 | 0.38407 | Normal | 74.7824 | 0.87993 | Night | 202512 | 2025-12-19 | 0.87993
2025-12-19 22:59 | 74.6348 | FALSE | FALSE | -1.2701 | -1.7312 | -0.1701 | -0.22739 | 0.2826 |  |  | none | FALSE | 0 | 73.3647 | FALSE | FALSE | 0.1018 |  | 74.0848 | 0 | 0.2826 | 0.07056 | 0.15534 | 1.365 | 0.36005 | Normal | 74.8049 | 1.5276 | Night | 202512 | 2025-12-19 | 1.5276
2025-12-19 23:14 | 74.6348 | FALSE | FALSE | -1.1159 | -1.5179 | -0.15705 | -0.20998 | 0 |  |  | none | FALSE | 0 | 73.5189 | FALSE | FALSE | 0.1004 |  | 74.1554 | 0 | 0 | 0.07056 | 0.15534 | -0.45424 | 0.31824 | Normal | 74.7918 | 1.5065 | Night | 202512 | 2025-12-19 | 1.5065
2025-12-19 23:28 | 74.3522 | FALSE | FALSE | -0.60631 | -0.82217 | -0.32551 | -0.43589 | -0.2826 |  |  | none | FALSE | 0 | 73.7459 | FALSE | FALSE | 0.0402 |  | 74.2118 | 0 | -0.2826 | 0.05643 | 0.17384 | -1.9502 | 0.23296 | Normal | 74.6777 | 0.60269 | Night | 202512 | 2025-12-19 | 0.60269
2025-12-19 23:43 | 74.3522 | FALSE | FALSE | -0.53675 | -0.72715 | -0.31229 | -0.41825 | 0 |  |  | none | FALSE | 0 | 73.8155 | FALSE | FALSE | 0.0352 |  | 74.24 | 0 | 0 | 0.02817 | 0.12619 | -0.22323 | 0.21226 | Normal | 74.6645 | 0.52874 | Night | 202512 | 2025-12-19 | 0.52874
2025-12-19 23:58 | 74.3522 | FALSE | FALSE | -0.45375 | -0.61402 | -0.28563 | -0.38269 | 0 |  |  | none | FALSE | 0 | 73.8984 | FALSE | FALSE | 0.0303 |  | 74.2681 | 0 | 0 | 0.02817 | 0.12619 | -0.22323 | 0.18485 | Normal | 74.6378 | 0.45476 | Night | 202512 | 2025-12-19 | 0.45476
2025-12-20 00:14 | 74.0714 | TRUE | FALSE | -0.17295 | -0.23404 | -0.56643 | -0.75891 | -0.2808 |  |  | none | FALSE | 1 | 73.8984 | FALSE | FALSE | 0.0995 |  | 74.2681 | 0 | -0.2808 | 0 | 0.12925 | -2.1725 | 0.18485 | Normal | 74.6378 | -1.0643 | Night | 202512 | 2025-12-20 | 1.0643
2025-12-20 00:28 | 74.0714 | FALSE | FALSE | -0.17295 | -0.23404 | -0.56643 | -0.75891 | 0 |  |  | none | FALSE | 1 | 73.8984 | FALSE | FALSE | 0.0995 |  | 74.2681 | 0 | 0 | 0 | 0.12925 | 0 | 0.18485 | Normal | 74.6378 | -1.0643 | Night | 202512 | 2025-12-20 | 1.0643
2025-12-20 00:43 | 74.0714 | FALSE | FALSE | -0.17295 | -0.23404 | -0.56643 | -0.75891 | 0 |  |  | none | FALSE | 1 | 73.8984 | FALSE | FALSE | 0.0995 |  | 74.2681 | 0 | 0 | 0 | 0.12925 | 0 | 0.18485 | Normal | 74.6378 | -1.0643 | Night | 202512 | 2025-12-20 | 1.0643
2025-12-20 00:58 | 74.0714 | FALSE | FALSE | -0.17295 | -0.23404 | -0.56643 | -0.75891 | 0 |  |  | none | FALSE | 1 | 73.8984 | FALSE | FALSE | 0.0995 |  | 74.2681 | 0 | 0 | 0 | 0.12925 | 0 | 0.18485 | Normal | 74.6378 | -1.0643 | Night | 202512 | 2025-12-20 | 1.0643
2025-12-20 01:13 | 74.0714 | FALSE | FALSE | -0.17295 | -0.23404 | -0.56643 | -0.75891 | 0 |  |  | none | FALSE | 1 | 73.8984 | FALSE | FALSE | 0.0995 |  | 74.2681 | 0 | 0 | 0 | 0.12925 | 0 | 0.18485 | Normal | 74.6378 | -1.0643 | Night | 202512 | 2025-12-20 | 1.0643
2025-12-20 01:28 | 74.0714 | FALSE | FALSE | -0.17295 | -0.23404 | -0.56643 | -0.75891 | 0 |  |  | none | FALSE | 1 | 73.8984 | FALSE | FALSE | 0.0995 |  | 74.2681 | 0 | 0 | 0 | 0.12925 | 0 | 0.18485 | Normal | 74.6378 | -1.0643 | Night | 202512 | 2025-12-20 | 1.0643
2025-12-20 01:43 | 74.0714 | FALSE | FALSE | -0.17295 | -0.23404 | -0.56643 | -0.75891 | 0 |  |  | none | FALSE | 1 | 73.8984 | FALSE | FALSE | 0.0995 |  | 74.2681 | 0 | 0 | 0 | 0.12925 | 0 | 0.18485 | Normal | 74.6378 | -1.0643 | Night | 202512 | 2025-12-20 | 1.0643
2025-12-20 01:58 | 74.0714 | FALSE | FALSE | -0.17295 | -0.23404 | -0.56643 | -0.75891 | 0 |  |  | none | FALSE | 1 | 73.8984 | FALSE | FALSE | 0.0995 |  | 74.2681 | 0 | 0 | 0 | 0.12925 | 0 | 0.18485 | Normal | 74.6378 | -1.0643 | Night | 202512 | 2025-12-20 | 1.0643
2025-12-20 02:13 | 74.0714 | FALSE | FALSE | -0.1948 | -0.26368 | -0.5602 | -0.75062 | 0 |  |  | none | FALSE | 1 | 73.8766 | FALSE | FALSE | 0.0931 |  | 74.2541 | 0 | 0 | -0.01404 | 0.11113 | 0.12634 | 0.18875 | Normal | 74.6316 | -0.96796 | Night | 202512 | 2025-12-20 | 0.96796
2025-12-20 02:27 | 74.0714 | FALSE | FALSE | -0.21432 | -0.29018 | -0.55164 | -0.73924 | 0 |  |  | none | FALSE | 1 | 73.8571 | FALSE | FALSE | 0.0873 |  | 74.2401 | 0 | 0 | -0.01404 | 0.11113 | 0.12634 | 0.19149 | Normal | 74.623 | -0.88077 | Night | 202512 | 2025-12-20 | 0.88077
2025-12-20 02:43 | 73.7888 | TRUE | FALSE | -0.005345 | -0.0072442 | -0.85152 | -1.1408 | -0.2826 |  |  | none | FALSE | 1 | 73.7835 | FALSE | FALSE | 0.1602 |  | 74.2119 | 0 | -0.2826 | -0.02817 | 0.12619 | -2.0162 | 0.21422 | Normal | 74.6403 | -1.975 | Night | 202512 | 2025-12-20 | 1.975
2025-12-20 02:58 | 73.7888 | FALSE | FALSE | -0.067418 | -0.091449 | -0.85726 | -1.1484 | 0 |  |  | none | FALSE | 1 | 73.7214 | FALSE | FALSE | 0.1425 |  | 74.1837 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.23117 | Normal | 74.6461 | -1.7084 | Night | 202512 | 2025-12-20 | 1.7084
2025-12-20 03:13 | 73.7888 | FALSE | FALSE | -0.12036 | -0.16338 | -0.85386 | -1.1439 | 0 |  |  | none | FALSE | 1 | 73.6684 | FALSE | FALSE | 0.129 |  | 74.1556 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.24355 | Normal | 74.6427 | -1.5058 | Night | 202512 | 2025-12-20 | 1.5058
2025-12-20 03:27 | 73.7888 | FALSE | FALSE | -0.16551 | -0.22481 | -0.84267 | -1.1291 | 0 |  |  | none | FALSE | 1 | 73.6233 | FALSE | FALSE | 0.1181 |  | 74.1274 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.25205 | Normal | 74.6315 | -1.3433 | Night | 202512 | 2025-12-20 | 1.3433
2025-12-20 03:42 | 73.7888 | FALSE | FALSE | -0.20365 | -0.27676 | -0.82447 | -1.105 | 0 |  |  | none | FALSE | 1 | 73.5851 | FALSE | FALSE | 0.1091 |  | 74.0992 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.25703 | Normal | 74.6133 | -1.2077 | Night | 202512 | 2025-12-20 | 1.2077
2025-12-20 03:57 | 73.5062 | FALSE | FALSE | 0.02229 | 0.030315 | -1.0509 | -1.4095 | -0.2826 | 2025-12-20 08:30 | 2025-12-20 03:57 | lower | TRUE | 1 | 73.5285 | FALSE | FALSE | 0.2248 | 2.0867 | 74.0428 | 1 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.25715 | Extreme triggered | 74.5571 | -2.0867 | Night | 202512 | 2025-12-20 | 2.0867
2025-12-20 04:12 | 73.5062 | FALSE | FALSE | -0.0076143 | -0.01036 | -0.96791 | -1.2997 | 0 |  | 2025-12-20 03:57 | none | FALSE | 1 | 73.4986 | FALSE | FALSE | 0.2741 | 2.0277 | 73.9864 | 2 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.24388 | Extreme/elevated | 74.4741 | -1.9688 | Night | 202512 | 2025-12-20 | 1.9688
2025-12-20 04:27 | 73.5062 | FALSE | FALSE | -0.062887 | -0.085627 | -0.93859 | -1.2608 | 0 |  | 2025-12-20 03:57 | none | FALSE | 1 | 73.4433 | FALSE | FALSE | 0.3166 | 1.9348 | 73.9441 | 3 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.25037 | Persistent | 74.4448 | -1.7488 | Night | 202512 | 2025-12-20 | 1.7488
2025-12-20 04:42 | 73.5062 | FALSE | FALSE | -0.10294 | -0.14024 | -0.89404 | -1.2017 | 0 |  | 2025-12-20 03:57 | none | FALSE | 1 | 73.4033 | FALSE | FALSE | 0.3629 | 1.8478 | 73.9018 | 4 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.24925 | Persistent | 74.4002 | -1.587 | Night | 202512 | 2025-12-20 | 1.587
2025-12-20 04:57 | 73.5062 | FALSE | FALSE | -0.12756 | -0.17384 | -0.83406 | -1.122 | 0 |  | 2025-12-20 03:57 | none | FALSE | 1 | 73.3786 | FALSE | FALSE | 0.4122 | 1.7721 | 73.8594 | 5 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.24041 | Persistent | 74.3403 | -1.4694 | Night | 202512 | 2025-12-20 | 1.4694
2025-12-20 05:12 | 73.5062 | FALSE | FALSE | -0.16961 | -0.23128 | -0.81959 | -1.1027 | 0 |  | 2025-12-20 03:57 | none | FALSE | 0 | 73.3366 | FALSE | FALSE | 0.4305 | 1.6958 | 73.8312 | 6 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.2473 | Persistent | 74.3258 | -1.3141 | Night | 202512 | 2025-12-20 | 1.3141
2025-12-20 05:27 | 73.2236 | TRUE | TRUE | 0.015075 | 0.020583 | -1.1153 | -1.5003 | -0.2826 |  | 2025-12-20 03:57 | lower | TRUE | 1 | 73.2387 | FALSE | TRUE | 0.5656 | 1.7471 | 73.7888 | 7 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.27506 | Confirmed/Materialized Shift | 74.3389 | -2.0548 | Night | 202512 | 2025-12-20 | 2.0548
2025-12-20 05:42 | 73.2236 | FALSE | TRUE | -0.064992 | -0.088838 | -1.1106 | -1.4941 | 0 |  | 2025-12-20 03:57 | none | FALSE | 1 | 73.1586 | FALSE | FALSE | 0.5472 | 1.7511 | 73.7464 | 8 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.2939 | Confirmed/Materialized Shift | 74.3342 | -1.7789 | Night | 202512 | 2025-12-20 | 1.7789
2025-12-20 05:57 | 73.2236 | FALSE | TRUE | -0.13052 | -0.17857 | -1.0914 | -1.4686 | 0 |  | 2025-12-20 03:57 | none | FALSE | 1 | 73.0931 | FALSE | FALSE | 0.5334 | 1.7312 | 73.704 | 9 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.30547 | Confirmed/Materialized Shift | 74.315 | -1.5727 | Night | 202512 | 2025-12-20 | 1.5727
2025-12-20 06:12 | 73.2236 | FALSE | TRUE | -0.18315 | -0.25075 | -1.0592 | -1.4259 | 0 |  | 2025-12-20 03:57 | none | FALSE | 1 | 73.0405 | FALSE | FALSE | 0.5226 | 1.6991 | 73.6616 | 10 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.31059 | Confirmed/Materialized Shift | 74.2828 | -1.4103 | Night | 202512 | 2025-12-20 | 1.4103
2025-12-20 06:26 | 73.2236 | FALSE | TRUE | -0.22351 | -0.30617 | -1.0148 | -1.3669 | 0 |  | 2025-12-20 03:57 | none | FALSE | 1 | 73.0001 | FALSE | FALSE | 0.5138 | 1.6609 | 73.6192 | 11 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.30957 | Confirmed/Materialized Shift | 74.2384 | -1.278 | Night | 202512 | 2025-12-20 | 1.278
2025-12-20 06:41 | 72.941 | FALSE | TRUE | -0.029197 | -0.040044 | -1.2726 | -1.7148 | -0.2826 |  | 2025-12-20 03:57 | none | FALSE | 1 | 72.9118 | FALSE | FALSE | 0.5559 | 1.6817 | 73.5627 | 12 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.32546 | Confirmed/Materialized Shift | 74.2136 | -1.9103 | Night | 202512 | 2025-12-20 | 1.9103
2025-12-20 06:56 | 72.941 | FALSE | TRUE | -0.095968 | -0.13174 | -1.2264 | -1.6535 | 0 |  | 2025-12-20 03:57 | none | FALSE | 1 | 72.845 | FALSE | FALSE | 0.5426 | 1.6838 | 73.5062 | 13 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.33058 | Confirmed/Materialized Shift | 74.1674 | -1.7097 | Night | 202512 | 2025-12-20 | 1.7097
2025-12-20 07:11 | 72.941 | FALSE | TRUE | -0.14224 | -0.19538 | -1.1596 | -1.5649 | 0 |  | 2025-12-20 03:57 | none | FALSE | 1 | 72.7988 | FALSE | FALSE | 0.5328 | 1.6752 | 73.4497 | 14 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.32546 | Confirmed/Materialized Shift | 74.1006 | -1.563 | Day | 202512 | 2025-12-20 | 1.563
2025-12-20 07:26 | 72.941 | FALSE | TRUE | -0.16699 | -0.22946 | -1.0713 | -1.4475 | 0 |  | 2025-12-20 03:57 | none | FALSE | 1 | 72.774 | FALSE | FALSE | 0.5259 | 1.6609 | 73.3932 | 15 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.30957 | Confirmed/Materialized Shift | 74.0123 | -1.4606 | Day | 202512 | 2025-12-20 | 1.4606
2025-12-20 07:30 | 72.941 | FALSE | TRUE | -0.21141 | -0.29068 | -1.0309 | -1.3937 | 0 |  | 2025-12-20 03:57 | none | FALSE | 1 | 72.7296 | FALSE | FALSE | 0.5165 | 1.6395 | 73.3508 | 16 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.31059 | Confirmed/Materialized Shift | 73.9719 | -1.3193 | Day | 202512 | 2025-12-20 | 1.3193
2025-12-20 07:45 | 72.941 | FALSE | TRUE | -0.24356 | -0.33504 | -0.97832 | -1.3235 | 0 |  | 2025-12-20 03:57 | none | FALSE | 0 | 72.6974 | FALSE | FALSE | 0.4802 | 1.6138 | 73.3084 | 17 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.30547 | Confirmed/Materialized Shift | 73.9193 | -1.2027 | Day | 202512 | 2025-12-20 | 1.2027
2025-12-20 08:01 | 72.941 | FALSE | TRUE | -0.26281 | -0.36161 | -0.91279 | -1.2359 | 0 |  | 2025-12-20 03:57 | none | FALSE | 0 | 72.6782 | FALSE | FALSE | 0.4737 | 1.5856 | 73.266 | 18 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.2939 | Confirmed/Materialized Shift | 73.8538 | -1.1058 | Day | 202512 | 2025-12-20 | 1.1058
2025-12-20 08:16 | 72.941 | FALSE | TRUE | -0.26753 | -0.36812 | -0.83273 | -1.1288 | 0 |  | 2025-12-20 03:57 | none | FALSE | 0 | 72.6735 | FALSE | FALSE | 0.4685 | 1.5562 | 73.2236 | 19 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27506 | Confirmed/Materialized Shift | 73.7737 | -1.0274 | Day | 202512 | 2025-12-20 | 1.0274
2025-12-20 08:30 | 73.2236 | TRUE | FALSE | -0.50995 | -0.70131 | -0.45343 | -0.61543 | 0.2826 |  |  | none | FALSE | 1 | 72.7137 | FALSE | FALSE | 0.0364 |  | 73.1953 | 0 | 0.2826 | -0.02826 | 0.12638 | 2.4597 | 0.24084 | Persistence ends | 73.677 | 0.11734 | Day | 202512 | 2025-12-20 | 0.11734
2025-12-20 08:30 | 73.2236 | FALSE | FALSE | -0.50174 | -0.68995 | -0.41696 | -0.56621 | 0 |  |  | none | FALSE | 1 | 72.7219 | FALSE | FALSE | 0.0409 |  | 73.1812 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.22968 | Normal | 73.6406 | 0.18456 | Day | 202512 | 2025-12-20 | 0.18456
2025-12-20 08:45 | 73.5062 | TRUE | FALSE | -0.78434 | -1.0786 | -0.13436 | -0.18246 | 0.2826 |  |  | none | FALSE | 2 | 72.7219 | TRUE | FALSE | 0.1515 |  | 73.1812 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.22968 | Normal | 73.6406 | 1.415 | Day | 202512 | 2025-12-20 | 1.415
2025-12-20 09:00 | 73.5062 | FALSE | FALSE | -0.78434 | -1.0786 | -0.13436 | -0.18246 | 0 |  |  | none | FALSE | 2 | 72.7219 | FALSE | FALSE | 0.1515 |  | 73.1812 | 0 | 0 | 0 | 0.12967 | 0 | 0.22968 | Normal | 73.6406 | 1.415 | Day | 202512 | 2025-12-20 | 1.415
2025-12-20 09:11 | 74.0714 | TRUE | FALSE | -1.4554 | -2.0043 | 0.26843 | 0.36372 | 0.5652 | 2025-12-20 09:29 | 2025-12-20 09:11 | upper | TRUE | 3 | 72.616 | TRUE | FALSE | 0.3365 | 2.9046 | 73.2095 | 1 | 0.5652 | 0.02826 | 0.18107 | 2.9654 | 0.29675 | Extreme triggered | 73.803 | 2.9046 | Day | 202512 | 2025-12-20 | 2.9046
2025-12-20 09:14 | 74.0714 | FALSE | FALSE | -1.5313 | -2.111 | 0.136 | 0.18395 | 0 |  | 2025-12-20 09:11 | upper | TRUE | 3 | 72.5401 | FALSE | FALSE | 0.3593 | 2.6472 | 73.2377 | 2 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.34883 | Extreme/elevated | 73.9354 | 2.3899 | Day | 202512 | 2025-12-20 | 2.3899
2025-12-20 09:29 | 73.5062 | TRUE | FALSE | -0.96614 | -1.3319 | -0.4292 | -0.58051 | -0.5652 |  |  | none | FALSE | 4 | 72.5401 | TRUE | FALSE | 0.1656 |  | 73.2377 | 0 | -0.5652 | 0 | 0.22459 | -2.5166 | 0.34883 | Persistence ends | 73.9354 | 0.76962 | Day | 202512 | 2025-12-20 | 0.76962
2025-12-20 09:30 | 73.5062 | FALSE | FALSE | -0.96218 | -1.3263 | -0.4535 | -0.61317 | 0 |  |  | none | FALSE | 4 | 72.544 | FALSE | FALSE | 0.1622 |  | 73.2519 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.35392 | Normal | 73.9597 | 0.71864 | Day | 202512 | 2025-12-20 | 0.71864
2025-12-20 09:45 | 73.2236 | FALSE | FALSE | -0.67958 | -0.93678 | -0.7361 | -0.99527 | -0.2826 |  |  | none | FALSE | 4 | 72.544 | FALSE | FALSE | 0.1196 |  | 73.2519 | 0 | -0.2826 | 0 | 0.22459 | -1.2583 | 0.35392 | Normal | 73.9597 | -0.079849 | Day | 202512 | 2025-12-20 | 0.079849
2025-12-20 10:00 | 72.941 | FALSE | FALSE | -0.42464 | -0.58557 | -1.0181 | -1.3766 | -0.2826 |  |  | none | FALSE | 4 | 72.5164 | FALSE | FALSE | 0.1691 |  | 73.2377 | 0 | -0.2826 | -0.01413 | 0.23331 | -1.1507 | 0.36068 | Normal | 73.9591 | -0.82269 | Day | 202512 | 2025-12-20 | 0.82269
2025-12-20 10:15 | 72.941 | FALSE | FALSE | -0.4509 | -0.62202 | -1.0161 | -1.3739 | 0 |  |  | none | FALSE | 3 | 72.4901 | FALSE | FALSE | 0.1371 |  | 73.2236 | 0 | 0 | -0.01413 | 0.23331 | 0.060564 | 0.36675 | Normal | 73.9571 | -0.77055 | Day | 202512 | 2025-12-20 | 0.77055
2025-12-20 10:29 | 72.941 | FALSE | FALSE | -0.47584 | -0.65664 | -1.0128 | -1.3695 | 0 |  |  | none | FALSE | 3 | 72.4652 | FALSE | FALSE | 0.1338 |  | 73.2095 | 0 | 0 | -0.01413 | 0.23331 | 0.060564 | 0.37215 | Normal | 73.9538 | -0.72139 | Day | 202512 | 2025-12-20 | 0.72139
2025-12-20 10:44 | 72.941 | FALSE | FALSE | -0.47584 | -0.65664 | -1.0128 | -1.3695 | 0 |  |  | none | FALSE | 2 | 72.4652 | FALSE | FALSE | 0.1052 |  | 73.2095 | 0 | 0 | 0 | 0.22459 | 0 | 0.37215 | Normal | 73.9538 | -0.72139 | Day | 202512 | 2025-12-20 | 0.72139
2025-12-20 10:59 | 72.941 | FALSE | FALSE | -0.47584 | -0.65664 | -1.0128 | -1.3695 | 0 |  |  | none | FALSE | 2 | 72.4652 | FALSE | FALSE | 0.1052 |  | 73.2095 | 0 | 0 | 0 | 0.22459 | 0 | 0.37215 | Normal | 73.9538 | -0.72139 | Day | 202512 | 2025-12-20 | 0.72139
2025-12-20 11:14 | 72.941 | FALSE | FALSE | -0.47584 | -0.65664 | -1.0128 | -1.3695 | 0 |  |  | none | FALSE | 1 | 72.4652 | FALSE | FALSE | 0.0767 |  | 73.2095 | 0 | 0 | 0 | 0.22459 | 0 | 0.37215 | Normal | 73.9538 | -0.72139 | Day | 202512 | 2025-12-20 | 0.72139
2025-12-20 11:29 | 72.3758 | TRUE | FALSE | -0.020287 | -0.028038 | -1.6311 | -2.204 | -0.5652 |  |  | none | FALSE | 2 | 72.3555 | TRUE | FALSE | 0.1872 |  | 73.1812 | 0 | -0.5652 | -0.02826 | 0.25771 | -2.0835 | 0.41285 | Normal | 74.0069 | -1.9509 | Day | 202512 | 2025-12-20 | 1.9509
2025-12-20 11:44 | 72.6584 | FALSE | FALSE | -0.34357 | -0.4751 | -1.3609 | -1.8386 | 0.2826 |  |  | none | FALSE | 1 | 72.3148 | FALSE | FALSE | 0.1082 |  | 73.1671 | 0 | 0.2826 | -0.01413 | 0.26692 | 1.1117 | 0.42613 | Normal | 74.0193 | -1.1937 | Day | 202512 | 2025-12-20 | 1.1937
2025-12-20 11:59 | 72.941 | FALSE | FALSE | -0.62617 | -0.86589 | -1.0783 | -1.4568 | 0.2826 |  |  | none | FALSE | 1 | 72.3148 | FALSE | FALSE | 0.0639 |  | 73.1671 | 0 | 0.2826 | 0 | 0.27506 | 1.0274 | 0.42613 | Normal | 74.0193 | -0.53055 | Day | 202512 | 2025-12-20 | 0.53055
2025-12-20 12:14 | 72.941 | FALSE | FALSE | -0.62617 | -0.86589 | -1.0783 | -1.4568 | 0 |  |  | none | FALSE | 1 | 72.3148 | FALSE | FALSE | 0.0639 |  | 73.1671 | 0 | 0 | 0 | 0.27506 | 0 | 0.42613 | Normal | 74.0193 | -0.53055 | Day | 202512 | 2025-12-20 | 0.53055
2025-12-20 12:29 | 72.6584 | FALSE | FALSE | -0.38249 | -0.52921 | -1.3716 | -1.8528 | -0.2826 |  |  | none | FALSE | 1 | 72.2759 | FALSE | FALSE | 0.1038 |  | 73.153 | 0 | -0.2826 | -0.01413 | 0.28223 | -0.95125 | 0.43852 | Normal | 74.03 | -1.1278 | Day | 202512 | 2025-12-20 | 1.1278
2025-12-20 12:44 | 72.941 | FALSE | FALSE | -0.68353 | -0.94596 | -1.0792 | -1.4579 | 0.2826 |  |  | none | FALSE | 1 | 72.2575 | FALSE | FALSE | 0.0585 |  | 73.1388 | 0 | 0.2826 | -0.01413 | 0.28223 | 1.0514 | 0.44067 | Normal | 74.0202 | -0.4489 | Day | 202512 | 2025-12-20 | 0.4489
2025-12-20 12:59 | 72.941 | FALSE | FALSE | -0.70099 | -0.97036 | -1.0684 | -1.4436 | 0 |  |  | none | FALSE | 1 | 72.24 | FALSE | FALSE | 0.0563 |  | 73.1247 | 0 | 0 | -0.01413 | 0.28223 | 0.050066 | 0.44234 | Normal | 74.0094 | -0.41527 | Day | 202512 | 2025-12-20 | 0.41527
2025-12-20 13:14 | 72.941 | FALSE | FALSE | -0.71391 | -0.98843 | -1.0248 | -1.3855 | 0 |  |  | none | FALSE | 1 | 72.2271 | FALSE | FALSE | 0.0524 |  | 73.0964 | 0 | 0 | -0.02826 | 0.27353 | 0.10332 | 0.43467 | Normal | 73.9658 | -0.35758 | Day | 202512 | 2025-12-20 | 0.35758
2025-12-20 13:28 | 72.941 | FALSE | FALSE | -0.72261 | -1.0006 | -0.97695 | -1.3217 | 0 |  |  | none | FALSE | 1 | 72.2184 | FALSE | FALSE | 0.0485 |  | 73.0682 | 0 | 0 | -0.02826 | 0.27353 | 0.10332 | 0.42489 | Normal | 73.918 | -0.2993 | Day | 202512 | 2025-12-20 | 0.2993
2025-12-20 13:43 | 72.941 | FALSE | FALSE | -0.63659 | -0.88043 | -0.77789 | -1.0552 | 0 |  |  | none | FALSE | 1 | 72.3044 | FALSE | FALSE | 0.0419 |  | 73.0117 | 0 | 0 | -0.05652 | 0.23555 | 0.23995 | 0.35362 | Normal | 73.7189 | -0.19979 | Day | 202512 | 2025-12-20 | 0.19979
2025-12-20 13:58 | 72.941 | FALSE | FALSE | -0.48723 | -0.67246 | -0.51549 | -0.70176 | 0 |  |  | none | FALSE | 0 | 72.4538 | FALSE | FALSE | 0.0038 |  | 72.9551 | 0 | 0 | -0.05652 | 0.23555 | 0.23995 | 0.25068 | Normal | 73.4565 | -0.056367 | Day | 202512 | 2025-12-20 | 0.056367
2025-12-20 14:14 | 72.6584 | FALSE | FALSE | -0.19108 | -0.26367 | -0.69976 | -0.95389 | -0.2826 |  |  | none | FALSE | 0 | 72.4673 | FALSE | FALSE | 0.0761 |  | 72.9127 | 0 | -0.2826 | -0.04239 | 0.21058 | -1.1407 | 0.22271 | Normal | 73.3582 | -1.142 | Day | 202512 | 2025-12-20 | 1.142
2025-12-20 14:28 | 72.941 | FALSE | FALSE | -0.40445 | -0.55758 | -0.29141 | -0.39792 | 0.2826 |  |  | none | FALSE | 0 | 72.5366 | FALSE | FALSE | 0.0217 |  | 72.8845 | 0 | 0.2826 | -0.02826 | 0.22271 | 1.3958 | 0.17396 | Normal | 73.2324 | 0.32489 | Day | 202512 | 2025-12-20 | 0.32489
2025-12-20 14:43 | 72.941 | FALSE | FALSE | -0.38158 | -0.52588 | -0.24028 | -0.32833 | 0 |  |  | none | FALSE | 0 | 72.5594 | FALSE | FALSE | 0.0303 |  | 72.8704 | 0 | 0 | -0.01413 | 0.21454 | 0.065863 | 0.15546 | Normal | 73.1813 | 0.45445 | Day | 202512 | 2025-12-20 | 0.45445
2025-12-20 14:58 | 72.6584 | FALSE | FALSE | -0.12505 | -0.1724 | -0.52069 | -0.71152 | -0.2826 |  |  | none | FALSE | 0 | 72.5334 | FALSE | FALSE | 0.0817 |  | 72.8562 | 0 | -0.2826 | -0.01413 | 0.21454 | -1.2514 | 0.16143 | Normal | 73.1791 | -1.2254 | Day | 202512 | 2025-12-20 | 1.2254
2025-12-20 15:13 | 72.941 | FALSE | FALSE | -0.40765 | -0.56201 | -0.23809 | -0.32535 | 0.2826 |  |  | none | FALSE | 0 | 72.5334 | FALSE | FALSE | 0.035 |  | 72.8562 | 0 | 0.2826 | 0 | 0.22459 | 1.2583 | 0.16143 | Normal | 73.1791 | 0.52517 | Day | 202512 | 2025-12-20 | 0.52517
2025-12-20 15:28 | 72.941 | FALSE | FALSE | -0.40765 | -0.56201 | -0.23809 | -0.32535 | 0 |  |  | none | FALSE | 0 | 72.5334 | FALSE | FALSE | 0.035 |  | 72.8562 | 0 | 0 | 0 | 0.22459 | 0 | 0.16143 | Normal | 73.1791 | 0.52517 | Day | 202512 | 2025-12-20 | 0.52517
2025-12-20 15:43 | 72.3758 | TRUE | FALSE | 0.067509 | 0.093189 | -0.83681 | -1.143 | -0.5652 | 2025-12-20 17:46 | 2025-12-20 15:43 | lower | TRUE | 1 | 72.4433 | FALSE | FALSE | 0.2424 | 2.351 | 72.828 | 1 | -0.5652 | -0.02826 | 0.25771 | -2.0835 | 0.19233 | Extreme triggered | 73.2126 | -2.351 | Day | 202512 | 2025-12-20 | 2.351
2025-12-20 15:58 | 72.3758 | FALSE | FALSE | -0.0061527 | -0.0085018 | -0.85395 | -1.1661 | 0 |  | 2025-12-20 15:43 | none | FALSE | 1 | 72.3696 | FALSE | FALSE | 0.2743 | 2.1612 | 72.7997 | 2 | 0 | -0.02826 | 0.25771 | 0.10966 | 0.21503 | Extreme/elevated | 73.2298 | -1.9714 | Day | 202512 | 2025-12-20 | 1.9714
2025-12-20 16:13 | 72.3758 | FALSE | FALSE | -0.068266 | -0.094411 | -0.85955 | -1.1737 | 0 |  | 2025-12-20 15:43 | none | FALSE | 1 | 72.3075 | FALSE | FALSE | 0.3137 | 2.0094 | 72.7714 | 3 | 0 | -0.02826 | 0.25771 | 0.10966 | 0.23195 | Persistent | 73.2353 | -1.7057 | Day | 202512 | 2025-12-20 | 1.7057
2025-12-20 16:27 | 72.3758 | FALSE | FALSE | -0.068266 | -0.094411 | -0.85955 | -1.1737 | 0 |  | 2025-12-20 15:43 | none | FALSE | 1 | 72.3075 | FALSE | FALSE | 0.3709 | 1.9334 | 72.7714 | 4 | 0 | 0 | 0.22459 | 0 | 0.23195 | Persistent | 73.2353 | -1.7057 | Day | 202512 | 2025-12-20 | 1.7057
2025-12-20 16:43 | 72.3758 | FALSE | FALSE | -0.11309 | -0.1565 | -0.87611 | -1.196 | 0 |  | 2025-12-20 15:43 | none | FALSE | 1 | 72.2627 | FALSE | FALSE | 0.4171 | 1.8553 | 72.7573 | 5 | 0 | -0.01413 | 0.21454 | 0.065863 | 0.2473 | Persistent | 73.2519 | -1.5427 | Day | 202512 | 2025-12-20 | 1.5427
2025-12-20 16:58 | 72.095 | FALSE | FALSE | 0.052257 | 0.072431 | -1.1878 | -1.6208 | -0.2808 |  | 2025-12-20 15:43 | lower | TRUE | 1 | 72.1473 | FALSE | TRUE | 0.517 | 1.9101 | 72.715 | 6 | -0.2808 | -0.0423 | 0.21047 | -1.1332 | 0.28388 | Persistent | 73.2828 | -2.1841 | Day | 202512 | 2025-12-20 | 2.1841
2025-12-20 17:13 | 72.095 | FALSE | TRUE | -0.042763 | -0.05935 | -1.1982 | -1.6348 | 0 |  | 2025-12-20 15:43 | none | FALSE | 1 | 72.0522 | FALSE | FALSE | 0.5527 | 1.9032 | 72.6727 | 7 | 0 | -0.0423 | 0.21047 | 0.20097 | 0.31024 | Confirmed/Materialized Shift | 73.2932 | -1.8622 | Day | 202512 | 2025-12-20 | 1.8622
2025-12-20 17:27 | 72.095 | FALSE | TRUE | -0.12267 | -0.17044 | -1.2217 | -1.6664 | 0 |  | 2025-12-20 15:43 | none | FALSE | 1 | 71.9723 | FALSE | FALSE | 0.5376 | 1.8697 | 72.6445 | 8 | 0 | -0.02817 | 0.20284 | 0.13888 | 0.3361 | Confirmed/Materialized Shift | 73.3167 | -1.635 | Day | 202512 | 2025-12-20 | 1.635
2025-12-20 17:30 | 72.095 | FALSE | TRUE | -0.19234 | -0.26749 | -1.2068 | -1.6464 | 0 |  | 2025-12-20 15:43 | none | FALSE | 1 | 71.9027 | FALSE | FALSE | 0.5252 | 1.8231 | 72.6022 | 9 | 0 | -0.0423 | 0.18945 | 0.22327 | 0.34979 | Confirmed/Materialized Shift | 73.3018 | -1.4501 | Day | 202512 | 2025-12-20 | 1.4501
2025-12-20 17:31 | 72.095 | FALSE | TRUE | -0.25052 | -0.34869 | -1.1804 | -1.6109 | 0 |  | 2025-12-20 15:43 | none | FALSE | 1 | 71.8445 | FALSE | FALSE | 0.5152 | 1.7708 | 72.5599 | 10 | 0 | -0.0423 | 0.18945 | 0.22327 | 0.35773 | Confirmed/Materialized Shift | 73.2754 | -1.2997 | Day | 202512 | 2025-12-20 | 1.2997
2025-12-20 17:46 | 72.3758 | FALSE | FALSE | -0.5406 | -0.75256 | -0.85236 | -1.164 | 0.2808 |  |  | none | FALSE | 0 | 71.8352 | FALSE | FALSE | 0.0298 |  | 72.5317 | 0 | 0.2808 | -0.02826 | 0.2027 | 1.5247 | 0.34824 | Persistence ends | 73.2282 | -0.44762 | Night | 202512 | 2025-12-20 | 0.44762
2025-12-20 18:01 | 72.941 | TRUE | FALSE | -1.1058 | -1.5394 | -0.28716 | -0.39214 | 0.5652 |  |  | none | FALSE | 1 | 71.8352 | FALSE | FALSE | 0.1069 |  | 72.5317 | 0 | 0.5652 | 0 | 0.24236 | 2.332 | 0.34824 | Normal | 73.2282 | 1.1754 | Night | 202512 | 2025-12-20 | 1.1754
2025-12-20 18:16 | 73.2236 | FALSE | FALSE | -1.4192 | -1.9766 | -0.06367 | -0.086877 | 0.2826 |  |  | none | FALSE | 1 | 71.8044 | FALSE | FALSE | 0.1505 |  | 72.5458 | 0 | 0.2826 | 0.01413 | 0.25046 | 1.0719 | 0.37073 | Normal | 73.2873 | 1.8283 | Night | 202512 | 2025-12-20 | 1.8283
2025-12-20 18:30 | 73.2236 | FALSE | FALSE | -1.4464 | -2.0152 | -0.11913 | -0.16243 | 0 |  |  | none | FALSE | 1 | 71.7772 | FALSE | FALSE | 0.1416 |  | 72.5599 | 0 | 0 | 0.01413 | 0.25046 | -0.056415 | 0.39139 | Normal | 73.3427 | 1.6956 | Night | 202512 | 2025-12-20 | 1.6956
2025-12-20 18:45 | 73.5062 | FALSE | FALSE | -1.7936 | -2.5011 | 0.014118 | 0.01921 | 0.2826 | 2025-12-20 21:14 | 2025-12-20 18:45 | upper | TRUE | 1 | 71.7126 | FALSE | FALSE | 0.2212 | 2.0317 | 72.6023 | 1 | 0.2826 | 0.04239 | 0.24709 | 0.97217 | 0.44488 | Extreme triggered | 73.4921 | 2.0317 | Night | 202512 | 2025-12-20 | 2.0317
2025-12-20 19:00 | 73.5062 | FALSE | FALSE | -1.8432 | -2.572 | -0.091936 | -0.12492 | 0 |  | 2025-12-20 18:45 | none | FALSE | 1 | 71.663 | FALSE | FALSE | 0.2635 | 1.9208 | 72.6306 | 2 | 0 | 0.02826 | 0.24062 | -0.11745 | 0.48377 | Extreme/elevated | 73.5981 | 1.81 | Night | 202512 | 2025-12-20 | 1.81
2025-12-20 19:15 | 73.5062 | FALSE | FALSE | -1.8836 | -2.63 | -0.18894 | -0.25639 | 0 |  | 2025-12-20 18:45 | none | FALSE | 1 | 71.6226 | FALSE | FALSE | 0.309 | 1.8257 | 72.6589 | 3 | 0 | 0.02826 | 0.24062 | -0.11745 | 0.51815 | Persistent | 73.6951 | 1.6353 | Night | 202512 | 2025-12-20 | 1.6353
2025-12-20 19:29 | 73.7888 | FALSE | FALSE | -2.2264 | -3.1111 | -0.079502 | -0.10763 | 0.2826 |  | 2025-12-20 18:45 | none | FALSE | 1 | 71.5624 | FALSE | FALSE | 0.3813 | 1.8348 | 72.7154 | 4 | 0.2826 | 0.05652 | 0.23532 | 0.96072 | 0.57647 | Persistent | 73.8683 | 1.8621 | Night | 202512 | 2025-12-20 | 1.8621
2025-12-20 19:44 | 73.5062 | FALSE | FALSE | -1.9654 | -2.7473 | -0.44028 | -0.5954 | -0.2826 |  | 2025-12-20 18:45 | none | FALSE | 1 | 71.5408 | FALSE | FALSE | 0.3988 | 1.7214 | 72.7436 | 5 | -0.2826 | 0.02826 | 0.24062 | -1.2919 | 0.60142 | Persistent | 73.9465 | 1.2679 | Night | 202512 | 2025-12-20 | 1.2679
2025-12-20 19:59 | 73.7888 | FALSE | FALSE | -2.2916 | -3.2052 | -0.28604 | -0.38614 | 0.2826 |  | 2025-12-20 18:45 | none | FALSE | 1 | 71.4972 | FALSE | FALSE | 0.4752 | 1.6939 | 72.786 | 6 | 0.2826 | 0.04239 | 0.24709 | 0.97217 | 0.64441 | Persistent | 74.0748 | 1.5561 | Night | 202512 | 2025-12-20 | 1.5561
2025-12-20 20:15 | 73.7888 | FALSE | TRUE | -2.2798 | -3.1882 | -0.41557 | -0.56004 | 0 |  | 2025-12-20 18:45 | none | FALSE | 1 | 71.509 | FALSE | FALSE | 0.5208 | 1.6495 | 72.8567 | 7 | 0 | 0.07065 | 0.20218 | -0.34945 | 0.67385 | Confirmed/Materialized Shift | 74.2044 | 1.3833 | Night | 202512 | 2025-12-20 | 1.3833
2025-12-20 20:29 | 73.7888 | FALSE | TRUE | -2.2506 | -3.1459 | -0.52759 | -0.70993 | 0 |  | 2025-12-20 18:45 | none | FALSE | 0 | 71.5382 | FALSE | FALSE | 0.4827 | 1.5984 | 72.9273 | 8 | 0 | 0.07065 | 0.20218 | -0.34945 | 0.69454 | Confirmed/Materialized Shift | 74.3164 | 1.2404 | Night | 202512 | 2025-12-20 | 1.2404
2025-12-20 20:44 | 73.7888 | FALSE | TRUE | -2.2053 | -3.0807 | -0.62363 | -0.83808 | 0 |  | 2025-12-20 18:45 | none | FALSE | 0 | 71.5835 | FALSE | FALSE | 0.4745 | 1.545 | 72.998 | 9 | 0 | 0.07065 | 0.20218 | -0.34945 | 0.70723 | Confirmed/Materialized Shift | 74.4124 | 1.1182 | Night | 202512 | 2025-12-20 | 1.1182
2025-12-20 20:59 | 73.7888 | FALSE | TRUE | -2.1449 | -2.9939 | -0.70455 | -0.94579 | 0 |  | 2025-12-20 18:45 | none | FALSE | 0 | 71.6439 | FALSE | FALSE | 0.4674 | 1.4916 | 73.0686 | 10 | 0 | 0.07065 | 0.20218 | -0.34945 | 0.71237 | Confirmed/Materialized Shift | 74.4934 | 1.011 | Night | 202512 | 2025-12-20 | 1.011
2025-12-20 21:14 | 73.7888 | FALSE | FALSE | -2.0697 | -2.8859 | -0.77068 | -1.0336 | 0 |  |  | none | FALSE | 0 | 71.7191 | FALSE | FALSE | 0.061 |  | 73.1393 | 0 | 0 | 0.07065 | 0.20218 | -0.34945 | 0.7101 | Persistence ends | 74.5595 | 0.9147 | Night | 202512 | 2025-12-20 | 0.9147
2025-12-20 21:29 | 73.7888 | FALSE | FALSE | -1.9235 | -2.6766 | -0.79385 | -1.0644 | 0 |  |  | none | FALSE | 0 | 71.8653 | FALSE | FALSE | 0.0554 |  | 73.224 | 0 | 0 | 0.08469 | 0.18555 | -0.45642 | 0.67934 | Normal | 74.5826 | 0.83145 | Night | 202512 | 2025-12-20 | 0.83145
2025-12-20 21:44 | 73.7888 | FALSE | FALSE | -1.7508 | -2.4305 | -0.79055 | -1.06 | 0 |  |  | none | FALSE | 0 | 72.038 | FALSE | FALSE | 0.0504 |  | 73.3087 | 0 | 0 | 0.08469 | 0.18555 | -0.45642 | 0.63535 | Normal | 74.5793 | 0.75573 | Night | 202512 | 2025-12-20 | 0.75573
2025-12-20 21:59 | 73.7888 | FALSE | FALSE | -1.5456 | -2.1395 | -0.75472 | -1.0125 | 0 |  |  | none | FALSE | 0 | 72.2432 | FALSE | FALSE | 0.0458 |  | 73.3933 | 0 | 0 | 0.08469 | 0.18555 | -0.45642 | 0.57509 | Normal | 74.5435 | 0.68765 | Night | 202512 | 2025-12-20 | 0.68765
2025-12-20 22:14 | 73.7888 | FALSE | FALSE | -1.296 | -1.7878 | -0.6745 | -0.90581 | 0 |  |  | none | FALSE | 0 | 72.4928 | FALSE | FALSE | 0.0421 |  | 73.478 | 0 | 0 | 0.08469 | 0.18555 | -0.45642 | 0.49263 | Normal | 74.4633 | 0.63083 | Night | 202512 | 2025-12-20 | 0.63083
2025-12-20 22:28 | 73.7888 | FALSE | FALSE | -0.97321 | -1.3365 | -0.52105 | -0.70118 | 0 |  |  | none | FALSE | 0 | 72.8156 | FALSE | FALSE | 0.0403 |  | 73.5627 | 0 | 0 | 0.08469 | 0.18555 | -0.45642 | 0.37356 | Normal | 74.3098 | 0.6052 | Night | 202512 | 2025-12-20 | 0.6052
2025-12-20 22:43 | 73.5062 | FALSE | FALSE | -0.38579 | -0.52761 | -0.61187 | -0.82554 | -0.2826 |  |  | none | FALSE | 0 | 73.1204 | FALSE | FALSE | 0.0302 |  | 73.6192 | 0 | -0.2826 | 0.05652 | 0.19665 | -1.7245 | 0.24942 | Normal | 74.1181 | -0.45322 | Night | 202512 | 2025-12-20 | 0.45322
2025-12-20 22:59 | 73.5062 | FALSE | FALSE | -0.2477 | -0.33811 | -0.5303 | -0.71626 | 0 |  |  | none | FALSE | 0 | 73.2585 | FALSE | FALSE | 0.0484 |  | 73.6475 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.1945 | Normal | 74.0365 | -0.72648 | Night | 202512 | 2025-12-20 | 0.72648
2025-12-20 23:14 | 73.5062 | FALSE | FALSE | -0.18641 | -0.25424 | -0.49727 | -0.67195 | 0 |  |  | none | FALSE | 0 | 73.3198 | FALSE | FALSE | 0.0606 |  | 73.6616 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.17092 | Normal | 74.0035 | -0.90938 | Night | 202512 | 2025-12-20 | 0.90938
2025-12-20 23:28 | 73.5062 | FALSE | FALSE | -0.11452 | -0.15604 | -0.45364 | -0.61336 | 0 |  |  | none | FALSE | 0 | 73.3917 | FALSE | FALSE | 0.0796 |  | 73.6758 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.14204 | Normal | 73.9598 | -1.1937 | Night | 202512 | 2025-12-20 | 1.1937
2025-12-20 23:43 | 73.5062 | FALSE | FALSE | -0.11452 | -0.15604 | -0.45364 | -0.61336 | 0 |  |  | none | FALSE | 0 | 73.3917 | FALSE | FALSE | 0.0796 |  | 73.6758 | 0 | 0 | 0 | 0.12967 | 0 | 0.14204 | Normal | 73.9598 | -1.1937 | Night | 202512 | 2025-12-20 | 1.1937
2025-12-20 23:58 | 73.5062 | FALSE | FALSE | -0.11452 | -0.15604 | -0.45364 | -0.61336 | 0 |  |  | none | FALSE | 0 | 73.3917 | FALSE | FALSE | 0.0796 |  | 73.6758 | 0 | 0 | 0 | 0.12967 | 0 | 0.14204 | Normal | 73.9598 | -1.1937 | Night | 202512 | 2025-12-20 | 1.1937
2025-12-21 00:13 | 73.5062 | FALSE | FALSE | -0.11452 | -0.15604 | -0.45364 | -0.61336 | 0 |  |  | none | FALSE | 0 | 73.3917 | FALSE | FALSE | 0.0796 |  | 73.6758 | 0 | 0 | 0 | 0.12967 | 0 | 0.14204 | Normal | 73.9598 | -1.1937 | Night | 202512 | 2025-12-21 | 1.1937
2025-12-21 00:28 | 73.5062 | FALSE | FALSE | -0.13306 | -0.18134 | -0.44392 | -0.60029 | 0 |  |  | none | FALSE | 0 | 73.3731 | FALSE | FALSE | 0.0718 |  | 73.6616 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14424 | Normal | 73.9501 | -1.0775 | Night | 202512 | 2025-12-21 | 1.0775
2025-12-21 00:43 | 73.5062 | FALSE | FALSE | -0.13306 | -0.18134 | -0.44392 | -0.60029 | 0 |  |  | none | FALSE | 0 | 73.3731 | FALSE | FALSE | 0.0718 |  | 73.6616 | 0 | 0 | 0 | 0.091688 | 0 | 0.14424 | Normal | 73.9501 | -1.0775 | Night | 202512 | 2025-12-21 | 1.0775
2025-12-21 00:58 | 73.5062 | FALSE | FALSE | -0.14864 | -0.20263 | -0.43124 | -0.58325 | 0 |  |  | none | FALSE | 0 | 73.3576 | FALSE | FALSE | 0.065 |  | 73.6475 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14497 | Normal | 73.9374 | -0.97468 | Night | 202512 | 2025-12-21 | 0.97468
2025-12-21 01:13 | 73.5062 | FALSE | FALSE | -0.16132 | -0.21994 | -0.41566 | -0.56229 | 0 |  |  | none | FALSE | 0 | 73.3449 | FALSE | FALSE | 0.0588 |  | 73.6334 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14424 | Normal | 73.9219 | -0.88163 | Night | 202512 | 2025-12-21 | 0.88163
2025-12-21 01:28 | 73.2236 | TRUE | FALSE | 0.049657 | 0.067769 | -0.71336 | -0.96483 | -0.2826 | 2025-12-21 05:26 | 2025-12-21 01:28 | lower | TRUE | 1 | 73.2733 | FALSE | FALSE | 0.239 | 2.2993 | 73.6051 | 1 | -0.2826 | -0.02826 | 0.086982 | -2.924 | 0.16593 | Extreme triggered | 73.937 | -2.2993 | Night | 202512 | 2025-12-21 | 2.2993
2025-12-21 01:43 | 73.2236 | FALSE | FALSE | -0.0077242 | -0.01055 | -0.71422 | -0.96598 | 0 |  | 2025-12-21 01:28 | none | FALSE | 1 | 73.2159 | FALSE | FALSE | 0.2733 | 2.1282 | 73.5768 | 2 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18049 | Extreme/elevated | 73.9378 | -1.9572 | Night | 202512 | 2025-12-21 | 1.9572
2025-12-21 01:58 | 73.2236 | FALSE | FALSE | -0.054158 | -0.074017 | -0.70414 | -0.95247 | 0 |  | 2025-12-21 01:28 | none | FALSE | 1 | 73.1694 | FALSE | FALSE | 0.3143 | 1.9903 | 73.5486 | 3 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18957 | Persistent | 73.9277 | -1.7143 | Night | 202512 | 2025-12-21 | 1.7143
2025-12-21 02:13 | 73.2236 | FALSE | FALSE | -0.091185 | -0.12469 | -0.68465 | -0.92634 | 0 |  | 2025-12-21 01:28 | none | FALSE | 1 | 73.1324 | FALSE | FALSE | 0.3591 | 1.8752 | 73.5203 | 4 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.19396 | Persistent | 73.9082 | -1.5299 | Night | 202512 | 2025-12-21 | 1.5299
2025-12-21 02:27 | 73.2236 | FALSE | FALSE | -0.11945 | -0.16339 | -0.65639 | -0.88845 | 0 |  | 2025-12-21 01:28 | none | FALSE | 1 | 73.1042 | FALSE | FALSE | 0.4066 | 1.777 | 73.4921 | 5 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.19396 | Persistent | 73.88 | -1.3842 | Night | 202512 | 2025-12-21 | 1.3842
2025-12-21 02:42 | 73.2236 | FALSE | FALSE | -0.13894 | -0.19011 | -0.61936 | -0.83875 | 0 |  | 2025-12-21 01:28 | none | FALSE | 1 | 73.0847 | FALSE | FALSE | 0.4559 | 1.692 | 73.4638 | 6 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18957 | Persistent | 73.843 | -1.2671 | Night | 202512 | 2025-12-21 | 1.2671
2025-12-21 02:57 | 73.2236 | FALSE | TRUE | -0.14902 | -0.20393 | -0.57292 | -0.77636 | 0 |  | 2025-12-21 01:28 | none | FALSE | 1 | 73.0746 | FALSE | FALSE | 0.5069 | 1.618 | 73.4356 | 7 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18049 | Confirmed/Materialized Shift | 73.7965 | -1.1743 | Night | 202512 | 2025-12-21 | 1.1743
2025-12-21 03:12 | 73.2236 | FALSE | TRUE | -0.14816 | -0.20275 | -0.51554 | -0.69914 | 0 |  | 2025-12-21 01:28 | none | FALSE | 1 | 73.0754 | FALSE | FALSE | 0.5024 | 1.5542 | 73.4073 | 8 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.16593 | Confirmed/Materialized Shift | 73.7391 | -1.1071 | Night | 202512 | 2025-12-21 | 1.1071
2025-12-21 03:27 | 72.941 | TRUE | TRUE | 0.080837 | 0.1107 | -0.76696 | -1.0405 | -0.2826 |  | 2025-12-21 01:28 | lower | TRUE | 2 | 73.0218 | TRUE | TRUE | 0.6219 | 1.6561 | 73.3649 | 9 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.17153 | Confirmed/Materialized Shift | 73.708 | -2.4713 | Night | 202512 | 2025-12-21 | 2.4713
2025-12-21 03:42 | 72.941 | FALSE | TRUE | 0.010989 | 0.015064 | -0.78029 | -1.0584 | 0 |  | 2025-12-21 01:28 | lower | TRUE | 2 | 72.952 | FALSE | TRUE | 0.5943 | 1.6962 | 73.3366 | 10 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.19233 | Confirmed/Materialized Shift | 73.7213 | -2.0571 | Night | 202512 | 2025-12-21 | 2.0571
2025-12-21 03:57 | 72.941 | FALSE | TRUE | -0.046739 | -0.064119 | -0.7815 | -1.0601 | 0 |  | 2025-12-21 01:28 | none | FALSE | 1 | 72.8943 | FALSE | FALSE | 0.5469 | 1.7033 | 73.3084 | 11 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.20706 | Confirmed/Materialized Shift | 73.7225 | -1.7743 | Night | 202512 | 2025-12-21 | 1.7743
2025-12-21 04:12 | 72.941 | FALSE | TRUE | -0.094825 | -0.13017 | -0.77306 | -1.0487 | 0 |  | 2025-12-21 01:28 | none | FALSE | 1 | 72.8462 | FALSE | FALSE | 0.5328 | 1.6916 | 73.2801 | 12 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21697 | Confirmed/Materialized Shift | 73.7141 | -1.563 | Night | 202512 | 2025-12-21 | 1.563
2025-12-21 04:27 | 72.941 | FALSE | TRUE | -0.13456 | -0.18481 | -0.75628 | -1.0262 | 0 |  | 2025-12-21 01:28 | none | FALSE | 1 | 72.8064 | FALSE | FALSE | 0.5216 | 1.6688 | 73.2519 | 13 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22271 | Confirmed/Materialized Shift | 73.6973 | -1.3958 | Night | 202512 | 2025-12-21 | 1.3958
2025-12-21 04:42 | 72.941 | FALSE | TRUE | -0.16658 | -0.22889 | -0.73178 | -0.99328 | 0 |  | 2025-12-21 01:28 | none | FALSE | 1 | 72.7744 | FALSE | FALSE | 0.5125 | 1.6395 | 73.2236 | 14 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22459 | Confirmed/Materialized Shift | 73.6728 | -1.2583 | Night | 202512 | 2025-12-21 | 1.2583
2025-12-21 04:57 | 72.941 | FALSE | TRUE | -0.19108 | -0.26265 | -0.69976 | -0.95023 | 0 |  | 2025-12-21 01:28 | none | FALSE | 1 | 72.7499 | FALSE | FALSE | 0.5047 | 1.6063 | 73.1953 | 15 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22271 | Confirmed/Materialized Shift | 73.6408 | -1.142 | Night | 202512 | 2025-12-21 | 1.142
2025-12-21 05:12 | 72.941 | FALSE | TRUE | -0.20786 | -0.28579 | -0.66002 | -0.89676 | 0 |  | 2025-12-21 01:28 | none | FALSE | 1 | 72.7331 | FALSE | FALSE | 0.498 | 1.5711 | 73.1671 | 16 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21697 | Confirmed/Materialized Shift | 73.601 | -1.042 | Night | 202512 | 2025-12-21 | 1.042
2025-12-21 05:26 | 72.941 | FALSE | FALSE | -0.2163 | -0.29742 | -0.61194 | -0.83197 | 0 |  |  | none | FALSE | 1 | 72.7247 | FALSE | FALSE | 0.0923 |  | 73.1388 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.20706 | Persistence ends | 73.5529 | -0.95538 | Night | 202512 | 2025-12-21 | 0.95538
2025-12-21 05:41 | 72.941 | FALSE | FALSE | -0.21509 | -0.29576 | -0.55421 | -0.75408 | 0 |  |  | none | FALSE | 1 | 72.7259 | FALSE | FALSE | 0.0873 |  | 73.1106 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.19233 | Normal | 73.4952 | -0.88163 | Night | 202512 | 2025-12-21 | 0.88163
2025-12-21 05:56 | 72.6584 | TRUE | FALSE | 0.021855 | 0.03007 | -0.79769 | -1.0859 | -0.2826 | 2025-12-21 07:41 | 2025-12-21 05:56 | lower | TRUE | 1 | 72.6803 | FALSE | FALSE | 0.2266 | 2.1127 | 73.0682 | 1 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.19396 | Extreme triggered | 73.4561 | -2.1127 | Night | 202512 | 2025-12-21 | 2.1127
2025-12-21 06:11 | 72.6584 | FALSE | FALSE | -0.0039263 | -0.005404 | -0.73869 | -1.0064 | 0 |  | 2025-12-21 05:56 | none | FALSE | 1 | 72.6545 | FALSE | FALSE | 0.2748 | 2.0458 | 73.0258 | 2 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.18565 | Extreme/elevated | 73.3971 | -1.9789 | Night | 202512 | 2025-12-21 | 1.9789
2025-12-21 06:26 | 72.6584 | FALSE | FALSE | -0.054176 | -0.074618 | -0.73242 | -0.99797 | 0 |  | 2025-12-21 05:56 | none | FALSE | 1 | 72.6042 | FALSE | FALSE | 0.315 | 1.9387 | 72.9975 | 3 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.19665 | Persistent | 73.3908 | -1.7245 | Night | 202512 | 2025-12-21 | 1.7245
2025-12-21 06:41 | 72.6584 | FALSE | FALSE | -0.095058 | -0.131 | -0.71678 | -0.97687 | 0 |  | 2025-12-21 05:56 | none | FALSE | 1 | 72.5633 | FALSE | FALSE | 0.3593 | 1.8369 | 72.9693 | 4 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.20296 | Persistent | 73.3752 | -1.5316 | Night | 202512 | 2025-12-21 | 1.5316
2025-12-21 06:56 | 72.6584 | FALSE | FALSE | -0.12744 | -0.1757 | -0.69264 | -0.94428 | 0 |  | 2025-12-21 05:56 | none | FALSE | 1 | 72.531 | FALSE | FALSE | 0.4062 | 1.7452 | 72.941 | 5 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.20502 | Persistent | 73.351 | -1.3784 | Night | 202512 | 2025-12-21 | 1.3784
2025-12-21 07:11 | 72.6584 | FALSE | FALSE | -0.15158 | -0.20905 | -0.66026 | -0.90053 | 0 |  | 2025-12-21 05:56 | none | FALSE | 1 | 72.5068 | FALSE | FALSE | 0.455 | 1.6632 | 72.9127 | 6 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.20296 | Persistent | 73.3187 | -1.2532 | Day | 202512 | 2025-12-21 | 1.2532
2025-12-21 07:26 | 72.3758 | TRUE | TRUE | 0.050078 | 0.069144 | -0.93902 | -1.2808 | -0.2826 |  | 2025-12-21 05:56 | lower | TRUE | 2 | 72.4259 | TRUE | TRUE | 0.6055 | 1.7435 | 72.8704 | 7 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.22224 | Confirmed/Materialized Shift | 73.3148 | -2.2253 | Day | 202512 | 2025-12-21 | 2.2253
2025-12-21 07:41 | 72.6584 | TRUE | FALSE | -0.23747 | -0.32791 | -0.60485 | -0.82559 | 0.2826 |  |  | none | FALSE | 3 | 72.4209 | TRUE | FALSE | 0.1439 |  | 72.8421 | 0 | 0.2826 | -0.02826 | 0.12638 | 2.4597 | 0.21058 | Persistence ends | 73.2633 | -0.8723 | Day | 202512 | 2025-12-21 | 0.8723
2025-12-21 07:56 | 72.6584 | FALSE | FALSE | -0.23249 | -0.321 | -0.54335 | -0.74226 | 0 |  |  | none | FALSE | 3 | 72.4259 | FALSE | FALSE | 0.1391 |  | 72.8138 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.19396 | Normal | 73.2017 | -0.80136 | Day | 202512 | 2025-12-21 | 0.80136
2025-12-21 08:11 | 72.6584 | FALSE | FALSE | -0.21467 | -0.29632 | -0.46901 | -0.64135 | 0 |  |  | none | FALSE | 3 | 72.4437 | FALSE | FALSE | 0.1353 |  | 72.7856 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.17092 | Normal | 73.1274 | -0.74404 | Day | 202512 | 2025-12-21 | 0.74404
2025-12-21 08:25 | 72.941 | TRUE | FALSE | -0.49727 | -0.68642 | -0.18641 | -0.25491 | 0.2826 |  |  | none | FALSE | 3 | 72.4437 | TRUE | FALSE | 0.1463 |  | 72.7856 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.17092 | Normal | 73.1274 | 0.90938 | Day | 202512 | 2025-12-21 | 0.90938
2025-12-21 08:30 | 72.941 | FALSE | FALSE | -0.49727 | -0.68642 | -0.18641 | -0.25491 | 0 |  |  | none | FALSE | 3 | 72.4437 | FALSE | FALSE | 0.1463 |  | 72.7856 | 0 | 0 | 0 | 0.12967 | 0 | 0.17092 | Normal | 73.1274 | 0.90938 | Day | 202512 | 2025-12-21 | 0.90938
2025-12-21 08:45 | 73.2236 | FALSE | FALSE | -0.8129 | -1.1226 | 0.034903 | 0.047689 | 0.2826 | 2025-12-21 10:06 | 2025-12-21 08:45 | upper | TRUE | 3 | 72.4107 | FALSE | FALSE | 0.2882 | 2.1794 | 72.7997 | 1 | 0.2826 | 0.01413 | 0.14424 | 1.8612 | 0.1945 | Extreme triggered | 73.1887 | 2.1794 | Day | 202512 | 2025-12-21 | 2.1794
2025-12-21 09:00 | 73.2236 | FALSE | FALSE | -0.83884 | -1.1589 | -0.019304 | -0.026356 | 0 |  | 2025-12-21 08:45 | none | FALSE | 3 | 72.3848 | FALSE | FALSE | 0.3273 | 2.0447 | 72.8138 | 2 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.21454 | Extreme/elevated | 73.2429 | 1.91 | Day | 202512 | 2025-12-21 | 1.91
2025-12-21 09:16 | 73.5062 | FALSE | FALSE | -1.1916 | -1.6478 | 0.13661 | 0.18619 | 0.2826 |  | 2025-12-21 08:45 | upper | TRUE | 3 | 72.3146 | FALSE | TRUE | 0.425 | 2.2025 | 72.8421 | 3 | 0.2826 | 0.02826 | 0.15614 | 1.6289 | 0.26375 | Persistent | 73.3696 | 2.5179 | Day | 202512 | 2025-12-21 | 2.5179
2025-12-21 09:30 | 74.0714 | TRUE | FALSE | -1.935 | -2.6824 | 0.41062 | 0.55745 | 0.5652 |  | 2025-12-21 08:45 | upper | TRUE | 4 | 72.1364 | TRUE | TRUE | 0.548 | 2.4212 | 72.8986 | 4 | 0.5652 | 0.05652 | 0.19665 | 2.5868 | 0.38108 | Persistent | 73.6608 | 3.0775 | Day | 202512 | 2025-12-21 | 3.0775
2025-12-21 09:30 | 73.7888 | FALSE | FALSE | -1.7079 | -2.3694 | -0.012305 | -0.016674 | -0.2826 |  | 2025-12-21 08:45 | none | FALSE | 3 | 72.0809 | FALSE | FALSE | 0.5029 | 2.3313 | 72.941 | 5 | -0.2826 | 0.04239 | 0.21058 | -1.5433 | 0.43005 | Persistent | 73.8011 | 1.9714 | Day | 202512 | 2025-12-21 | 1.9714
2025-12-21 09:33 | 74.0714 | FALSE | FALSE | -2.0715 | -2.8772 | 0.076212 | 0.103 | 0.2826 |  | 2025-12-21 08:45 | upper | TRUE | 2 | 71.9999 | FALSE | TRUE | 0.5435 | 2.3015 | 72.9975 | 6 | 0.2826 | 0.05652 | 0.21697 | 1.042 | 0.49883 | Persistent | 73.9952 | 2.1528 | Day | 202512 | 2025-12-21 | 2.1528
2025-12-21 09:36 | 74.0714 | FALSE | TRUE | -2.1237 | -2.9517 | -0.088986 | -0.11999 | 0 |  | 2025-12-21 08:45 | none | FALSE | 2 | 71.9477 | FALSE | FALSE | 0.5798 | 2.2355 | 73.054 | 7 | 0 | 0.05652 | 0.21697 | -0.26049 | 0.55317 | Confirmed/Materialized Shift | 74.1604 | 1.8391 | Day | 202512 | 2025-12-21 | 1.8391
2025-12-21 09:51 | 74.0714 | FALSE | TRUE | -2.1549 | -2.9964 | -0.23321 | -0.31386 | 0 |  | 2025-12-21 08:45 | none | FALSE | 2 | 71.9165 | FALSE | FALSE | 0.5644 | 2.1572 | 73.1106 | 8 | 0 | 0.05652 | 0.21697 | -0.26049 | 0.59703 | Confirmed/Materialized Shift | 74.3046 | 1.6094 | Day | 202512 | 2025-12-21 | 1.6094
2025-12-21 10:06 | 73.5062 | TRUE | FALSE | -1.5399 | -2.1397 | -0.83339 | -1.1211 | -0.5652 |  |  | none | FALSE | 2 | 71.9663 | TRUE | FALSE | 0.0968 |  | 73.153 | 0 | -0.5652 | 0.04239 | 0.2473 | -2.4569 | 0.59332 | Persistence ends | 74.3396 | 0.59538 | Day | 202512 | 2025-12-21 | 0.59538
2025-12-21 10:21 | 73.2236 | FALSE | FALSE | -1.2061 | -1.6748 | -1.1214 | -1.5083 | -0.2826 |  |  | none | FALSE | 2 | 72.0175 | FALSE | FALSE | 0.062 |  | 73.1812 | 0 | -0.2826 | 0.02826 | 0.25771 | -1.2063 | 0.58187 | Normal | 74.345 | 0.072851 | Day | 202512 | 2025-12-21 | 0.072851
2025-12-21 10:30 | 73.2236 | FALSE | FALSE | -1.1516 | -1.5978 | -1.1233 | -1.5109 | 0 |  |  | none | FALSE | 2 | 72.072 | FALSE | FALSE | 0.0588 |  | 73.2095 | 0 | 0 | 0.02826 | 0.25771 | -0.10966 | 0.56872 | Normal | 74.3469 | 0.024845 | Day | 202512 | 2025-12-21 | 0.024845
2025-12-21 10:45 | 72.6584 | FALSE | FALSE | -0.58637 | -0.81359 | -1.6885 | -2.2711 | -0.5652 |  |  | none | FALSE | 2 | 72.072 | FALSE | FALSE | 0.1217 |  | 73.2095 | 0 | -0.5652 | 0 | 0.28994 | -1.9494 | 0.56872 | Normal | 74.3469 | -0.96896 | Day | 202512 | 2025-12-21 | 0.96896
2025-12-21 11:00 | 72.6584 | FALSE | FALSE | -0.58637 | -0.81359 | -1.6885 | -2.2711 | 0 |  |  | none | FALSE | 2 | 72.072 | FALSE | FALSE | 0.1217 |  | 73.2095 | 0 | 0 | 0 | 0.28994 | 0 | 0.56872 | Normal | 74.3469 | -0.96896 | Day | 202512 | 2025-12-21 | 0.96896
2025-12-21 11:15 | 72.6584 | FALSE | FALSE | -0.58637 | -0.81359 | -1.6885 | -2.2711 | 0 |  |  | none | FALSE | 1 | 72.072 | FALSE | FALSE | 0.0932 |  | 73.2095 | 0 | 0 | 0 | 0.28994 | 0 | 0.56872 | Normal | 74.3469 | -0.96896 | Day | 202512 | 2025-12-21 | 0.96896
2025-12-21 11:29 | 72.6584 | FALSE | FALSE | -0.53505 | -0.74185 | -1.6655 | -2.2408 | 0 |  |  | none | FALSE | 1 | 72.1233 | FALSE | FALSE | 0.0971 |  | 73.2236 | 0 | 0 | 0.01413 | 0.28223 | -0.050066 | 0.55013 | Normal | 74.3239 | -1.0274 | Day | 202512 | 2025-12-21 | 1.0274
2025-12-21 11:44 | 72.941 | FALSE | FALSE | -0.77996 | -1.0809 | -1.3734 | -1.8481 | 0.2826 |  |  | none | FALSE | 1 | 72.161 | FALSE | FALSE | 0.0653 |  | 73.2377 | 0 | 0.2826 | 0.01413 | 0.28223 | 0.95125 | 0.53835 | Normal | 74.3144 | -0.55119 | Day | 202512 | 2025-12-21 | 0.55119
2025-12-21 11:59 | 72.941 | FALSE | FALSE | -0.74095 | -1.0262 | -1.3627 | -1.8339 | 0 |  |  | none | FALSE | 1 | 72.2 | FALSE | FALSE | 0.068 |  | 73.2519 | 0 | 0 | 0.01413 | 0.28223 | -0.050066 | 0.52591 | Normal | 74.3037 | -0.59109 | Day | 202512 | 2025-12-21 | 0.59109
2025-12-21 12:14 | 72.941 | FALSE | FALSE | -0.70052 | -0.9697 | -1.3505 | -1.8178 | 0 |  |  | none | FALSE | 1 | 72.2405 | FALSE | FALSE | 0.0708 |  | 73.266 | 0 | 0 | 0.01413 | 0.28223 | -0.050066 | 0.51275 | Normal | 74.2915 | -0.63381 | Day | 202512 | 2025-12-21 | 0.63381
2025-12-21 12:29 | 72.941 | FALSE | FALSE | -0.70052 | -0.9697 | -1.3505 | -1.8178 | 0 |  |  | none | FALSE | 0 | 72.2405 | FALSE | FALSE | 0.0423 |  | 73.266 | 0 | 0 | 0 | 0.27506 | 0 | 0.51275 | Normal | 74.2915 | -0.63381 | Day | 202512 | 2025-12-21 | 0.63381
2025-12-21 12:44 | 73.2236 | FALSE | FALSE | -0.95786 | -1.3255 | -1.0709 | -1.4414 | 0.2826 |  |  | none | FALSE | 0 | 72.2657 | FALSE | FALSE | 0.0074 |  | 73.2801 | 0 | 0.2826 | 0.01413 | 0.28223 | 0.95125 | 0.50719 | Normal | 74.2945 | -0.11144 | Day | 202512 | 2025-12-21 | 0.11144
2025-12-21 12:59 | 72.941 | FALSE | FALSE | -0.70052 | -0.9697 | -1.3505 | -1.8178 | -0.2826 |  |  | none | FALSE | 0 | 72.2405 | FALSE | FALSE | 0.0423 |  | 73.266 | 0 | -0.2826 | -0.01413 | 0.28223 | -0.95125 | 0.51275 | Normal | 74.2915 | -0.63381 | Day | 202512 | 2025-12-21 | 0.63381
2025-12-21 13:14 | 72.941 | FALSE | FALSE | -0.72484 | -1.0037 | -1.3466 | -1.8126 | 0 |  |  | none | FALSE | 0 | 72.2162 | FALSE | FALSE | 0.04 |  | 73.2519 | 0 | 0 | -0.01413 | 0.28223 | 0.050066 | 0.51785 | Normal | 74.2876 | -0.60029 | Day | 202512 | 2025-12-21 | 0.60029
2025-12-21 13:29 | 73.2236 | FALSE | FALSE | -1.0147 | -1.4052 | -1.0429 | -1.4043 | 0.2826 |  |  | none | FALSE | 0 | 72.2089 | FALSE | FALSE | 0.0018 |  | 73.2377 | 0 | 0.2826 | -0.01413 | 0.28223 | 1.0514 | 0.51439 | Normal | 74.2665 | -0.027469 | Day | 202512 | 2025-12-21 | 0.027469
2025-12-21 13:44 | 73.5062 | FALSE | FALSE | -1.2579 | -1.7411 | -0.66446 | -0.89585 | 0.2826 |  |  | none | FALSE | 0 | 72.2483 | FALSE | FALSE | 0.0412 |  | 73.2095 | 0 | 0.2826 | -0.02826 | 0.25771 | 1.2063 | 0.48059 | Normal | 74.1707 | 0.61742 | Day | 202512 | 2025-12-21 | 0.61742
2025-12-21 13:59 | 73.5062 | FALSE | FALSE | -1.2441 | -1.7216 | -0.62237 | -0.83959 | 0 |  |  | none | FALSE | 0 | 72.2621 | FALSE | FALSE | 0.0444 |  | 73.1953 | 0 | 0 | -0.01413 | 0.25068 | 0.056367 | 0.46662 | Normal | 74.1286 | 0.6662 | Day | 202512 | 2025-12-21 | 0.6662
2025-12-21 14:14 | 73.5062 | FALSE | FALSE | -1.1914 | -1.6475 | -0.51313 | -0.69324 | 0 |  |  | none | FALSE | 0 | 72.3148 | FALSE | FALSE | 0.0531 |  | 73.1671 | 0 | 0 | -0.02826 | 0.24084 | 0.11734 | 0.42613 | Normal | 74.0193 | 0.79582 | Day | 202512 | 2025-12-21 | 0.79582
2025-12-21 14:28 | 73.5062 | FALSE | FALSE | -1.1257 | -1.5552 | -0.39092 | -0.529 | 0 |  |  | none | FALSE | 0 | 72.3805 | FALSE | FALSE | 0.0646 |  | 73.1388 | 0 | 0 | -0.02826 | 0.24084 | 0.11734 | 0.37915 | Normal | 73.8971 | 0.96896 | Day | 202512 | 2025-12-21 | 0.96896
2025-12-21 14:43 | 73.5062 | FALSE | FALSE | -1.0414 | -1.4371 | -0.25009 | -0.33908 | 0 |  |  | none | FALSE | 0 | 72.4648 | FALSE | FALSE | 0.0817 |  | 73.1106 | 0 | 0 | -0.02826 | 0.24084 | 0.11734 | 0.32287 | Normal | 73.7563 | 1.2254 | Day | 202512 | 2025-12-21 | 1.2254
2025-12-21 14:59 | 73.5062 | FALSE | FALSE | -1.0414 | -1.4371 | -0.25009 | -0.33908 | 0 |  |  | none | FALSE | 0 | 72.4648 | FALSE | FALSE | 0.0817 |  | 73.1106 | 0 | 0 | 0 | 0.20502 | 0 | 0.32287 | Normal | 73.7563 | 1.2254 | Day | 202512 | 2025-12-21 | 1.2254
2025-12-21 15:14 | 73.5062 | FALSE | FALSE | -1.0496 | -1.4486 | -0.28661 | -0.3884 | 0 |  |  | none | FALSE | 0 | 72.4566 | FALSE | FALSE | 0.0761 |  | 73.1247 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.33406 | Normal | 73.7928 | 1.142 | Day | 202512 | 2025-12-21 | 1.142
2025-12-21 15:28 | 73.2236 | FALSE | FALSE | -0.76703 | -1.0586 | -0.56921 | -0.77137 | -0.2826 |  |  | none | FALSE | 0 | 72.4566 | FALSE | FALSE | 0.0197 |  | 73.1247 | 0 | -0.2826 | 0 | 0.20502 | -1.3784 | 0.33406 | Normal | 73.7928 | 0.29608 | Day | 202512 | 2025-12-21 | 0.29608
2025-12-21 15:43 | 73.2236 | FALSE | FALSE | -0.70256 | -0.96877 | -0.56126 | -0.76067 | 0 |  |  | none | FALSE | 0 | 72.521 | FALSE | FALSE | 0.0149 |  | 73.153 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.31596 | Normal | 73.7849 | 0.22361 | Day | 202512 | 2025-12-21 | 0.22361
2025-12-21 15:58 | 73.2236 | FALSE | FALSE | -0.63019 | -0.86811 | -0.54541 | -0.73935 | 0 |  |  | none | FALSE | 0 | 72.5934 | FALSE | FALSE | 0.0096 |  | 73.1812 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.2939 | Normal | 73.769 | 0.14423 | Day | 202512 | 2025-12-21 | 0.14423
2025-12-21 16:13 | 73.2236 | FALSE | FALSE | -0.54797 | -0.75399 | -0.51971 | -0.70475 | 0 |  |  | none | FALSE | 0 | 72.6756 | FALSE | FALSE | 0.0035 |  | 73.2095 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.26692 | Normal | 73.7433 | 0.052937 | Day | 202512 | 2025-12-21 | 0.052937
2025-12-21 16:28 | 73.2236 | FALSE | FALSE | -0.45249 | -0.62179 | -0.48075 | -0.65226 | 0 |  |  | none | FALSE | 0 | 72.7711 | FALSE | FALSE | 0.004 |  | 73.2377 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.23331 | Normal | 73.7043 | -0.060564 | Day | 202512 | 2025-12-21 | 0.060564
2025-12-21 16:43 | 72.941 | FALSE | FALSE | -0.16989 | -0.23345 | -0.76335 | -1.0357 | -0.2826 |  |  | none | FALSE | 0 | 72.7711 | FALSE | FALSE | 0.0848 |  | 73.2377 | 0 | -0.2826 | 0 | 0.15881 | -1.7795 | 0.23331 | Normal | 73.7043 | -1.2718 | Day | 202512 | 2025-12-21 | 1.2718
2025-12-21 16:58 | 72.941 | FALSE | FALSE | -0.16989 | -0.23345 | -0.76335 | -1.0357 | 0 |  |  | none | FALSE | 0 | 72.7711 | FALSE | FALSE | 0.0848 |  | 73.2377 | 0 | 0 | 0 | 0.15881 | 0 | 0.23331 | Normal | 73.7043 | -1.2718 | Day | 202512 | 2025-12-21 | 1.2718
2025-12-21 17:13 | 72.6584 | FALSE | FALSE | 0.046537 | 0.064008 | -1.0839 | -1.4698 | -0.2826 | 2025-12-21 17:46 | 2025-12-21 17:13 | lower | TRUE | 0 | 72.7049 | FALSE | FALSE | 0.2024 | 2.1794 | 73.2236 | 1 | -0.2826 | -0.01413 | 0.17092 | -1.5708 | 0.25933 | Extreme triggered | 73.7423 | -2.1794 | Day | 202512 | 2025-12-21 | 2.1794
2025-12-21 17:28 | 72.6584 | FALSE | FALSE | -0.013386 | -0.018426 | -1.1155 | -1.5121 | 0 |  | 2025-12-21 17:13 | none | FALSE | 0 | 72.645 | FALSE | FALSE | 0.2445 | 2.066 | 73.2095 | 2 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.28223 | Extreme/elevated | 73.7739 | -1.9526 | Day | 202512 | 2025-12-21 | 1.9526
2025-12-21 17:30 | 72.6584 | FALSE | FALSE | -0.092932 | -0.12807 | -1.1386 | -1.5428 | 0 |  | 2025-12-21 17:13 | none | FALSE | 0 | 72.5655 | FALSE | FALSE | 0.2846 | 1.9434 | 73.1812 | 3 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.30787 | Persistent | 73.797 | -1.6981 | Day | 202512 | 2025-12-21 | 1.6981
2025-12-21 17:31 | 72.6584 | FALSE | FALSE | -0.14224 | -0.19615 | -1.1596 | -1.5709 | 0 |  | 2025-12-21 17:13 | none | FALSE | 0 | 72.5162 | FALSE | FALSE | 0.3328 | 1.8483 | 73.1671 | 4 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.32546 | Persistent | 73.818 | -1.563 | Day | 202512 | 2025-12-21 | 1.563
2025-12-21 17:46 | 73.2236 | TRUE | FALSE | -0.68486 | -0.94413 | -0.60008 | -0.81285 | 0.5652 |  |  | none | FALSE | 1 | 72.5387 | FALSE | FALSE | 0.0374 |  | 73.1812 | 0 | 0.5652 | 0.01413 | 0.19396 | 2.8412 | 0.32123 | Persistence ends | 73.8237 | 0.13196 | Night | 202512 | 2025-12-21 | 0.13196
2025-12-21 18:01 | 73.7888 | TRUE | FALSE | -1.277 | -1.7611 | -0.11834 | -0.16012 | 0.5652 |  |  | none | FALSE | 2 | 72.5118 | TRUE | FALSE | 0.1679 |  | 73.2095 | 0 | 0.5652 | 0.02826 | 0.22271 | 2.411 | 0.34883 | Normal | 73.9071 | 1.6608 | Night | 202512 | 2025-12-21 | 1.6608
2025-12-21 18:16 | 74.0714 | FALSE | FALSE | -1.6219 | -2.2386 | 0.045477 | 0.061434 | 0.2826 | 2025-12-21 21:29 | 2025-12-21 18:16 | upper | TRUE | 2 | 72.4495 | FALSE | FALSE | 0.2553 | 2.1154 | 73.2377 | 1 | 0.2826 | 0.02826 | 0.22271 | 1.142 | 0.3941 | Extreme triggered | 74.0259 | 2.1154 | Night | 202512 | 2025-12-21 | 2.1154
2025-12-21 18:30 | 74.3522 | FALSE | FALSE | -1.9995 | -2.7636 | 0.1448 | 0.19512 | 0.2808 |  | 2025-12-21 18:16 | upper | TRUE | 2 | 72.3527 | FALSE | FALSE | 0.3256 | 2.2138 | 73.28 | 2 | 0.2808 | 0.0423 | 0.22958 | 1.0389 | 0.46369 | Extreme/elevated | 74.2074 | 2.3123 | Night | 202512 | 2025-12-21 | 2.3123
2025-12-21 18:45 | 74.3522 | FALSE | FALSE | -2.0709 | -2.865 | -0.011154 | -0.014999 | 0 |  | 2025-12-21 18:16 | none | FALSE | 2 | 72.2813 | FALSE | FALSE | 0.3605 | 2.1354 | 73.3223 | 3 | 0 | 0.0423 | 0.22958 | -0.18425 | 0.52051 | Persistent | 74.3634 | 1.9786 | Night | 202512 | 2025-12-21 | 1.9786
2025-12-21 19:00 | 74.3522 | FALSE | FALSE | -2.1244 | -2.9412 | -0.14925 | -0.20034 | 0 |  | 2025-12-21 18:16 | none | FALSE | 2 | 72.2278 | FALSE | FALSE | 0.4015 | 2.0359 | 73.3646 | 4 | 0 | 0.0423 | 0.22958 | -0.18425 | 0.56841 | Persistent | 74.5015 | 1.7374 | Night | 202512 | 2025-12-21 | 1.7374
2025-12-21 19:15 | 74.3522 | FALSE | FALSE | -2.1643 | -2.9981 | -0.27372 | -0.36679 | 0 |  | 2025-12-21 18:16 | none | FALSE | 2 | 72.1879 | FALSE | FALSE | 0.4463 | 1.9389 | 73.4069 | 5 | 0 | 0.0423 | 0.22958 | -0.18425 | 0.6095 | Persistent | 74.6259 | 1.5509 | Night | 202512 | 2025-12-21 | 1.5509
2025-12-21 19:29 | 74.6348 | FALSE | FALSE | -2.5085 | -3.478 | -0.16567 | -0.22148 | 0.2826 |  | 2025-12-21 18:16 | none | FALSE | 2 | 72.1263 | FALSE | FALSE | 0.5168 | 1.9078 | 73.4634 | 6 | 0.2826 | 0.05643 | 0.23546 | 0.96055 | 0.66855 | Persistent | 74.8005 | 1.7522 | Night | 202512 | 2025-12-21 | 1.7522
2025-12-21 19:44 | 74.6348 | FALSE | TRUE | -2.5513 | -3.5394 | -0.32129 | -0.42864 | 0 |  | 2025-12-21 18:16 | none | FALSE | 2 | 72.0835 | FALSE | FALSE | 0.5607 | 1.8571 | 73.5198 | 7 | 0 | 0.05643 | 0.23546 | -0.23966 | 0.71815 | Confirmed/Materialized Shift | 74.9561 | 1.5526 | Night | 202512 | 2025-12-21 | 1.5526
2025-12-21 19:59 | 74.6348 | FALSE | TRUE | -2.5562 | -3.5464 | -0.46726 | -0.62217 | 0 |  | 2025-12-21 18:16 | none | FALSE | 2 | 72.0786 | FALSE | FALSE | 0.5493 | 1.7976 | 73.5904 | 8 | 0 | 0.07056 | 0.22215 | -0.31763 | 0.75586 | Confirmed/Materialized Shift | 75.1021 | 1.3818 | Night | 202512 | 2025-12-21 | 1.3818
2025-12-21 20:15 | 74.6348 | FALSE | TRUE | -2.5441 | -3.5291 | -0.59635 | -0.79269 | 0 |  | 2025-12-21 18:16 | none | FALSE | 1 | 72.0907 | FALSE | FALSE | 0.5113 | 1.7357 | 73.6609 | 9 | 0 | 0.07056 | 0.22215 | -0.31763 | 0.78512 | Confirmed/Materialized Shift | 75.2311 | 1.2404 | Night | 202512 | 2025-12-21 | 1.2404
2025-12-21 20:29 | 74.9174 | FALSE | TRUE | -2.8233 | -3.9162 | -0.47973 | -0.63627 | 0.2826 |  | 2025-12-21 18:16 | none | FALSE | 0 | 72.0941 | FALSE | FALSE | 0.4946 | 1.7041 | 73.7456 | 10 | 0.2826 | 0.08469 | 0.22637 | 0.87428 | 0.82577 | Confirmed/Materialized Shift | 75.3971 | 1.419 | Night | 202512 | 2025-12-21 | 1.419
2025-12-21 20:44 | 74.9174 | FALSE | TRUE | -2.7986 | -3.8805 | -0.62434 | -0.82649 | 0 |  | 2025-12-21 18:16 | none | FALSE | 0 | 72.1188 | FALSE | FALSE | 0.4847 | 1.6646 | 73.8303 | 11 | 0 | 0.08469 | 0.22637 | -0.37412 | 0.85573 | Confirmed/Materialized Shift | 75.5417 | 1.2704 | Night | 202512 | 2025-12-21 | 1.2704
2025-12-21 20:59 | 74.9174 | FALSE | TRUE | -2.7546 | -3.8172 | -0.74977 | -0.99089 | 0 |  | 2025-12-21 18:16 | none | FALSE | 0 | 72.1628 | FALSE | FALSE | 0.4763 | 1.6213 | 73.915 | 12 | 0 | 0.08469 | 0.22637 | -0.37412 | 0.8761 | Confirmed/Materialized Shift | 75.6672 | 1.1442 | Night | 202512 | 2025-12-21 | 1.1442
2025-12-21 21:14 | 74.9174 | FALSE | TRUE | -2.6474 | -3.6632 | -0.84022 | -1.1091 | 0 |  | 2025-12-21 18:16 | none | FALSE | 0 | 72.27 | FALSE | FALSE | 0.4691 | 1.5763 | 74.0138 | 13 | 0 | 0.09882 | 0.2105 | -0.46945 | 0.87191 | Confirmed/Materialized Shift | 75.7576 | 1.0363 | Night | 202512 | 2025-12-21 | 1.0363
2025-12-21 21:29 | 74.9174 | FALSE | FALSE | -2.5163 | -3.4755 | -0.90676 | -1.1959 | 0 |  |  | none | FALSE | 0 | 72.4011 | FALSE | FALSE | 0.0627 |  | 74.1126 | 0 | 0 | 0.09882 | 0.2105 | -0.46945 | 0.85577 | Persistence ends | 75.8242 | 0.94041 | Night | 202512 | 2025-12-21 | 0.94041
2025-12-21 21:44 | 74.9174 | FALSE | FALSE | -2.294 | -3.1587 | -0.9103 | -1.2005 | 0 |  |  | none | FALSE | 0 | 72.6234 | FALSE | FALSE | 0.0576 |  | 74.2256 | 0 | 0 | 0.11295 | 0.19224 | -0.58754 | 0.80106 | Normal | 75.8277 | 0.86364 | Night | 202512 | 2025-12-21 | 0.86364
2025-12-21 21:59 | 74.9174 | FALSE | FALSE | -2.0269 | -2.7808 | -0.86915 | -1.1468 | 0 |  |  | none | FALSE | 0 | 72.8905 | FALSE | FALSE | 0.0533 |  | 74.3385 | 0 | 0 | 0.11295 | 0.19224 | -0.58754 | 0.72402 | Normal | 75.7866 | 0.79954 | Night | 202512 | 2025-12-21 | 0.79954
2025-12-21 22:14 | 74.9174 | FALSE | FALSE | -1.6986 | -2.3198 | -0.76669 | -1.013 | 0 |  |  | none | FALSE | 0 | 73.2188 | FALSE | FALSE | 0.0504 |  | 74.4515 | 0 | 0 | 0.11295 | 0.19224 | -0.58754 | 0.61631 | Normal | 75.6841 | 0.756 | Night | 202512 | 2025-12-21 | 0.756
2025-12-21 22:28 | 74.9174 | FALSE | FALSE | -1.2665 | -1.7196 | -0.56052 | -0.74262 | 0 |  |  | none | FALSE | 0 | 73.6509 | FALSE | FALSE | 0.0515 |  | 74.5644 | 0 | 0 | 0.11295 | 0.19224 | -0.58754 | 0.45675 | Normal | 75.4779 | 0.77281 | Night | 202512 | 2025-12-21 | 0.77281
2025-12-21 22:44 | 74.9174 | FALSE | FALSE | -0.94062 | -1.2715 | -0.40404 | -0.53642 | 0 |  |  | none | FALSE | 0 | 73.9768 | FALSE | FALSE | 0.0532 |  | 74.6491 | 0 | 0 | 0.08469 | 0.16132 | -0.52499 | 0.33616 | Normal | 75.3214 | 0.79809 | Night | 202512 | 2025-12-21 | 0.79809
2025-12-21 22:59 | 74.9174 | FALSE | FALSE | -0.75771 | -1.0217 | -0.33399 | -0.44383 | 0 |  |  | none | FALSE | 0 | 74.1597 | FALSE | FALSE | 0.0518 |  | 74.7055 | 0 | 0 | 0.05643 | 0.11579 | -0.48734 | 0.27293 | Normal | 75.2514 | 0.77626 | Night | 202512 | 2025-12-21 | 0.77626
2025-12-21 23:14 | 74.9174 | FALSE | FALSE | -0.63347 | -0.85276 | -0.29435 | -0.39136 | 0 |  |  | none | FALSE | 0 | 74.2839 | FALSE | FALSE | 0.0487 |  | 74.7478 | 0 | 0 | 0.0423 | 0.10331 | -0.40945 | 0.23195 | Normal | 75.2117 | 0.73101 | Night | 202512 | 2025-12-21 | 0.73101
2025-12-21 23:28 | 74.9174 | FALSE | FALSE | -0.57135 | -0.7685 | -0.28875 | -0.38395 | 0 |  |  | none | FALSE | 0 | 74.346 | FALSE | FALSE | 0.0438 |  | 74.7761 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.21503 | Normal | 75.2062 | 0.65713 | Night | 202512 | 2025-12-21 | 0.65713
2025-12-21 23:43 | 74.9174 | FALSE | FALSE | -0.49769 | -0.66876 | -0.27161 | -0.36124 | 0 |  |  | none | FALSE | 0 | 74.4197 | FALSE | FALSE | 0.0392 |  | 74.8044 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.19233 | Normal | 75.189 | 0.58775 | Night | 202512 | 2025-12-21 | 0.58775
2025-12-21 23:58 | 74.9174 | FALSE | FALSE | -0.40765 | -0.5471 | -0.23809 | -0.31679 | 0 |  |  | none | FALSE | 0 | 74.5098 | FALSE | FALSE | 0.035 |  | 74.8326 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.16143 | Normal | 75.1555 | 0.52517 | Night | 202512 | 2025-12-21 | 0.52517
2025-12-22 00:13 | 74.9174 | FALSE | FALSE | -0.28847 | -0.38654 | -0.17543 | -0.23362 | 0 |  |  | none | FALSE | 0 | 74.6289 | FALSE | FALSE | 0.0325 |  | 74.8609 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.11598 | Normal | 75.0928 | 0.48734 | Night | 202512 | 2025-12-22 | 0.48734
2025-12-22 00:28 | 74.9174 | FALSE | FALSE | -0.24945 | -0.33408 | -0.16467 | -0.21932 | 0 |  |  | none | FALSE | 0 | 74.668 | FALSE | FALSE | 0.0273 |  | 74.875 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.10353 | Normal | 75.0821 | 0.40945 | Night | 202512 | 2025-12-22 | 0.40945
2025-12-22 00:43 | 74.9174 | FALSE | FALSE | -0.20222 | -0.27066 | -0.1457 | -0.19411 | 0 |  |  | none | FALSE | 0 | 74.7152 | FALSE | FALSE | 0.0217 |  | 74.8891 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.086982 | Normal | 75.0631 | 0.32489 | Night | 202512 | 2025-12-22 | 0.32489
2025-12-22 00:58 | 74.9174 | FALSE | FALSE | -0.14051 | -0.18791 | -0.11225 | -0.14961 | 0 |  |  | none | FALSE | 0 | 74.7769 | FALSE | FALSE | 0.0149 |  | 74.9033 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.063191 | Normal | 75.0297 | 0.22361 | Night | 202512 | 2025-12-22 | 0.22361
2025-12-22 01:13 | 74.6348 | TRUE | FALSE | 0.14209 | 0.19002 | -0.39485 | -0.52626 | -0.2826 | 2025-12-22 03:57 | 2025-12-22 01:13 | lower | TRUE | 1 | 74.7769 | FALSE | FALSE | 0.3689 | 4.2485 | 74.9033 | 1 | -0.2826 | 0 | 0.091688 | -3.0822 | 0.063191 | Extreme triggered | 75.0297 | -4.2485 | Night | 202512 | 2025-12-22 | 4.2485
2025-12-22 01:28 | 74.6348 | FALSE | FALSE | 0.080375 | 0.10758 | -0.4283 | -0.57059 | 0 |  | 2025-12-22 01:13 | lower | TRUE | 1 | 74.7152 | FALSE | FALSE | 0.3378 | 3.5863 | 74.8891 | 2 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.086982 | Extreme/elevated | 75.0631 | -2.924 | Night | 202512 | 2025-12-22 | 2.924
2025-12-22 01:43 | 74.6348 | FALSE | FALSE | 0.03315 | 0.044397 | -0.44727 | -0.59571 | 0 |  | 2025-12-22 01:13 | lower | TRUE | 1 | 74.668 | FALSE | TRUE | 0.3547 | 3.1643 | 74.875 | 3 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.10353 | Persistent | 75.0821 | -2.3202 | Night | 202512 | 2025-12-22 | 2.3202
2025-12-22 01:58 | 74.3522 | TRUE | FALSE | 0.18362 | 0.24635 | -0.80548 | -1.0717 | -0.2826 |  | 2025-12-22 01:13 | lower | TRUE | 2 | 74.5358 | TRUE | TRUE | 0.4978 | 3.1685 | 74.8468 | 4 | -0.2826 | -0.02826 | 0.086982 | -2.924 | 0.15546 | Persistent | 75.1577 | -3.1811 | Night | 202512 | 2025-12-22 | 3.1811
2025-12-22 02:13 | 74.3522 | FALSE | FALSE | 0.087142 | 0.11706 | -0.84544 | -1.1243 | 0 |  | 2025-12-22 01:13 | lower | TRUE | 2 | 74.4393 | FALSE | TRUE | 0.5068 | 3.0267 | 74.8185 | 5 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18957 | Persistent | 75.1976 | -2.4597 | Night | 202512 | 2025-12-22 | 2.4597
2025-12-22 02:27 | 74.3522 | FALSE | FALSE | 0.0089558 | 0.012044 | -0.8671 | -1.1528 | 0 |  | 2025-12-22 01:13 | lower | TRUE | 2 | 74.3612 | FALSE | TRUE | 0.5361 | 2.8626 | 74.7902 | 6 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21454 | Persistent | 75.2193 | -2.0417 | Night | 202512 | 2025-12-22 | 2.0417
2025-12-22 02:28 | 74.3522 | FALSE | TRUE | -0.056847 | -0.076514 | -0.87639 | -1.165 | 0 |  | 2025-12-22 01:13 | none | FALSE | 2 | 74.2954 | FALSE | FALSE | 0.5742 | 2.7045 | 74.762 | 7 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.23331 | Confirmed/Materialized Shift | 75.2286 | -1.7563 | Night | 202512 | 2025-12-22 | 1.7563
2025-12-22 02:43 | 74.3522 | FALSE | TRUE | -0.11309 | -0.15234 | -0.87611 | -1.1646 | 0 |  | 2025-12-22 01:13 | none | FALSE | 2 | 74.2391 | FALSE | FALSE | 0.56 | 2.5593 | 74.7337 | 8 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.2473 | Confirmed/Materialized Shift | 75.2283 | -1.5427 | Night | 202512 | 2025-12-22 | 1.5427
2025-12-22 02:58 | 74.3522 | FALSE | TRUE | -0.16135 | -0.21747 | -0.86785 | -1.1537 | 0 |  | 2025-12-22 01:13 | none | FALSE | 2 | 74.1909 | FALSE | FALSE | 0.5487 | 2.4275 | 74.7054 | 9 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.2573 | Confirmed/Materialized Shift | 75.22 | -1.3729 | Night | 202512 | 2025-12-22 | 1.3729
2025-12-22 03:13 | 74.3522 | FALSE | TRUE | -0.20251 | -0.27311 | -0.85249 | -1.1336 | 0 |  | 2025-12-22 01:13 | none | FALSE | 2 | 74.1497 | FALSE | FALSE | 0.5393 | 2.3079 | 74.6772 | 10 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.26375 | Confirmed/Materialized Shift | 75.2047 | -1.2322 | Night | 202512 | 2025-12-22 | 1.2322
2025-12-22 03:27 | 74.3522 | FALSE | TRUE | -0.23711 | -0.31992 | -0.83057 | -1.1047 | 0 |  | 2025-12-22 01:13 | none | FALSE | 1 | 74.1151 | FALSE | FALSE | 0.5027 | 2.1992 | 74.6489 | 11 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.26692 | Confirmed/Materialized Shift | 75.1828 | -1.1117 | Night | 202512 | 2025-12-22 | 1.1117
2025-12-22 03:42 | 74.3522 | FALSE | TRUE | -0.26537 | -0.35819 | -0.80231 | -1.0675 | 0 |  | 2025-12-22 01:13 | none | FALSE | 1 | 74.0868 | FALSE | FALSE | 0.4956 | 2.0997 | 74.6207 | 12 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.26692 | Confirmed/Materialized Shift | 75.1545 | -1.0058 | Night | 202512 | 2025-12-22 | 1.0058
2025-12-22 03:57 | 74.3522 | FALSE | FALSE | -0.28729 | -0.38789 | -0.76771 | -1.022 | 0 |  |  | none | FALSE | 1 | 74.0649 | FALSE | FALSE | 0.0893 |  | 74.5924 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.26375 | Persistence ends | 75.1199 | -0.91074 | Night | 202512 | 2025-12-22 | 0.91074
2025-12-22 04:12 | 74.3522 | FALSE | FALSE | -0.30265 | -0.40871 | -0.72655 | -0.96771 | 0 |  |  | none | FALSE | 0 | 74.0496 | FALSE | FALSE | 0.0549 |  | 74.5641 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.2573 | Normal | 75.0787 | -0.82375 | Night | 202512 | 2025-12-22 | 0.82375
2025-12-22 04:27 | 74.3522 | FALSE | FALSE | -0.31091 | -0.41992 | -0.67829 | -0.90402 | 0 |  |  | none | FALSE | 0 | 74.0413 | FALSE | FALSE | 0.0495 |  | 74.5359 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.2473 | Normal | 75.0305 | -0.74278 | Night | 202512 | 2025-12-22 | 0.74278
2025-12-22 04:42 | 74.3522 | FALSE | FALSE | -0.31119 | -0.42029 | -0.62205 | -0.82968 | 0 |  |  | none | FALSE | 0 | 74.041 | FALSE | FALSE | 0.0444 |  | 74.5076 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.23331 | Normal | 74.9742 | -0.6662 | Night | 202512 | 2025-12-22 | 0.6662
2025-12-22 04:57 | 74.0714 | TRUE | FALSE | -0.069654 | -0.094125 | -0.85751 | -1.1444 | -0.2808 |  |  | none | FALSE | 1 | 74.0017 | FALSE | FALSE | 0.1419 |  | 74.4653 | 0 | -0.2808 | -0.0423 | 0.10331 | -2.3086 | 0.23179 | Normal | 74.9289 | -1.6995 | Night | 202512 | 2025-12-22 | 1.6995
2025-12-22 05:12 | 74.0714 | FALSE | FALSE | -0.092241 | -0.12468 | -0.7955 | -1.0626 | 0 |  |  | none | FALSE | 1 | 73.9792 | FALSE | FALSE | 0.1342 |  | 74.423 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.22194 | Normal | 74.8669 | -1.5844 | Night | 202512 | 2025-12-22 | 1.5844
2025-12-22 05:27 | 74.0714 | FALSE | FALSE | -0.095719 | -0.12939 | -0.71438 | -0.95523 | 0 |  |  | none | FALSE | 1 | 73.9757 | FALSE | FALSE | 0.1304 |  | 74.3807 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.20252 | Normal | 74.7858 | -1.5274 | Night | 202512 | 2025-12-22 | 1.5274
2025-12-22 05:42 | 74.0714 | FALSE | FALSE | -0.073617 | -0.099485 | -0.60768 | -0.81372 | 0 |  |  | none | FALSE | 1 | 73.9978 | FALSE | FALSE | 0.1331 |  | 74.3384 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.17032 | Normal | 74.6791 | -1.5678 | Night | 202512 | 2025-12-22 | 1.5678
2025-12-22 05:57 | 74.0714 | FALSE | FALSE | -0.091623 | -0.12385 | -0.56934 | -0.76278 | 0 |  |  | none | FALSE | 1 | 73.9798 | FALSE | FALSE | 0.1249 |  | 74.3103 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.16524 | Normal | 74.6407 | -1.4455 | Night | 202512 | 2025-12-22 | 1.4455
2025-12-22 06:12 | 74.0714 | FALSE | FALSE | -0.098688 | -0.13341 | -0.52007 | -0.69722 | 0 |  |  | none | FALSE | 1 | 73.9727 | FALSE | FALSE | 0.1194 |  | 74.2821 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.15469 | Normal | 74.5915 | -1.362 | Night | 202512 | 2025-12-22 | 1.362
2025-12-22 06:26 | 74.0714 | FALSE | FALSE | -0.092305 | -0.12477 | -0.45734 | -0.61365 | 0 |  |  | none | FALSE | 1 | 73.9791 | FALSE | FALSE | 0.1171 |  | 74.2539 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.13741 | Normal | 74.5287 | -1.3283 | Night | 202512 | 2025-12-22 | 1.3283
2025-12-22 06:41 | 74.0714 | FALSE | FALSE | -0.11379 | -0.15386 | -0.45075 | -0.60486 | 0 |  |  | none | FALSE | 1 | 73.9576 | FALSE | FALSE | 0.1082 |  | 74.2399 | 0 | 0 | -0.01404 | 0.062789 | 0.22361 | 0.14114 | Normal | 74.5222 | -1.1937 | Night | 202512 | 2025-12-22 | 1.1937
2025-12-22 06:56 | 74.0714 | FALSE | FALSE | -0.13221 | -0.17881 | -0.44109 | -0.59197 | 0 |  |  | none | FALSE | 1 | 73.9392 | FALSE | FALSE | 0.1004 |  | 74.2258 | 0 | 0 | -0.01404 | 0.062789 | 0.22361 | 0.14333 | Normal | 74.5125 | -1.0775 | Night | 202512 | 2025-12-22 | 1.0775
2025-12-22 07:12 | 74.0714 | FALSE | FALSE | -0.14769 | -0.19979 | -0.42849 | -0.57516 | 0 |  |  | none | FALSE | 1 | 73.9237 | FALSE | FALSE | 0.0936 |  | 74.2118 | 0 | 0 | -0.01404 | 0.062789 | 0.22361 | 0.14405 | Normal | 74.4999 | -0.97468 | Day | 202512 | 2025-12-22 | 0.97468
2025-12-22 07:26 | 74.0714 | FALSE | FALSE | -0.16029 | -0.21687 | -0.41301 | -0.55449 | 0 |  |  | none | FALSE | 0 | 73.9111 | FALSE | FALSE | 0.0588 |  | 74.1978 | 0 | 0 | -0.01404 | 0.062789 | 0.22361 | 0.14333 | Normal | 74.4844 | -0.88163 | Day | 202512 | 2025-12-22 | 0.88163
2025-12-22 07:30 | 74.0714 | FALSE | FALSE | -0.16995 | -0.22997 | -0.39459 | -0.5299 | 0 |  |  | none | FALSE | 0 | 73.9014 | FALSE | FALSE | 0.0531 |  | 74.1837 | 0 | 0 | -0.01404 | 0.062789 | 0.22361 | 0.14114 | Normal | 74.466 | -0.79582 | Day | 202512 | 2025-12-22 | 0.79582
2025-12-22 07:45 | 74.0714 | FALSE | FALSE | -0.17654 | -0.23891 | -0.3731 | -0.50119 | 0 |  |  | none | FALSE | 0 | 73.8949 | FALSE | FALSE | 0.0477 |  | 74.1697 | 0 | 0 | -0.01404 | 0.062789 | 0.22361 | 0.13741 | Normal | 74.4445 | -0.71522 | Day | 202512 | 2025-12-22 | 0.71522
2025-12-22 08:01 | 74.0714 | FALSE | FALSE | -0.1798 | -0.24333 | -0.34828 | -0.468 | 0 |  |  | none | FALSE | 0 | 73.8916 | FALSE | FALSE | 0.0425 |  | 74.1556 | 0 | 0 | -0.01404 | 0.062789 | 0.22361 | 0.13202 | Normal | 74.4197 | -0.63808 | Day | 202512 | 2025-12-22 | 0.63808
2025-12-22 08:16 | 74.0714 | FALSE | FALSE | -0.1793 | -0.24265 | -0.3197 | -0.42975 | 0 |  |  | none | FALSE | 0 | 73.8921 | FALSE | FALSE | 0.0375 |  | 74.1416 | 0 | 0 | -0.01404 | 0.062789 | 0.22361 | 0.12475 | Normal | 74.3911 | -0.56273 | Day | 202512 | 2025-12-22 | 0.56273
2025-12-22 08:30 | 74.0714 | FALSE | FALSE | -0.17432 | -0.23589 | -0.28664 | -0.38548 | 0 |  |  | none | FALSE | 0 | 73.8971 | FALSE | FALSE | 0.0325 |  | 74.1276 | 0 | 0 | -0.01404 | 0.062789 | 0.22361 | 0.11524 | Normal | 74.358 | -0.48734 | Day | 202512 | 2025-12-22 | 0.48734
2025-12-22 08:30 | 74.0714 | FALSE | FALSE | -0.16362 | -0.22139 | -0.24786 | -0.33351 | 0 |  |  | none | FALSE | 0 | 73.9078 | FALSE | FALSE | 0.0273 |  | 74.1135 | 0 | 0 | -0.01404 | 0.062789 | 0.22361 | 0.10287 | Normal | 74.3193 | -0.40945 | Day | 202512 | 2025-12-22 | 0.40945
2025-12-22 08:33 | 74.3522 | TRUE | FALSE | -0.44442 | -0.60132 | 0.032939 | 0.044321 | 0.2808 | 2025-12-22 10:59 | 2025-12-22 08:33 | upper | TRUE | 1 | 73.9078 | FALSE | FALSE | 0.2404 | 2.3202 | 74.1135 | 1 | 0.2808 | 0 | 0.091104 | 3.0822 | 0.10287 | Extreme triggered | 74.3193 | 2.3202 | Day | 202512 | 2025-12-22 | 2.3202
2025-12-22 08:48 | 73.7888 | TRUE | FALSE | 0.074754 | 0.10121 | -0.51835 | -0.69757 | -0.5634 |  | 2025-12-22 08:33 | lower | TRUE | 2 | 73.8636 | TRUE | FALSE | 0.3497 | 2.4971 | 74.0854 | 2 | -0.5634 | -0.02817 | 0.15547 | -3.4427 | 0.1109 | Extreme/elevated | 74.3071 | -2.6741 | Day | 202512 | 2025-12-22 | 2.6741
2025-12-22 09:03 | 73.5062 | FALSE | FALSE | 0.22495 | 0.30509 | -0.84875 | -1.1415 | -0.2826 |  | 2025-12-22 08:33 | lower | TRUE | 2 | 73.7311 | FALSE | TRUE | 0.4581 | 2.8122 | 74.043 | 3 | -0.2826 | -0.0423 | 0.16531 | -1.4537 | 0.15595 | Persistent | 74.355 | -3.4424 | Day | 202512 | 2025-12-22 | 3.4424
2025-12-22 09:18 | 72.941 | TRUE | FALSE | 0.46299 | 0.63075 | -1.6281 | -2.1833 | -0.5652 |  | 2025-12-22 08:33 | lower | TRUE | 3 | 73.404 | TRUE | TRUE | 0.5536 | 3.0066 | 73.9865 | 4 | -0.5652 | -0.05652 | 0.19624 | -2.5921 | 0.29127 | Persistent | 74.5691 | -3.5896 | Day | 202512 | 2025-12-22 | 3.5896
2025-12-22 09:30 | 72.6584 | FALSE | FALSE | 0.42792 | 0.5855 | -2.087 | -2.7922 | -0.2826 |  | 2025-12-22 08:33 | lower | TRUE | 3 | 73.0863 | FALSE | TRUE | 0.5735 | 3.0116 | 73.9159 | 5 | -0.2826 | -0.07065 | 0.20204 | -1.049 | 0.41478 | Persistent | 74.7454 | -3.0317 | Day | 202512 | 2025-12-22 | 3.0317
2025-12-22 09:45 | 72.6584 | FALSE | FALSE | 0.18935 | 0.25993 | -2.1843 | -2.9185 | 0 |  | 2025-12-22 08:33 | lower | TRUE | 3 | 72.8478 | FALSE | TRUE | 0.5872 | 2.9063 | 73.8452 | 6 | 0 | -0.07065 | 0.20204 | 0.34968 | 0.49874 | Persistent | 74.8427 | -2.3797 | Day | 202512 | 2025-12-22 | 2.3797
2025-12-22 10:00 | 72.941 | FALSE | TRUE | -0.22134 | -0.30438 | -1.9168 | -2.5605 | 0.2826 |  | 2025-12-22 08:33 | none | FALSE | 3 | 72.7197 | FALSE | FALSE | 0.5914 | 2.7177 | 73.7887 | 7 | 0.2826 | -0.05652 | 0.2166 | 1.5656 | 0.53453 | Confirmed/Materialized Shift | 74.8578 | -1.5859 | Day | 202512 | 2025-12-22 | 1.5859
2025-12-22 10:15 | 72.6584 | FALSE | TRUE | -0.11252 | -0.1551 | -2.2318 | -2.9801 | -0.2826 |  | 2025-12-22 08:33 | none | FALSE | 3 | 72.5459 | FALSE | FALSE | 0.6062 | 2.6039 | 73.7181 | 8 | -0.2826 | -0.07065 | 0.22188 | -0.95527 | 0.58609 | Confirmed/Materialized Shift | 74.8902 | -1.808 | Day | 202512 | 2025-12-22 | 1.808
2025-12-22 10:29 | 72.6584 | FALSE | TRUE | -0.26123 | -0.36083 | -2.2392 | -2.9897 | 0 |  | 2025-12-22 08:33 | none | FALSE | 3 | 72.3972 | FALSE | FALSE | 0.5912 | 2.4904 | 73.6474 | 9 | 0 | -0.07065 | 0.22188 | 0.31842 | 0.62512 | Confirmed/Materialized Shift | 74.8976 | -1.5821 | Day | 202512 | 2025-12-22 | 1.5821
2025-12-22 10:44 | 72.6584 | FALSE | TRUE | -0.38937 | -0.53878 | -2.2261 | -2.9727 | 0 |  | 2025-12-22 08:33 | none | FALSE | 3 | 72.269 | FALSE | FALSE | 0.5793 | 2.3818 | 73.5768 | 10 | 0 | -0.07065 | 0.22188 | 0.31842 | 0.65386 | Confirmed/Materialized Shift | 74.8845 | -1.4045 | Day | 202512 | 2025-12-22 | 1.4045
2025-12-22 10:59 | 72.941 | FALSE | FALSE | -0.73616 | -1.0196 | -1.8946 | -2.5317 | 0.2826 |  |  | none | FALSE | 2 | 72.2048 | FALSE | FALSE | 0.1159 |  | 73.5202 | 0 | 0.2826 | -0.05652 | 0.23521 | 1.4418 | 0.6577 | Persistence ends | 74.8356 | -0.8807 | Day | 202512 | 2025-12-22 | 0.8807
2025-12-22 11:14 | 72.6584 | FALSE | FALSE | -0.55108 | -0.76425 | -2.1335 | -2.8525 | -0.2826 |  |  | none | FALSE | 1 | 72.1073 | FALSE | FALSE | 0.1072 |  | 73.4496 | 0 | -0.2826 | -0.07065 | 0.24007 | -0.88286 | 0.67114 | Normal | 74.7919 | -1.1789 | Day | 202512 | 2025-12-22 | 1.1789
2025-12-22 11:29 | 72.6584 | FALSE | FALSE | -0.63263 | -0.87833 | -2.0737 | -2.7749 | 0 |  |  | none | FALSE | 1 | 72.0258 | FALSE | FALSE | 0.0996 |  | 73.3789 | 0 | 0 | -0.07065 | 0.24007 | 0.29429 | 0.67658 | Normal | 74.7321 | -1.065 | Day | 202512 | 2025-12-22 | 1.065
2025-12-22 11:44 | 72.941 | FALSE | FALSE | -0.94411 | -1.3113 | -1.707 | -2.2867 | 0.2826 |  |  | none | FALSE | 0 | 71.9969 | FALSE | FALSE | 0.0384 |  | 73.3224 | 0 | 0.2826 | -0.05652 | 0.25245 | 1.3433 | 0.66277 | Normal | 74.648 | -0.5755 | Day | 202512 | 2025-12-22 | 0.5755
2025-12-22 11:59 | 73.2236 | FALSE | FALSE | -1.2216 | -1.6967 | -1.3345 | -1.7899 | 0.2826 |  |  | none | FALSE | 0 | 72.002 | FALSE | FALSE | 0.0059 |  | 73.28 | 0 | 0.2826 | -0.04239 | 0.26345 | 1.2336 | 0.63903 | Normal | 74.5581 | -0.088306 | Day | 202512 | 2025-12-22 | 0.088306
2025-12-22 12:14 | 73.2236 | FALSE | FALSE | -1.2085 | -1.6782 | -1.2366 | -1.6608 | 0 |  |  | none | FALSE | 0 | 72.0151 | FALSE | FALSE | 0.0015 |  | 73.2376 | 0 | 0 | -0.04239 | 0.26345 | 0.16091 | 0.61129 | Normal | 74.4602 | -0.022968 | Day | 202512 | 2025-12-22 | 0.022968
2025-12-22 12:29 | 73.2236 | FALSE | FALSE | -1.1863 | -1.6468 | -1.1296 | -1.5192 | 0 |  |  | none | FALSE | 0 | 72.0373 | FALSE | FALSE | 0.0033 |  | 73.1953 | 0 | 0 | -0.04239 | 0.26345 | 0.16091 | 0.57897 | Normal | 74.3532 | 0.048966 | Day | 202512 | 2025-12-22 | 0.048966
2025-12-22 12:44 | 73.2236 | FALSE | FALSE | -1.1532 | -1.6002 | -1.0118 | -1.3629 | 0 |  |  | none | FALSE | 0 | 72.0704 | FALSE | FALSE | 0.0087 |  | 73.1529 | 0 | 0 | -0.04239 | 0.26345 | 0.16091 | 0.54125 | Normal | 74.2354 | 0.1307 | Day | 202512 | 2025-12-22 | 0.1307
2025-12-22 12:59 | 73.5062 | FALSE | FALSE | -1.3901 | -1.9276 | -0.62692 | -0.84567 | 0.2826 |  |  | none | FALSE | 0 | 72.1161 | FALSE | FALSE | 0.0505 |  | 73.1246 | 0 | 0.2826 | -0.02826 | 0.27324 | 1.1377 | 0.50426 | Normal | 74.1331 | 0.75675 | Day | 202512 | 2025-12-22 | 0.75675
2025-12-22 13:14 | 73.2236 | FALSE | FALSE | -1.0485 | -1.4527 | -0.76574 | -1.0349 | -0.2826 |  |  | none | FALSE | 0 | 72.1751 | FALSE | FALSE | 0.0208 |  | 73.0822 | 0 | -0.2826 | -0.04239 | 0.27895 | -0.86113 | 0.45356 | Normal | 73.9893 | 0.31173 | Day | 202512 | 2025-12-22 | 0.31173
2025-12-22 13:28 | 73.2236 | FALSE | FALSE | -0.88639 | -1.2254 | -0.49075 | -0.66575 | 0 |  |  | none | FALSE | 0 | 72.3372 | FALSE | FALSE | 0.0383 |  | 73.0258 | 0 | 0 | -0.05643 | 0.2687 | 0.21001 | 0.34429 | Normal | 73.7144 | 0.57458 | Day | 202512 | 2025-12-22 | 0.57458
2025-12-22 13:43 | 73.5062 | FALSE | FALSE | -1.1265 | -1.5563 | -0.13736 | -0.18652 | 0.2826 |  |  | none | FALSE | 0 | 72.3797 | FALSE | FALSE | 0.1043 |  | 73.0117 | 0 | 0.2826 | -0.01413 | 0.25068 | 1.1837 | 0.31596 | Normal | 73.6436 | 1.5652 | Day | 202512 | 2025-12-22 | 1.5652
2025-12-22 13:59 | 73.2236 | FALSE | FALSE | -0.82311 | -1.1369 | -0.37095 | -0.50404 | -0.2826 |  |  | none | FALSE | 0 | 72.4005 | FALSE | FALSE | 0.0505 |  | 72.9975 | 0 | -0.2826 | -0.01413 | 0.25068 | -1.071 | 0.29851 | Normal | 73.5945 | 0.75735 | Day | 202512 | 2025-12-22 | 0.75735
2025-12-22 14:14 | 73.5062 | FALSE | FALSE | -1.1183 | -1.5449 | -0.15745 | -0.21374 | 0.2826 |  |  | none | FALSE | 0 | 72.3879 | FALSE | FALSE | 0.1004 |  | 73.0258 | 0 | 0.2826 | 0.02826 | 0.22271 | 1.142 | 0.31894 | Normal | 73.6637 | 1.5063 | Day | 202512 | 2025-12-22 | 1.5063
2025-12-22 14:28 | 73.5062 | FALSE | FALSE | -1.0857 | -1.4992 | -0.20965 | -0.2844 | 0 |  |  | none | FALSE | 0 | 72.4205 | FALSE | FALSE | 0.0902 |  | 73.0682 | 0 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.32384 | Normal | 73.7159 | 1.3526 | Day | 202512 | 2025-12-22 | 1.3526
2025-12-22 14:43 | 73.5062 | FALSE | FALSE | -1.0414 | -1.4371 | -0.25009 | -0.33908 | 0 |  |  | none | FALSE | 0 | 72.4648 | FALSE | FALSE | 0.0817 |  | 73.1106 | 0 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.32287 | Normal | 73.7563 | 1.2254 | Day | 202512 | 2025-12-22 | 1.2254
2025-12-22 14:58 | 73.5062 | FALSE | FALSE | -1.0311 | -1.4227 | -0.29633 | -0.40151 | 0 |  |  | none | FALSE | 0 | 72.4751 | FALSE | FALSE | 0.0738 |  | 73.1388 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.33185 | Normal | 73.8025 | 1.1071 | Day | 202512 | 2025-12-22 | 1.1071
2025-12-22 15:13 | 73.5062 | FALSE | FALSE | -0.96746 | -1.3337 | -0.31748 | -0.43005 | 0 |  |  | none | FALSE | 0 | 72.5387 | FALSE | FALSE | 0.0674 |  | 73.1812 | 0 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.32123 | Normal | 73.8237 | 1.0117 | Day | 202512 | 2025-12-22 | 1.0117
2025-12-22 15:28 | 73.5062 | FALSE | FALSE | -0.89079 | -1.2267 | -0.32559 | -0.44098 | 0 |  |  | none | FALSE | 0 | 72.6154 | FALSE | FALSE | 0.062 |  | 73.2236 | 0 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.30409 | Normal | 73.8318 | 0.92932 | Day | 202512 | 2025-12-22 | 0.92932
2025-12-22 15:43 | 73.2236 | FALSE | FALSE | -0.5188 | -0.71357 | -0.57532 | -0.77958 | -0.2826 |  |  | none | FALSE | 0 | 72.7048 | FALSE | FALSE | 0.0069 |  | 73.2519 | 0 | -0.2826 | 0.02826 | 0.20296 | -1.5316 | 0.27353 | Normal | 73.7989 | -0.10332 | Day | 202512 | 2025-12-22 | 0.10332
2025-12-22 15:58 | 73.2236 | FALSE | FALSE | -0.48511 | -0.66693 | -0.56989 | -0.77228 | 0 |  |  | none | FALSE | 0 | 72.7385 | FALSE | FALSE | 0.0107 |  | 73.266 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.26375 | Normal | 73.7935 | -0.16072 | Day | 202512 | 2025-12-22 | 0.16072
2025-12-22 16:13 | 73.2236 | FALSE | FALSE | -0.37382 | -0.51314 | -0.51512 | -0.69858 | 0 |  |  | none | FALSE | 0 | 72.8498 | FALSE | FALSE | 0.0212 |  | 73.2943 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.22224 | Normal | 73.7387 | -0.31791 | Day | 202512 | 2025-12-22 | 0.31791
2025-12-22 16:28 | 72.941 | FALSE | FALSE | -0.0039263 | -0.0053831 | -0.73869 | -1.0026 | -0.2826 |  |  | none | FALSE | 0 | 72.9371 | FALSE | FALSE | 0.1319 |  | 73.3084 | 0 | -0.2826 | 0.01413 | 0.19396 | -1.5299 | 0.18565 | Normal | 73.6797 | -1.9789 | Day | 202512 | 2025-12-22 | 1.9789
2025-12-22 16:43 | 72.941 | FALSE | FALSE | -0.0039263 | -0.0053831 | -0.73869 | -1.0026 | 0 |  |  | none | FALSE | 0 | 72.9371 | FALSE | FALSE | 0.1319 |  | 73.3084 | 0 | 0 | 0 | 0.18338 | 0 | 0.18565 | Normal | 73.6797 | -1.9789 | Day | 202512 | 2025-12-22 | 1.9789
2025-12-22 16:58 | 72.6584 | FALSE | FALSE | 0.15062 | 0.20687 | -1.0928 | -1.4818 | -0.2826 | 2025-12-22 18:31 | 2025-12-22 16:58 | lower | TRUE | 0 | 72.809 | FALSE | FALSE | 0.2331 | 2.6394 | 73.2801 | 1 | -0.2826 | -0.02826 | 0.18107 | -1.4047 | 0.23555 | Extreme triggered | 73.7512 | -2.6394 | Day | 202512 | 2025-12-22 | 2.6394
2025-12-22 17:13 | 72.3758 | FALSE | FALSE | 0.24075 | 0.33154 | -1.4831 | -2.008 | -0.2826 |  | 2025-12-22 16:58 | lower | TRUE | 0 | 72.6166 | FALSE | FALSE | 0.2993 | 2.7073 | 73.2377 | 2 | -0.2826 | -0.04239 | 0.18957 | -1.2671 | 0.31059 | Extreme/elevated | 73.8589 | -2.7751 | Day | 202512 | 2025-12-22 | 2.7751
2025-12-22 17:27 | 72.3758 | FALSE | FALSE | 0.088335 | 0.1219 | -1.5507 | -2.0977 | 0 |  | 2025-12-22 16:58 | lower | TRUE | 0 | 72.4641 | FALSE | TRUE | 0.3209 | 2.5521 | 73.1953 | 3 | 0 | -0.04239 | 0.18957 | 0.22361 | 0.3656 | Persistent | 73.9265 | -2.2416 | Day | 202512 | 2025-12-22 | 2.2416
2025-12-22 17:42 | 72.3758 | FALSE | FALSE | -0.040362 | -0.055798 | -1.5947 | -2.1558 | 0 |  | 2025-12-22 16:58 | none | FALSE | 0 | 72.3354 | FALSE | FALSE | 0.3553 | 2.3894 | 73.153 | 4 | 0 | -0.04239 | 0.18957 | 0.22361 | 0.40876 | Persistent | 73.9705 | -1.9013 | Night | 202512 | 2025-12-22 | 1.9013
2025-12-22 17:57 | 72.095 | FALSE | FALSE | 0.061796 | 0.085641 | -1.913 | -2.5848 | -0.2808 |  | 2025-12-22 16:58 | lower | TRUE | 0 | 72.1568 | FALSE | TRUE | 0.4279 | 2.3382 | 73.0824 | 5 | -0.2808 | -0.07056 | 0.18038 | -1.1656 | 0.4628 | Persistent | 74.008 | -2.1335 | Night | 202512 | 2025-12-22 | 2.1335
2025-12-22 18:12 | 72.095 | FALSE | FALSE | -0.090984 | -0.12636 | -1.9529 | -2.6374 | 0 |  | 2025-12-22 16:58 | none | FALSE | 0 | 72.004 | FALSE | FALSE | 0.4643 | 2.2522 | 73.026 | 6 | 0 | -0.05643 | 0.17384 | 0.3246 | 0.51097 | Persistent | 74.0479 | -1.8219 | Night | 202512 | 2025-12-22 | 1.8219
2025-12-22 18:27 | 72.095 | FALSE | TRUE | -0.22329 | -0.31067 | -1.9723 | -2.6629 | 0 |  | 2025-12-22 16:58 | none | FALSE | 0 | 71.8717 | FALSE | FALSE | 0.5062 | 2.158 | 72.9695 | 7 | 0 | -0.05643 | 0.17384 | 0.3246 | 0.54891 | Confirmed/Materialized Shift | 74.0673 | -1.5932 | Night | 202512 | 2025-12-22 | 1.5932
2025-12-22 18:30 | 72.095 | FALSE | TRUE | -0.32944 | -0.45905 | -1.9374 | -2.6169 | 0 |  | 2025-12-22 16:58 | none | FALSE | 0 | 71.7656 | FALSE | FALSE | 0.4946 | 2.0656 | 72.899 | 8 | 0 | -0.07056 | 0.15534 | 0.45424 | 0.5667 | Confirmed/Materialized Shift | 74.0324 | -1.4187 | Night | 202512 | 2025-12-22 | 1.4187
2025-12-22 18:31 | 72.3758 | FALSE | FALSE | -0.66486 | -0.92713 | -1.6264 | -2.1978 | 0.2808 |  |  | none | FALSE | 0 | 71.7109 | FALSE | FALSE | 0.056 |  | 72.8566 | 0 | 0.2808 | -0.04239 | 0.1656 | 1.9516 | 0.57282 | Persistence ends | 74.0022 | -0.83932 | Night | 202512 | 2025-12-22 | 0.83932
2025-12-22 18:46 | 72.941 | TRUE | FALSE | -1.218 | -1.6982 | -0.99266 | -1.3426 | 0.5652 |  |  | none | FALSE | 1 | 71.723 | FALSE | FALSE | 0.0422 |  | 72.8283 | 0 | 0.5652 | -0.02826 | 0.2027 | 2.9278 | 0.55267 | Normal | 73.9337 | 0.20388 | Night | 202512 | 2025-12-22 | 0.20388
2025-12-22 19:01 | 73.2236 | FALSE | FALSE | -1.4851 | -2.0701 | -0.66627 | -0.90171 | 0.2826 |  |  | none | FALSE | 1 | 71.7385 | FALSE | FALSE | 0.0793 |  | 72.8142 | 0 | 0.2826 | -0.01413 | 0.21429 | 1.3847 | 0.53784 | Normal | 73.8899 | 0.76121 | Night | 202512 | 2025-12-22 | 0.76121
2025-12-22 19:16 | 73.5062 | FALSE | FALSE | -1.7677 | -2.4641 | -0.38367 | -0.51925 | 0.2826 |  |  | none | FALSE | 1 | 71.7385 | FALSE | FALSE | 0.1143 |  | 72.8142 | 0 | 0.2826 | 0 | 0.22435 | 1.2596 | 0.53784 | Normal | 73.8899 | 1.2866 | Night | 202512 | 2025-12-22 | 1.2866
2025-12-22 19:30 | 73.5062 | FALSE | FALSE | -1.7677 | -2.4641 | -0.38367 | -0.51925 | 0 |  |  | none | FALSE | 1 | 71.7385 | FALSE | FALSE | 0.1143 |  | 72.8142 | 0 | 0 | 0 | 0.22435 | 0 | 0.53784 | Normal | 73.8899 | 1.2866 | Night | 202512 | 2025-12-22 | 1.2866
2025-12-22 19:45 | 73.7888 | FALSE | FALSE | -2.0809 | -2.902 | -0.15997 | -0.21632 | 0.2826 |  |  | none | FALSE | 1 | 71.7079 | FALSE | FALSE | 0.1429 |  | 72.8283 | 0 | 0.2826 | 0.01413 | 0.23308 | 1.1518 | 0.56022 | Normal | 73.9488 | 1.7145 | Night | 202512 | 2025-12-22 | 1.7145
2025-12-22 20:00 | 73.7888 | FALSE | FALSE | -2.1091 | -2.9424 | -0.21642 | -0.29244 | 0 |  |  | none | FALSE | 1 | 71.6797 | FALSE | FALSE | 0.1371 |  | 72.8424 | 0 | 0 | 0.01413 | 0.23308 | -0.060623 | 0.58139 | Normal | 74.0052 | 1.6277 | Night | 202512 | 2025-12-22 | 1.6277
2025-12-22 20:15 | 73.7888 | FALSE | FALSE | -2.1455 | -2.9948 | -0.30936 | -0.4175 | 0 |  |  | none | FALSE | 1 | 71.6433 | FALSE | FALSE | 0.1283 |  | 72.8707 | 0 | 0 | 0.02826 | 0.22247 | -0.12703 | 0.61372 | Normal | 74.0982 | 1.4959 | Night | 202512 | 2025-12-22 | 1.4959
2025-12-22 20:29 | 73.7888 | FALSE | FALSE | -2.1761 | -3.0387 | -0.39644 | -0.5344 | 0 |  |  | none | FALSE | 1 | 71.6127 | FALSE | FALSE | 0.1208 |  | 72.899 | 0 | 0 | 0.02826 | 0.22247 | -0.12703 | 0.64314 | Normal | 74.1852 | 1.3836 | Night | 202512 | 2025-12-22 | 1.3836
2025-12-22 20:44 | 73.7888 | FALSE | FALSE | -2.2016 | -3.0754 | -0.47845 | -0.64422 | 0 |  |  | none | FALSE | 1 | 71.5872 | FALSE | FALSE | 0.1143 |  | 72.9272 | 0 | 0 | 0.02826 | 0.22247 | -0.12703 | 0.67001 | Normal | 74.2672 | 1.2859 | Night | 202512 | 2025-12-22 | 1.2859
2025-12-22 20:59 | 74.0714 | FALSE | FALSE | -2.5221 | -3.525 | -0.34684 | -0.46607 | 0.2826 |  |  | none | FALSE | 1 | 71.5493 | FALSE | FALSE | 0.1297 |  | 72.9838 | 0 | 0.2826 | 0.05652 | 0.21673 | 1.0432 | 0.71725 | Normal | 74.4182 | 1.5164 | Night | 202512 | 2025-12-22 | 1.5164
2025-12-22 21:14 | 74.0714 | FALSE | FALSE | -2.5454 | -3.5587 | -0.48313 | -0.64802 | 0 |  |  | none | FALSE | 0 | 71.526 | FALSE | FALSE | 0.0908 |  | 73.0403 | 0 | 0 | 0.05652 | 0.21673 | -0.26079 | 0.75713 | Normal | 74.5545 | 1.3619 | Night | 202512 | 2025-12-22 | 1.3619
2025-12-22 21:29 | 74.0714 | FALSE | FALSE | -2.5305 | -3.5372 | -0.60958 | -0.81625 | 0 |  |  | none | FALSE | 0 | 71.5409 | FALSE | FALSE | 0.0816 |  | 73.1109 | 0 | 0 | 0.07065 | 0.20218 | -0.34945 | 0.78503 | Normal | 74.681 | 1.2235 | Night | 202512 | 2025-12-22 | 1.2235
2025-12-22 21:44 | 74.0714 | FALSE | FALSE | -2.4617 | -3.4376 | -0.71026 | -0.94978 | 0 |  |  | none | FALSE | 0 | 71.6097 | FALSE | FALSE | 0.0736 |  | 73.1957 | 0 | 0 | 0.08478 | 0.18537 | -0.45737 | 0.79298 | Normal | 74.7817 | 1.1043 | Night | 202512 | 2025-12-22 | 1.1043
2025-12-22 21:59 | 74.0714 | FALSE | FALSE | -2.3736 | -3.3106 | -0.79178 | -1.0576 | 0 |  |  | none | FALSE | 0 | 71.6978 | FALSE | FALSE | 0.0666 |  | 73.2805 | 0 | 0 | 0.08478 | 0.18537 | -0.45737 | 0.79135 | Normal | 74.8632 | 0.99946 | Night | 202512 | 2025-12-22 | 0.99946
2025-12-22 22:14 | 74.0714 | FALSE | FALSE | -2.2663 | -3.1562 | -0.85401 | -1.1398 | 0 |  |  | none | FALSE | 0 | 71.8051 | FALSE | FALSE | 0.0603 |  | 73.3653 | 0 | 0 | 0.08478 | 0.18537 | -0.45737 | 0.78007 | Normal | 74.9254 | 0.90522 | Night | 202512 | 2025-12-22 | 0.90522
2025-12-22 22:29 | 74.0714 | FALSE | FALSE | -2.0764 | -2.8841 | -0.86177 | -1.1501 | 0 |  |  | none | FALSE | 0 | 71.995 | FALSE | FALSE | 0.0551 |  | 73.4641 | 0 | 0 | 0.09882 | 0.16582 | -0.59594 | 0.73454 | Normal | 74.9332 | 0.8268 | Night | 202512 | 2025-12-22 | 0.8268
2025-12-22 22:44 | 74.3522 | FALSE | FALSE | -2.1449 | -2.9705 | -0.59443 | -0.79313 | 0.2808 |  |  | none | FALSE | 0 | 72.2073 | FALSE | FALSE | 0.0755 |  | 73.5769 | 0 | 0.2808 | 0.11286 | 0.16887 | 0.99447 | 0.68484 | Normal | 74.9466 | 1.132 | Night | 202512 | 2025-12-22 | 1.132
2025-12-22 22:59 | 74.3522 | FALSE | FALSE | -1.8817 | -2.5964 | -0.55686 | -0.74338 | 0 |  |  | none | FALSE | 0 | 72.4705 | FALSE | FALSE | 0.0724 |  | 73.6898 | 0 | 0 | 0.11286 | 0.16887 | -0.66831 | 0.60963 | Normal | 74.9091 | 1.0866 | Night | 202512 | 2025-12-22 | 1.0866
2025-12-22 23:14 | 74.3522 | FALSE | FALSE | -1.5445 | -2.1213 | -0.44539 | -0.59546 | 0 |  |  | none | FALSE | 0 | 72.8077 | FALSE | FALSE | 0.0736 |  | 73.8027 | 0 | 0 | 0.11286 | 0.16887 | -0.66831 | 0.49747 | Normal | 74.7976 | 1.1047 | Night | 202512 | 2025-12-22 | 1.1047
2025-12-22 23:28 | 74.3522 | FALSE | FALSE | -1.2147 | -1.6609 | -0.3133 | -0.41961 | 0 |  |  | none | FALSE | 0 | 73.1375 | FALSE | FALSE | 0.0787 |  | 73.9015 | 0 | 0 | 0.09882 | 0.16582 | -0.59594 | 0.38201 | Normal | 74.6655 | 1.1799 | Night | 202512 | 2025-12-22 | 1.1799
2025-12-22 23:43 | 74.3522 | FALSE | FALSE | -1.0215 | -1.393 | -0.26118 | -0.35005 | 0 |  |  | none | FALSE | 0 | 73.3307 | FALSE | FALSE | 0.079 |  | 73.972 | 0 | 0 | 0.07056 | 0.12539 | -0.56273 | 0.32067 | Normal | 74.6134 | 1.1855 | Night | 202512 | 2025-12-22 | 1.1855
2025-12-22 23:59 | 74.6348 | FALSE | FALSE | -1.1963 | -1.6289 | -0.011872 | -0.015904 | 0.2826 |  |  | none | FALSE | 0 | 73.4385 | FALSE | FALSE | 0.1307 |  | 74.0426 | 0 | 0.2826 | 0.07056 | 0.12539 | 1.6911 | 0.30204 | Normal | 74.6467 | 1.9607 | Night | 202512 | 2025-12-22 | 1.9607
2025-12-23 00:14 | 74.6348 | FALSE | FALSE | -1.1397 | -1.5507 | -0.068178 | -0.091266 | 0 |  |  | none | FALSE | 0 | 73.4951 | FALSE | FALSE | 0.1183 |  | 74.099 | 0 | 0 | 0.05643 | 0.11579 | -0.48734 | 0.30197 | Normal | 74.703 | 1.7742 | Night | 202512 | 2025-12-23 | 1.7742
2025-12-23 00:28 | 74.3522 | TRUE | FALSE | -0.75559 | -1.0267 | -0.33385 | -0.44701 | -0.2826 |  |  | none | FALSE | 1 | 73.5966 | FALSE | FALSE | 0.0802 |  | 74.1413 | 0 | -0.2826 | 0.0423 | 0.13813 | -2.3521 | 0.27236 | Normal | 74.6861 | 0.77423 | Night | 202512 | 2025-12-23 | 0.77423
2025-12-23 00:43 | 74.3522 | FALSE | FALSE | -0.70861 | -0.96221 | -0.34321 | -0.45948 | 0 |  |  | none | FALSE | 1 | 73.6436 | FALSE | FALSE | 0.0749 |  | 74.1695 | 0 | 0 | 0.02817 | 0.12619 | -0.22323 | 0.26295 | Normal | 74.6954 | 0.6948 | Night | 202512 | 2025-12-23 | 0.6948
2025-12-23 00:58 | 74.6348 | FALSE | FALSE | -0.95602 | -1.2976 | -0.11002 | -0.1472 | 0.2826 |  |  | none | FALSE | 1 | 73.6788 | FALSE | FALSE | 0.1344 |  | 74.2118 | 0 | 0.2826 | 0.0423 | 0.13813 | 1.7397 | 0.26651 | Normal | 74.7448 | 1.5872 | Night | 202512 | 2025-12-23 | 1.5872
2025-12-23 01:13 | 74.6348 | FALSE | FALSE | -0.90661 | -1.2297 | -0.14521 | -0.19418 | 0 |  |  | none | FALSE | 1 | 73.7282 | FALSE | FALSE | 0.1251 |  | 74.2541 | 0 | 0 | 0.0423 | 0.13813 | -0.30624 | 0.26295 | Normal | 74.78 | 1.4478 | Night | 202512 | 2025-12-23 | 1.4478
2025-12-23 01:28 | 74.6348 | FALSE | FALSE | -0.84236 | -1.1415 | -0.16556 | -0.22134 | 0 |  |  | none | FALSE | 1 | 73.7924 | FALSE | FALSE | 0.1181 |  | 74.2964 | 0 | 0 | 0.0423 | 0.13813 | -0.30624 | 0.25198 | Normal | 74.8004 | 1.343 | Night | 202512 | 2025-12-23 | 1.343
2025-12-23 01:43 | 74.3522 | FALSE | FALSE | -0.47153 | -0.63824 | -0.41627 | -0.55675 | -0.2826 |  |  | none | FALSE | 1 | 73.8807 | FALSE | FALSE | 0.0369 |  | 74.3246 | 0 | -0.2826 | 0.02817 | 0.15598 | -1.9923 | 0.22195 | Normal | 74.7685 | 0.12449 | Night | 202512 | 2025-12-23 | 0.12449
2025-12-23 01:58 | 74.3522 | FALSE | FALSE | -0.44124 | -0.59699 | -0.41406 | -0.55381 | 0 |  |  | none | FALSE | 1 | 73.911 | FALSE | FALSE | 0.0328 |  | 74.3386 | 0 | 0 | 0.01404 | 0.14407 | -0.097454 | 0.21383 | Normal | 74.7663 | 0.063556 | Night | 202512 | 2025-12-23 | 0.063556
2025-12-23 02:13 | 74.6348 | FALSE | FALSE | -0.69578 | -0.94103 | -0.15974 | -0.21358 | 0.2826 |  |  | none | FALSE | 1 | 73.939 | FALSE | FALSE | 0.1121 |  | 74.3668 | 0 | 0.2826 | 0.02817 | 0.15598 | 1.6311 | 0.21388 | Normal | 74.7945 | 1.2531 | Night | 202512 | 2025-12-23 | 1.2531
2025-12-23 02:28 | 74.6348 | FALSE | FALSE | -0.65985 | -0.89199 | -0.18015 | -0.24079 | 0 |  |  | none | FALSE | 1 | 73.975 | FALSE | FALSE | 0.1047 |  | 74.3949 | 0 | 0 | 0.02817 | 0.15598 | -0.18059 | 0.21 | Normal | 74.8149 | 1.1422 | Night | 202512 | 2025-12-23 | 1.1422
2025-12-23 02:43 | 74.6348 | FALSE | FALSE | -0.61557 | -0.83164 | -0.19221 | -0.25687 | 0 |  |  | none | FALSE | 1 | 74.0192 | FALSE | FALSE | 0.0985 |  | 74.4231 | 0 | 0 | 0.02817 | 0.15598 | -0.18059 | 0.20195 | Normal | 74.827 | 1.0482 | Night | 202512 | 2025-12-23 | 1.0482
2025-12-23 02:58 | 74.6348 | FALSE | FALSE | -0.5619 | -0.75857 | -0.19488 | -0.26043 | 0 |  |  | none | FALSE | 0 | 74.0729 | FALSE | FALSE | 0.0647 |  | 74.4513 | 0 | 0 | 0.02817 | 0.15598 | -0.18059 | 0.18919 | Normal | 74.8297 | 0.96996 | Night | 202512 | 2025-12-23 | 0.96996
2025-12-23 03:13 | 74.3522 | FALSE | FALSE | -0.22455 | -0.30293 | -0.45081 | -0.60267 | -0.2826 |  |  | none | FALSE | 0 | 74.1276 | FALSE | FALSE | 0.0447 |  | 74.4653 | 0 | -0.2826 | 0.01404 | 0.17077 | -1.7371 | 0.16884 | Normal | 74.803 | -0.67003 | Night | 202512 | 2025-12-23 | 0.67003
2025-12-23 03:27 | 74.3522 | FALSE | FALSE | -0.16132 | -0.21744 | -0.41566 | -0.55593 | 0 |  |  | none | FALSE | 0 | 74.1909 | FALSE | FALSE | 0.0588 |  | 74.4794 | 0 | 0 | 0.01404 | 0.17077 | -0.082216 | 0.14424 | Normal | 74.7679 | -0.88163 | Night | 202512 | 2025-12-23 | 0.88163
2025-12-23 03:42 | 74.3522 | FALSE | FALSE | -0.16132 | -0.21744 | -0.41566 | -0.55593 | 0 |  |  | none | FALSE | 0 | 74.1909 | FALSE | FALSE | 0.0588 |  | 74.4794 | 0 | 0 | 0 | 0.15881 | 0 | 0.14424 | Normal | 74.7679 | -0.88163 | Night | 202512 | 2025-12-23 | 0.88163
2025-12-23 03:57 | 74.3522 | FALSE | FALSE | -0.16132 | -0.21744 | -0.41566 | -0.55593 | 0 |  |  | none | FALSE | 0 | 74.1909 | FALSE | FALSE | 0.0588 |  | 74.4794 | 0 | 0 | 0 | 0.15881 | 0 | 0.14424 | Normal | 74.7679 | -0.88163 | Night | 202512 | 2025-12-23 | 0.88163
2025-12-23 04:13 | 74.6348 | FALSE | FALSE | -0.43124 | -0.58116 | -0.14864 | -0.19876 | 0.2826 |  |  | none | FALSE | 0 | 74.2036 | FALSE | FALSE | 0.065 |  | 74.4935 | 0 | 0.2826 | 0.01413 | 0.17092 | 1.5708 | 0.14497 | Normal | 74.7834 | 0.97468 | Night | 202512 | 2025-12-23 | 0.97468
2025-12-23 04:27 | 74.3522 | FALSE | FALSE | -0.14864 | -0.20032 | -0.43124 | -0.57665 | -0.2826 |  |  | none | FALSE | 0 | 74.2036 | FALSE | FALSE | 0.065 |  | 74.4935 | 0 | -0.2826 | 0 | 0.18338 | -1.5411 | 0.14497 | Normal | 74.7834 | -0.97468 | Night | 202512 | 2025-12-23 | 0.97468
2025-12-23 04:42 | 74.3522 | FALSE | FALSE | -0.14864 | -0.20032 | -0.43124 | -0.57665 | 0 |  |  | none | FALSE | 0 | 74.2036 | FALSE | FALSE | 0.065 |  | 74.4935 | 0 | 0 | 0 | 0.18338 | 0 | 0.14497 | Normal | 74.7834 | -0.97468 | Night | 202512 | 2025-12-23 | 0.97468
2025-12-23 04:57 | 74.3522 | FALSE | FALSE | -0.16132 | -0.21744 | -0.41566 | -0.55593 | 0 |  |  | none | FALSE | 0 | 74.1909 | FALSE | FALSE | 0.0588 |  | 74.4794 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.14424 | Normal | 74.7679 | -0.88163 | Night | 202512 | 2025-12-23 | 0.88163
2025-12-23 05:12 | 74.3522 | FALSE | FALSE | -0.17104 | -0.23058 | -0.39712 | -0.53127 | 0 |  |  | none | FALSE | 0 | 74.1812 | FALSE | FALSE | 0.0531 |  | 74.4652 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.14204 | Normal | 74.7493 | -0.79582 | Night | 202512 | 2025-12-23 | 0.79582
2025-12-23 05:27 | 74.3522 | FALSE | FALSE | -0.17104 | -0.23058 | -0.39712 | -0.53127 | 0 |  |  | none | FALSE | 0 | 74.1812 | FALSE | FALSE | 0.0531 |  | 74.4652 | 0 | 0 | 0 | 0.15881 | 0 | 0.14204 | Normal | 74.7493 | -0.79582 | Night | 202512 | 2025-12-23 | 0.79582
2025-12-23 05:42 | 74.3522 | FALSE | FALSE | -0.17104 | -0.23058 | -0.39712 | -0.53127 | 0 |  |  | none | FALSE | 0 | 74.1812 | FALSE | FALSE | 0.0531 |  | 74.4652 | 0 | 0 | 0 | 0.15881 | 0 | 0.14204 | Normal | 74.7493 | -0.79582 | Night | 202512 | 2025-12-23 | 0.79582
2025-12-23 05:57 | 74.3522 | FALSE | FALSE | -0.17768 | -0.23954 | -0.3755 | -0.50249 | 0 |  |  | none | FALSE | 0 | 74.1745 | FALSE | FALSE | 0.0477 |  | 74.4511 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.13829 | Normal | 74.7277 | -0.71522 | Night | 202512 | 2025-12-23 | 0.71522
2025-12-23 06:12 | 74.3522 | FALSE | FALSE | -0.18096 | -0.24397 | -0.35052 | -0.46921 | 0 |  |  | none | FALSE | 0 | 74.1712 | FALSE | FALSE | 0.0425 |  | 74.437 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.13287 | Normal | 74.7027 | -0.63808 | Night | 202512 | 2025-12-23 | 0.63808
2025-12-23 06:26 | 74.0714 | FALSE | FALSE | 0.04216 | 0.056886 | -0.63266 | -0.84689 | -0.2808 | 2025-12-23 06:41 | 2025-12-23 06:26 | lower | TRUE | 0 | 74.1136 | FALSE | FALSE | 0.2095 | 2.2856 | 74.4088 | 1 | -0.2808 | -0.02817 | 0.15598 | -1.6196 | 0.14762 | Extreme triggered | 74.7041 | -2.2856 | Night | 202512 | 2025-12-23 | 2.2856
2025-12-23 06:41 | 74.3522 | FALSE | FALSE | -0.23864 | -0.32199 | -0.35186 | -0.471 | 0.2808 |  |  | none | FALSE | 0 | 74.1136 | FALSE | FALSE | 0.0256 |  | 74.4088 | 0 | 0.2808 | 0 | 0.15847 | 1.7719 | 0.14762 | Persistence ends | 74.7041 | -0.38347 | Night | 202512 | 2025-12-23 | 0.38347
2025-12-23 06:57 | 74.3522 | FALSE | FALSE | -0.23864 | -0.32199 | -0.35186 | -0.471 | 0 |  |  | none | FALSE | 0 | 74.1136 | FALSE | FALSE | 0.0256 |  | 74.4088 | 0 | 0 | 0 | 0.15847 | 0 | 0.14762 | Normal | 74.7041 | -0.38347 | Night | 202512 | 2025-12-23 | 0.38347
2025-12-23 07:12 | 74.0714 | FALSE | FALSE | -0.0022831 | -0.0030824 | -0.62076 | -0.8311 | -0.2808 |  |  | none | FALSE | 0 | 74.0691 | FALSE | FALSE | 0.1324 |  | 74.3806 | 0 | -0.2808 | -0.02817 | 0.15564 | -1.6231 | 0.15576 | Normal | 74.6922 | -1.9853 | Day | 202512 | 2025-12-23 | 1.9853
2025-12-23 07:26 | 74.0714 | FALSE | FALSE | -0.035535 | -0.047996 | -0.59767 | -0.80043 | 0 |  |  | none | FALSE | 0 | 74.0359 | FALSE | FALSE | 0.1184 |  | 74.3525 | 0 | 0 | -0.02817 | 0.15564 | 0.18099 | 0.1583 | Normal | 74.6691 | -1.7755 | Day | 202512 | 2025-12-23 | 1.7755
2025-12-23 07:30 | 74.0714 | FALSE | FALSE | -0.058143 | -0.078558 | -0.56394 | -0.7556 | 0 |  |  | none | FALSE | 0 | 74.0133 | FALSE | FALSE | 0.1084 |  | 74.3243 | 0 | 0 | -0.02817 | 0.15564 | 0.18099 | 0.15552 | Normal | 74.6353 | -1.6261 | Day | 202512 | 2025-12-23 | 1.6261
2025-12-23 07:45 | 74.0714 | FALSE | FALSE | -0.069506 | -0.093924 | -0.51897 | -0.69575 | 0 |  |  | none | FALSE | 0 | 74.0019 | FALSE | FALSE | 0.1018 |  | 74.2961 | 0 | 0 | -0.02817 | 0.15564 | 0.18099 | 0.14712 | Normal | 74.5904 | -1.5276 | Day | 202512 | 2025-12-23 | 1.5276
2025-12-23 08:00 | 74.0714 | FALSE | FALSE | -0.098688 | -0.13341 | -0.52007 | -0.69722 | 0 |  |  | none | FALSE | 0 | 73.9727 | FALSE | FALSE | 0.0908 |  | 74.2821 | 0 | 0 | -0.01404 | 0.1437 | 0.097705 | 0.15469 | Normal | 74.5915 | -1.362 | Day | 202512 | 2025-12-23 | 1.362
2025-12-23 08:16 | 74.0714 | FALSE | FALSE | -0.12459 | -0.16849 | -0.51789 | -0.69432 | 0 |  |  | none | FALSE | 0 | 73.9468 | FALSE | FALSE | 0.0816 |  | 74.2681 | 0 | 0 | -0.01404 | 0.1437 | 0.097705 | 0.16062 | Normal | 74.5893 | -1.2243 | Day | 202512 | 2025-12-23 | 1.2243
2025-12-23 08:30 | 74.0714 | FALSE | FALSE | -0.14757 | -0.19962 | -0.51279 | -0.68753 | 0 |  |  | none | FALSE | 0 | 73.9238 | FALSE | FALSE | 0.0737 |  | 74.254 | 0 | 0 | -0.01404 | 0.1437 | 0.097705 | 0.16509 | Normal | 74.5842 | -1.1061 | Day | 202512 | 2025-12-23 | 1.1061
2025-12-23 08:30 | 74.0714 | FALSE | FALSE | -0.16785 | -0.22712 | -0.50499 | -0.67714 | 0 |  |  | none | FALSE | 0 | 73.9036 | FALSE | FALSE | 0.0668 |  | 74.24 | 0 | 0 | -0.01404 | 0.1437 | 0.097705 | 0.16821 | Normal | 74.5764 | -1.0021 | Day | 202512 | 2025-12-23 | 1.0021
2025-12-23 08:33 | 74.0714 | FALSE | FALSE | -0.14769 | -0.19979 | -0.42849 | -0.57516 | 0 |  |  | none | FALSE | 0 | 73.9237 | FALSE | FALSE | 0.065 |  | 74.2118 | 0 | 0 | -0.02817 | 0.12577 | 0.22398 | 0.14405 | Normal | 74.4999 | -0.97468 | Day | 202512 | 2025-12-23 | 0.97468
2025-12-23 08:48 | 73.5062 | TRUE | FALSE | 0.24362 | 0.33034 | -1.083 | -1.4519 | -0.5652 | 2025-12-23 10:44 | 2025-12-23 08:48 | lower | TRUE | 1 | 73.7498 | FALSE | FALSE | 0.2964 | 3.161 | 74.1695 | 1 | -0.5652 | -0.0423 | 0.16547 | -3.1601 | 0.20984 | Extreme triggered | 74.5892 | -3.161 | Day | 202512 | 2025-12-23 | 3.161
2025-12-23 09:03 | 72.3758 | TRUE | FALSE | 0.79748 | 1.0899 | -2.5923 | -3.4578 | -1.1304 |  | 2025-12-23 08:48 | lower | TRUE | 2 | 73.1733 | TRUE | FALSE | 0.4232 | 3.4692 | 74.0707 | 2 | -1.1304 | -0.09882 | 0.29366 | -3.5128 | 0.4487 | Extreme/elevated | 74.9681 | -3.7773 | Day | 202512 | 2025-12-23 | 3.7773
2025-12-23 09:18 | 72.095 | FALSE | FALSE | 0.61512 | 0.84599 | -3.1105 | -4.136 | -0.2808 |  | 2025-12-23 08:48 | lower | TRUE | 2 | 72.7101 | FALSE | TRUE | 0.4276 | 3.3081 | 73.9578 | 3 | -0.2808 | -0.11286 | 0.29539 | -0.56853 | 0.62385 | Persistent | 75.2055 | -2.986 | Day | 202512 | 2025-12-23 | 2.986
2025-12-23 09:30 | 72.095 | FALSE | FALSE | 0.26641 | 0.36816 | -3.2335 | -4.2925 | 0 |  | 2025-12-23 08:48 | lower | TRUE | 2 | 72.3614 | FALSE | TRUE | 0.443 | 3.0709 | 73.845 | 4 | 0 | -0.11286 | 0.29539 | 0.38207 | 0.74178 | Persistent | 75.3285 | -2.3591 | Day | 202512 | 2025-12-23 | 2.3591
2025-12-23 09:45 | 72.095 | FALSE | FALSE | -0.017542 | -0.024337 | -3.2917 | -4.3665 | 0 |  | 2025-12-23 08:48 | none | FALSE | 2 | 72.0775 | FALSE | FALSE | 0.4748 | 2.8525 | 73.7321 | 5 | 0 | -0.11286 | 0.29539 | 0.38207 | 0.82732 | Persistent | 75.3867 | -1.9788 | Day | 202512 | 2025-12-23 | 1.9788
2025-12-23 10:00 | 72.3758 | FALSE | FALSE | -0.47545 | -0.66126 | -2.9904 | -3.9678 | 0.2808 |  | 2025-12-23 08:48 | none | FALSE | 2 | 71.9004 | FALSE | FALSE | 0.4968 | 2.6189 | 73.6333 | 6 | 0.2808 | -0.09882 | 0.30747 | 1.2347 | 0.86646 | Persistent | 75.3662 | -1.4513 | Day | 202512 | 2025-12-23 | 1.4513
2025-12-23 10:15 | 72.3758 | FALSE | TRUE | -0.62628 | -0.87287 | -2.9436 | -3.9082 | 0 |  | 2025-12-23 08:48 | none | FALSE | 2 | 71.7495 | FALSE | FALSE | 0.5437 | 2.4303 | 73.5345 | 7 | 0 | -0.09882 | 0.30747 | 0.3214 | 0.89247 | Confirmed/Materialized Shift | 75.3194 | -1.2983 | Day | 202512 | 2025-12-23 | 1.2983
2025-12-23 10:29 | 72.3758 | FALSE | TRUE | -0.7531 | -1.0515 | -2.8728 | -3.8177 | 0 |  | 2025-12-23 08:48 | none | FALSE | 2 | 71.6227 | FALSE | FALSE | 0.5351 | 2.2726 | 73.4356 | 8 | 0 | -0.09882 | 0.30747 | 0.3214 | 0.90647 | Confirmed/Materialized Shift | 75.2486 | -1.1692 | Day | 202512 | 2025-12-23 | 1.1692
2025-12-23 10:44 | 72.6584 | FALSE | FALSE | -1.1122 | -1.5544 | -2.5253 | -3.3589 | 0.2826 |  |  | none | FALSE | 2 | 71.5462 | FALSE | FALSE | 0.1089 |  | 73.365 | 0 | 0.2826 | -0.07065 | 0.31562 | 1.1192 | 0.90937 | Persistence ends | 75.1837 | -0.77701 | Day | 202512 | 2025-12-23 | 0.77701
2025-12-23 10:59 | 72.6584 | FALSE | FALSE | -1.1607 | -1.6234 | -2.4045 | -3.2033 | 0 |  |  | none | FALSE | 2 | 71.4977 | FALSE | FALSE | 0.1037 |  | 73.2803 | 0 | 0 | -0.08469 | 0.30524 | 0.27746 | 0.89128 | Normal | 75.0629 | -0.69776 | Day | 202512 | 2025-12-23 | 0.69776
2025-12-23 11:15 | 72.6584 | FALSE | FALSE | -1.1911 | -1.6666 | -2.2655 | -3.0237 | 0 |  |  | none | FALSE | 1 | 71.4673 | FALSE | FALSE | 0.07 |  | 73.1956 | 0 | 0 | -0.08469 | 0.30524 | 0.27746 | 0.86413 | Normal | 74.9239 | -0.62168 | Day | 202512 | 2025-12-23 | 0.62168
2025-12-23 11:29 | 72.941 | FALSE | FALSE | -1.4829 | -2.0752 | -1.879 | -2.5114 | 0.2826 |  |  | none | FALSE | 0 | 71.4581 | FALSE | FALSE | 0.0157 |  | 73.1391 | 0 | 0.2826 | -0.05652 | 0.31211 | 1.0866 | 0.84048 | Normal | 74.82 | -0.23569 | Day | 202512 | 2025-12-23 | 0.23569
2025-12-23 11:44 | 72.941 | FALSE | FALSE | -1.4824 | -2.0746 | -1.7656 | -2.3634 | 0 |  |  | none | FALSE | 0 | 71.4586 | FALSE | FALSE | 0.0116 |  | 73.0826 | 0 | 0 | -0.05652 | 0.31211 | 0.18109 | 0.81201 | Normal | 74.7066 | -0.17435 | Day | 202512 | 2025-12-23 | 0.17435
2025-12-23 11:59 | 73.2236 | FALSE | FALSE | -1.7417 | -2.4365 | -1.3748 | -1.843 | 0.2826 |  |  | none | FALSE | 0 | 71.4819 | FALSE | FALSE | 0.0157 |  | 73.0402 | 0 | 0.2826 | -0.04239 | 0.32107 | 1.0122 | 0.77913 | Normal | 74.5984 | 0.23542 | Day | 202512 | 2025-12-23 | 0.23542
2025-12-23 12:14 | 73.2236 | FALSE | FALSE | -1.7103 | -2.3916 | -1.2587 | -1.69 | 0 |  |  | none | FALSE | 0 | 71.5133 | FALSE | FALSE | 0.0203 |  | 72.9978 | 0 | 0 | -0.04239 | 0.32107 | 0.13203 | 0.74227 | Normal | 74.4823 | 0.30422 | Day | 202512 | 2025-12-23 | 0.30422
2025-12-23 12:29 | 73.2236 | FALSE | FALSE | -1.6698 | -2.3336 | -1.1334 | -1.5242 | 0 |  |  | none | FALSE | 0 | 71.5538 | FALSE | FALSE | 0.0255 |  | 72.9554 | 0 | 0 | -0.04239 | 0.32107 | 0.13203 | 0.70078 | Normal | 74.357 | 0.38272 | Day | 202512 | 2025-12-23 | 0.38272
2025-12-23 12:44 | 72.941 | FALSE | FALSE | -1.3416 | -1.8738 | -1.2574 | -1.6946 | -0.2826 |  |  | none | FALSE | 0 | 71.5994 | FALSE | FALSE | 0.0043 |  | 72.8989 | 0 | -0.2826 | -0.05652 | 0.32529 | -0.695 | 0.64976 | Normal | 74.1984 | 0.064824 | Day | 202512 | 2025-12-23 | 0.064824
2025-12-23 12:59 | 72.6584 | FALSE | FALSE | -1.0093 | -1.4087 | -1.349 | -1.8228 | -0.2826 |  |  | none | FALSE | 0 | 71.6491 | FALSE | FALSE | 0.0192 |  | 72.8282 | 0 | -0.2826 | -0.07065 | 0.32883 | -0.64456 | 0.58959 | Normal | 74.0074 | -0.28805 | Day | 202512 | 2025-12-23 | 0.28805
2025-12-23 13:14 | 72.941 | FALSE | FALSE | -1.1961 | -1.6672 | -0.85752 | -1.162 | 0.2826 |  |  | none | FALSE | 0 | 71.7449 | FALSE | FALSE | 0.022 |  | 72.7717 | 0 | 0.2826 | -0.05652 | 0.33797 | 1.0034 | 0.5134 | Normal | 73.7985 | 0.32974 | Day | 202512 | 2025-12-23 | 0.32974
2025-12-23 13:28 | 72.941 | FALSE | FALSE | -1.0573 | -1.4708 | -0.60563 | -0.82346 | 0 |  |  | none | FALSE | 0 | 71.8837 | FALSE | FALSE | 0.0362 |  | 72.7152 | 0 | 0 | -0.05652 | 0.33797 | 0.16723 | 0.41572 | Normal | 73.5466 | 0.54318 | Day | 202512 | 2025-12-23 | 0.54318
2025-12-23 13:43 | 72.941 | FALSE | FALSE | -1.007 | -1.3999 | -0.49888 | -0.67931 | 0 |  |  | none | FALSE | 0 | 71.934 | FALSE | FALSE | 0.045 |  | 72.6869 | 0 | 0 | -0.02826 | 0.31612 | 0.089396 | 0.37648 | Normal | 73.4399 | 0.67486 | Day | 202512 | 2025-12-23 | 0.67486
2025-12-23 13:59 | 73.2236 | FALSE | FALSE | -1.2686 | -1.7631 | -0.28008 | -0.38104 | 0.2826 |  |  | none | FALSE | 0 | 71.955 | FALSE | FALSE | 0.0851 |  | 72.7293 | 0 | 0.2826 | 0.04239 | 0.18929 | 1.269 | 0.38718 | Normal | 73.5037 | 1.2766 | Day | 202512 | 2025-12-23 | 1.2766
2025-12-23 14:14 | 73.2236 | FALSE | FALSE | -1.1815 | -1.6399 | -0.30575 | -0.41583 | 0 |  |  | none | FALSE | 0 | 72.0421 | FALSE | FALSE | 0.0785 |  | 72.7857 | 0 | 0 | 0.05643 | 0.17384 | -0.3246 | 0.3718 | Normal | 73.5294 | 1.1776 | Day | 202512 | 2025-12-23 | 1.1776
2025-12-23 14:28 | 73.2236 | FALSE | FALSE | -1.0738 | -1.4884 | -0.311 | -0.42293 | 0 |  |  | none | FALSE | 0 | 72.1498 | FALSE | FALSE | 0.0734 |  | 72.8422 | 0 | 0 | 0.05643 | 0.17384 | -0.3246 | 0.34621 | Normal | 73.5346 | 1.1017 | Day | 202512 | 2025-12-23 | 1.1017
2025-12-23 14:43 | 73.2236 | FALSE | FALSE | -0.94073 | -1.3015 | -0.29075 | -0.3955 | 0 |  |  | none | FALSE | 0 | 72.2829 | FALSE | FALSE | 0.0704 |  | 72.8986 | 0 | 0 | 0.05643 | 0.17384 | -0.3246 | 0.30787 | Normal | 73.5144 | 1.0556 | Day | 202512 | 2025-12-23 | 1.0556
2025-12-23 14:58 | 72.941 | FALSE | FALSE | -0.57859 | -0.79957 | -0.55033 | -0.74883 | -0.2826 |  |  | none | FALSE | 0 | 72.3624 | FALSE | FALSE | 0.0033 |  | 72.9269 | 0 | -0.2826 | 0.02826 | 0.18107 | -1.7168 | 0.28223 | Normal | 73.4913 | 0.050066 | Day | 202512 | 2025-12-23 | 0.050066
2025-12-23 15:13 | 72.941 | FALSE | FALSE | -0.48723 | -0.67246 | -0.51549 | -0.70176 | 0 |  |  | none | FALSE | 0 | 72.4538 | FALSE | FALSE | 0.0038 |  | 72.9551 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.25068 | Normal | 73.4565 | -0.056367 | Day | 202512 | 2025-12-23 | 0.056367
2025-12-23 15:28 | 72.941 | FALSE | FALSE | -0.37877 | -0.522 | -0.46355 | -0.63151 | 0 |  |  | none | FALSE | 0 | 72.5622 | FALSE | FALSE | 0.0134 |  | 72.9834 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.21058 | Normal | 73.4046 | -0.2013 | Day | 202512 | 2025-12-23 | 0.2013
2025-12-23 15:43 | 72.941 | FALSE | FALSE | -0.33678 | -0.46385 | -0.44982 | -0.6129 | 0 |  |  | none | FALSE | 0 | 72.6042 | FALSE | FALSE | 0.0192 |  | 72.9975 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.19665 | Normal | 73.3908 | -0.28742 | Day | 202512 | 2025-12-23 | 0.28742
2025-12-23 15:58 | 72.941 | FALSE | FALSE | -0.29032 | -0.39962 | -0.43162 | -0.58826 | 0 |  |  | none | FALSE | 0 | 72.6507 | FALSE | FALSE | 0.0261 |  | 73.0117 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.18049 | Normal | 73.3726 | -0.39144 | Day | 202512 | 2025-12-23 | 0.39144
2025-12-23 16:13 | 72.6584 | FALSE | FALSE | -0.0077242 | -0.010632 | -0.71422 | -0.97342 | -0.2826 |  |  | none | FALSE | 0 | 72.6507 | FALSE | FALSE | 0.1305 |  | 73.0117 | 0 | -0.2826 | 0 | 0.18338 | -1.5411 | 0.18049 | Normal | 73.3726 | -1.9572 | Day | 202512 | 2025-12-23 | 1.9572
2025-12-23 16:28 | 72.6584 | FALSE | FALSE | -0.054176 | -0.074618 | -0.73242 | -0.99797 | 0 |  |  | none | FALSE | 0 | 72.6042 | FALSE | FALSE | 0.115 |  | 72.9975 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.19665 | Normal | 73.3908 | -1.7245 | Day | 202512 | 2025-12-23 | 1.7245
2025-12-23 16:43 | 72.6584 | FALSE | FALSE | -0.096174 | -0.13254 | -0.74615 | -1.0165 | 0 |  |  | none | FALSE | 0 | 72.5622 | FALSE | FALSE | 0.1029 |  | 72.9834 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.21058 | Normal | 73.4046 | -1.5433 | Day | 202512 | 2025-12-23 | 1.5433
2025-12-23 16:58 | 72.3758 | FALSE | FALSE | 0.080035 | 0.11046 | -1.0504 | -1.4305 | -0.2826 | 2025-12-23 18:42 | 2025-12-23 16:58 | lower | TRUE | 0 | 72.4558 | FALSE | FALSE | 0.2125 | 2.3299 | 72.941 | 1 | -0.2826 | -0.04239 | 0.16593 | -1.4477 | 0.24258 | Extreme triggered | 73.4262 | -2.3299 | Day | 202512 | 2025-12-23 | 2.3299
2025-12-23 17:13 | 72.3758 | FALSE | FALSE | -0.0046923 | -0.0064837 | -1.0503 | -1.4304 | 0 |  | 2025-12-23 16:58 | none | FALSE | 0 | 72.3711 | FALSE | FALSE | 0.2464 | 2.1561 | 72.8986 | 2 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.26375 | Extreme/elevated | 73.4261 | -1.9822 | Day | 202512 | 2025-12-23 | 1.9822
2025-12-23 17:27 | 72.095 | FALSE | FALSE | 0.1319 | 0.18262 | -1.3625 | -1.8548 | -0.2808 |  | 2025-12-23 16:58 | lower | TRUE | 0 | 72.2269 | FALSE | TRUE | 0.3333 | 2.247 | 72.8422 | 3 | -0.2808 | -0.05643 | 0.17384 | -1.2907 | 0.30764 | Persistent | 73.4575 | -2.4287 | Day | 202512 | 2025-12-23 | 2.4287
2025-12-23 17:42 | 72.095 | FALSE | FALSE | 0.0073748 | 0.010228 | -1.4024 | -1.9081 | 0 |  | 2025-12-23 16:58 | lower | TRUE | 0 | 72.1024 | FALSE | TRUE | 0.3633 | 2.1905 | 72.7999 | 4 | 0 | -0.0423 | 0.16579 | 0.25514 | 0.34875 | Persistent | 73.4974 | -2.0211 | Night | 202512 | 2025-12-23 | 2.0211
2025-12-23 17:57 | 71.8124 | FALSE | FALSE | 0.12053 | 0.16755 | -1.7698 | -2.4052 | -0.2826 |  | 2025-12-23 16:58 | lower | TRUE | 0 | 71.9329 | FALSE | TRUE | 0.4385 | 2.2109 | 72.7576 | 5 | -0.2826 | -0.0423 | 0.16579 | -1.4494 | 0.41233 | Persistent | 73.5822 | -2.2923 | Night | 202512 | 2025-12-23 | 2.2923
2025-12-23 18:12 | 72.095 | FALSE | FALSE | -0.25027 | -0.34835 | -1.4908 | -2.026 | 0.2826 |  | 2025-12-23 16:58 | none | FALSE | 0 | 71.8447 | FALSE | FALSE | 0.4379 | 2.0799 | 72.7153 | 6 | 0.2826 | -0.0423 | 0.16579 | 1.9597 | 0.43528 | Persistent | 73.5858 | -1.425 | Night | 202512 | 2025-12-23 | 1.425
2025-12-23 18:27 | 72.095 | FALSE | TRUE | -0.32789 | -0.45688 | -1.4838 | -2.0167 | 0 |  | 2025-12-23 16:58 | none | FALSE | 0 | 71.7671 | FALSE | FALSE | 0.4851 | 1.9651 | 72.673 | 7 | 0 | -0.0423 | 0.16579 | 0.25514 | 0.45293 | Confirmed/Materialized Shift | 73.5788 | -1.2761 | Night | 202512 | 2025-12-23 | 1.2761
2025-12-23 18:42 | 72.3758 | FALSE | FALSE | -0.63701 | -0.88796 | -1.1748 | -1.5973 | 0.2808 |  |  | none | FALSE | 0 | 71.7388 | FALSE | FALSE | 0.0396 |  | 72.6447 | 0 | 0.2808 | -0.02826 | 0.18077 | 1.7097 | 0.45296 | Persistence ends | 73.5506 | -0.59369 | Night | 202512 | 2025-12-23 | 0.59369
2025-12-23 18:42 | 72.3758 | FALSE | FALSE | -0.644 | -0.89779 | -1.0971 | -1.4931 | 0 |  |  | none | FALSE | 0 | 71.7318 | FALSE | FALSE | 0.0347 |  | 72.6023 | 0 | 0 | -0.04239 | 0.1656 | 0.25597 | 0.43526 | Normal | 73.4729 | -0.52044 | Night | 202512 | 2025-12-23 | 0.52044
2025-12-23 18:43 | 72.3758 | FALSE | FALSE | -0.64036 | -0.89267 | -1.0086 | -1.3745 | 0 |  |  | none | FALSE | 0 | 71.7354 | FALSE | FALSE | 0.0298 |  | 72.5599 | 0 | 0 | -0.04239 | 0.1656 | 0.25597 | 0.41225 | Normal | 73.3844 | -0.44667 | Night | 202512 | 2025-12-23 | 0.44667
2025-12-23 18:58 | 72.941 | TRUE | FALSE | -1.1806 | -1.6451 | -0.39018 | -0.53208 | 0.5652 |  |  | none | FALSE | 1 | 71.7604 | FALSE | FALSE | 0.0957 |  | 72.5458 | 0 | 0.5652 | -0.01413 | 0.21429 | 2.7035 | 0.39268 | Normal | 73.3312 | 1.0064 | Night | 202512 | 2025-12-23 | 1.0064
2025-12-23 19:13 | 73.2236 | FALSE | FALSE | -1.4632 | -2.0389 | -0.10758 | -0.1467 | 0.2826 |  |  | none | FALSE | 1 | 71.7604 | FALSE | FALSE | 0.1436 |  | 72.5458 | 0 | 0.2826 | 0 | 0.22435 | 1.2596 | 0.39268 | Normal | 73.3312 | 1.726 | Night | 202512 | 2025-12-23 | 1.726
2025-12-23 19:28 | 73.2236 | FALSE | FALSE | -1.4882 | -2.0745 | -0.16084 | -0.21917 | 0 |  |  | none | FALSE | 1 | 71.7354 | FALSE | FALSE | 0.1359 |  | 72.5599 | 0 | 0 | 0.01413 | 0.21429 | -0.065939 | 0.41225 | Normal | 73.3844 | 1.6099 | Night | 202512 | 2025-12-23 | 1.6099
2025-12-23 19:42 | 73.2236 | FALSE | FALSE | -1.5104 | -2.1062 | -0.21135 | -0.2878 | 0 |  |  | none | FALSE | 1 | 71.7132 | FALSE | FALSE | 0.1292 |  | 72.5741 | 0 | 0 | 0.01413 | 0.21429 | -0.065939 | 0.43044 | Normal | 73.4349 | 1.509 | Night | 202512 | 2025-12-23 | 1.509
2025-12-23 19:57 | 73.2236 | FALSE | FALSE | -1.5302 | -2.1344 | -0.25944 | -0.35307 | 0 |  |  | none | FALSE | 1 | 71.6934 | FALSE | FALSE | 0.1232 |  | 72.5882 | 0 | 0 | 0.01413 | 0.21429 | -0.065939 | 0.44742 | Normal | 73.483 | 1.4201 | Night | 202512 | 2025-12-23 | 1.4201
2025-12-23 20:12 | 73.2236 | FALSE | FALSE | -1.5479 | -2.1596 | -0.30539 | -0.41533 | 0 |  |  | none | FALSE | 1 | 71.6757 | FALSE | FALSE | 0.118 |  | 72.6023 | 0 | 0 | 0.01413 | 0.21429 | -0.065939 | 0.46333 | Normal | 73.529 | 1.3409 | Night | 202512 | 2025-12-23 | 1.3409
2025-12-23 20:27 | 73.2236 | FALSE | FALSE | -1.5637 | -2.1821 | -0.3494 | -0.4749 | 0 |  |  | none | FALSE | 1 | 71.6599 | FALSE | FALSE | 0.1132 |  | 72.6165 | 0 | 0 | 0.01413 | 0.21429 | -0.065939 | 0.47827 | Normal | 73.573 | 1.2695 | Night | 202512 | 2025-12-23 | 1.2695
2025-12-23 20:41 | 73.2236 | FALSE | FALSE | -1.5733 | -2.1958 | -0.41552 | -0.56427 | 0 |  |  | none | FALSE | 1 | 71.6503 | FALSE | FALSE | 0.1062 |  | 72.6447 | 0 | 0 | 0.02826 | 0.2027 | -0.13942 | 0.4972 | Normal | 73.6391 | 1.1643 | Night | 202512 | 2025-12-23 | 1.1643
2025-12-23 20:56 | 73.2236 | FALSE | FALSE | -1.5782 | -2.2028 | -0.47699 | -0.6472 | 0 |  |  | none | FALSE | 1 | 71.6454 | FALSE | FALSE | 0.1 |  | 72.673 | 0 | 0 | 0.02826 | 0.2027 | -0.13942 | 0.51381 | Normal | 73.7006 | 1.0717 | Night | 202512 | 2025-12-23 | 1.0717
2025-12-23 21:11 | 73.2236 | FALSE | FALSE | -1.579 | -2.2039 | -0.53424 | -0.72432 | 0 |  |  | none | FALSE | 1 | 71.6446 | FALSE | FALSE | 0.0945 |  | 72.7012 | 0 | 0 | 0.02826 | 0.2027 | -0.13942 | 0.5283 | Normal | 73.7578 | 0.98876 | Night | 202512 | 2025-12-23 | 0.98876
2025-12-23 21:26 | 73.2236 | FALSE | FALSE | -1.5495 | -2.1619 | -0.5896 | -0.79878 | 0 |  |  | none | FALSE | 0 | 71.6741 | FALSE | FALSE | 0.0598 |  | 72.7436 | 0 | 0 | 0.04239 | 0.18929 | -0.22394 | 0.53479 | Normal | 73.8132 | 0.8975 | Night | 202512 | 2025-12-23 | 0.8975
2025-12-23 21:41 | 73.2236 | FALSE | FALSE | -1.513 | -2.1098 | -0.6378 | -0.86351 | 0 |  |  | none | FALSE | 0 | 71.7106 | FALSE | FALSE | 0.0543 |  | 72.786 | 0 | 0 | 0.04239 | 0.18929 | -0.22394 | 0.53769 | Normal | 73.8614 | 0.81382 | Night | 202512 | 2025-12-23 | 0.81382
2025-12-23 21:56 | 73.2236 | FALSE | FALSE | -1.4217 | -1.9801 | -0.65943 | -0.89253 | 0 |  |  | none | FALSE | 0 | 71.8019 | FALSE | FALSE | 0.0488 |  | 72.8424 | 0 | 0 | 0.05643 | 0.17384 | -0.3246 | 0.52029 | Normal | 73.883 | 0.73257 | Night | 202512 | 2025-12-23 | 0.73257
2025-12-23 22:11 | 73.2236 | FALSE | FALSE | -1.3159 | -1.8299 | -0.66643 | -0.90192 | 0 |  |  | none | FALSE | 0 | 71.9077 | FALSE | FALSE | 0.0437 |  | 72.8989 | 0 | 0 | 0.05643 | 0.17384 | -0.3246 | 0.49557 | Normal | 73.89 | 0.65524 | Night | 202512 | 2025-12-23 | 0.65524
2025-12-23 22:26 | 73.2236 | FALSE | FALSE | -1.1115 | -1.5414 | -0.60322 | -0.81707 | 0 |  |  | none | FALSE | 0 | 72.1121 | FALSE | FALSE | 0.0395 |  | 72.9694 | 0 | 0 | 0.07056 | 0.15534 | -0.45424 | 0.42869 | Normal | 73.8268 | 0.59288 | Night | 202512 | 2025-12-23 | 0.59288
2025-12-23 22:41 | 73.2236 | FALSE | FALSE | -0.95556 | -1.3222 | -0.5601 | -0.75911 | 0 |  |  | none | FALSE | 0 | 72.268 | FALSE | FALSE | 0.0348 |  | 73.0259 | 0 | 0 | 0.05643 | 0.1477 | -0.38207 | 0.37891 | Normal | 73.7837 | 0.52183 | Night | 202512 | 2025-12-23 | 0.52183
2025-12-23 22:56 | 73.2236 | FALSE | FALSE | -0.76316 | -1.0532 | -0.48056 | -0.65201 | 0 |  |  | none | FALSE | 0 | 72.4604 | FALSE | FALSE | 0.0303 |  | 73.0823 | 0 | 0 | 0.05643 | 0.1477 | -0.38207 | 0.31093 | Normal | 73.7042 | 0.45445 | Night | 202512 | 2025-12-23 | 0.45445
2025-12-23 23:11 | 72.941 | FALSE | FALSE | -0.36191 | -0.49864 | -0.70103 | -0.95194 | -0.2826 |  |  | none | FALSE | 0 | 72.5791 | FALSE | FALSE | 0.0425 |  | 73.1106 | 0 | -0.2826 | 0.02826 | 0.15614 | -1.9909 | 0.26574 | Normal | 73.642 | -0.63808 | Night | 202512 | 2025-12-23 | 0.63808
2025-12-23 23:26 | 72.941 | FALSE | FALSE | -0.2163 | -0.29742 | -0.61194 | -0.83197 | 0 |  |  | none | FALSE | 0 | 72.7247 | FALSE | FALSE | 0.0637 |  | 73.1388 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.20706 | Normal | 73.5529 | -0.95538 | Night | 202512 | 2025-12-23 | 0.95538
2025-12-23 23:40 | 72.941 | FALSE | FALSE | -0.0058732 | -0.0080526 | -0.45803 | -0.62403 | 0 |  |  | none | FALSE | 0 | 72.9351 | FALSE | FALSE | 0.13 |  | 73.1671 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.11598 | Normal | 73.399 | -1.9494 | Night | 202512 | 2025-12-23 | 1.9494
2025-12-23 23:55 | 72.941 | FALSE | FALSE | -0.0058732 | -0.0080526 | -0.45803 | -0.62403 | 0 |  |  | none | FALSE | 0 | 72.9351 | FALSE | FALSE | 0.13 |  | 73.1671 | 0 | 0 | 0 | 0.091688 | 0 | 0.11598 | Normal | 73.399 | -1.9494 | Night | 202512 | 2025-12-23 | 1.9494
2025-12-24 00:10 | 72.941 | FALSE | FALSE | -0.039147 | -0.053698 | -0.46305 | -0.63082 | 0 |  |  | none | FALSE | 0 | 72.9019 | FALSE | FALSE | 0.1125 |  | 73.153 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.12555 | Normal | 73.404 | -1.6882 | Night | 202512 | 2025-12-24 | 1.6882
2025-12-24 00:26 | 72.941 | FALSE | FALSE | -0.067916 | -0.093197 | -0.46356 | -0.63151 | 0 |  |  | none | FALSE | 0 | 72.8731 | FALSE | FALSE | 0.0993 |  | 73.1388 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13287 | Normal | 73.4046 | -1.4888 | Night | 202512 | 2025-12-24 | 1.4888
2025-12-24 00:40 | 72.6584 | TRUE | FALSE | 0.11403 | 0.1567 | -0.79029 | -1.076 | -0.2826 | 2025-12-24 06:09 | 2025-12-24 00:40 | lower | TRUE | 1 | 72.7724 | FALSE | FALSE | 0.264 | 2.6745 | 73.1106 | 1 | -0.2826 | -0.02826 | 0.086982 | -2.924 | 0.16906 | Extreme triggered | 73.4487 | -2.6745 | Night | 202512 | 2025-12-24 | 2.6745
2025-12-24 00:55 | 72.6584 | FALSE | FALSE | 0.034903 | 0.048014 | -0.8129 | -1.1064 | 0 |  | 2025-12-24 00:40 | lower | TRUE | 1 | 72.6933 | FALSE | FALSE | 0.2882 | 2.427 | 73.0823 | 2 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.1945 | Extreme/elevated | 73.4713 | -2.1794 | Night | 202512 | 2025-12-24 | 2.1794
2025-12-24 01:10 | 72.6584 | FALSE | FALSE | -0.030485 | -0.041975 | -0.82177 | -1.1183 | 0 |  | 2025-12-24 00:40 | none | FALSE | 1 | 72.6279 | FALSE | FALSE | 0.3238 | 2.237 | 73.054 | 3 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21306 | Persistent | 73.4802 | -1.8569 | Night | 202512 | 2025-12-24 | 1.8569
2025-12-24 01:25 | 72.6584 | FALSE | FALSE | -0.085523 | -0.11784 | -0.82028 | -1.1164 | 0 |  | 2025-12-24 00:40 | none | FALSE | 1 | 72.5729 | FALSE | FALSE | 0.3653 | 2.0833 | 73.0258 | 4 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22645 | Persistent | 73.4787 | -1.6223 | Night | 202512 | 2025-12-24 | 1.6223
2025-12-24 01:40 | 72.6584 | FALSE | FALSE | -0.13198 | -0.18197 | -0.81022 | -1.1028 | 0 |  | 2025-12-24 00:40 | none | FALSE | 1 | 72.5264 | FALSE | FALSE | 0.4103 | 1.9546 | 72.9975 | 5 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.23555 | Persistent | 73.4686 | -1.4397 | Night | 202512 | 2025-12-24 | 1.4397
2025-12-24 01:55 | 72.6584 | FALSE | FALSE | -0.17083 | -0.23566 | -0.79255 | -1.079 | 0 |  | 2025-12-24 00:40 | none | FALSE | 1 | 72.4876 | FALSE | FALSE | 0.4575 | 1.8439 | 72.9693 | 6 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.24084 | Persistent | 73.4509 | -1.2907 | Night | 202512 | 2025-12-24 | 1.2907
2025-12-24 02:10 | 72.6584 | FALSE | TRUE | -0.20256 | -0.27957 | -0.76776 | -1.0456 | 0 |  | 2025-12-24 00:40 | none | FALSE | 1 | 72.4558 | FALSE | FALSE | 0.5062 | 1.7469 | 72.941 | 7 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.24258 | Confirmed/Materialized Shift | 73.4262 | -1.165 | Night | 202512 | 2025-12-24 | 1.165
2025-12-24 02:25 | 72.3758 | TRUE | TRUE | -0.0046923 | -0.0064837 | -1.0503 | -1.4304 | -0.2826 |  | 2025-12-24 00:40 | none | FALSE | 2 | 72.3711 | TRUE | FALSE | 0.5893 | 1.7763 | 72.8986 | 8 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.26375 | Confirmed/Materialized Shift | 73.4261 | -1.9822 | Night | 202512 | 2025-12-24 | 1.9822
2025-12-24 02:39 | 72.3758 | FALSE | TRUE | -0.072753 | -0.10062 | -1.0336 | -1.408 | 0 |  | 2025-12-24 00:40 | none | FALSE | 2 | 72.303 | FALSE | FALSE | 0.5729 | 1.772 | 72.8562 | 9 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27659 | Confirmed/Materialized Shift | 73.4094 | -1.737 | Night | 202512 | 2025-12-24 | 1.737
2025-12-24 02:55 | 72.3758 | FALSE | TRUE | -0.12643 | -0.17499 | -1.0025 | -1.3662 | 0 |  | 2025-12-24 00:40 | none | FALSE | 2 | 72.2494 | FALSE | FALSE | 0.5606 | 1.75 | 72.8138 | 10 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.28223 | Confirmed/Materialized Shift | 73.3783 | -1.552 | Night | 202512 | 2025-12-24 | 1.552
2025-12-24 03:10 | 72.3758 | FALSE | TRUE | -0.16658 | -0.23069 | -0.95786 | -1.3062 | 0 |  | 2025-12-24 00:40 | none | FALSE | 1 | 72.2092 | FALSE | FALSE | 0.5224 | 1.7188 | 72.7714 | 11 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.28111 | Confirmed/Materialized Shift | 73.3337 | -1.4074 | Night | 202512 | 2025-12-24 | 1.4074
2025-12-24 03:25 | 72.3758 | FALSE | TRUE | -0.19304 | -0.26743 | -0.89954 | -1.2276 | 0 |  | 2025-12-24 00:40 | none | FALSE | 1 | 72.1828 | FALSE | FALSE | 0.5148 | 1.6834 | 72.7291 | 12 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27315 | Confirmed/Materialized Shift | 73.2753 | -1.2933 | Night | 202512 | 2025-12-24 | 1.2933
2025-12-24 03:39 | 72.3758 | FALSE | TRUE | -0.20455 | -0.28342 | -0.82627 | -1.1288 | 0 |  | 2025-12-24 00:40 | none | FALSE | 1 | 72.1712 | FALSE | FALSE | 0.509 | 1.6467 | 72.6867 | 13 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.25771 | Confirmed/Materialized Shift | 73.2021 | -1.2063 | Night | 202512 | 2025-12-24 | 1.2063
2025-12-24 03:54 | 72.3758 | FALSE | TRUE | -0.19815 | -0.27453 | -0.73509 | -1.0054 | 0 |  | 2025-12-24 00:40 | none | FALSE | 1 | 72.1777 | FALSE | FALSE | 0.5053 | 1.6112 | 72.6443 | 14 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.23331 | Confirmed/Materialized Shift | 73.1109 | -1.1507 | Night | 202512 | 2025-12-24 | 1.1507
2025-12-24 04:09 | 72.095 | TRUE | TRUE | 0.0018206 | 0.0025252 | -1.0121 | -1.3844 | -0.2808 |  | 2025-12-24 00:40 | lower | TRUE | 2 | 72.0968 | TRUE | TRUE | 0.591 | 1.6376 | 72.602 | 15 | -0.2808 | -0.0423 | 0.10331 | -2.3086 | 0.25257 | Confirmed/Materialized Shift | 73.1071 | -2.0072 | Night | 202512 | 2025-12-24 | 2.0072
2025-12-24 04:24 | 72.095 | FALSE | TRUE | -0.062163 | -0.086298 | -0.9915 | -1.3566 | 0 |  | 2025-12-24 00:40 | none | FALSE | 2 | 72.0328 | FALSE | FALSE | 0.5747 | 1.6455 | 72.5597 | 16 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.26342 | Confirmed/Materialized Shift | 73.0865 | -1.764 | Night | 202512 | 2025-12-24 | 1.764
2025-12-24 04:39 | 72.095 | FALSE | TRUE | -0.11136 | -0.1547 | -0.9561 | -1.3088 | 0 |  | 2025-12-24 00:40 | none | FALSE | 2 | 71.9836 | FALSE | FALSE | 0.5627 | 1.6418 | 72.5174 | 17 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.26686 | Confirmed/Materialized Shift | 73.0511 | -1.5827 | Night | 202512 | 2025-12-24 | 1.5827
2025-12-24 04:54 | 72.095 | FALSE | TRUE | -0.14634 | -0.20339 | -0.90648 | -1.2417 | 0 |  | 2025-12-24 00:40 | none | FALSE | 1 | 71.9487 | FALSE | FALSE | 0.5248 | 1.6309 | 72.4751 | 18 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.2632 | Confirmed/Materialized Shift | 73.0015 | -1.444 | Night | 202512 | 2025-12-24 | 1.444
2025-12-24 05:09 | 72.095 | FALSE | TRUE | -0.16649 | -0.23147 | -0.84203 | -1.1545 | 0 |  | 2025-12-24 00:40 | none | FALSE | 1 | 71.9285 | FALSE | FALSE | 0.5179 | 1.6155 | 72.4328 | 19 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.25213 | Confirmed/Materialized Shift | 72.937 | -1.3397 | Night | 202512 | 2025-12-24 | 1.3397
2025-12-24 05:24 | 72.095 | FALSE | TRUE | -0.1697 | -0.23594 | -0.76064 | -1.044 | 0 |  | 2025-12-24 00:40 | none | FALSE | 1 | 71.9253 | FALSE | FALSE | 0.5133 | 1.5983 | 72.3905 | 20 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.23259 | Confirmed/Materialized Shift | 72.8556 | -1.2704 | Night | 202512 | 2025-12-24 | 1.2704
2025-12-24 05:39 | 72.095 | FALSE | TRUE | -0.19779 | -0.2751 | -0.73239 | -1.0057 | 0 |  | 2025-12-24 00:40 | none | FALSE | 1 | 71.8972 | FALSE | FALSE | 0.5052 | 1.5769 | 72.3623 | 21 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.23255 | Confirmed/Materialized Shift | 72.8274 | -1.1495 | Night | 202512 | 2025-12-24 | 1.1495
2025-12-24 05:54 | 72.095 | FALSE | TRUE | -0.21864 | -0.30419 | -0.6969 | -0.95739 | 0 |  | 2025-12-24 00:40 | none | FALSE | 1 | 71.8764 | FALSE | FALSE | 0.4982 | 1.5527 | 72.3341 | 22 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.22888 | Confirmed/Materialized Shift | 72.7919 | -1.0448 | Night | 202512 | 2025-12-24 | 1.0448
2025-12-24 06:09 | 72.095 | FALSE | FALSE | -0.23189 | -0.32268 | -0.65381 | -0.89872 | 0 |  |  | none | FALSE | 1 | 71.8631 | FALSE | FALSE | 0.0921 |  | 72.306 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.22142 | Persistence ends | 72.7488 | -0.95275 | Night | 202512 | 2025-12-24 | 0.95275
2025-12-24 06:24 | 72.095 | FALSE | FALSE | -0.23672 | -0.32943 | -0.6023 | -0.82851 | 0 |  |  | none | FALSE | 1 | 71.8583 | FALSE | FALSE | 0.0867 |  | 72.2778 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.20976 | Normal | 72.6973 | -0.87144 | Night | 202512 | 2025-12-24 | 0.87144
2025-12-24 06:38 | 71.8124 | TRUE | FALSE | -0.005345 | -0.0074435 | -0.85152 | -1.1719 | -0.2826 |  |  | none | FALSE | 1 | 71.8071 | FALSE | FALSE | 0.1602 |  | 72.2355 | 0 | -0.2826 | -0.0423 | 0.10331 | -2.326 | 0.21422 | Normal | 72.6639 | -1.975 | Night | 202512 | 2025-12-24 | 1.975
2025-12-24 06:53 | 71.8124 | FALSE | FALSE | -0.038799 | -0.054057 | -0.80038 | -1.1023 | 0 |  |  | none | FALSE | 1 | 71.7736 | FALSE | FALSE | 0.1496 |  | 72.1932 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.20979 | Normal | 72.6128 | -1.8151 | Night | 202512 | 2025-12-24 | 1.8151
2025-12-24 07:08 | 71.8124 | FALSE | FALSE | -0.053282 | -0.074251 | -0.73026 | -1.0067 | 0 |  |  | none | FALSE | 1 | 71.7591 | FALSE | FALSE | 0.1438 |  | 72.1509 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.19589 | Normal | 72.5427 | -1.728 | Night | 202512 | 2025-12-24 | 1.728
2025-12-24 07:23 | 71.8124 | FALSE | FALSE | -0.094174 | -0.13131 | -0.71481 | -0.98558 | 0 |  |  | none | FALSE | 1 | 71.7182 | FALSE | FALSE | 0.1309 |  | 72.1227 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.20225 | Normal | 72.5272 | -1.5344 | Day | 202512 | 2025-12-24 | 1.5344
2025-12-24 07:30 | 71.8124 | FALSE | FALSE | -0.12658 | -0.17658 | -0.69088 | -0.9529 | 0 |  |  | none | FALSE | 1 | 71.6858 | FALSE | FALSE | 0.1206 |  | 72.0945 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.20437 | Normal | 72.5033 | -1.3806 | Day | 202512 | 2025-12-24 | 1.3806
2025-12-24 07:45 | 71.8124 | FALSE | FALSE | -0.15078 | -0.2104 | -0.65874 | -0.90897 | 0 |  |  | none | FALSE | 1 | 71.6616 | FALSE | FALSE | 0.1122 |  | 72.0664 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.20238 | Normal | 72.4711 | -1.255 | Day | 202512 | 2025-12-24 | 1.255
2025-12-24 08:00 | 71.8124 | FALSE | FALSE | -0.16651 | -0.2324 | -0.61813 | -0.85341 | 0 |  |  | none | FALSE | 1 | 71.6459 | FALSE | FALSE | 0.1053 |  | 72.0382 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.19616 | Normal | 72.4305 | -1.1512 | Day | 202512 | 2025-12-24 | 1.1512
2025-12-24 08:15 | 71.8124 | FALSE | FALSE | -0.17292 | -0.24137 | -0.5682 | -0.78501 | 0 |  |  | none | FALSE | 1 | 71.6395 | FALSE | FALSE | 0.0997 |  | 72.01 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.18528 | Normal | 72.3806 | -1.0667 | Day | 202512 | 2025-12-24 | 1.0667
2025-12-24 08:30 | 72.095 | TRUE | FALSE | -0.43042 | -0.6006 | -0.23242 | -0.32134 | 0.2826 |  |  | none | FALSE | 2 | 71.6646 | TRUE | FALSE | 0.097 |  | 71.996 | 0 | 0.2826 | -0.01404 | 0.11113 | 2.6694 | 0.16571 | Normal | 72.3274 | 0.59743 | Day | 202512 | 2025-12-24 | 0.59743
2025-12-24 08:45 | 72.095 | FALSE | FALSE | -0.39712 | -0.55388 | -0.17104 | -0.23669 | 0 |  |  | none | FALSE | 2 | 71.6979 | FALSE | FALSE | 0.1102 |  | 71.982 | 0 | 0 | -0.01404 | 0.11113 | 0.12634 | 0.14204 | Normal | 72.266 | 0.79582 | Day | 202512 | 2025-12-24 | 0.79582
2025-12-24 08:45 | 72.095 | FALSE | FALSE | -0.39712 | -0.55388 | -0.17104 | -0.23669 | 0 |  |  | none | FALSE | 1 | 71.6979 | FALSE | FALSE | 0.0816 |  | 71.982 | 0 | 0 | 0 | 0.091688 | 0 | 0.14204 | Normal | 72.266 | 0.79582 | Day | 202512 | 2025-12-24 | 0.79582
2025-12-24 09:00 | 72.3758 | TRUE | FALSE | -0.71122 | -0.99243 | 0.048382 | 0.066893 | 0.2808 | 2025-12-24 12:17 | 2025-12-24 09:00 | upper | TRUE | 2 | 71.6646 | TRUE | FALSE | 0.2671 | 2.292 | 71.996 | 1 | 0.2808 | 0.01404 | 0.11113 | 2.4005 | 0.16571 | Extreme triggered | 72.3274 | 2.292 | Day | 202512 | 2025-12-24 | 2.292
2025-12-24 09:15 | 72.3758 | FALSE | FALSE | -0.73632 | -1.0278 | -0.0047973 | -0.0066279 | 0 |  | 2025-12-24 09:00 | none | FALSE | 2 | 71.6395 | FALSE | FALSE | 0.303 | 2.133 | 72.01 | 2 | 0 | 0.01404 | 0.11113 | -0.12634 | 0.18528 | Extreme/elevated | 72.3806 | 1.9741 | Day | 202512 | 2025-12-24 | 1.9741
2025-12-24 09:30 | 72.6584 | TRUE | FALSE | -1.0902 | -1.5234 | 0.15014 | 0.20706 | 0.2826 |  | 2025-12-24 09:00 | upper | TRUE | 3 | 71.5682 | TRUE | TRUE | 0.4331 | 2.3016 | 72.0382 | 3 | 0.2826 | 0.02817 | 0.12619 | 2.0162 | 0.23503 | Persistent | 72.5083 | 2.6388 | Day | 202512 | 2025-12-24 | 2.6388
2025-12-24 09:44 | 72.941 | FALSE | FALSE | -1.4804 | -2.0717 | 0.24055 | 0.33088 | 0.2826 |  | 2025-12-24 09:00 | upper | TRUE | 3 | 71.4606 | FALSE | TRUE | 0.4994 | 2.4202 | 72.0805 | 4 | 0.2826 | 0.0423 | 0.13813 | 1.7397 | 0.30997 | Persistent | 72.7004 | 2.7761 | Day | 202512 | 2025-12-24 | 2.7761
2025-12-24 09:59 | 72.941 | FALSE | FALSE | -1.548 | -2.1683 | 0.088376 | 0.12131 | 0 |  | 2025-12-24 09:00 | upper | TRUE | 3 | 71.393 | FALSE | TRUE | 0.5209 | 2.3846 | 72.1228 | 5 | 0 | 0.0423 | 0.13813 | -0.30624 | 0.36491 | Persistent | 72.8526 | 2.2422 | Day | 202512 | 2025-12-24 | 2.2422
2025-12-24 10:14 | 73.2236 | FALSE | FALSE | -1.9242 | -2.6988 | 0.1645 | 0.22515 | 0.2826 |  | 2025-12-24 09:00 | upper | TRUE | 3 | 71.2994 | FALSE | TRUE | 0.5868 | 2.3828 | 72.1792 | 6 | 0.2826 | 0.05643 | 0.1477 | 1.5313 | 0.43993 | Persistent | 73.0591 | 2.3739 | Day | 202512 | 2025-12-24 | 2.3739
2025-12-24 10:30 | 73.2236 | FALSE | TRUE | -1.9824 | -2.7826 | -0.006493 | -0.0088665 | 0 |  | 2025-12-24 09:00 | none | FALSE | 3 | 71.2412 | FALSE | FALSE | 0.6182 | 2.3263 | 72.2357 | 7 | 0 | 0.05643 | 0.1477 | -0.38207 | 0.49721 | Confirmed/Materialized Shift | 73.2301 | 1.9869 | Day | 202512 | 2025-12-24 | 1.9869
2025-12-24 10:44 | 73.2236 | FALSE | TRUE | -2.0163 | -2.8316 | -0.15329 | -0.20891 | 0 |  | 2025-12-24 09:00 | none | FALSE | 2 | 71.2073 | FALSE | FALSE | 0.5716 | 2.2502 | 72.2921 | 8 | 0 | 0.05643 | 0.1477 | -0.38207 | 0.5424 | Confirmed/Materialized Shift | 73.3769 | 1.7174 | Day | 202512 | 2025-12-24 | 1.7174
2025-12-24 10:59 | 73.5062 | FALSE | TRUE | -2.351 | -3.304 | -0.06392 | -0.086884 | 0.2826 |  | 2025-12-24 09:00 | none | FALSE | 2 | 71.1552 | FALSE | FALSE | 0.5834 | 2.2106 | 72.3627 | 9 | 0.2826 | 0.07056 | 0.15534 | 1.365 | 0.60373 | Confirmed/Materialized Shift | 73.5701 | 1.8941 | Day | 202512 | 2025-12-24 | 1.8941
2025-12-24 11:14 | 73.5062 | FALSE | TRUE | -2.3392 | -3.2869 | -0.22151 | -0.30044 | 0 |  | 2025-12-24 09:00 | none | FALSE | 2 | 71.167 | FALSE | FALSE | 0.5674 | 2.1549 | 72.4474 | 10 | 0 | 0.08469 | 0.13273 | -0.63807 | 0.64018 | Confirmed/Materialized Shift | 73.7277 | 1.654 | Day | 202512 | 2025-12-24 | 1.654
2025-12-24 11:29 | 73.7888 | FALSE | TRUE | -2.6182 | -3.6788 | -0.13293 | -0.17982 | 0.2826 |  | 2025-12-24 09:00 | none | FALSE | 1 | 71.1706 | FALSE | FALSE | 0.549 | 2.1233 | 72.5462 | 11 | 0.2826 | 0.09882 | 0.13817 | 1.3301 | 0.68778 | Confirmed/Materialized Shift | 73.9217 | 1.8067 | Day | 202512 | 2025-12-24 | 1.8067
2025-12-24 11:44 | 73.7888 | FALSE | TRUE | -2.58 | -3.6232 | -0.29243 | -0.39474 | 0 |  | 2025-12-24 09:00 | none | FALSE | 1 | 71.2088 | FALSE | FALSE | 0.5348 | 2.0791 | 72.645 | 12 | 0 | 0.09882 | 0.13817 | -0.71522 | 0.71812 | Confirmed/Materialized Shift | 74.0812 | 1.5928 | Day | 202512 | 2025-12-24 | 1.5928
2025-12-24 11:44 | 74.0714 | FALSE | TRUE | -2.8272 | -3.9684 | -0.2003 | -0.26968 | 0.2826 |  | 2025-12-24 09:00 | none | FALSE | 0 | 71.2442 | FALSE | FALSE | 0.5157 | 2.0526 | 72.7579 | 13 | 0.2826 | 0.11295 | 0.14193 | 1.1953 | 0.75688 | Confirmed/Materialized Shift | 74.2717 | 1.7354 | Day | 202512 | 2025-12-24 | 1.7354
2025-12-24 11:47 | 74.0714 | FALSE | TRUE | -2.7538 | -3.8613 | -0.35279 | -0.47402 | 0 |  | 2025-12-24 09:00 | none | FALSE | 0 | 71.3176 | FALSE | FALSE | 0.5031 | 2.0164 | 72.8709 | 14 | 0 | 0.11295 | 0.14193 | -0.79582 | 0.77665 | Confirmed/Materialized Shift | 74.4242 | 1.5458 | Day | 202512 | 2025-12-24 | 1.5458
2025-12-24 12:02 | 73.7888 | TRUE | TRUE | -2.34 | -3.275 | -0.7018 | -0.94214 | -0.2826 |  | 2025-12-24 09:00 | none | FALSE | 1 | 71.4488 | FALSE | FALSE | 0.5004 | 1.9538 | 72.9697 | 15 | -0.2826 | 0.09882 | 0.16582 | -2.3002 | 0.76045 | Confirmed/Materialized Shift | 74.4906 | 1.0771 | Day | 202512 | 2025-12-24 | 1.0771
2025-12-24 12:17 | 73.5062 | FALSE | FALSE | -1.8876 | -2.6356 | -0.98401 | -1.321 | -0.2826 |  |  | none | FALSE | 1 | 71.6186 | FALSE | FALSE | 0.0705 |  | 73.0544 | 0 | -0.2826 | 0.08469 | 0.18555 | -1.9794 | 0.7179 | Persistence ends | 74.4902 | 0.62933 | Day | 202512 | 2025-12-24 | 0.62933
2025-12-24 12:32 | 73.5062 | FALSE | FALSE | -1.6898 | -2.353 | -0.9556 | -1.2833 | 0 |  |  | none | FALSE | 1 | 71.8164 | FALSE | FALSE | 0.0656 |  | 73.1391 | 0 | 0 | 0.08469 | 0.18555 | -0.45642 | 0.66135 | Normal | 74.4618 | 0.55509 | Day | 202512 | 2025-12-24 | 0.55509
2025-12-24 12:43 | 73.2236 | FALSE | FALSE | -1.2562 | -1.7454 | -1.2 | -1.6124 | -0.2826 |  |  | none | FALSE | 1 | 71.9674 | FALSE | FALSE | 0.0316 |  | 73.1955 | 0 | -0.2826 | 0.05643 | 0.19654 | -1.725 | 0.61404 | Normal | 74.4236 | 0.04573 | Day | 202512 | 2025-12-24 | 0.04573
2025-12-24 12:59 | 73.2236 | FALSE | FALSE | -1.0852 | -1.5043 | -1.1419 | -1.5355 | 0 |  |  | none | FALSE | 1 | 72.1384 | FALSE | FALSE | 0.032 |  | 73.2519 | 0 | 0 | 0.05643 | 0.19654 | -0.28712 | 0.55676 | Normal | 74.3655 | -0.050919 | Day | 202512 | 2025-12-24 | 0.050919
2025-12-24 13:14 | 73.2236 | FALSE | FALSE | -0.88728 | -1.2266 | -1.0568 | -1.4228 | 0 |  |  | none | FALSE | 1 | 72.3363 | FALSE | FALSE | 0.0402 |  | 73.3084 | 0 | 0 | 0.05643 | 0.19654 | -0.28712 | 0.48603 | Normal | 74.2804 | -0.17443 | Day | 202512 | 2025-12-24 | 0.17443
2025-12-24 13:29 | 72.941 | FALSE | FALSE | -0.49141 | -0.67828 | -1.2827 | -1.7281 | -0.2826 |  |  | none | FALSE | 1 | 72.4496 | FALSE | FALSE | 0.088 |  | 73.3366 | 0 | -0.2826 | 0.02826 | 0.20296 | -1.5316 | 0.44353 | Normal | 74.2237 | -0.89204 | Day | 202512 | 2025-12-24 | 0.89204
2025-12-24 13:43 | 72.941 | FALSE | FALSE | -0.36483 | -0.50268 | -1.2126 | -1.6353 | 0 |  |  | none | FALSE | 1 | 72.5762 | FALSE | FALSE | 0.1002 |  | 73.3649 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.39436 | Normal | 74.1536 | -1.0749 | Day | 202512 | 2025-12-24 | 1.0749
2025-12-24 13:58 | 72.941 | FALSE | FALSE | -0.30628 | -0.42167 | -1.1823 | -1.5951 | 0 |  |  | none | FALSE | 1 | 72.6347 | FALSE | FALSE | 0.107 |  | 73.379 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.37215 | Normal | 74.1233 | -1.177 | Day | 202512 | 2025-12-24 | 1.177
2025-12-24 14:13 | 72.6584 | FALSE | FALSE | -0.082226 | -0.1133 | -1.4952 | -2.0164 | -0.2826 |  |  | none | FALSE | 1 | 72.5762 | FALSE | FALSE | 0.148 |  | 73.3649 | 0 | -0.2826 | -0.01413 | 0.19396 | -1.3842 | 0.39436 | Normal | 74.1536 | -1.7915 | Day | 202512 | 2025-12-24 | 1.7915
2025-12-24 14:28 | 72.6584 | FALSE | FALSE | -0.13739 | -0.18945 | -1.5221 | -2.0519 | 0 |  |  | none | FALSE | 0 | 72.521 | FALSE | FALSE | 0.1113 |  | 73.3508 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.41488 | Normal | 74.1805 | -1.6688 | Day | 202512 | 2025-12-24 | 1.6688
2025-12-24 14:43 | 72.6584 | FALSE | FALSE | -0.22057 | -0.30449 | -1.5488 | -2.0871 | 0 |  |  | none | FALSE | 0 | 72.4378 | FALSE | FALSE | 0.1001 |  | 73.3225 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.44234 | Normal | 74.2072 | -1.5014 | Day | 202512 | 2025-12-24 | 1.5014
2025-12-24 14:58 | 72.3758 | FALSE | FALSE | -0.076351 | -0.1056 | -1.885 | -2.5383 | -0.2826 |  |  | none | FALSE | 0 | 72.2994 | FALSE | FALSE | 0.123 |  | 73.2801 | 0 | -0.2826 | -0.04239 | 0.18957 | -1.2671 | 0.49034 | Normal | 74.2608 | -1.8443 | Day | 202512 | 2025-12-24 | 1.8443
2025-12-24 15:13 | 72.3758 | FALSE | FALSE | -0.19903 | -0.27576 | -1.9229 | -2.5881 | 0 |  |  | none | FALSE | 0 | 72.1768 | FALSE | FALSE | 0.1083 |  | 73.2377 | 0 | 0 | -0.04239 | 0.18957 | 0.22361 | 0.53048 | Normal | 74.2987 | -1.6248 | Day | 202512 | 2025-12-24 | 1.6248
2025-12-24 15:28 | 72.6584 | FALSE | FALSE | -0.54637 | -0.75767 | -1.6203 | -2.1813 | 0.2826 |  |  | none | FALSE | 0 | 72.112 | FALSE | FALSE | 0.0661 |  | 73.1953 | 0 | 0.2826 | -0.04239 | 0.18957 | 1.7143 | 0.54166 | Normal | 74.2787 | -0.99129 | Day | 202512 | 2025-12-24 | 0.99129
2025-12-24 15:43 | 72.3758 | FALSE | FALSE | -0.36887 | -0.51227 | -1.8949 | -2.5514 | -0.2826 |  |  | none | FALSE | 0 | 72.0069 | FALSE | FALSE | 0.0899 |  | 73.1388 | 0 | -0.2826 | -0.05652 | 0.19665 | -1.1497 | 0.56594 | Normal | 74.2707 | -1.3482 | Day | 202512 | 2025-12-24 | 1.3482
2025-12-24 15:58 | 72.3758 | FALSE | FALSE | -0.44507 | -0.61875 | -1.8298 | -2.4659 | 0 |  |  | none | FALSE | 0 | 71.9307 | FALSE | FALSE | 0.0812 |  | 73.0682 | 0 | 0 | -0.07065 | 0.18049 | 0.39144 | 0.56872 | Normal | 74.2056 | -1.2174 | Day | 202512 | 2025-12-24 | 1.2174
2025-12-24 16:13 | 72.3758 | FALSE | FALSE | -0.50271 | -0.69945 | -1.7462 | -2.3558 | 0 |  |  | none | FALSE | 0 | 71.8731 | FALSE | FALSE | 0.0737 |  | 72.9975 | 0 | 0 | -0.07065 | 0.18049 | 0.39144 | 0.56222 | Normal | 74.122 | -1.1058 | Day | 202512 | 2025-12-24 | 1.1058
2025-12-24 16:28 | 72.095 | FALSE | FALSE | -0.26958 | -0.37533 | -1.877 | -2.5374 | -0.2808 |  |  | none | FALSE | 0 | 71.8254 | FALSE | FALSE | 0.0998 |  | 72.8987 | 0 | -0.2808 | -0.09882 | 0.16582 | -1.0974 | 0.53664 | Normal | 73.972 | -1.4976 | Day | 202512 | 2025-12-24 | 1.4976
2025-12-24 16:42 | 72.095 | FALSE | FALSE | -0.27353 | -0.38085 | -1.6833 | -2.2816 | 0 |  |  | none | FALSE | 0 | 71.8215 | FALSE | FALSE | 0.0961 |  | 72.7999 | 0 | 0 | -0.09882 | 0.16582 | 0.59594 | 0.4892 | Normal | 73.7783 | -1.4409 | Day | 202512 | 2025-12-24 | 1.4409
2025-12-24 16:56 | 71.8124 | FALSE | FALSE | -0.068193 | -0.09505 | -1.8455 | -2.5055 | -0.2826 |  |  | none | FALSE | 0 | 71.7442 | FALSE | FALSE | 0.1238 |  | 72.7011 | 0 | -0.2826 | -0.09882 | 0.16582 | -1.1083 | 0.47843 | Normal | 73.6579 | -1.8575 | Day | 202512 | 2025-12-24 | 1.8575
2025-12-24 17:11 | 72.941 | TRUE | FALSE | -1.1558 | -1.6101 | -0.61941 | -0.84204 | 1.1286 |  |  | none | FALSE | 1 | 71.7852 | FALSE | FALSE | 0.0689 |  | 72.6728 | 0 | 1.1286 | -0.02826 | 0.31587 | 3.6625 | 0.4438 | Normal | 73.5604 | 0.60432 | Day | 202512 | 2025-12-24 | 0.60432
2025-12-24 17:26 | 73.2236 | FALSE | FALSE | -1.4044 | -1.9554 | -0.27451 | -0.37349 | 0.2826 |  |  | none | FALSE | 1 | 71.8192 | FALSE | FALSE | 0.1183 |  | 72.6587 | 0 | 0.2826 | -0.01413 | 0.32343 | 0.91746 | 0.41972 | Normal | 73.4981 | 1.346 | Day | 202512 | 2025-12-24 | 1.346
2025-12-24 17:41 | 73.5062 | FALSE | FALSE | -1.721 | -2.3974 | -0.05421 | -0.073694 | 0.2826 |  |  | none | FALSE | 1 | 71.7852 | FALSE | FALSE | 0.1538 |  | 72.6728 | 0 | 0.2826 | 0.01413 | 0.32343 | 0.83008 | 0.4438 | Normal | 73.5604 | 1.8779 | Night | 202512 | 2025-12-24 | 1.8779
2025-12-24 17:42 | 73.5062 | FALSE | FALSE | -1.7517 | -2.4412 | -0.11313 | -0.15366 | 0 |  |  | none | FALSE | 1 | 71.7545 | FALSE | FALSE | 0.1457 |  | 72.6869 | 0 | 0 | 0.01413 | 0.32343 | -0.043688 | 0.4662 | Normal | 73.6193 | 1.7573 | Night | 202512 | 2025-12-24 | 1.7573
2025-12-24 17:57 | 73.5062 | FALSE | FALSE | -1.7794 | -2.4808 | -0.16913 | -0.22956 | 0 |  |  | none | FALSE | 1 | 71.7268 | FALSE | FALSE | 0.1388 |  | 72.7011 | 0 | 0 | 0.01413 | 0.32343 | -0.043688 | 0.48713 | Normal | 73.6753 | 1.6528 | Night | 202512 | 2025-12-24 | 1.6528
2025-12-24 18:12 | 72.6584 | TRUE | FALSE | -0.93926 | -1.3096 | -0.99632 | -1.3527 | -0.8478 |  |  | none | FALSE | 2 | 71.7191 | TRUE | FALSE | 0.0611 |  | 72.6869 | 0 | -0.8478 | -0.01413 | 0.37179 | -2.2423 | 0.48389 | Normal | 73.6547 | -0.058959 | Night | 202512 | 2025-12-24 | 0.058959
2025-12-24 18:27 | 72.095 | FALSE | FALSE | -0.44498 | -0.62105 | -1.5442 | -2.097 | -0.5634 |  |  | none | FALSE | 2 | 71.65 | FALSE | FALSE | 0.1308 |  | 72.6446 | 0 | -0.5634 | -0.0423 | 0.39149 | -1.3311 | 0.49731 | Normal | 73.6392 | -1.1052 | Night | 202512 | 2025-12-24 | 1.1052
2025-12-24 18:30 | 72.095 | FALSE | FALSE | -0.506 | -0.70681 | -1.5207 | -2.0657 | 0 |  |  | none | FALSE | 2 | 71.589 | FALSE | FALSE | 0.1239 |  | 72.6023 | 0 | 0 | -0.0423 | 0.39149 | 0.10805 | 0.50666 | Normal | 73.6157 | -1.0013 | Night | 202512 | 2025-12-24 | 1.0013
2025-12-24 18:31 | 72.095 | FALSE | FALSE | -0.55863 | -0.78091 | -1.517 | -2.0607 | 0 |  |  | none | FALSE | 2 | 71.5364 | FALSE | FALSE | 0.1187 |  | 72.5742 | 0 | 0 | -0.02817 | 0.38744 | 0.072708 | 0.5189 | Normal | 73.612 | -0.92342 | Night | 202512 | 2025-12-24 | 0.92342
2025-12-24 18:46 | 72.3758 | FALSE | FALSE | -0.85642 | -1.1975 | -1.2249 | -1.6642 | 0.2808 |  |  | none | FALSE | 2 | 71.5194 | FALSE | FALSE | 0.0807 |  | 72.56 | 0 | 0.2808 | -0.01413 | 0.39355 | 0.7494 | 0.52033 | Normal | 73.6007 | -0.35407 | Night | 202512 | 2025-12-24 | 0.35407
2025-12-24 19:01 | 72.941 | FALSE | FALSE | -1.4207 | -1.9864 | -0.68703 | -0.93311 | 0.5652 |  |  | none | FALSE | 1 | 71.5203 | FALSE | FALSE | 0.075 |  | 72.5742 | 0 | 0.5652 | 0.01413 | 0.41436 | 1.3299 | 0.52693 | Normal | 73.628 | 0.69618 | Night | 202512 | 2025-12-24 | 0.69618
2025-12-24 19:16 | 73.2236 | FALSE | FALSE | -1.695 | -2.3696 | -0.48088 | -0.65244 | 0.2826 |  |  | none | FALSE | 1 | 71.5286 | FALSE | FALSE | 0.103 |  | 72.6166 | 0 | 0.2826 | 0.04239 | 0.41233 | 0.58257 | 0.54396 | Normal | 73.7045 | 1.116 | Night | 202512 | 2025-12-24 | 1.116
2025-12-24 19:30 | 73.5062 | FALSE | FALSE | -1.984 | -2.774 | -0.31776 | -0.43043 | 0.2826 |  |  | none | FALSE | 1 | 71.5222 | FALSE | FALSE | 0.1251 |  | 72.6731 | 0 | 0.2826 | 0.05652 | 0.41563 | 0.54395 | 0.57545 | Normal | 73.824 | 1.4478 | Night | 202512 | 2025-12-24 | 1.4478
2025-12-24 19:45 | 73.7888 | FALSE | FALSE | -2.3135 | -3.2367 | -0.19504 | -0.26362 | 0.2826 |  |  | none | FALSE | 1 | 71.4753 | FALSE | FALSE | 0.1412 |  | 72.7296 | 0 | 0.2826 | 0.05652 | 0.41563 | 0.54395 | 0.62712 | Normal | 73.9838 | 1.689 | Night | 202512 | 2025-12-24 | 1.689
2025-12-24 20:00 | 73.7888 | FALSE | FALSE | -2.3159 | -3.2403 | -0.33883 | -0.45709 | 0 |  |  | none | FALSE | 1 | 71.4729 | FALSE | FALSE | 0.1279 |  | 72.8002 | 0 | 0 | 0.07065 | 0.40823 | -0.17306 | 0.66369 | Normal | 74.1276 | 1.4895 | Night | 202512 | 2025-12-24 | 1.4895
2025-12-24 20:15 | 73.7888 | FALSE | FALSE | -2.2995 | -3.2165 | -0.46367 | -0.62445 | 0 |  |  | none | FALSE | 0 | 71.4893 | FALSE | FALSE | 0.0886 |  | 72.8709 | 0 | 0 | 0.07065 | 0.40823 | -0.17306 | 0.69079 | Normal | 74.2525 | 1.3288 | Night | 202512 | 2025-12-24 | 1.3288
2025-12-24 20:29 | 73.7888 | FALSE | FALSE | -2.2662 | -3.1686 | -0.57173 | -0.76886 | 0 |  |  | none | FALSE | 0 | 71.5226 | FALSE | FALSE | 0.0796 |  | 72.9415 | 0 | 0 | 0.07065 | 0.40823 | -0.17306 | 0.70949 | Normal | 74.3605 | 1.1942 | Night | 202512 | 2025-12-24 | 1.1942
2025-12-24 20:44 | 73.7888 | FALSE | FALSE | -2.171 | -3.0313 | -0.64582 | -0.86764 | 0 |  |  | none | FALSE | 0 | 71.6178 | FALSE | FALSE | 0.0722 |  | 73.0262 | 0 | 0 | 0.08469 | 0.40026 | -0.21159 | 0.7042 | Normal | 74.4346 | 1.0829 | Night | 202512 | 2025-12-24 | 1.0829
2025-12-24 20:59 | 73.7888 | FALSE | FALSE | -2.0538 | -2.8631 | -0.69807 | -0.93717 | 0 |  |  | none | FALSE | 0 | 71.735 | FALSE | FALSE | 0.0657 |  | 73.1109 | 0 | 0 | 0.08469 | 0.40026 | -0.21159 | 0.68797 | Normal | 74.4869 | 0.98533 | Night | 202512 | 2025-12-24 | 0.98533
2025-12-24 21:14 | 73.7888 | FALSE | FALSE | -1.8415 | -2.5596 | -0.68343 | -0.9177 | 0 |  |  | none | FALSE | 0 | 71.9473 | FALSE | FALSE | 0.0612 |  | 73.2097 | 0 | 0 | 0.09882 | 0.3915 | -0.25241 | 0.63124 | Normal | 74.4722 | 0.91733 | Night | 202512 | 2025-12-24 | 0.91733
2025-12-24 21:29 | 73.7888 | FALSE | FALSE | -1.818 | -2.526 | -0.74462 | -0.99904 | 0 |  |  | none | FALSE | 0 | 71.9708 | FALSE | FALSE | 0.0558 |  | 73.2521 | 0 | 0 | 0.04239 | 0.30761 | -0.1378 | 0.64064 | Normal | 74.5334 | 0.8377 | Night | 202512 | 2025-12-24 | 0.8377
2025-12-24 21:44 | 73.7888 | FALSE | FALSE | -1.8118 | -2.5172 | -0.79497 | -1.0659 | 0 |  |  | none | FALSE | 0 | 71.977 | FALSE | FALSE | 0.052 |  | 73.2804 | 0 | 0 | 0.02826 | 0.30244 | -0.093439 | 0.65169 | Normal | 74.5838 | 0.78014 | Night | 202512 | 2025-12-24 | 0.78014
2025-12-24 21:59 | 73.7888 | FALSE | FALSE | -1.814 | -2.5203 | -0.82543 | -1.1063 | 0 |  |  | none | FALSE | 0 | 71.9748 | FALSE | FALSE | 0.0499 |  | 73.2945 | 0 | 0 | 0.01413 | 0.29648 | -0.04766 | 0.65986 | Normal | 74.6142 | 0.74907 | Night | 202512 | 2025-12-24 | 0.74907
2025-12-24 22:14 | 73.7888 | FALSE | FALSE | -1.8154 | -2.5223 | -0.85507 | -1.1455 | 0 |  |  | none | FALSE | 0 | 71.9734 | FALSE | FALSE | 0.0479 |  | 73.3087 | 0 | 0 | 0.01413 | 0.29648 | -0.04766 | 0.66761 | Normal | 74.6439 | 0.71921 | Night | 202512 | 2025-12-24 | 0.71921
2025-12-24 22:29 | 73.5062 | FALSE | FALSE | -1.5328 | -2.1296 | -1.1377 | -1.5241 | -0.2826 |  |  | none | FALSE | 0 | 71.9734 | FALSE | FALSE | 0.0197 |  | 73.3087 | 0 | -0.2826 | 0 | 0.30383 | -0.93013 | 0.66761 | Normal | 74.6439 | 0.29591 | Night | 202512 | 2025-12-24 | 0.29591
2025-12-24 22:44 | 73.5062 | FALSE | FALSE | -1.4569 | -2.022 | -1.1465 | -1.5358 | 0 |  |  | none | FALSE | 0 | 72.0493 | FALSE | FALSE | 0.0159 |  | 73.351 | 0 | 0 | 0.04239 | 0.22933 | -0.18484 | 0.65085 | Normal | 74.6527 | 0.2384 | Night | 202512 | 2025-12-24 | 0.2384
2025-12-24 22:59 | 73.5062 | FALSE | FALSE | -1.2449 | -1.7228 | -1.0757 | -1.4424 | 0 |  |  | none | FALSE | 0 | 72.2613 | FALSE | FALSE | 0.0097 |  | 73.4216 | 0 | 0 | 0.07056 | 0.18038 | -0.39118 | 0.58017 | Normal | 74.5819 | 0.14582 | Night | 202512 | 2025-12-24 | 0.14582
2025-12-24 23:14 | 73.5062 | FALSE | FALSE | -0.99202 | -1.368 | -0.96394 | -1.2944 | 0 |  |  | none | FALSE | 0 | 72.5142 | FALSE | FALSE | 0.0019 |  | 73.4922 | 0 | 0 | 0.07056 | 0.18038 | -0.39118 | 0.48899 | Normal | 74.4701 | 0.028712 | Night | 202512 | 2025-12-24 | 0.028712
2025-12-24 23:28 | 73.5062 | FALSE | FALSE | -0.66775 | -0.91676 | -0.78079 | -1.0511 | 0 |  |  | none | FALSE | 0 | 72.8384 | FALSE | FALSE | 0.0104 |  | 73.5627 | 0 | 0 | 0.07056 | 0.18038 | -0.39118 | 0.36214 | Normal | 74.287 | -0.15607 | Night | 202512 | 2025-12-24 | 0.15607
2025-12-24 23:43 | 73.5062 | FALSE | FALSE | -0.35087 | -0.47962 | -0.57695 | -0.77878 | 0 |  |  | none | FALSE | 0 | 73.1553 | FALSE | FALSE | 0.0325 |  | 73.6192 | 0 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.23195 | Normal | 74.0831 | -0.48734 | Night | 202512 | 2025-12-24 | 0.48734
2025-12-24 23:58 | 73.5062 | FALSE | FALSE | -0.20176 | -0.27524 | -0.48436 | -0.65463 | 0 |  |  | none | FALSE | 0 | 73.3044 | FALSE | FALSE | 0.0549 |  | 73.6475 | 0 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.17153 | Normal | 73.9906 | -0.82375 | Night | 202512 | 2025-12-24 | 0.82375
2025-12-25 00:14 | 73.2236 | TRUE | FALSE | 0.080837 | 0.11028 | -0.76696 | -1.0366 | -0.2826 | 2025-12-25 06:56 | 2025-12-25 00:14 | lower | TRUE | 1 | 73.3044 | FALSE | FALSE | 0.2505 | 2.4713 | 73.6475 | 1 | -0.2826 | 0 | 0.12967 | -2.1794 | 0.17153 | Extreme triggered | 73.9906 | -2.4713 | Night | 202512 | 2025-12-25 | 2.4713
2025-12-25 00:28 | 73.2236 | FALSE | FALSE | 0.021855 | 0.029838 | -0.79769 | -1.0776 | 0 |  | 2025-12-25 00:14 | lower | TRUE | 1 | 73.2455 | FALSE | FALSE | 0.2837 | 2.292 | 73.6334 | 2 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.19396 | Extreme/elevated | 74.0213 | -2.1127 | Night | 202512 | 2025-12-25 | 2.1127
2025-12-25 00:43 | 73.2236 | FALSE | FALSE | -0.039654 | -0.054184 | -0.80267 | -1.0843 | 0 |  | 2025-12-25 00:14 | none | FALSE | 1 | 73.1839 | FALSE | FALSE | 0.3208 | 2.1319 | 73.6051 | 3 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21058 | Persistent | 74.0263 | -1.8117 | Night | 202512 | 2025-12-25 | 1.8117
2025-12-25 00:58 | 73.2236 | FALSE | FALSE | -0.091222 | -0.12474 | -0.79772 | -1.0777 | 0 |  | 2025-12-25 00:14 | none | FALSE | 1 | 73.1324 | FALSE | FALSE | 0.3631 | 1.9963 | 73.5768 | 4 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22224 | Persistent | 74.0213 | -1.5895 | Night | 202512 | 2025-12-25 | 1.5895
2025-12-25 01:13 | 73.2236 | FALSE | FALSE | -0.13436 | -0.18384 | -0.78434 | -1.0598 | 0 |  | 2025-12-25 00:14 | none | FALSE | 1 | 73.0892 | FALSE | FALSE | 0.4086 | 1.88 | 73.5486 | 5 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22968 | Persistent | 74.0079 | -1.415 | Night | 202512 | 2025-12-25 | 1.415
2025-12-25 01:28 | 73.2236 | FALSE | FALSE | -0.16989 | -0.23255 | -0.76335 | -1.0317 | 0 |  | 2025-12-25 00:14 | none | FALSE | 1 | 73.0537 | FALSE | FALSE | 0.4562 | 1.7787 | 73.5203 | 6 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.23331 | Persistent | 73.9869 | -1.2718 | Night | 202512 | 2025-12-25 | 1.2718
2025-12-25 01:43 | 72.941 | TRUE | TRUE | 0.021529 | 0.029507 | -1.0524 | -1.4222 | -0.2826 |  | 2025-12-25 00:14 | lower | TRUE | 2 | 72.9625 | TRUE | TRUE | 0.596 | 1.8222 | 73.4779 | 7 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.25771 | Confirmed/Materialized Shift | 73.9934 | -2.0835 | Night | 202512 | 2025-12-25 | 2.0835
2025-12-25 01:58 | 72.941 | FALSE | TRUE | -0.051742 | -0.070987 | -1.0408 | -1.4069 | 0 |  | 2025-12-25 00:14 | none | FALSE | 2 | 72.8893 | FALSE | FALSE | 0.5778 | 1.8208 | 73.4356 | 8 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27315 | Confirmed/Materialized Shift | 73.9818 | -1.8106 | Night | 202512 | 2025-12-25 | 1.8106
2025-12-25 02:13 | 72.941 | FALSE | TRUE | -0.11006 | -0.15111 | -1.0144 | -1.3716 | 0 |  | 2025-12-25 00:14 | none | FALSE | 2 | 72.8309 | FALSE | FALSE | 0.5644 | 1.7972 | 73.3932 | 9 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.28111 | Confirmed/Materialized Shift | 73.9554 | -1.6085 | Night | 202512 | 2025-12-25 | 1.6085
2025-12-25 02:27 | 72.941 | FALSE | TRUE | -0.15469 | -0.21252 | -0.97423 | -1.318 | 0 |  | 2025-12-25 00:14 | none | FALSE | 2 | 72.7863 | FALSE | FALSE | 0.5539 | 1.7626 | 73.3508 | 10 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.28223 | Confirmed/Materialized Shift | 73.9152 | -1.4519 | Night | 202512 | 2025-12-25 | 1.4519
2025-12-25 02:43 | 72.941 | FALSE | TRUE | -0.18579 | -0.25537 | -0.92055 | -1.2463 | 0 |  | 2025-12-25 00:14 | none | FALSE | 1 | 72.7552 | FALSE | FALSE | 0.5171 | 1.7232 | 73.3084 | 11 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27659 | Confirmed/Materialized Shift | 73.8616 | -1.3283 | Night | 202512 | 2025-12-25 | 1.3283
2025-12-25 02:58 | 72.6584 | FALSE | TRUE | 0.016484 | 0.022681 | -1.1704 | -1.5853 | -0.2826 |  | 2025-12-25 00:14 | lower | TRUE | 1 | 72.6749 | FALSE | TRUE | 0.5657 | 1.751 | 73.2519 | 12 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.28849 | Confirmed/Materialized Shift | 73.8288 | -2.0571 | Night | 202512 | 2025-12-25 | 2.0571
2025-12-25 03:13 | 72.6584 | FALSE | TRUE | -0.040036 | -0.055132 | -1.1139 | -1.5099 | 0 |  | 2025-12-25 00:14 | none | FALSE | 1 | 72.6184 | FALSE | FALSE | 0.5527 | 1.7595 | 73.1953 | 13 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.28849 | Confirmed/Materialized Shift | 73.7723 | -1.8612 | Night | 202512 | 2025-12-25 | 1.8612
2025-12-25 03:27 | 72.6584 | FALSE | TRUE | -0.11017 | -0.15186 | -1.0993 | -1.4904 | 0 |  | 2025-12-25 00:14 | none | FALSE | 1 | 72.5482 | FALSE | FALSE | 0.5376 | 1.7506 | 73.153 | 14 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.30236 | Confirmed/Materialized Shift | 73.7577 | -1.6356 | Night | 202512 | 2025-12-25 | 1.6356
2025-12-25 03:42 | 72.3758 | FALSE | TRUE | 0.047491 | 0.065574 | -1.3938 | -1.8894 | -0.2826 |  | 2025-12-25 00:14 | lower | TRUE | 1 | 72.4233 | FALSE | TRUE | 0.5713 | 1.7767 | 73.0964 | 15 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.33657 | Confirmed/Materialized Shift | 73.7696 | -2.1411 | Night | 202512 | 2025-12-25 | 2.1411
2025-12-25 03:57 | 72.3758 | FALSE | TRUE | -0.052579 | -0.072701 | -1.3808 | -1.8721 | 0 |  | 2025-12-25 00:14 | none | FALSE | 1 | 72.3232 | FALSE | FALSE | 0.5521 | 1.7814 | 73.0399 | 16 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.35834 | Confirmed/Materialized Shift | 73.7566 | -1.8533 | Night | 202512 | 2025-12-25 | 1.8533
2025-12-25 04:12 | 72.3758 | FALSE | TRUE | -0.13219 | -0.18297 | -1.3474 | -1.8276 | 0 |  | 2025-12-25 00:14 | none | FALSE | 0 | 72.2436 | FALSE | FALSE | 0.5095 | 1.7733 | 72.9834 | 17 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.36989 | Confirmed/Materialized Shift | 73.7232 | -1.6426 | Night | 202512 | 2025-12-25 | 1.6426
2025-12-25 04:27 | 72.3758 | FALSE | TRUE | -0.19324 | -0.26771 | -1.2954 | -1.7583 | 0 |  | 2025-12-25 00:14 | none | FALSE | 0 | 72.1826 | FALSE | FALSE | 0.4987 | 1.757 | 72.9269 | 18 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.37215 | Confirmed/Materialized Shift | 73.6712 | -1.4808 | Night | 202512 | 2025-12-25 | 1.4808
2025-12-25 04:42 | 72.3758 | FALSE | TRUE | -0.23608 | -0.32725 | -1.2252 | -1.6646 | 0 |  | 2025-12-25 00:14 | none | FALSE | 0 | 72.1397 | FALSE | FALSE | 0.4903 | 1.7358 | 72.8704 | 19 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.36531 | Confirmed/Materialized Shift | 73.601 | -1.3538 | Night | 202512 | 2025-12-25 | 1.3538
2025-12-25 04:57 | 72.3758 | FALSE | TRUE | -0.25964 | -0.36003 | -1.1357 | -1.5449 | 0 |  | 2025-12-25 00:14 | none | FALSE | 0 | 72.1162 | FALSE | FALSE | 0.4837 | 1.7118 | 72.8138 | 20 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.34883 | Confirmed/Materialized Shift | 73.5115 | -1.2557 | Night | 202512 | 2025-12-25 | 1.2557
2025-12-25 05:12 | 72.095 | FALSE | TRUE | -0.077037 | -0.10697 | -1.4018 | -1.9073 | -0.2808 |  | 2025-12-25 00:14 | none | FALSE | 0 | 72.018 | FALSE | FALSE | 0.5194 | 1.7156 | 72.7574 | 21 | -0.2808 | -0.05643 | 0.11579 | -1.9377 | 0.36972 | Confirmed/Materialized Shift | 73.4968 | -1.7916 | Night | 202512 | 2025-12-25 | 1.7916
2025-12-25 05:27 | 72.095 | FALSE | TRUE | -0.15559 | -0.21628 | -1.3675 | -1.8615 | 0 |  | 2025-12-25 00:14 | none | FALSE | 0 | 71.9394 | FALSE | FALSE | 0.5061 | 1.71 | 72.701 | 22 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.38078 | Confirmed/Materialized Shift | 73.4625 | -1.5914 | Night | 202512 | 2025-12-25 | 1.5914
2025-12-25 05:42 | 72.095 | FALSE | TRUE | -0.21621 | -0.3008 | -1.3153 | -1.7917 | 0 |  | 2025-12-25 00:14 | none | FALSE | 0 | 71.8788 | FALSE | FALSE | 0.4957 | 1.698 | 72.6445 | 23 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.38287 | Confirmed/Materialized Shift | 73.4103 | -1.4353 | Night | 202512 | 2025-12-25 | 1.4353
2025-12-25 05:57 | 72.095 | FALSE | TRUE | -0.25919 | -0.3608 | -1.2454 | -1.6981 | 0 |  | 2025-12-25 00:14 | none | FALSE | 0 | 71.8358 | FALSE | FALSE | 0.4874 | 1.6819 | 72.5881 | 24 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.37615 | Confirmed/Materialized Shift | 73.3404 | -1.3109 | Night | 202512 | 2025-12-25 | 1.3109
2025-12-25 06:12 | 72.095 | FALSE | TRUE | -0.28354 | -0.39483 | -1.1569 | -1.5793 | 0 |  | 2025-12-25 00:14 | none | FALSE | 0 | 71.8115 | FALSE | FALSE | 0.4808 | 1.6631 | 72.5317 | 25 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.36011 | Confirmed/Materialized Shift | 73.2519 | -1.2126 | Night | 202512 | 2025-12-25 | 1.2126
2025-12-25 06:26 | 72.095 | FALSE | TRUE | -0.28658 | -0.39909 | -1.0471 | -1.4316 | 0 |  | 2025-12-25 00:14 | none | FALSE | 0 | 71.8084 | FALSE | FALSE | 0.476 | 1.643 | 72.4753 | 26 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.33341 | Confirmed/Materialized Shift | 73.1421 | -1.1405 | Night | 202512 | 2025-12-25 | 1.1405
2025-12-25 06:41 | 72.095 | FALSE | TRUE | -0.31159 | -0.43406 | -0.98749 | -1.3512 | 0 |  | 2025-12-25 00:14 | none | FALSE | 0 | 71.7834 | FALSE | FALSE | 0.4694 | 1.6207 | 72.433 | 27 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.32477 | Confirmed/Materialized Shift | 73.0825 | -1.0406 | Night | 202512 | 2025-12-25 | 1.0406
2025-12-25 06:56 | 72.095 | FALSE | FALSE | -0.32408 | -0.45155 | -0.91538 | -1.2538 | 0 |  |  | none | FALSE | 0 | 71.7709 | FALSE | FALSE | 0.0636 |  | 72.3906 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.30987 | Persistence ends | 73.0104 | -0.95412 | Night | 202512 | 2025-12-25 | 0.95412
2025-12-25 07:11 | 72.095 | FALSE | FALSE | -0.32212 | -0.44881 | -0.82882 | -1.1366 | 0 |  |  | none | FALSE | 0 | 71.7729 | FALSE | FALSE | 0.0587 |  | 72.3483 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.28774 | Normal | 72.9238 | -0.88049 | Day | 202512 | 2025-12-25 | 0.88049
2025-12-25 07:26 | 71.8124 | FALSE | FALSE | -0.072105 | -0.10051 | -1.0311 | -1.4156 | -0.2826 |  |  | none | FALSE | 0 | 71.7403 | FALSE | FALSE | 0.1159 |  | 72.2919 | 0 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.27581 | Normal | 72.8435 | -1.7386 | Day | 202512 | 2025-12-25 | 1.7386
2025-12-25 07:30 | 71.8124 | FALSE | FALSE | -0.077505 | -0.10804 | -0.92368 | -1.2699 | 0 |  |  | none | FALSE | 0 | 71.7349 | FALSE | FALSE | 0.1127 |  | 72.2355 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.2503 | Normal | 72.7361 | -1.6903 | Day | 202512 | 2025-12-25 | 1.6903
2025-12-25 07:45 | 72.095 | TRUE | FALSE | -0.35002 | -0.48786 | -0.57466 | -0.79078 | 0.2826 |  |  | none | FALSE | 1 | 71.745 | FALSE | FALSE | 0.061 |  | 72.2073 | 0 | 0.2826 | -0.02817 | 0.12619 | 2.4627 | 0.23117 | Normal | 72.6697 | -0.48588 | Day | 202512 | 2025-12-25 | 0.48588
2025-12-25 08:00 | 72.095 | FALSE | FALSE | -0.32844 | -0.45766 | -0.49674 | -0.6843 | 0 |  |  | none | FALSE | 1 | 71.7666 | FALSE | FALSE | 0.0558 |  | 72.1792 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.2063 | Normal | 72.5917 | -0.40791 | Day | 202512 | 2025-12-25 | 0.40791
2025-12-25 08:15 | 72.095 | FALSE | FALSE | -0.29047 | -0.40453 | -0.40243 | -0.5551 | 0 |  |  | none | FALSE | 1 | 71.8045 | FALSE | FALSE | 0.0501 |  | 72.151 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.17323 | Normal | 72.4974 | -0.32316 | Day | 202512 | 2025-12-25 | 0.32316
2025-12-25 08:30 | 72.095 | FALSE | FALSE | -0.28854 | -0.40183 | -0.37242 | -0.51392 | 0 |  |  | none | FALSE | 1 | 71.8065 | FALSE | FALSE | 0.0455 |  | 72.1369 | 0 | 0 | -0.01404 | 0.11113 | 0.12634 | 0.16524 | Normal | 72.4674 | -0.25381 | Day | 202512 | 2025-12-25 | 0.25381
2025-12-25 08:30 | 72.095 | FALSE | FALSE | -0.28314 | -0.39428 | -0.33894 | -0.46793 | 0 |  |  | none | FALSE | 1 | 71.8119 | FALSE | FALSE | 0.0405 |  | 72.1229 | 0 | 0 | -0.01404 | 0.11113 | 0.12634 | 0.15552 | Normal | 72.4339 | -0.1794 | Day | 202512 | 2025-12-25 | 0.1794
2025-12-25 08:45 | 72.3758 | TRUE | FALSE | -0.56394 | -0.78531 | -0.058143 | -0.08027 | 0.2808 |  |  | none | FALSE | 2 | 71.8119 | TRUE | FALSE | 0.1656 |  | 72.1229 | 0 | 0.2808 | 0 | 0.12925 | 2.1725 | 0.15552 | Normal | 72.4339 | 1.6261 | Day | 202512 | 2025-12-25 | 1.6261
2025-12-25 09:00 | 72.6584 | FALSE | FALSE | -0.89928 | -1.2532 | 0.14346 | 0.19784 | 0.2826 | 2025-12-25 11:59 | 2025-12-25 09:00 | upper | TRUE | 2 | 71.7591 | FALSE | FALSE | 0.2982 | 2.7593 | 72.137 | 1 | 0.2826 | 0.01413 | 0.14387 | 1.866 | 0.18895 | Extreme triggered | 72.5149 | 2.7593 | Day | 202512 | 2025-12-25 | 2.7593
2025-12-25 09:15 | 72.941 | FALSE | FALSE | -1.2891 | -1.7991 | 0.26236 | 0.36099 | 0.2826 |  | 2025-12-25 09:00 | upper | TRUE | 2 | 71.6519 | FALSE | FALSE | 0.3729 | 2.8907 | 72.1653 | 2 | 0.2826 | 0.02826 | 0.1558 | 1.6325 | 0.25667 | Extreme/elevated | 72.6786 | 3.0222 | Day | 202512 | 2025-12-25 | 3.0222
2025-12-25 09:30 | 73.2236 | FALSE | FALSE | -1.7105 | -2.3919 | 0.32135 | 0.4408 | 0.2826 |  | 2025-12-25 09:00 | upper | TRUE | 2 | 71.5131 | FALSE | TRUE | 0.4236 | 2.9023 | 72.2077 | 3 | 0.2826 | 0.04239 | 0.1656 | 1.4505 | 0.34728 | Persistent | 72.9022 | 2.9253 | Day | 202512 | 2025-12-25 | 2.9253
2025-12-25 09:45 | 72.941 | FALSE | FALSE | -1.4562 | -2.037 | -0.074113 | -0.1015 | -0.2826 |  | 2025-12-25 09:00 | none | FALSE | 2 | 71.4848 | FALSE | FALSE | 0.4061 | 2.6283 | 72.25 | 4 | -0.2826 | 0.0423 | 0.16579 | -1.9597 | 0.38257 | Persistent | 73.0151 | 1.8063 | Day | 202512 | 2025-12-25 | 1.8063
2025-12-25 10:00 | 73.2236 | FALSE | FALSE | -1.7927 | -2.5097 | 0.041673 | 0.056944 | 0.2826 |  | 2025-12-25 09:00 | upper | TRUE | 1 | 71.4309 | FALSE | TRUE | 0.454 | 2.5216 | 72.3064 | 5 | 0.2826 | 0.05643 | 0.17384 | 1.301 | 0.43776 | Persistent | 73.1819 | 2.0952 | Day | 202512 | 2025-12-25 | 2.0952
2025-12-25 10:15 | 73.2236 | FALSE | FALSE | -1.8204 | -2.5494 | -0.098831 | -0.13479 | 0 |  | 2025-12-25 09:00 | none | FALSE | 1 | 71.4032 | FALSE | FALSE | 0.491 | 2.4004 | 72.3628 | 6 | 0 | 0.05643 | 0.17384 | -0.3246 | 0.4798 | Persistent | 73.3224 | 1.794 | Day | 202512 | 2025-12-25 | 1.794
2025-12-25 10:29 | 73.5062 | FALSE | TRUE | -2.1498 | -3.0128 | -0.0042167 | -0.0057362 | 0.2826 |  | 2025-12-25 09:00 | none | FALSE | 1 | 71.3564 | FALSE | FALSE | 0.5614 | 2.3421 | 72.4334 | 7 | 0.2826 | 0.07056 | 0.18038 | 1.1755 | 0.53851 | Confirmed/Materialized Shift | 73.5104 | 1.9922 | Day | 202512 | 2025-12-25 | 1.9922
2025-12-25 10:44 | 73.5062 | FALSE | TRUE | -2.1672 | -3.0379 | -0.16274 | -0.22091 | 0 |  | 2025-12-25 09:00 | none | FALSE | 1 | 71.339 | FALSE | FALSE | 0.5433 | 2.2644 | 72.504 | 8 | 0 | 0.07056 | 0.18038 | -0.39118 | 0.58249 | Confirmed/Materialized Shift | 73.6689 | 1.7206 | Day | 202512 | 2025-12-25 | 1.7206
2025-12-25 10:59 | 73.7888 | FALSE | TRUE | -2.4805 | -3.4786 | -0.080209 | -0.10858 | 0.2826 |  | 2025-12-25 09:00 | none | FALSE | 1 | 71.3083 | FALSE | FALSE | 0.5536 | 2.2211 | 72.5887 | 9 | 0.2826 | 0.08469 | 0.18555 | 1.0666 | 0.64018 | Confirmed/Materialized Shift | 73.869 | 1.8747 | Day | 202512 | 2025-12-25 | 1.8747
2025-12-25 11:15 | 73.7888 | FALSE | TRUE | -2.4797 | -3.4773 | -0.24874 | -0.33597 | 0 |  | 2025-12-25 09:00 | none | FALSE | 0 | 71.3091 | FALSE | FALSE | 0.509 | 2.1625 | 72.6733 | 10 | 0 | 0.08469 | 0.18555 | -0.45642 | 0.6821 | Confirmed/Materialized Shift | 74.0375 | 1.6353 | Day | 202512 | 2025-12-25 | 1.6353
2025-12-25 11:22 | 74.0714 | FALSE | TRUE | -2.7693 | -3.8839 | -0.1708 | -0.23005 | 0.2826 |  | 2025-12-25 09:00 | none | FALSE | 0 | 71.3021 | FALSE | FALSE | 0.5178 | 2.1266 | 72.7722 | 11 | 0.2826 | 0.09882 | 0.18948 | 0.96991 | 0.73502 | Confirmed/Materialized Shift | 74.2422 | 1.7676 | Day | 202512 | 2025-12-25 | 1.7676
2025-12-25 11:25 | 73.7888 | FALSE | TRUE | -2.4326 | -3.4091 | -0.56867 | -0.76478 | -0.2826 |  | 2025-12-25 09:00 | none | FALSE | 0 | 71.3562 | FALSE | FALSE | 0.4828 | 2.0529 | 72.8568 | 12 | -0.2826 | 0.08469 | 0.20697 | -1.7746 | 0.75031 | Confirmed/Materialized Shift | 74.3575 | 1.2421 | Day | 202512 | 2025-12-25 | 1.2421
2025-12-25 11:29 | 73.7888 | FALSE | TRUE | -2.3042 | -3.2233 | -0.6379 | -0.85709 | 0 |  | 2025-12-25 09:00 | none | FALSE | 0 | 71.4846 | FALSE | FALSE | 0.4755 | 1.9821 | 72.9557 | 13 | 0 | 0.09882 | 0.18948 | -0.52153 | 0.73552 | Confirmed/Materialized Shift | 74.4267 | 1.1327 | Day | 202512 | 2025-12-25 | 1.1327
2025-12-25 11:44 | 73.7888 | FALSE | TRUE | -2.1463 | -2.9959 | -0.6777 | -0.91007 | 0 |  | 2025-12-25 09:00 | none | FALSE | 0 | 71.6425 | FALSE | FALSE | 0.4693 | 1.9148 | 73.0545 | 14 | 0 | 0.09882 | 0.18948 | -0.52153 | 0.706 | Confirmed/Materialized Shift | 74.4665 | 1.0401 | Day | 202512 | 2025-12-25 | 1.0401
2025-12-25 11:59 | 73.5062 | FALSE | FALSE | -1.7309 | -2.4116 | -0.96865 | -1.3006 | -0.2826 |  |  | none | FALSE | 0 | 71.7753 | FALSE | FALSE | 0.0377 |  | 73.1251 | 0 | -0.2826 | 0.07056 | 0.20234 | -1.7454 | 0.6749 | Persistence ends | 74.4748 | 0.56475 | Day | 202512 | 2025-12-25 | 0.56475
2025-12-25 12:14 | 73.2236 | FALSE | FALSE | -1.302 | -1.8103 | -1.2177 | -1.6358 | -0.2826 |  |  | none | FALSE | 0 | 71.9216 | FALSE | FALSE | 0.0045 |  | 73.1815 | 0 | -0.2826 | 0.05643 | 0.21687 | -1.5633 | 0.62992 | Normal | 74.4413 | 0.066865 | Day | 202512 | 2025-12-25 | 0.066865
2025-12-25 12:29 | 73.2236 | FALSE | FALSE | -1.1371 | -1.5774 | -1.1657 | -1.567 | 0 |  |  | none | FALSE | 0 | 72.0865 | FALSE | FALSE | 0.0017 |  | 73.2379 | 0 | 0 | 0.05643 | 0.21687 | -0.2602 | 0.57569 | Normal | 74.3893 | -0.024857 | Day | 202512 | 2025-12-25 | 0.024857
2025-12-25 12:44 | 73.2236 | FALSE | FALSE | -0.94774 | -1.3113 | -1.0892 | -1.4657 | 0 |  |  | none | FALSE | 0 | 72.2759 | FALSE | FALSE | 0.0093 |  | 73.2943 | 0 | 0 | 0.05643 | 0.21687 | -0.2602 | 0.50924 | Normal | 74.3128 | -0.13891 | Day | 202512 | 2025-12-25 | 0.13891
2025-12-25 12:59 | 73.2236 | FALSE | FALSE | -0.72261 | -0.99669 | -0.97695 | -1.3166 | 0 |  |  | none | FALSE | 0 | 72.501 | FALSE | FALSE | 0.02 |  | 73.3508 | 0 | 0 | 0.05643 | 0.21687 | -0.2602 | 0.42489 | Normal | 74.2006 | -0.2993 | Day | 202512 | 2025-12-25 | 0.2993
2025-12-25 13:14 | 73.2236 | FALSE | FALSE | -0.55006 | -0.75689 | -0.88918 | -1.1998 | 0 |  |  | none | FALSE | 0 | 72.6735 | FALSE | FALSE | 0.0314 |  | 73.3932 | 0 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.35981 | Normal | 74.1128 | -0.47125 | Day | 202512 | 2025-12-25 | 0.47125
2025-12-25 13:28 | 72.941 | FALSE | FALSE | -0.20183 | -0.27748 | -1.1344 | -1.5314 | -0.2826 |  |  | none | FALSE | 0 | 72.7392 | FALSE | FALSE | 0.0931 |  | 73.4073 | 0 | -0.2826 | 0.01413 | 0.21454 | -1.3831 | 0.33406 | Normal | 74.0754 | -1.3958 | Day | 202512 | 2025-12-25 | 1.3958
2025-12-25 13:43 | 72.941 | FALSE | FALSE | -0.20183 | -0.27748 | -1.1344 | -1.5314 | 0 |  |  | none | FALSE | 0 | 72.7392 | FALSE | FALSE | 0.0931 |  | 73.4073 | 0 | 0 | 0 | 0.20502 | 0 | 0.33406 | Normal | 74.0754 | -1.3958 | Day | 202512 | 2025-12-25 | 1.3958
2025-12-25 13:59 | 72.941 | FALSE | FALSE | -0.2437 | -0.33523 | -1.148 | -1.5495 | 0 |  |  | none | FALSE | 0 | 72.6973 | FALSE | FALSE | 0.0866 |  | 73.3932 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.34793 | Normal | 74.089 | -1.2996 | Day | 202512 | 2025-12-25 | 1.2996
2025-12-25 14:14 | 72.6584 | FALSE | FALSE | -0.023679 | -0.0326 | -1.4649 | -1.9764 | -0.2826 |  |  | none | FALSE | 0 | 72.6347 | FALSE | FALSE | 0.1291 |  | 73.379 | 0 | -0.2826 | -0.01413 | 0.19396 | -1.3842 | 0.37215 | Normal | 74.1233 | -1.9364 | Day | 202512 | 2025-12-25 | 1.9364
2025-12-25 14:28 | 72.6584 | FALSE | FALSE | -0.11687 | -0.16111 | -1.5016 | -2.0248 | 0 |  |  | none | FALSE | 0 | 72.5415 | FALSE | FALSE | 0.1141 |  | 73.3508 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.40462 | Normal | 74.16 | -1.7112 | Day | 202512 | 2025-12-25 | 1.7112
2025-12-25 14:43 | 72.6584 | FALSE | FALSE | -0.20135 | -0.27789 | -1.5296 | -2.0618 | 0 |  |  | none | FALSE | 0 | 72.457 | FALSE | FALSE | 0.1023 |  | 73.3225 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.43273 | Normal | 74.188 | -1.5347 | Day | 202512 | 2025-12-25 | 1.5347
2025-12-25 14:58 | 72.3758 | FALSE | FALSE | -0.067495 | -0.093343 | -1.8479 | -2.4896 | -0.2826 |  |  | none | FALSE | 0 | 72.3083 | FALSE | FALSE | 0.1239 |  | 73.266 | 0 | -0.2826 | -0.05652 | 0.17396 | -1.2996 | 0.47884 | Normal | 74.2237 | -1.859 | Day | 202512 | 2025-12-25 | 1.859
2025-12-25 15:13 | 72.6584 | FALSE | FALSE | -0.42231 | -0.58462 | -1.5527 | -2.0923 | 0.2826 |  |  | none | FALSE | 0 | 72.2361 | FALSE | FALSE | 0.0763 |  | 73.2236 | 0 | 0.2826 | -0.04239 | 0.18957 | 1.7143 | 0.49375 | Normal | 74.2111 | -1.1447 | Day | 202512 | 2025-12-25 | 1.1447
2025-12-25 15:28 | 72.3758 | FALSE | FALSE | -0.24178 | -0.33518 | -1.7961 | -2.4215 | -0.2826 |  |  | none | FALSE | 0 | 72.134 | FALSE | FALSE | 0.1017 |  | 73.153 | 0 | -0.2826 | -0.07065 | 0.18049 | -1.1743 | 0.50946 | Normal | 74.1719 | -1.5254 | Day | 202512 | 2025-12-25 | 1.5254
2025-12-25 15:43 | 72.3758 | FALSE | FALSE | -0.32269 | -0.44785 | -1.7357 | -2.342 | 0 |  |  | none | FALSE | 0 | 72.0531 | FALSE | FALSE | 0.0915 |  | 73.0823 | 0 | 0 | -0.07065 | 0.18049 | 0.39144 | 0.5146 | Normal | 74.1115 | -1.3729 | Day | 202512 | 2025-12-25 | 1.3729
2025-12-25 15:58 | 72.3758 | FALSE | FALSE | -0.34165 | -0.47429 | -1.5851 | -2.1432 | 0 |  |  | none | FALSE | 0 | 72.0341 | FALSE | FALSE | 0.086 |  | 72.9975 | 0 | 0 | -0.08478 | 0.16143 | 0.52517 | 0.48169 | Normal | 73.9609 | -1.2907 | Day | 202512 | 2025-12-25 | 1.2907
2025-12-25 16:13 | 72.3758 | FALSE | FALSE | -0.37447 | -0.52009 | -1.4766 | -1.9994 | 0 |  |  | none | FALSE | 0 | 72.0013 | FALSE | FALSE | 0.0794 |  | 72.9269 | 0 | 0 | -0.07065 | 0.15546 | 0.45445 | 0.46277 | Normal | 73.8524 | -1.1908 | Day | 202512 | 2025-12-25 | 1.1908
2025-12-25 16:28 | 72.3758 | FALSE | FALSE | -0.38164 | -0.5301 | -1.3425 | -1.8211 | 0 |  |  | none | FALSE | 0 | 71.9942 | FALSE | FALSE | 0.0743 |  | 72.8562 | 0 | 0 | -0.07065 | 0.15546 | 0.45445 | 0.43103 | Normal | 73.7183 | -1.1146 | Day | 202512 | 2025-12-25 | 1.1146
2025-12-25 16:43 | 72.095 | FALSE | FALSE | -0.13084 | -0.18181 | -1.4839 | -2.0167 | -0.2808 |  |  | none | FALSE | 0 | 71.9642 | FALSE | FALSE | 0.1117 |  | 72.7715 | 0 | -0.2808 | -0.08469 | 0.16132 | -1.2157 | 0.40368 | Normal | 73.5789 | -1.6759 | Day | 202512 | 2025-12-25 | 1.6759
2025-12-25 16:58 | 72.3758 | FALSE | FALSE | -0.4076 | -0.56636 | -1.086 | -1.4783 | 0.2808 |  |  | none | FALSE | 0 | 71.9682 | FALSE | FALSE | 0.0606 |  | 72.715 | 0 | 0.2808 | -0.05652 | 0.17366 | 1.9424 | 0.37341 | Normal | 73.4618 | -0.90842 | Day | 202512 | 2025-12-25 | 0.90842
2025-12-25 17:13 | 72.6584 | FALSE | FALSE | -0.67917 | -0.94356 | -0.73587 | -1.0026 | 0.2826 |  |  | none | FALSE | 0 | 71.9792 | FALSE | FALSE | 0.0053 |  | 72.6868 | 0 | 0.2826 | -0.02826 | 0.18077 | 1.7196 | 0.35376 | Normal | 73.3943 | -0.080139 | Day | 202512 | 2025-12-25 | 0.080139
2025-12-25 17:27 | 72.6584 | FALSE | FALSE | -0.66075 | -0.91774 | -0.66093 | -0.90145 | 0 |  |  | none | FALSE | 0 | 71.9976 | FALSE | FALSE | 0 |  | 72.6585 | 0 | 0 | -0.02826 | 0.18077 | 0.15633 | 0.33042 | Normal | 73.3193 | -0.00027238 | Day | 202512 | 2025-12-25 | 0.00027238
2025-12-25 17:42 | 72.6584 | FALSE | FALSE | -0.63325 | -0.87921 | -0.57691 | -0.78775 | 0 |  |  | none | FALSE | 0 | 72.0252 | FALSE | FALSE | 0.0062 |  | 72.6302 | 0 | 0 | -0.02826 | 0.18077 | 0.15633 | 0.30254 | Normal | 73.2353 | 0.093112 | Night | 202512 | 2025-12-25 | 0.093112
2025-12-25 17:57 | 72.6584 | FALSE | FALSE | -0.59383 | -0.82403 | -0.48097 | -0.65761 | 0 |  |  | none | FALSE | 0 | 72.0646 | FALSE | FALSE | 0.014 |  | 72.602 | 0 | 0 | -0.02826 | 0.18077 | 0.15633 | 0.2687 | Normal | 73.1394 | 0.21001 | Night | 202512 | 2025-12-25 | 0.21001
2025-12-25 18:12 | 72.6584 | FALSE | FALSE | -0.53719 | -0.74485 | -0.36781 | -0.50367 | 0 |  |  | none | FALSE | 0 | 72.1212 | FALSE | FALSE | 0.025 |  | 72.5737 | 0 | 0 | -0.02826 | 0.18077 | 0.15633 | 0.22625 | Normal | 73.0262 | 0.37432 | Night | 202512 | 2025-12-25 | 0.37432
2025-12-25 18:27 | 72.6584 | FALSE | FALSE | -0.51957 | -0.72023 | -0.32193 | -0.44111 | 0 |  |  | none | FALSE | 0 | 72.1388 | FALSE | FALSE | 0.0313 |  | 72.5596 | 0 | 0 | -0.01413 | 0.17061 | 0.082823 | 0.21037 | Normal | 72.9803 | 0.46974 | Night | 202512 | 2025-12-25 | 0.46974
2025-12-25 18:30 | 72.6584 | FALSE | FALSE | -0.49716 | -0.68895 | -0.27126 | -0.37194 | 0 |  |  | none | FALSE | 0 | 72.1612 | FALSE | FALSE | 0.0392 |  | 72.5455 | 0 | 0 | -0.01413 | 0.17061 | 0.082823 | 0.1921 | Normal | 72.9297 | 0.58797 | Night | 202512 | 2025-12-25 | 0.58797
2025-12-25 18:31 | 72.6584 | FALSE | FALSE | -0.46843 | -0.64889 | -0.21427 | -0.29403 | 0 |  |  | none | FALSE | 0 | 72.19 | FALSE | FALSE | 0.0496 |  | 72.5313 | 0 | 0 | -0.01413 | 0.17061 | 0.082823 | 0.17068 | Normal | 72.8727 | 0.74457 | Night | 202512 | 2025-12-25 | 0.74457
2025-12-25 18:46 | 73.2236 | TRUE | FALSE | -1.123 | -1.5575 | 0.20505 | 0.28082 | 0.5652 | 2025-12-25 21:29 | 2025-12-25 18:46 | upper | TRUE | 1 | 72.1006 | FALSE | FALSE | 0.2786 | 2.8935 | 72.5596 | 1 | 0.5652 | 0.02826 | 0.2027 | 2.649 | 0.22948 | Extreme triggered | 73.0185 | 2.8935 | Night | 202512 | 2025-12-25 | 2.8935
2025-12-25 19:01 | 73.5062 | FALSE | FALSE | -1.5285 | -2.1235 | 0.27999 | 0.38236 | 0.2826 |  | 2025-12-25 18:46 | upper | TRUE | 1 | 71.9777 | FALSE | FALSE | 0.336 | 2.8953 | 72.602 | 2 | 0.2826 | 0.04239 | 0.21033 | 1.1421 | 0.31212 | Extreme/elevated | 73.2262 | 2.897 | Night | 202512 | 2025-12-25 | 2.897
2025-12-25 19:16 | 73.5062 | FALSE | FALSE | -1.6059 | -2.2335 | 0.11781 | 0.16053 | 0 |  | 2025-12-25 18:46 | upper | TRUE | 1 | 71.9003 | FALSE | TRUE | 0.3544 | 2.7024 | 72.6444 | 3 | 0 | 0.04239 | 0.21033 | -0.20154 | 0.37201 | Persistent | 73.3884 | 2.3167 | Night | 202512 | 2025-12-25 | 2.3167
2025-12-25 19:30 | 73.7888 | FALSE | FALSE | -1.9644 | -2.7349 | 0.18322 | 0.24892 | 0.2826 |  | 2025-12-25 18:46 | upper | TRUE | 1 | 71.8244 | FALSE | TRUE | 0.4179 | 2.6297 | 72.715 | 4 | 0.2826 | 0.07065 | 0.20218 | 1.0483 | 0.44528 | Persistent | 73.6056 | 2.4115 | Night | 202512 | 2025-12-25 | 2.4115
2025-12-25 19:45 | 73.7888 | FALSE | FALSE | -2.0281 | -2.8262 | 0.0064634 | 0.0087601 | 0 |  | 2025-12-25 18:46 | upper | TRUE | 1 | 71.7607 | FALSE | TRUE | 0.4485 | 2.5063 | 72.7715 | 5 | 0 | 0.05652 | 0.19638 | -0.28781 | 0.5054 | Persistent | 73.7823 | 2.0128 | Night | 202512 | 2025-12-25 | 2.0128
2025-12-25 20:00 | 73.7888 | FALSE | FALSE | -2.0355 | -2.8368 | -0.14224 | -0.19239 | 0 |  | 2025-12-25 18:46 | none | FALSE | 1 | 71.7533 | FALSE | FALSE | 0.4873 | 2.3784 | 72.8422 | 6 | 0 | 0.07065 | 0.18019 | -0.39208 | 0.54443 | Persistent | 73.931 | 1.7387 | Night | 202512 | 2025-12-25 | 1.7387
2025-12-25 20:15 | 73.7888 | FALSE | TRUE | -2.0194 | -2.8137 | -0.26747 | -0.36117 | 0 |  | 2025-12-25 18:46 | none | FALSE | 1 | 71.7694 | FALSE | FALSE | 0.5307 | 2.2575 | 72.9128 | 7 | 0 | 0.07065 | 0.18019 | -0.39208 | 0.57172 | Confirmed/Materialized Shift | 74.0563 | 1.5322 | Night | 202512 | 2025-12-25 | 1.5322
2025-12-25 20:29 | 73.7888 | FALSE | TRUE | -1.9831 | -2.7618 | -0.3725 | -0.50228 | 0 |  | 2025-12-25 18:46 | none | FALSE | 1 | 71.8057 | FALSE | FALSE | 0.5197 | 2.1462 | 72.9835 | 8 | 0 | 0.07065 | 0.18019 | -0.39208 | 0.58891 | Confirmed/Materialized Shift | 74.1613 | 1.3675 | Night | 202512 | 2025-12-25 | 1.3675
2025-12-25 20:44 | 73.7888 | FALSE | TRUE | -1.9284 | -2.6836 | -0.45908 | -0.6183 | 0 |  | 2025-12-25 18:46 | none | FALSE | 1 | 71.8604 | FALSE | FALSE | 0.5106 | 2.0445 | 73.0541 | 9 | 0 | 0.07065 | 0.18019 | -0.39208 | 0.59687 | Confirmed/Materialized Shift | 74.2479 | 1.2309 | Night | 202512 | 2025-12-25 | 1.2309
2025-12-25 20:59 | 73.7888 | FALSE | TRUE | -1.856 | -2.5802 | -0.52794 | -0.7104 | 0 |  | 2025-12-25 18:46 | none | FALSE | 1 | 71.9328 | FALSE | FALSE | 0.5028 | 1.9515 | 73.1248 | 10 | 0 | 0.07065 | 0.18019 | -0.39208 | 0.59598 | Confirmed/Materialized Shift | 74.3167 | 1.1142 | Night | 202512 | 2025-12-25 | 1.1142
2025-12-25 21:15 | 73.7888 | FALSE | TRUE | -1.7019 | -2.3609 | -0.54323 | -0.73082 | 0 |  | 2025-12-25 18:46 | none | FALSE | 0 | 72.0869 | FALSE | FALSE | 0.4688 | 1.8679 | 73.2095 | 11 | 0 | 0.08469 | 0.16132 | -0.52499 | 0.56128 | Confirmed/Materialized Shift | 74.332 | 1.0322 | Night | 202512 | 2025-12-25 | 1.0322
2025-12-25 21:29 | 73.7888 | FALSE | FALSE | -1.5873 | -2.1985 | -0.56996 | -0.76651 | 0 |  |  | none | FALSE | 0 | 72.2015 | FALSE | FALSE | 0.0629 |  | 73.2801 | 0 | 0 | 0.07065 | 0.15546 | -0.45445 | 0.53932 | Persistence ends | 74.3588 | 0.94318 | Night | 202512 | 2025-12-25 | 0.94318
2025-12-25 21:44 | 73.7888 | FALSE | FALSE | -1.5119 | -2.0919 | -0.60761 | -0.81673 | 0 |  |  | none | FALSE | 0 | 72.2769 | FALSE | FALSE | 0.0569 |  | 73.3366 | 0 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.52989 | Normal | 74.3964 | 0.85331 | Night | 202512 | 2025-12-25 | 0.85331
2025-12-25 21:59 | 73.7888 | FALSE | FALSE | -1.4232 | -1.9667 | -0.63192 | -0.84911 | 0 |  |  | none | FALSE | 0 | 72.3656 | FALSE | FALSE | 0.0513 |  | 73.3932 | 0 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.51378 | Normal | 74.4207 | 0.77006 | Night | 202512 | 2025-12-25 | 0.77006
2025-12-25 22:14 | 73.5062 | FALSE | FALSE | -1.0388 | -1.4335 | -0.89751 | -1.2063 | -0.2826 |  |  | none | FALSE | 0 | 72.4674 | FALSE | FALSE | 0.0097 |  | 73.4356 | 0 | -0.2826 | 0.04239 | 0.16593 | -1.9586 | 0.48408 | Normal | 74.4037 | 0.14595 | Night | 202512 | 2025-12-25 | 0.14595
2025-12-25 22:29 | 73.5062 | FALSE | FALSE | -0.92474 | -1.2741 | -0.86822 | -1.1674 | 0 |  |  | none | FALSE | 0 | 72.5815 | FALSE | FALSE | 0.0042 |  | 73.4779 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.44824 | Normal | 74.3744 | 0.063047 | Night | 202512 | 2025-12-25 | 0.063047
2025-12-25 22:44 | 73.5062 | FALSE | FALSE | -0.79511 | -1.0935 | -0.82337 | -1.1077 | 0 |  |  | none | FALSE | 0 | 72.7111 | FALSE | FALSE | 0.0023 |  | 73.5203 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.40462 | Normal | 74.3296 | -0.034922 | Night | 202512 | 2025-12-25 | 0.034922
2025-12-25 22:59 | 73.5062 | FALSE | FALSE | -0.64416 | -0.88408 | -0.7572 | -1.0196 | 0 |  |  | none | FALSE | 0 | 72.862 | FALSE | FALSE | 0.0108 |  | 73.5627 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.35034 | Normal | 74.2634 | -0.16133 | Night | 202512 | 2025-12-25 | 0.16133
2025-12-25 23:14 | 73.5062 | FALSE | FALSE | -0.45956 | -0.62913 | -0.65738 | -0.88639 | 0 |  |  | none | FALSE | 0 | 73.0466 | FALSE | FALSE | 0.0236 |  | 73.6051 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.27923 | Normal | 74.1636 | -0.35422 | Night | 202512 | 2025-12-25 | 0.35422
2025-12-25 23:28 | 73.5062 | FALSE | FALSE | -0.20176 | -0.27524 | -0.48436 | -0.65463 | 0 |  |  | none | FALSE | 0 | 73.3044 | FALSE | FALSE | 0.0549 |  | 73.6475 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.17153 | Normal | 73.9906 | -0.82375 | Night | 202512 | 2025-12-25 | 0.82375
2025-12-25 23:44 | 73.5062 | FALSE | FALSE | -0.13306 | -0.18134 | -0.44392 | -0.60029 | 0 |  |  | none | FALSE | 0 | 73.3731 | FALSE | FALSE | 0.0718 |  | 73.6616 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.14424 | Normal | 73.9501 | -1.0775 | Night | 202512 | 2025-12-25 | 1.0775
2025-12-25 23:59 | 73.2236 | TRUE | FALSE | 0.080837 | 0.11028 | -0.76696 | -1.0366 | -0.2826 | 2025-12-26 08:30 | 2025-12-25 23:59 | lower | TRUE | 1 | 73.3044 | FALSE | FALSE | 0.2505 | 2.4713 | 73.6475 | 1 | -0.2826 | -0.01413 | 0.11135 | -2.411 | 0.17153 | Extreme triggered | 73.9906 | -2.4713 | Night | 202512 | 2025-12-25 | 2.4713
2025-12-26 00:14 | 73.2236 | FALSE | FALSE | 0.021855 | 0.029838 | -0.79769 | -1.0776 | 0 |  | 2025-12-25 23:59 | lower | TRUE | 1 | 73.2455 | FALSE | FALSE | 0.2837 | 2.292 | 73.6334 | 2 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.19396 | Extreme/elevated | 74.0213 | -2.1127 | Night | 202512 | 2025-12-26 | 2.1127
2025-12-26 00:28 | 73.2236 | FALSE | FALSE | -0.039654 | -0.054184 | -0.80267 | -1.0843 | 0 |  | 2025-12-25 23:59 | none | FALSE | 1 | 73.1839 | FALSE | FALSE | 0.3208 | 2.1319 | 73.6051 | 3 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21058 | Persistent | 74.0263 | -1.8117 | Night | 202512 | 2025-12-26 | 1.8117
2025-12-26 00:43 | 73.2236 | FALSE | FALSE | -0.091222 | -0.12474 | -0.79772 | -1.0777 | 0 |  | 2025-12-25 23:59 | none | FALSE | 1 | 73.1324 | FALSE | FALSE | 0.3631 | 1.9963 | 73.5768 | 4 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22224 | Persistent | 74.0213 | -1.5895 | Night | 202512 | 2025-12-26 | 1.5895
2025-12-26 00:58 | 73.2236 | FALSE | FALSE | -0.13436 | -0.18384 | -0.78434 | -1.0598 | 0 |  | 2025-12-25 23:59 | none | FALSE | 1 | 73.0892 | FALSE | FALSE | 0.4086 | 1.88 | 73.5486 | 5 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22968 | Persistent | 74.0079 | -1.415 | Night | 202512 | 2025-12-26 | 1.415
2025-12-26 01:13 | 73.2236 | FALSE | FALSE | -0.16989 | -0.23255 | -0.76335 | -1.0317 | 0 |  | 2025-12-25 23:59 | none | FALSE | 1 | 73.0537 | FALSE | FALSE | 0.4562 | 1.7787 | 73.5203 | 6 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.23331 | Persistent | 73.9869 | -1.2718 | Night | 202512 | 2025-12-26 | 1.2718
2025-12-26 01:28 | 73.2236 | FALSE | TRUE | -0.19815 | -0.27134 | -0.73509 | -0.99392 | 0 |  | 2025-12-25 23:59 | none | FALSE | 1 | 73.0255 | FALSE | FALSE | 0.5053 | 1.689 | 73.4921 | 7 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.23331 | Confirmed/Materialized Shift | 73.9587 | -1.1507 | Night | 202512 | 2025-12-26 | 1.1507
2025-12-26 01:43 | 72.941 | TRUE | TRUE | 0.0031498 | 0.004318 | -1.0142 | -1.3714 | -0.2826 |  | 2025-12-25 23:59 | lower | TRUE | 2 | 72.9441 | TRUE | TRUE | 0.5913 | 1.7294 | 73.4497 | 8 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.25277 | Confirmed/Materialized Shift | 73.9552 | -2.0125 | Night | 202512 | 2025-12-26 | 2.0125
2025-12-26 01:58 | 72.941 | FALSE | TRUE | -0.061212 | -0.083991 | -0.99379 | -1.3441 | 0 |  | 2025-12-25 23:59 | none | FALSE | 2 | 72.8798 | FALSE | FALSE | 0.575 | 1.7337 | 73.4073 | 9 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.26375 | Confirmed/Materialized Shift | 73.9348 | -1.7679 | Night | 202512 | 2025-12-26 | 1.7679
2025-12-26 02:13 | 72.941 | FALSE | TRUE | -0.11073 | -0.15203 | -0.95853 | -1.2971 | 0 |  | 2025-12-25 23:59 | none | FALSE | 2 | 72.8303 | FALSE | FALSE | 0.5629 | 1.7189 | 73.3649 | 10 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.26731 | Confirmed/Materialized Shift | 73.8995 | -1.5858 | Night | 202512 | 2025-12-26 | 1.5858
2025-12-26 02:28 | 72.6584 | FALSE | TRUE | 0.067205 | 0.092409 | -1.2328 | -1.6683 | -0.2826 |  | 2025-12-25 23:59 | lower | TRUE | 1 | 72.7256 | FALSE | TRUE | 0.5773 | 1.7654 | 73.3084 | 11 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.29139 | Confirmed/Materialized Shift | 73.8912 | -2.2306 | Night | 202512 | 2025-12-26 | 2.2306
2025-12-26 02:43 | 72.6584 | FALSE | TRUE | -0.011956 | -0.016457 | -1.1989 | -1.6232 | 0 |  | 2025-12-25 23:59 | none | FALSE | 1 | 72.6464 | FALSE | FALSE | 0.5593 | 1.7817 | 73.2519 | 12 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.30271 | Confirmed/Materialized Shift | 73.8573 | -1.9605 | Night | 202512 | 2025-12-26 | 1.9605
2025-12-26 02:58 | 72.6584 | FALSE | TRUE | -0.068476 | -0.094332 | -1.1424 | -1.5479 | 0 |  | 2025-12-25 23:59 | none | FALSE | 1 | 72.5899 | FALSE | FALSE | 0.5468 | 1.7811 | 73.1953 | 13 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.30271 | Confirmed/Materialized Shift | 73.8008 | -1.7738 | Night | 202512 | 2025-12-26 | 1.7738
2025-12-26 03:13 | 72.3758 | FALSE | TRUE | 0.074447 | 0.10276 | -1.4516 | -1.9662 | -0.2826 |  | 2025-12-25 23:59 | lower | TRUE | 1 | 72.4502 | FALSE | TRUE | 0.5763 | 1.8121 | 73.1388 | 14 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.34429 | Confirmed/Materialized Shift | 73.8274 | -2.2162 | Night | 202512 | 2025-12-26 | 2.2162
2025-12-26 03:27 | 72.3758 | FALSE | TRUE | -0.038373 | -0.053047 | -1.4514 | -1.9659 | 0 |  | 2025-12-25 23:59 | none | FALSE | 1 | 72.3374 | FALSE | FALSE | 0.555 | 1.8178 | 73.0823 | 15 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.37244 | Confirmed/Materialized Shift | 73.8272 | -1.897 | Night | 202512 | 2025-12-26 | 1.897
2025-12-26 03:42 | 72.3758 | FALSE | TRUE | -0.13017 | -0.18018 | -1.4301 | -1.9377 | 0 |  | 2025-12-25 23:59 | none | FALSE | 1 | 72.2456 | FALSE | FALSE | 0.5397 | 1.8083 | 73.0258 | 16 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.39008 | Confirmed/Materialized Shift | 73.8059 | -1.6663 | Night | 202512 | 2025-12-26 | 1.6663
2025-12-26 03:57 | 72.3758 | FALSE | TRUE | -0.20375 | -0.28231 | -1.3907 | -1.8852 | 0 |  | 2025-12-25 23:59 | none | FALSE | 1 | 72.1721 | FALSE | FALSE | 0.5278 | 1.7895 | 72.9693 | 17 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.3986 | Confirmed/Materialized Shift | 73.7665 | -1.4888 | Night | 202512 | 2025-12-26 | 1.4888
2025-12-26 04:12 | 72.3758 | FALSE | TRUE | -0.26027 | -0.3609 | -1.3341 | -1.81 | 0 |  | 2025-12-25 23:59 | none | FALSE | 0 | 72.1155 | FALSE | FALSE | 0.4898 | 1.765 | 72.9127 | 18 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.3986 | Confirmed/Materialized Shift | 73.7099 | -1.3471 | Night | 202512 | 2025-12-26 | 1.3471
2025-12-26 04:27 | 72.3758 | FALSE | TRUE | -0.29973 | -0.41586 | -1.2606 | -1.7119 | 0 |  | 2025-12-25 23:59 | none | FALSE | 0 | 72.0761 | FALSE | FALSE | 0.4821 | 1.7369 | 72.8562 | 19 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.39008 | Confirmed/Materialized Shift | 73.6364 | -1.2316 | Night | 202512 | 2025-12-26 | 1.2316
2025-12-26 04:42 | 72.095 | FALSE | TRUE | -0.0972 | -0.135 | -1.4785 | -2.0096 | -0.2808 |  | 2025-12-25 23:59 | none | FALSE | 0 | 71.9978 | FALSE | FALSE | 0.5169 | 1.7377 | 72.7857 | 20 | -0.2808 | -0.07056 | 0.12539 | -1.6767 | 0.39393 | Confirmed/Materialized Shift | 73.5735 | -1.7533 | Night | 202512 | 2025-12-26 | 1.7533
2025-12-26 04:57 | 72.095 | FALSE | TRUE | -0.18269 | -0.25405 | -1.4512 | -1.9731 | 0 |  | 2025-12-25 23:59 | none | FALSE | 0 | 71.9123 | FALSE | FALSE | 0.5035 | 1.7289 | 72.7292 | 21 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.40846 | Confirmed/Materialized Shift | 73.5462 | -1.5527 | Night | 202512 | 2025-12-26 | 1.5527
2025-12-26 05:12 | 72.095 | FALSE | TRUE | -0.25117 | -0.3496 | -1.4068 | -1.9139 | 0 |  | 2025-12-25 23:59 | none | FALSE | 0 | 71.8438 | FALSE | FALSE | 0.4929 | 1.7137 | 72.6728 | 22 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.41448 | Confirmed/Materialized Shift | 73.5018 | -1.394 | Night | 202512 | 2025-12-26 | 1.394
2025-12-26 05:27 | 72.095 | FALSE | TRUE | -0.30337 | -0.42257 | -1.3461 | -1.8329 | 0 |  | 2025-12-25 23:59 | none | FALSE | 0 | 71.7916 | FALSE | FALSE | 0.4843 | 1.6941 | 72.6164 | 23 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.41237 | Confirmed/Materialized Shift | 73.4411 | -1.2643 | Night | 202512 | 2025-12-26 | 1.2643
2025-12-26 05:42 | 71.8124 | FALSE | TRUE | -0.11375 | -0.15865 | -1.5806 | -2.1536 | -0.2826 |  | 2025-12-25 23:59 | none | FALSE | 0 | 71.6986 | FALSE | FALSE | 0.5154 | 1.6957 | 72.5458 | 24 | -0.2826 | -0.07056 | 0.12539 | -1.6911 | 0.42358 | Confirmed/Materialized Shift | 73.393 | -1.7315 | Night | 202512 | 2025-12-26 | 1.7315
2025-12-26 05:57 | 71.8124 | FALSE | TRUE | -0.18169 | -0.25364 | -1.5074 | -2.0559 | 0 |  | 2025-12-25 23:59 | none | FALSE | 0 | 71.6307 | FALSE | FALSE | 0.5046 | 1.6907 | 72.4753 | 25 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.42227 | Confirmed/Materialized Shift | 73.3198 | -1.5697 | Night | 202512 | 2025-12-26 | 1.5697
2025-12-26 06:12 | 71.8124 | FALSE | TRUE | -0.22434 | -0.31337 | -1.4089 | -1.9242 | 0 |  | 2025-12-25 23:59 | none | FALSE | 0 | 71.5881 | FALSE | FALSE | 0.4967 | 1.6814 | 72.4047 | 26 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.40831 | Confirmed/Materialized Shift | 73.2213 | -1.4506 | Night | 202512 | 2025-12-26 | 1.4506
2025-12-26 06:26 | 71.8124 | FALSE | TRUE | -0.23892 | -0.33381 | -1.2824 | -1.7544 | 0 |  | 2025-12-25 23:59 | none | FALSE | 0 | 71.5735 | FALSE | FALSE | 0.4915 | 1.67 | 72.3341 | 27 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.38032 | Confirmed/Materialized Shift | 73.0948 | -1.3718 | Night | 202512 | 2025-12-26 | 1.3718
2025-12-26 06:41 | 71.8124 | FALSE | TRUE | -0.27291 | -0.38148 | -1.2035 | -1.6483 | 0 |  | 2025-12-25 23:59 | none | FALSE | 0 | 71.5395 | FALSE | FALSE | 0.484 | 1.6553 | 72.2777 | 28 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.3691 | Confirmed/Materialized Shift | 73.0159 | -1.2606 | Night | 202512 | 2025-12-26 | 1.2606
2025-12-26 06:56 | 71.8124 | FALSE | TRUE | -0.28719 | -0.40152 | -1.1049 | -1.5153 | 0 |  | 2025-12-25 23:59 | none | FALSE | 0 | 71.5252 | FALSE | FALSE | 0.4783 | 1.6388 | 72.2213 | 29 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.34803 | Confirmed/Materialized Shift | 72.9173 | -1.1748 | Night | 202512 | 2025-12-26 | 1.1748
2025-12-26 07:11 | 71.5298 | FALSE | TRUE | -0.053729 | -0.075171 | -1.2955 | -1.779 | -0.2826 |  | 2025-12-25 23:59 | none | FALSE | 0 | 71.4761 | FALSE | FALSE | 0.5227 | 1.6455 | 72.1507 | 30 | -0.2826 | -0.07056 | 0.12539 | -1.6911 | 0.33732 | Confirmed/Materialized Shift | 72.8253 | -1.8407 | Day | 202512 | 2025-12-26 | 1.8407
2025-12-26 07:26 | 71.5298 | FALSE | TRUE | -0.12009 | -0.16817 | -1.249 | -1.7162 | 0 |  | 2025-12-25 23:59 | none | FALSE | 0 | 71.4097 | FALSE | FALSE | 0.5099 | 1.6456 | 72.0943 | 31 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.34228 | Confirmed/Materialized Shift | 72.7788 | -1.6492 | Day | 202512 | 2025-12-26 | 1.6492
2025-12-26 07:30 | 71.5298 | FALSE | TRUE | -0.16672 | -0.23362 | -1.1828 | -1.6267 | 0 |  | 2025-12-25 23:59 | none | FALSE | 0 | 71.3631 | FALSE | FALSE | 0.5004 | 1.6412 | 72.0379 | 32 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.33738 | Confirmed/Materialized Shift | 72.7126 | -1.5059 | Day | 202512 | 2025-12-26 | 1.5059
2025-12-26 07:45 | 71.5298 | FALSE | TRUE | -0.19272 | -0.27015 | -1.096 | -1.509 | 0 |  | 2025-12-25 23:59 | none | FALSE | 0 | 71.3371 | FALSE | FALSE | 0.4935 | 1.634 | 71.9814 | 33 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.32217 | Confirmed/Materialized Shift | 72.6258 | -1.4018 | Day | 202512 | 2025-12-26 | 1.4018
2025-12-26 08:00 | 71.5298 | FALSE | TRUE | -0.23708 | -0.33254 | -1.0557 | -1.4544 | 0 |  | 2025-12-25 23:59 | none | FALSE | 0 | 71.2927 | FALSE | FALSE | 0.4844 | 1.6232 | 71.9391 | 34 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.3232 | Confirmed/Materialized Shift | 72.5855 | -1.2665 | Day | 202512 | 2025-12-26 | 1.2665
2025-12-26 08:15 | 71.5298 | FALSE | TRUE | -0.26971 | -0.37849 | -1.0038 | -1.3838 | 0 |  | 2025-12-25 23:59 | none | FALSE | 0 | 71.2601 | FALSE | FALSE | 0.4769 | 1.6097 | 71.8968 | 35 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.31837 | Confirmed/Materialized Shift | 72.5336 | -1.1528 | Day | 202512 | 2025-12-26 | 1.1528
2025-12-26 08:30 | 71.8124 | TRUE | FALSE | -0.53981 | -0.75739 | -0.65231 | -0.90017 | 0.2826 |  |  | none | FALSE | 1 | 71.2726 | FALSE | FALSE | 0.0412 |  | 71.8687 | 0 | 0.2826 | -0.02817 | 0.12619 | 2.4627 | 0.29803 | Persistence ends | 72.4647 | -0.18874 | Day | 202512 | 2025-12-26 | 0.18874
2025-12-26 08:30 | 71.8124 | FALSE | FALSE | -0.51824 | -0.7269 | -0.5744 | -0.79351 | 0 |  |  | none | FALSE | 1 | 71.2942 | FALSE | FALSE | 0.0354 |  | 71.8405 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.27316 | Normal | 72.3868 | -0.1028 | Day | 202512 | 2025-12-26 | 0.1028
2025-12-26 08:45 | 72.095 | TRUE | FALSE | -0.7695 | -1.0789 | -0.23238 | -0.32129 | 0.2826 |  |  | none | FALSE | 2 | 71.3255 | TRUE | FALSE | 0.1286 |  | 71.8264 | 0 | 0.2826 | -0.01404 | 0.14407 | 2.059 | 0.25047 | Normal | 72.3274 | 1.0722 | Day | 202512 | 2025-12-26 | 1.0722
2025-12-26 09:00 | 72.095 | FALSE | FALSE | -0.73178 | -1.0254 | -0.16658 | -0.23052 | 0 |  |  | none | FALSE | 2 | 71.3632 | FALSE | FALSE | 0.141 |  | 71.8124 | 0 | 0 | -0.01404 | 0.14407 | 0.097454 | 0.22459 | Normal | 72.2616 | 1.2583 | Day | 202512 | 2025-12-26 | 1.2583
2025-12-26 09:15 | 72.3758 | FALSE | FALSE | -1.0503 | -1.4725 | 0.04842 | 0.066946 | 0.2808 | 2025-12-26 11:59 | 2025-12-26 09:15 | upper | TRUE | 2 | 71.3255 | FALSE | FALSE | 0.2605 | 2.1933 | 71.8264 | 1 | 0.2808 | 0.01404 | 0.14407 | 1.8516 | 0.25047 | Extreme triggered | 72.3274 | 2.1933 | Day | 202512 | 2025-12-26 | 2.1933
2025-12-26 09:30 | 72.941 | TRUE | FALSE | -1.7721 | -2.49 | 0.37244 | 0.51323 | 0.5652 |  | 2025-12-26 09:15 | upper | TRUE | 3 | 71.1689 | TRUE | FALSE | 0.4043 | 2.6289 | 71.8687 | 2 | 0.5652 | 0.0423 | 0.18945 | 2.76 | 0.34991 | Extreme/elevated | 72.5686 | 3.0644 | Day | 202512 | 2025-12-26 | 3.0644
2025-12-26 09:45 | 72.941 | FALSE | FALSE | -1.8746 | -2.6379 | 0.18528 | 0.25466 | 0 |  | 2025-12-26 09:15 | upper | TRUE | 3 | 71.0664 | FALSE | TRUE | 0.4197 | 2.5655 | 71.911 | 3 | 0 | 0.0423 | 0.18945 | -0.22327 | 0.42234 | Persistent | 72.7557 | 2.4387 | Day | 202512 | 2025-12-26 | 2.4387
2025-12-26 10:00 | 73.2236 | FALSE | FALSE | -2.2836 | -3.219 | 0.22868 | 0.31328 | 0.2826 |  | 2025-12-26 09:15 | upper | TRUE | 3 | 70.94 | FALSE | TRUE | 0.4773 | 2.5354 | 71.9675 | 4 | 0.2826 | 0.05643 | 0.19654 | 1.1508 | 0.51372 | Persistent | 72.9949 | 2.4451 | Day | 202512 | 2025-12-26 | 2.4451
2025-12-26 10:15 | 73.2236 | FALSE | FALSE | -2.3525 | -3.3195 | 0.018604 | 0.025414 | 0 |  | 2025-12-26 09:15 | upper | TRUE | 3 | 70.8711 | FALSE | TRUE | 0.5069 | 2.4347 | 72.038 | 5 | 0 | 0.07056 | 0.18038 | -0.39118 | 0.58348 | Persistent | 73.205 | 2.0319 | Day | 202512 | 2025-12-26 | 2.0319
2025-12-26 10:29 | 73.2236 | FALSE | FALSE | -2.3902 | -3.3744 | -0.16015 | -0.21824 | 0 |  | 2025-12-26 09:15 | none | FALSE | 3 | 70.8334 | FALSE | FALSE | 0.5452 | 2.3204 | 72.1086 | 6 | 0 | 0.07056 | 0.18038 | -0.39118 | 0.63758 | Persistent | 73.3838 | 1.7488 | Day | 202512 | 2025-12-26 | 1.7488
2025-12-26 10:44 | 73.5062 | FALSE | TRUE | -2.7231 | -3.8471 | -0.097255 | -0.13213 | 0.2826 |  | 2025-12-26 09:15 | none | FALSE | 2 | 70.7831 | FALSE | FALSE | 0.5813 | 2.2549 | 72.1933 | 7 | 0.2826 | 0.08469 | 0.18555 | 1.0666 | 0.70509 | Confirmed/Materialized Shift | 73.6035 | 1.8621 | Day | 202512 | 2025-12-26 | 1.8621
2025-12-26 10:59 | 73.5062 | FALSE | TRUE | -2.7418 | -3.8745 | -0.28529 | -0.38662 | 0 |  | 2025-12-26 09:15 | none | FALSE | 2 | 70.7644 | FALSE | FALSE | 0.5653 | 2.1759 | 72.278 | 8 | 0 | 0.08469 | 0.18555 | -0.45642 | 0.75676 | Confirmed/Materialized Shift | 73.7915 | 1.623 | Day | 202512 | 2025-12-26 | 1.623
2025-12-26 11:15 | 73.7888 | FALSE | TRUE | -3.0505 | -4.3123 | -0.22645 | -0.30595 | 0.2826 |  | 2025-12-26 09:15 | none | FALSE | 1 | 70.7383 | FALSE | FALSE | 0.5435 | 2.1257 | 72.3768 | 9 | 0.2826 | 0.09882 | 0.18948 | 0.96991 | 0.81923 | Confirmed/Materialized Shift | 74.0152 | 1.7236 | Day | 202512 | 2025-12-26 | 1.7236
2025-12-26 11:25 | 74.0714 | FALSE | TRUE | -3.3616 | -4.7541 | -0.19832 | -0.26703 | 0.2826 |  | 2025-12-26 09:15 | none | FALSE | 1 | 70.7098 | FALSE | FALSE | 0.547 | 2.0908 | 72.4897 | 10 | 0.2826 | 0.11295 | 0.19224 | 0.88248 | 0.88999 | Confirmed/Materialized Shift | 74.2697 | 1.7772 | Day | 202512 | 2025-12-26 | 1.7772
2025-12-26 11:28 | 73.7888 | TRUE | TRUE | -2.9961 | -4.2322 | -0.62384 | -0.83835 | -0.2826 |  | 2025-12-26 09:15 | none | FALSE | 2 | 70.7927 | TRUE | FALSE | 0.5445 | 2.0199 | 72.6027 | 11 | -0.2826 | 0.11295 | 0.19224 | -2.0576 | 0.90497 | Confirmed/Materialized Shift | 74.4126 | 1.3107 | Day | 202512 | 2025-12-26 | 1.3107
2025-12-26 11:29 | 74.0714 | FALSE | TRUE | -3.1909 | -4.5018 | -0.50761 | -0.68064 | 0.2826 |  | 2025-12-26 09:15 | none | FALSE | 1 | 70.8805 | FALSE | FALSE | 0.5253 | 1.9725 | 72.7298 | 12 | 0.2826 | 0.12708 | 0.19388 | 0.80214 | 0.92462 | Confirmed/Materialized Shift | 74.579 | 1.451 | Day | 202512 | 2025-12-26 | 1.451
2025-12-26 11:44 | 73.7888 | FALSE | TRUE | -2.7624 | -3.8892 | -0.87022 | -1.1656 | -0.2826 |  | 2025-12-26 09:15 | none | FALSE | 1 | 71.0264 | FALSE | FALSE | 0.498 | 1.9009 | 72.8427 | 13 | -0.2826 | 0.11295 | 0.21299 | -1.8572 | 0.90815 | Confirmed/Materialized Shift | 74.659 | 1.0418 | Day | 202512 | 2025-12-26 | 1.0418
2025-12-26 11:59 | 73.7888 | FALSE | FALSE | -2.5855 | -3.6311 | -0.91923 | -1.2304 | 0 |  |  | none | FALSE | 1 | 71.2033 | FALSE | FALSE | 0.092 |  | 72.9557 | 0 | 0 | 0.11295 | 0.21299 | -0.53031 | 0.87618 | Persistence ends | 74.708 | 0.95086 | Day | 202512 | 2025-12-26 | 0.95086
2025-12-26 12:14 | 73.5062 | FALSE | FALSE | -2.0843 | -2.9183 | -1.1809 | -1.5811 | -0.2826 |  |  | none | FALSE | 1 | 71.4219 | FALSE | FALSE | 0.0655 |  | 73.0545 | 0 | -0.2826 | 0.09882 | 0.2296 | -1.6612 | 0.81631 | Normal | 74.6871 | 0.55336 | Day | 202512 | 2025-12-26 | 0.55336
2025-12-26 12:29 | 73.5062 | FALSE | FALSE | -1.8287 | -2.5512 | -1.1229 | -1.5046 | 0 |  |  | none | FALSE | 1 | 71.6775 | FALSE | FALSE | 0.0605 |  | 73.1533 | 0 | 0 | 0.09882 | 0.2296 | -0.4304 | 0.73788 | Normal | 74.6291 | 0.47825 | Day | 202512 | 2025-12-26 | 0.47825
2025-12-26 12:44 | 73.2236 | FALSE | FALSE | -1.3337 | -1.8552 | -1.3342 | -1.7895 | -0.2826 |  |  | none | FALSE | 1 | 71.8899 | FALSE | FALSE | 0.0286 |  | 73.2239 | 0 | -0.2826 | 0.07056 | 0.24032 | -1.4695 | 0.66697 | Normal | 74.5578 | -0.00040481 | Day | 202512 | 2025-12-26 | 0.00040481
2025-12-26 12:59 | 73.2236 | FALSE | FALSE | -1.0863 | -1.5059 | -1.228 | -1.6494 | 0 |  |  | none | FALSE | 1 | 72.1373 | FALSE | FALSE | 0.0367 |  | 73.2944 | 0 | 0 | 0.07056 | 0.24032 | -0.2936 | 0.57858 | Normal | 74.4516 | -0.12242 | Day | 202512 | 2025-12-26 | 0.12242
2025-12-26 13:14 | 73.2236 | FALSE | FALSE | -0.88458 | -1.2228 | -1.1391 | -1.5318 | 0 |  |  | none | FALSE | 1 | 72.339 | FALSE | FALSE | 0.0453 |  | 73.3509 | 0 | 0 | 0.05643 | 0.23546 | -0.23966 | 0.50592 | Normal | 74.3627 | -0.25154 | Day | 202512 | 2025-12-26 | 0.25154
2025-12-26 13:28 | 73.2236 | FALSE | FALSE | -0.64201 | -0.88453 | -1.0094 | -1.3598 | 0 |  |  | none | FALSE | 1 | 72.5816 | FALSE | FALSE | 0.0582 |  | 73.4073 | 0 | 0 | 0.05643 | 0.23546 | -0.23966 | 0.41285 | Normal | 74.233 | -0.44493 | Day | 202512 | 2025-12-26 | 0.44493
2025-12-26 13:44 | 73.2236 | FALSE | FALSE | -0.45017 | -0.6186 | -0.90233 | -1.2173 | 0 |  |  | none | FALSE | 0 | 72.7734 | FALSE | FALSE | 0.0446 |  | 73.4497 | 0 | 0 | 0.04239 | 0.22968 | -0.18456 | 0.33813 | Normal | 74.1259 | -0.66862 | Day | 202512 | 2025-12-26 | 0.66862
2025-12-26 13:59 | 72.941 | FALSE | FALSE | -0.16757 | -0.23027 | -1.1849 | -1.5985 | -0.2826 |  |  | none | FALSE | 0 | 72.7734 | FALSE | FALSE | 0.1003 |  | 73.4497 | 0 | -0.2826 | 0 | 0.20502 | -1.3784 | 0.33813 | Normal | 74.1259 | -1.5044 | Day | 202512 | 2025-12-26 | 1.5044
2025-12-26 14:14 | 72.941 | FALSE | FALSE | -0.16757 | -0.23027 | -1.1849 | -1.5985 | 0 |  |  | none | FALSE | 0 | 72.7734 | FALSE | FALSE | 0.1003 |  | 73.4497 | 0 | 0 | 0 | 0.20502 | 0 | 0.33813 | Normal | 74.1259 | -1.5044 | Day | 202512 | 2025-12-26 | 1.5044
2025-12-26 14:28 | 72.941 | FALSE | FALSE | -0.21269 | -0.29245 | -1.2018 | -1.6209 | 0 |  |  | none | FALSE | 0 | 72.7283 | FALSE | FALSE | 0.0932 |  | 73.4356 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.35362 | Normal | 74.1428 | -1.3985 | Day | 202512 | 2025-12-26 | 1.3985
2025-12-26 14:43 | 72.941 | FALSE | FALSE | -0.25537 | -0.35133 | -1.2162 | -1.64 | 0 |  |  | none | FALSE | 0 | 72.6856 | FALSE | FALSE | 0.0871 |  | 73.4214 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.36789 | Normal | 74.1572 | -1.3059 | Day | 202512 | 2025-12-26 | 1.3059
2025-12-26 14:58 | 72.941 | FALSE | FALSE | -0.29588 | -0.40729 | -1.2285 | -1.6563 | 0 |  |  | none | FALSE | 0 | 72.6451 | FALSE | FALSE | 0.0816 |  | 73.4073 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.38108 | Normal | 74.1695 | -1.2236 | Day | 202512 | 2025-12-26 | 1.2236
2025-12-26 15:13 | 72.941 | FALSE | FALSE | -0.35016 | -0.48238 | -1.2262 | -1.6533 | 0 |  |  | none | FALSE | 0 | 72.5908 | FALSE | FALSE | 0.0741 |  | 73.379 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.3941 | Normal | 74.1672 | -1.1115 | Day | 202512 | 2025-12-26 | 1.1115
2025-12-26 15:28 | 72.941 | FALSE | FALSE | -0.39947 | -0.55068 | -1.219 | -1.6438 | 0 |  |  | none | FALSE | 0 | 72.5415 | FALSE | FALSE | 0.0675 |  | 73.3508 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.40462 | Normal | 74.16 | -1.0127 | Day | 202512 | 2025-12-26 | 1.0127
2025-12-26 15:43 | 72.941 | FALSE | FALSE | -0.43403 | -0.59861 | -1.1688 | -1.5771 | 0 |  |  | none | FALSE | 0 | 72.507 | FALSE | FALSE | 0.0611 |  | 73.3084 | 0 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.40071 | Normal | 74.1098 | -0.91683 | Day | 202512 | 2025-12-26 | 0.91683
2025-12-26 15:58 | 72.6584 | FALSE | FALSE | -0.18723 | -0.25836 | -1.3459 | -1.8187 | -0.2826 |  |  | none | FALSE | 0 | 72.4712 | FALSE | FALSE | 0.1008 |  | 73.2377 | 0 | -0.2826 | -0.07065 | 0.15546 | -1.3633 | 0.38328 | Normal | 74.0043 | -1.5115 | Day | 202512 | 2025-12-26 | 1.5115
2025-12-26 16:13 | 72.941 | FALSE | FALSE | -0.47686 | -0.65807 | -0.98554 | -1.3331 | 0.2826 |  |  | none | FALSE | 0 | 72.4641 | FALSE | FALSE | 0.0464 |  | 73.1953 | 0 | 0.2826 | -0.04239 | 0.16593 | 1.9586 | 0.3656 | Normal | 73.9265 | -0.69567 | Day | 202512 | 2025-12-26 | 0.69567
2025-12-26 16:28 | 72.3758 | TRUE | FALSE | 0.0389 | 0.053719 | -1.4306 | -1.9383 | -0.5652 | 2025-12-26 17:13 | 2025-12-26 16:28 | lower | TRUE | 1 | 72.4147 | FALSE | FALSE | 0.2265 | 2.1118 | 73.1106 | 1 | -0.5652 | -0.08478 | 0.18565 | -2.5877 | 0.34793 | Extreme triggered | 73.8064 | -2.1118 | Day | 202512 | 2025-12-26 | 2.1118
2025-12-26 16:43 | 72.3758 | FALSE | FALSE | -0.028723 | -0.039701 | -1.3569 | -1.8404 | 0 |  | 2025-12-26 16:28 | none | FALSE | 1 | 72.3471 | FALSE | FALSE | 0.2707 | 2.0144 | 73.0399 | 2 | 0 | -0.07065 | 0.18049 | 0.39144 | 0.34642 | Extreme/elevated | 73.7327 | -1.9171 | Day | 202512 | 2025-12-26 | 1.9171
2025-12-26 16:58 | 72.095 | FALSE | FALSE | 0.13931 | 0.19285 | -1.5811 | -2.1461 | -0.2808 |  | 2025-12-26 16:28 | lower | TRUE | 1 | 72.2343 | FALSE | TRUE | 0.3591 | 2.1385 | 72.9552 | 3 | -0.2808 | -0.08469 | 0.18555 | -1.0569 | 0.36046 | Persistent | 73.6761 | -2.3865 | Day | 202512 | 2025-12-26 | 2.3865
2025-12-26 17:13 | 72.6584 | TRUE | FALSE | -0.42879 | -0.59365 | -0.93765 | -1.274 | 0.5634 |  |  | none | FALSE | 2 | 72.2296 | TRUE | FALSE | 0.1068 |  | 72.9128 | 0 | 0.5634 | -0.04239 | 0.22933 | 2.6416 | 0.34161 | Persistence ends | 73.596 | -0.7448 | Day | 202512 | 2025-12-26 | 0.7448
2025-12-26 17:27 | 72.6584 | FALSE | FALSE | -0.41941 | -0.58058 | -0.84349 | -1.1476 | 0 |  |  | none | FALSE | 2 | 72.239 | FALSE | FALSE | 0.1019 |  | 72.8704 | 0 | 0 | -0.04239 | 0.22933 | 0.18484 | 0.31572 | Normal | 73.5019 | -0.6716 | Day | 202512 | 2025-12-26 | 0.6716
2025-12-26 17:42 | 72.6584 | FALSE | FALSE | -0.4315 | -0.59742 | -0.79906 | -1.0878 | 0 |  |  | none | FALSE | 2 | 72.2269 | FALSE | FALSE | 0.097 |  | 72.8422 | 0 | 0 | -0.02826 | 0.22235 | 0.1271 | 0.30764 | Normal | 73.4575 | -0.59739 | Night | 202512 | 2025-12-26 | 0.59739
2025-12-26 17:57 | 72.941 | FALSE | FALSE | -0.70385 | -0.97436 | -0.47795 | -0.65099 | 0.2826 |  |  | none | FALSE | 2 | 72.2372 | FALSE | FALSE | 0.0826 |  | 72.8281 | 0 | 0.2826 | -0.01413 | 0.23296 | 1.2737 | 0.29545 | Normal | 73.4189 | 0.3823 | Night | 202512 | 2025-12-26 | 0.3823
2025-12-26 18:12 | 72.941 | FALSE | FALSE | -0.69105 | -0.95647 | -0.43689 | -0.5954 | 0 |  |  | none | FALSE | 2 | 72.2499 | FALSE | FALSE | 0.0872 |  | 72.8139 | 0 | 0 | -0.01413 | 0.23296 | 0.060653 | 0.28199 | Normal | 73.3779 | 0.45066 | Night | 202512 | 2025-12-26 | 0.45066
2025-12-26 18:27 | 72.941 | FALSE | FALSE | -0.67534 | -0.93452 | -0.39292 | -0.53579 | 0 |  |  | none | FALSE | 2 | 72.2657 | FALSE | FALSE | 0.0924 |  | 72.7998 | 0 | 0 | -0.01413 | 0.23296 | 0.060653 | 0.26706 | Normal | 73.3339 | 0.52875 | Night | 202512 | 2025-12-26 | 0.52875
2025-12-26 18:30 | 72.941 | FALSE | FALSE | -0.65617 | -0.90776 | -0.34549 | -0.47143 | 0 |  |  | none | FALSE | 2 | 72.2848 | FALSE | FALSE | 0.0985 |  | 72.7857 | 0 | 0 | -0.01413 | 0.23296 | 0.060653 | 0.25042 | Normal | 73.2865 | 0.62033 | Night | 202512 | 2025-12-26 | 0.62033
2025-12-26 18:31 | 72.941 | FALSE | FALSE | -0.65617 | -0.90776 | -0.34549 | -0.47143 | 0 |  |  | none | FALSE | 1 | 72.2848 | FALSE | FALSE | 0.0699 |  | 72.7857 | 0 | 0 | 0 | 0.22423 | 0 | 0.25042 | Normal | 73.2865 | 0.62033 | Night | 202512 | 2025-12-26 | 0.62033
2025-12-26 18:46 | 73.5062 | TRUE | FALSE | -1.2853 | -1.7797 | 0.099244 | 0.1352 | 0.5652 | 2025-12-26 20:15 | 2025-12-26 18:46 | upper | TRUE | 2 | 72.2209 | TRUE | FALSE | 0.2699 | 2.3347 | 72.8139 | 1 | 0.5652 | 0.02826 | 0.25739 | 2.0861 | 0.29652 | Extreme triggered | 73.407 | 2.3347 | Night | 202512 | 2025-12-26 | 2.3347
2025-12-26 19:01 | 73.7888 | FALSE | FALSE | -1.6679 | -2.3126 | 0.19709 | 0.26782 | 0.2826 |  | 2025-12-26 18:46 | upper | TRUE | 2 | 72.1209 | FALSE | FALSE | 0.3405 | 2.4354 | 72.8563 | 2 | 0.2826 | 0.04239 | 0.26345 | 0.9118 | 0.3677 | Extreme/elevated | 73.5917 | 2.536 | Night | 202512 | 2025-12-26 | 2.536
2025-12-26 19:16 | 73.7888 | FALSE | FALSE | -1.7356 | -2.4087 | 0.044646 | 0.060542 | 0 |  | 2025-12-26 18:46 | upper | TRUE | 1 | 72.0532 | FALSE | TRUE | 0.3404 | 2.3254 | 72.8987 | 3 | 0 | 0.04239 | 0.26345 | -0.16091 | 0.42273 | Persistent | 73.7442 | 2.1056 | Night | 202512 | 2025-12-26 | 2.1056
2025-12-26 19:30 | 73.7888 | FALSE | FALSE | -1.7824 | -2.4753 | -0.08698 | -0.11774 | 0 |  | 2025-12-26 18:46 | none | FALSE | 1 | 72.0064 | FALSE | FALSE | 0.3781 | 2.1976 | 72.9411 | 4 | 0 | 0.04239 | 0.26345 | -0.16091 | 0.46734 | Persistent | 73.8758 | 1.8139 | Night | 202512 | 2025-12-26 | 1.8139
2025-12-26 19:45 | 73.7888 | FALSE | FALSE | -1.814 | -2.5203 | -0.20333 | -0.27479 | 0 |  | 2025-12-26 18:46 | none | FALSE | 1 | 71.9748 | FALSE | FALSE | 0.4207 | 2.0774 | 72.9835 | 5 | 0 | 0.04239 | 0.26345 | -0.16091 | 0.50432 | Persistent | 73.9921 | 1.5968 | Night | 202512 | 2025-12-26 | 1.5968
2025-12-26 20:00 | 73.7888 | FALSE | FALSE | -1.8334 | -2.548 | -0.30756 | -0.41508 | 0 |  | 2025-12-26 18:46 | none | FALSE | 1 | 71.9554 | FALSE | FALSE | 0.4665 | 1.9687 | 73.0259 | 6 | 0 | 0.04239 | 0.26345 | -0.16091 | 0.53525 | Persistent | 74.0964 | 1.4254 | Night | 202512 | 2025-12-26 | 1.4254
2025-12-26 20:15 | 73.5062 | FALSE | FALSE | -1.5428 | -2.1438 | -0.63864 | -0.86134 | -0.2826 |  |  | none | FALSE | 1 | 71.9634 | FALSE | FALSE | 0.0838 |  | 73.0541 | 0 | -0.2826 | 0.02826 | 0.27324 | -1.1377 | 0.54535 | Persistence ends | 74.1448 | 0.82895 | Night | 202512 | 2025-12-26 | 0.82895
2025-12-26 20:29 | 73.5062 | FALSE | FALSE | -1.5015 | -2.0853 | -0.68217 | -0.91951 | 0 |  |  | none | FALSE | 1 | 72.0047 | FALSE | FALSE | 0.0786 |  | 73.0965 | 0 | 0 | 0.04239 | 0.26345 | -0.16091 | 0.54593 | Normal | 74.1884 | 0.75043 | Night | 202512 | 2025-12-26 | 0.75043
2025-12-26 20:44 | 73.5062 | FALSE | FALSE | -1.4855 | -2.0626 | -0.72267 | -0.97357 | 0 |  |  | none | FALSE | 1 | 72.0207 | FALSE | FALSE | 0.0746 |  | 73.1248 | 0 | 0 | 0.02826 | 0.25739 | -0.10979 | 0.55205 | Normal | 74.2289 | 0.69092 | Night | 202512 | 2025-12-26 | 0.69092
2025-12-26 20:59 | 73.5062 | FALSE | FALSE | -1.3823 | -1.9166 | -0.7325 | -0.98668 | 0 |  |  | none | FALSE | 1 | 72.1239 | FALSE | FALSE | 0.0695 |  | 73.1813 | 0 | 0 | 0.05652 | 0.2166 | -0.26094 | 0.5287 | Normal | 74.2387 | 0.61453 | Night | 202512 | 2025-12-26 | 0.61453
2025-12-26 21:14 | 73.5062 | FALSE | FALSE | -1.2635 | -1.749 | -0.72674 | -0.979 | 0 |  |  | none | FALSE | 0 | 72.2427 | FALSE | FALSE | 0.036 |  | 73.2378 | 0 | 0 | 0.05652 | 0.2166 | -0.26094 | 0.49756 | Normal | 74.2329 | 0.53939 | Night | 202512 | 2025-12-26 | 0.53939
2025-12-26 21:29 | 73.5062 | FALSE | FALSE | -1.0401 | -1.4354 | -0.64451 | -0.86919 | 0 |  |  | none | FALSE | 0 | 72.4661 | FALSE | FALSE | 0.0313 |  | 73.3084 | 0 | 0 | 0.07056 | 0.20221 | -0.34895 | 0.42116 | Normal | 74.1507 | 0.4697 | Night | 202512 | 2025-12-26 | 0.4697
2025-12-26 21:44 | 73.5062 | FALSE | FALSE | -0.94362 | -1.3004 | -0.63276 | -0.85348 | 0 |  |  | none | FALSE | 0 | 72.5626 | FALSE | FALSE | 0.0263 |  | 73.3508 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.3941 | Normal | 74.139 | 0.3944 | Night | 202512 | 2025-12-26 | 0.3944
2025-12-26 21:59 | 73.5062 | FALSE | FALSE | -0.83266 | -1.1457 | -0.60658 | -0.81845 | 0 |  |  | none | FALSE | 0 | 72.6735 | FALSE | FALSE | 0.0209 |  | 73.3932 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.35981 | Normal | 74.1128 | 0.31417 | Night | 202512 | 2025-12-26 | 0.31417
2025-12-26 22:14 | 73.2236 | FALSE | FALSE | -0.44005 | -0.6046 | -0.83569 | -1.1284 | -0.2826 |  |  | none | FALSE | 0 | 72.7835 | FALSE | FALSE | 0.0414 |  | 73.4214 | 0 | -0.2826 | 0.02826 | 0.18107 | -1.7168 | 0.31894 | Normal | 74.0593 | -0.62025 | Night | 202512 | 2025-12-26 | 0.62025
2025-12-26 22:29 | 73.2236 | FALSE | FALSE | -0.39277 | -0.53929 | -0.81667 | -1.103 | 0 |  |  | none | FALSE | 0 | 72.8308 | FALSE | FALSE | 0.0467 |  | 73.4356 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.30236 | Normal | 74.0403 | -0.70098 | Night | 202512 | 2025-12-26 | 0.70098
2025-12-26 22:44 | 73.2236 | FALSE | FALSE | -0.34209 | -0.46937 | -0.79425 | -1.073 | 0 |  |  | none | FALSE | 0 | 72.8815 | FALSE | FALSE | 0.0531 |  | 73.4497 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.28408 | Normal | 74.0178 | -0.79582 | Night | 202512 | 2025-12-26 | 0.79582
2025-12-26 22:59 | 73.2236 | FALSE | FALSE | -0.28729 | -0.39389 | -0.76771 | -1.0376 | 0 |  |  | none | FALSE | 0 | 72.9363 | FALSE | FALSE | 0.0607 |  | 73.4638 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.26375 | Normal | 73.9913 | -0.91074 | Night | 202512 | 2025-12-26 | 0.91074
2025-12-26 23:14 | 73.2236 | FALSE | FALSE | -0.22735 | -0.31145 | -0.73603 | -0.99517 | 0 |  |  | none | FALSE | 0 | 72.9963 | FALSE | FALSE | 0.0704 |  | 73.4779 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.24084 | Normal | 73.9596 | -1.056 | Night | 202512 | 2025-12-26 | 1.056
2025-12-26 23:28 | 72.941 | FALSE | FALSE | 0.055253 | 0.075693 | -1.0186 | -1.3773 | -0.2826 | 2025-12-27 04:42 | 2025-12-26 23:28 | lower | TRUE | 0 | 72.9963 | FALSE | FALSE | 0.2058 | 2.2294 | 73.4779 | 1 | -0.2826 | 0 | 0.18338 | -1.5411 | 0.24084 | Extreme triggered | 73.9596 | -2.2294 | Night | 202512 | 2025-12-26 | 2.2294
2025-12-26 23:43 | 72.941 | FALSE | FALSE | -0.029081 | -0.039886 | -1.0464 | -1.4143 | 0 |  | 2025-12-26 23:28 | none | FALSE | 0 | 72.9119 | FALSE | FALSE | 0.2404 | 2.0606 | 73.4497 | 2 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.26888 | Extreme/elevated | 73.9874 | -1.8918 | Night | 202512 | 2025-12-26 | 1.8918
2025-12-26 23:59 | 72.941 | FALSE | FALSE | -0.092177 | -0.12653 | -1.0248 | -1.3854 | 0 |  | 2025-12-26 23:28 | none | FALSE | 0 | 72.8488 | FALSE | FALSE | 0.2828 | 1.9304 | 73.4073 | 3 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27923 | Persistent | 73.9658 | -1.6699 | Night | 202512 | 2025-12-26 | 1.6699
2025-12-27 00:14 | 72.941 | FALSE | FALSE | -0.1413 | -0.19409 | -0.9891 | -1.3379 | 0 |  | 2025-12-26 23:28 | none | FALSE | 0 | 72.7997 | FALSE | FALSE | 0.3286 | 1.8228 | 73.3649 | 4 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.2826 | Persistent | 73.9301 | -1.5 | Night | 202512 | 2025-12-27 | 1.5
2025-12-27 00:28 | 72.941 | FALSE | FALSE | -0.17696 | -0.24319 | -0.93998 | -1.2723 | 0 |  | 2025-12-26 23:28 | none | FALSE | 0 | 72.764 | FALSE | FALSE | 0.3768 | 1.7315 | 73.3225 | 5 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27923 | Persistent | 73.881 | -1.3663 | Night | 202512 | 2025-12-27 | 1.3663
2025-12-27 00:43 | 72.941 | FALSE | FALSE | -0.19864 | -0.27308 | -0.87688 | -1.1879 | 0 |  | 2025-12-26 23:28 | none | FALSE | 0 | 72.7424 | FALSE | FALSE | 0.4269 | 1.6531 | 73.2801 | 6 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.26888 | Persistent | 73.8179 | -1.2612 | Night | 202512 | 2025-12-27 | 1.2612
2025-12-27 00:58 | 72.6584 | FALSE | TRUE | 0.015075 | 0.020743 | -1.1153 | -1.5118 | -0.2826 |  | 2025-12-26 23:28 | lower | TRUE | 0 | 72.6735 | FALSE | TRUE | 0.537 | 1.7105 | 73.2236 | 7 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.27506 | Confirmed/Materialized Shift | 73.7737 | -2.0548 | Night | 202512 | 2025-12-27 | 2.0548
2025-12-27 01:13 | 72.6584 | FALSE | TRUE | -0.064992 | -0.089529 | -1.1106 | -1.5055 | 0 |  | 2025-12-26 23:28 | none | FALSE | 0 | 72.5934 | FALSE | FALSE | 0.5186 | 1.719 | 73.1812 | 8 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.2939 | Confirmed/Materialized Shift | 73.769 | -1.7789 | Night | 202512 | 2025-12-27 | 1.7789
2025-12-27 01:28 | 72.3758 | FALSE | TRUE | 0.080765 | 0.11147 | -1.417 | -1.9203 | -0.2826 |  | 2025-12-26 23:28 | lower | TRUE | 0 | 72.4566 | FALSE | TRUE | 0.5495 | 1.7771 | 73.1247 | 9 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.33406 | Confirmed/Materialized Shift | 73.7928 | -2.2418 | Night | 202512 | 2025-12-27 | 2.2418
2025-12-27 01:43 | 72.3758 | FALSE | TRUE | -0.028996 | -0.040079 | -1.4137 | -1.9159 | 0 |  | 2025-12-26 23:28 | none | FALSE | 0 | 72.3468 | FALSE | FALSE | 0.528 | 1.7914 | 73.0682 | 10 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.36068 | Confirmed/Materialized Shift | 73.7895 | -1.9196 | Night | 202512 | 2025-12-27 | 1.9196
2025-12-27 01:58 | 72.3758 | FALSE | TRUE | -0.11744 | -0.16253 | -1.3891 | -1.8832 | 0 |  | 2025-12-26 23:28 | none | FALSE | 0 | 72.2584 | FALSE | FALSE | 0.5125 | 1.782 | 73.0117 | 11 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.37665 | Confirmed/Materialized Shift | 73.7649 | -1.6882 | Night | 202512 | 2025-12-27 | 1.6882
2025-12-27 02:13 | 72.3758 | FALSE | TRUE | -0.18723 | -0.25937 | -1.3459 | -1.8256 | 0 |  | 2025-12-26 23:28 | none | FALSE | 0 | 72.1886 | FALSE | FALSE | 0.5008 | 1.7594 | 72.9551 | 12 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.38328 | Confirmed/Materialized Shift | 73.7217 | -1.5115 | Night | 202512 | 2025-12-27 | 1.5115
2025-12-27 02:28 | 72.3758 | FALSE | TRUE | -0.23936 | -0.33181 | -1.285 | -1.7445 | 0 |  | 2025-12-26 23:28 | none | FALSE | 0 | 72.1364 | FALSE | FALSE | 0.4915 | 1.7296 | 72.8986 | 13 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.38108 | Confirmed/Materialized Shift | 73.6608 | -1.3719 | Night | 202512 | 2025-12-27 | 1.3719
2025-12-27 02:43 | 72.3758 | FALSE | TRUE | -0.27349 | -0.3793 | -1.2061 | -1.6391 | 0 |  | 2025-12-26 23:28 | none | FALSE | 0 | 72.1023 | FALSE | FALSE | 0.484 | 1.6961 | 72.8421 | 14 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.36989 | Confirmed/Materialized Shift | 73.5819 | -1.2606 | Night | 202512 | 2025-12-27 | 1.2606
2025-12-27 02:58 | 72.095 | FALSE | TRUE | -0.065737 | -0.091264 | -1.4188 | -1.93 | -0.2808 |  | 2025-12-26 23:28 | none | FALSE | 0 | 72.0293 | FALSE | FALSE | 0.5215 | 1.7046 | 72.7715 | 15 | -0.2808 | -0.07056 | 0.12539 | -1.6767 | 0.37113 | Confirmed/Materialized Shift | 73.5138 | -1.8229 | Night | 202512 | 2025-12-27 | 1.8229
2025-12-27 03:13 | 72.095 | FALSE | TRUE | -0.14859 | -0.20653 | -1.3888 | -1.8899 | 0 |  | 2025-12-26 23:28 | none | FALSE | 0 | 71.9464 | FALSE | FALSE | 0.5076 | 1.6989 | 72.7151 | 16 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.38434 | Confirmed/Materialized Shift | 73.4838 | -1.6134 | Night | 202512 | 2025-12-27 | 1.6134
2025-12-27 03:27 | 72.095 | FALSE | TRUE | -0.2135 | -0.29702 | -1.3408 | -1.8259 | 0 |  | 2025-12-26 23:28 | none | FALSE | 0 | 71.8815 | FALSE | FALSE | 0.4967 | 1.6843 | 72.6587 | 17 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.38858 | Confirmed/Materialized Shift | 73.4358 | -1.4506 | Night | 202512 | 2025-12-27 | 1.4506
2025-12-27 03:42 | 72.095 | FALSE | TRUE | -0.26106 | -0.36342 | -1.2755 | -1.7385 | 0 |  | 2025-12-26 23:28 | none | FALSE | 0 | 71.8339 | FALSE | FALSE | 0.488 | 1.6641 | 72.6022 | 18 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.38415 | Confirmed/Materialized Shift | 73.3705 | -1.3204 | Night | 202512 | 2025-12-27 | 1.3204
2025-12-27 03:57 | 72.095 | FALSE | TRUE | -0.29065 | -0.40478 | -1.1923 | -1.6268 | 0 |  | 2025-12-26 23:28 | none | FALSE | 0 | 71.8044 | FALSE | FALSE | 0.4811 | 1.6405 | 72.5458 | 19 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.37073 | Confirmed/Materialized Shift | 73.2873 | -1.216 | Night | 202512 | 2025-12-27 | 1.216
2025-12-27 04:12 | 72.095 | FALSE | TRUE | -0.30019 | -0.41812 | -1.0889 | -1.488 | 0 |  | 2025-12-26 23:28 | none | FALSE | 0 | 71.7948 | FALSE | FALSE | 0.4757 | 1.6152 | 72.4894 | 20 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.34728 | Confirmed/Materialized Shift | 73.1839 | -1.1356 | Night | 202512 | 2025-12-27 | 1.1356
2025-12-27 04:27 | 72.095 | FALSE | TRUE | -0.32961 | -0.45928 | -1.0338 | -1.4136 | 0 |  | 2025-12-26 23:28 | none | FALSE | 0 | 71.7654 | FALSE | FALSE | 0.4689 | 1.5875 | 72.4471 | 21 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.34084 | Confirmed/Materialized Shift | 73.1288 | -1.033 | Night | 202512 | 2025-12-27 | 1.033
2025-12-27 04:42 | 72.095 | FALSE | FALSE | -0.34741 | -0.48421 | -0.96697 | -1.3235 | 0 |  |  | none | FALSE | 0 | 71.7476 | FALSE | FALSE | 0.0628 |  | 72.4048 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.3286 | Persistence ends | 73.062 | -0.94274 | Night | 202512 | 2025-12-27 | 0.94274
2025-12-27 04:57 | 72.095 | FALSE | FALSE | -0.35223 | -0.49096 | -0.88719 | -1.2156 | 0 |  |  | none | FALSE | 0 | 71.7428 | FALSE | FALSE | 0.0575 |  | 72.3625 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.30985 | Normal | 72.9822 | -0.86325 | Night | 202512 | 2025-12-27 | 0.86325
2025-12-27 05:12 | 71.8124 | FALSE | FALSE | -0.10957 | -0.15281 | -1.0969 | -1.5044 | -0.2826 |  |  | none | FALSE | 0 | 71.7028 | FALSE | FALSE | 0.1091 |  | 72.306 | 0 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.30161 | Normal | 72.9093 | -1.6367 | Night | 202512 | 2025-12-27 | 1.6367
2025-12-27 05:27 | 71.8124 | FALSE | FALSE | -0.12571 | -0.17536 | -1.0001 | -1.3736 | 0 |  |  | none | FALSE | 0 | 71.6867 | FALSE | FALSE | 0.1036 |  | 72.2496 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.28146 | Normal | 72.8125 | -1.5534 | Night | 202512 | 2025-12-27 | 1.5534
2025-12-27 05:42 | 71.8124 | FALSE | FALSE | -0.11226 | -0.15656 | -0.87384 | -1.2022 | 0 |  |  | none | FALSE | 0 | 71.7001 | FALSE | FALSE | 0.103 |  | 72.1932 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.24652 | Normal | 72.6862 | -1.5446 | Night | 202512 | 2025-12-27 | 1.5446
2025-12-27 05:57 | 71.8124 | FALSE | FALSE | -0.13111 | -0.18291 | -0.80809 | -1.1128 | 0 |  |  | none | FALSE | 0 | 71.6813 | FALSE | FALSE | 0.0961 |  | 72.1509 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.2348 | Normal | 72.6205 | -1.4416 | Night | 202512 | 2025-12-27 | 1.4416
2025-12-27 06:12 | 71.8124 | FALSE | FALSE | -0.13146 | -0.1834 | -0.72384 | -0.9979 | 0 |  |  | none | FALSE | 0 | 71.6809 | FALSE | FALSE | 0.0923 |  | 72.1086 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.21383 | Normal | 72.5362 | -1.3852 | Night | 202512 | 2025-12-27 | 1.3852
2025-12-27 06:26 | 71.8124 | FALSE | FALSE | -0.15974 | -0.22294 | -0.69578 | -0.95959 | 0 |  |  | none | FALSE | 0 | 71.6527 | FALSE | FALSE | 0.0835 |  | 72.0804 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.21388 | Normal | 72.5082 | -1.2531 | Night | 202512 | 2025-12-27 | 1.2531
2025-12-27 06:41 | 71.5298 | TRUE | FALSE | 0.038311 | 0.053531 | -0.97833 | -1.3493 | -0.2826 | 2025-12-27 08:30 | 2025-12-27 06:41 | lower | TRUE | 1 | 71.5681 | FALSE | FALSE | 0.2299 | 2.163 | 72.0381 | 1 | -0.2826 | -0.0423 | 0.10331 | -2.326 | 0.235 | Extreme triggered | 72.5081 | -2.163 | Night | 202512 | 2025-12-27 | 2.163
2025-12-27 06:56 | 71.5298 | FALSE | FALSE | -0.027707 | -0.03875 | -0.95975 | -1.324 | 0 |  | 2025-12-27 06:41 | none | FALSE | 1 | 71.5021 | FALSE | FALSE | 0.2687 | 2.0254 | 71.9958 | 2 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.24686 | Extreme/elevated | 72.4895 | -1.8878 | Night | 202512 | 2025-12-27 | 1.8878
2025-12-27 07:11 | 71.5298 | FALSE | FALSE | -0.077834 | -0.10893 | -0.92527 | -1.277 | 0 |  | 2025-12-27 06:41 | none | FALSE | 1 | 71.452 | FALSE | FALSE | 0.3126 | 1.9135 | 71.9535 | 3 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.25078 | Persistent | 72.4551 | -1.6896 | Day | 202512 | 2025-12-27 | 1.6896
2025-12-27 07:26 | 71.5298 | FALSE | FALSE | -0.11283 | -0.15798 | -0.87567 | -1.2094 | 0 |  | 2025-12-27 06:41 | none | FALSE | 1 | 71.417 | FALSE | FALSE | 0.36 | 1.821 | 71.9112 | 4 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.24712 | Persistent | 72.4055 | -1.5434 | Day | 202512 | 2025-12-27 | 1.5434
2025-12-27 07:30 | 71.5298 | FALSE | FALSE | -0.13198 | -0.18485 | -0.81022 | -1.12 | 0 |  | 2025-12-27 06:41 | none | FALSE | 1 | 71.3978 | FALSE | FALSE | 0.4103 | 1.7447 | 71.8689 | 5 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.23555 | Persistent | 72.34 | -1.4397 | Day | 202512 | 2025-12-27 | 1.4397
2025-12-27 07:45 | 71.5298 | FALSE | FALSE | -0.17083 | -0.23939 | -0.79255 | -1.0959 | 0 |  | 2025-12-27 06:41 | none | FALSE | 1 | 71.359 | FALSE | FALSE | 0.4575 | 1.669 | 71.8407 | 6 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.24084 | Persistent | 72.3223 | -1.2907 | Day | 202512 | 2025-12-27 | 1.2907
2025-12-27 08:01 | 71.5298 | FALSE | TRUE | -0.20256 | -0.28399 | -0.76776 | -1.062 | 0 |  | 2025-12-27 06:41 | none | FALSE | 1 | 71.3272 | FALSE | FALSE | 0.5062 | 1.597 | 71.8124 | 7 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.24258 | Confirmed/Materialized Shift | 72.2976 | -1.165 | Day | 202512 | 2025-12-27 | 1.165
2025-12-27 08:16 | 71.5298 | FALSE | TRUE | -0.22735 | -0.31885 | -0.73603 | -1.0185 | 0 |  | 2025-12-27 06:41 | none | FALSE | 1 | 71.3025 | FALSE | FALSE | 0.499 | 1.5294 | 71.7841 | 8 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.24084 | Confirmed/Materialized Shift | 72.2658 | -1.056 | Day | 202512 | 2025-12-27 | 1.056
2025-12-27 08:30 | 71.5298 | FALSE | FALSE | -0.24502 | -0.34372 | -0.69718 | -0.96526 | 0 |  |  | none | FALSE | 1 | 71.2848 | FALSE | FALSE | 0.0926 |  | 71.7559 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.23555 | Persistence ends | 72.227 | -0.9598 | Day | 202512 | 2025-12-27 | 0.9598
2025-12-27 08:30 | 71.8124 | TRUE | FALSE | -0.51512 | -0.7225 | -0.37382 | -0.51786 | 0.2826 |  |  | none | FALSE | 2 | 71.2973 | TRUE | FALSE | 0.0783 |  | 71.7417 | 0 | 0.2826 | -0.01413 | 0.11135 | 2.6647 | 0.22224 | Normal | 72.1862 | 0.31791 | Day | 202512 | 2025-12-27 | 0.31791
2025-12-27 08:45 | 71.8124 | FALSE | FALSE | -0.4989 | -0.69959 | -0.32934 | -0.45652 | 0 |  |  | none | FALSE | 1 | 71.3135 | FALSE | FALSE | 0.0559 |  | 71.7276 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.20706 | Normal | 72.1417 | 0.40945 | Day | 202512 | 2025-12-27 | 0.40945
2025-12-27 09:00 | 72.095 | TRUE | FALSE | -0.7815 | -1.0959 | -0.046739 | -0.064788 | 0.2826 |  |  | none | FALSE | 2 | 71.3135 | TRUE | FALSE | 0.1754 |  | 71.7276 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.20706 | Normal | 72.1417 | 1.7743 | Day | 202512 | 2025-12-27 | 1.7743
2025-12-27 09:15 | 72.095 | FALSE | FALSE | -0.7815 | -1.0959 | -0.046739 | -0.064788 | 0 |  |  | none | FALSE | 2 | 71.3135 | FALSE | FALSE | 0.1754 |  | 71.7276 | 0 | 0 | 0 | 0.12967 | 0 | 0.20706 | Normal | 72.1417 | 1.7743 | Day | 202512 | 2025-12-27 | 1.7743
2025-12-27 09:30 | 72.6584 | TRUE | FALSE | -1.4702 | -2.0652 | 0.33505 | 0.46326 | 0.5634 | 2025-12-27 12:18 | 2025-12-27 09:30 | upper | TRUE | 3 | 71.1882 | TRUE | FALSE | 0.3549 | 3.1806 | 71.7558 | 1 | 0.5634 | 0.02817 | 0.18079 | 2.9605 | 0.28378 | Extreme triggered | 72.3234 | 3.1806 | Day | 202512 | 2025-12-27 | 3.1806
2025-12-27 09:45 | 72.941 | FALSE | FALSE | -1.9058 | -2.6829 | 0.35175 | 0.48457 | 0.2826 |  | 2025-12-27 09:30 | upper | TRUE | 3 | 71.0352 | FALSE | FALSE | 0.3937 | 3.043 | 71.8122 | 2 | 0.2826 | 0.05643 | 0.17369 | 1.3022 | 0.38852 | Extreme/elevated | 72.5893 | 2.9054 | Day | 202512 | 2025-12-27 | 2.9054
2025-12-27 10:00 | 72.941 | FALSE | FALSE | -1.999 | -2.8177 | 0.14574 | 0.2002 | 0 |  | 2025-12-27 09:30 | upper | TRUE | 3 | 70.942 | FALSE | TRUE | 0.4114 | 2.8002 | 71.8687 | 3 | 0 | 0.05643 | 0.17369 | -0.32489 | 0.46331 | Persistent | 72.7953 | 2.3146 | Day | 202512 | 2025-12-27 | 2.3146
2025-12-27 10:15 | 73.2236 | FALSE | FALSE | -2.3905 | -3.3748 | 0.17828 | 0.24406 | 0.2826 |  | 2025-12-27 09:30 | upper | TRUE | 3 | 70.8331 | FALSE | TRUE | 0.4691 | 2.6807 | 71.9392 | 4 | 0.2826 | 0.07056 | 0.18023 | 1.1765 | 0.55306 | Persistent | 73.0453 | 2.3223 | Day | 202512 | 2025-12-27 | 2.3223
2025-12-27 10:29 | 73.2236 | FALSE | FALSE | -2.4574 | -3.4725 | -0.029726 | -0.04058 | 0 |  | 2025-12-27 09:30 | none | FALSE | 3 | 70.7662 | FALSE | FALSE | 0.5016 | 2.535 | 72.0098 | 5 | 0 | 0.07056 | 0.18023 | -0.3915 | 0.62178 | Persistent | 73.2533 | 1.9522 | Day | 202512 | 2025-12-27 | 1.9522
2025-12-27 10:44 | 73.5062 | FALSE | FALSE | -2.8187 | -3.9875 | 0.0048057 | 0.0065382 | 0.2826 |  | 2025-12-27 09:30 | upper | TRUE | 3 | 70.6875 | FALSE | TRUE | 0.5624 | 2.447 | 72.0945 | 6 | 0.2826 | 0.08469 | 0.18541 | 1.0674 | 0.70347 | Persistent | 73.5014 | 2.0068 | Day | 202512 | 2025-12-27 | 2.0068
2025-12-27 10:59 | 73.2236 | FALSE | TRUE | -2.5452 | -3.6012 | -0.42808 | -0.58123 | -0.2826 |  | 2025-12-27 09:30 | none | FALSE | 2 | 70.6784 | FALSE | FALSE | 0.5521 | 2.3009 | 72.165 | 7 | -0.2826 | 0.07056 | 0.20221 | -1.7465 | 0.74333 | Confirmed/Materialized Shift | 73.6517 | 1.4241 | Day | 202512 | 2025-12-27 | 1.4241
2025-12-27 11:14 | 73.5062 | FALSE | TRUE | -2.8117 | -3.9772 | -0.32697 | -0.44284 | 0.2826 |  | 2025-12-27 09:30 | none | FALSE | 2 | 70.6945 | FALSE | FALSE | 0.5627 | 2.2112 | 72.2638 | 8 | 0.2826 | 0.09882 | 0.18934 | 0.97063 | 0.78466 | Confirmed/Materialized Shift | 73.8332 | 1.5833 | Day | 202512 | 2025-12-27 | 1.5833
2025-12-27 11:29 | 73.7888 | FALSE | TRUE | -3.0809 | -4.3572 | -0.25689 | -0.34693 | 0.2826 |  | 2025-12-27 09:30 | none | FALSE | 1 | 70.7079 | FALSE | FALSE | 0.5414 | 2.1535 | 72.3768 | 9 | 0.2826 | 0.11295 | 0.1921 | 0.88312 | 0.83445 | Confirmed/Materialized Shift | 74.0457 | 1.6921 | Day | 202512 | 2025-12-27 | 1.6921
2025-12-27 11:44 | 73.7888 | FALSE | TRUE | -3.0312 | -4.2839 | -0.43305 | -0.58345 | 0 |  | 2025-12-27 09:30 | none | FALSE | 1 | 70.7576 | FALSE | FALSE | 0.5286 | 2.0881 | 72.4897 | 10 | 0 | 0.11295 | 0.1921 | -0.58797 | 0.86606 | Confirmed/Materialized Shift | 74.2219 | 1.5 | Day | 202512 | 2025-12-27 | 1.5
2025-12-27 11:45 | 74.0714 | FALSE | TRUE | -3.2615 | -4.606 | -0.35232 | -0.47339 | 0.2826 |  | 2025-12-27 09:30 | none | FALSE | 0 | 70.8099 | FALSE | FALSE | 0.5073 | 2.0447 | 72.6168 | 11 | 0.2826 | 0.12708 | 0.19374 | 0.80271 | 0.90345 | Confirmed/Materialized Shift | 74.4237 | 1.61 | Day | 202512 | 2025-12-27 | 1.61
2025-12-27 11:48 | 74.0714 | FALSE | TRUE | -3.1697 | -4.4705 | -0.51466 | -0.69002 | 0 |  | 2025-12-27 09:30 | none | FALSE | 0 | 70.9017 | FALSE | FALSE | 0.4961 | 1.9944 | 72.7439 | 12 | 0 | 0.12708 | 0.19374 | -0.65592 | 0.92108 | Confirmed/Materialized Shift | 74.5861 | 1.4412 | Day | 202512 | 2025-12-27 | 1.4412
2025-12-27 12:03 | 74.0714 | FALSE | TRUE | -3.0406 | -4.2807 | -0.63975 | -0.8563 | 0 |  | 2025-12-27 09:30 | none | FALSE | 0 | 71.0308 | FALSE | FALSE | 0.487 | 1.9413 | 72.871 | 13 | 0 | 0.12708 | 0.19374 | -0.65592 | 0.92009 | Confirmed/Materialized Shift | 74.7112 | 1.3047 | Day | 202512 | 2025-12-27 | 1.3047
2025-12-27 12:18 | 73.7888 | FALSE | FALSE | -2.5744 | -3.615 | -0.96464 | -1.2904 | -0.2826 |  |  | none | FALSE | 0 | 71.2144 | FALSE | FALSE | 0.0606 |  | 72.9839 | 0 | -0.2826 | 0.11295 | 0.21286 | -1.8582 | 0.88476 | Persistence ends | 74.7534 | 0.90971 | Day | 202512 | 2025-12-27 | 0.90971
2025-12-27 12:29 | 73.5062 | FALSE | FALSE | -2.0673 | -2.8938 | -1.2204 | -1.6332 | -0.2826 |  |  | none | FALSE | 0 | 71.4389 | FALSE | FALSE | 0.0343 |  | 73.0828 | 0 | -0.2826 | 0.09882 | 0.22948 | -1.6621 | 0.82194 | Normal | 74.7266 | 0.51519 | Day | 202512 | 2025-12-27 | 0.51519
2025-12-27 12:44 | 73.5062 | FALSE | FALSE | -1.8049 | -2.5173 | -1.1557 | -1.5479 | 0 |  |  | none | FALSE | 0 | 71.7013 | FALSE | FALSE | 0.0292 |  | 73.1816 | 0 | 0 | 0.09882 | 0.22948 | -0.43062 | 0.74014 | Normal | 74.6619 | 0.43861 | Day | 202512 | 2025-12-27 | 0.43861
2025-12-27 12:59 | 73.5062 | FALSE | FALSE | -1.5773 | -2.1929 | -1.0974 | -1.471 | 0 |  |  | none | FALSE | 0 | 71.9289 | FALSE | FALSE | 0.0239 |  | 73.2663 | 0 | 0 | 0.08469 | 0.22625 | -0.37432 | 0.66869 | Normal | 74.6036 | 0.35882 | Day | 202512 | 2025-12-27 | 0.35882
2025-12-27 13:14 | 73.2236 | FALSE | FALSE | -1.037 | -1.4365 | -1.2634 | -1.6962 | -0.2826 |  |  | none | FALSE | 0 | 72.1866 | FALSE | FALSE | 0.0131 |  | 73.3368 | 0 | -0.2826 | 0.07056 | 0.24021 | -1.4702 | 0.57511 | Normal | 74.487 | -0.19687 | Day | 202512 | 2025-12-27 | 0.19687
2025-12-27 13:28 | 72.941 | FALSE | FALSE | -0.57371 | -0.79277 | -1.4499 | -1.9491 | -0.2826 |  |  | none | FALSE | 0 | 72.3673 | FALSE | FALSE | 0.0577 |  | 73.3791 | 0 | -0.2826 | 0.0423 | 0.2471 | -1.3148 | 0.50591 | Normal | 74.3909 | -0.866 | Day | 202512 | 2025-12-27 | 0.866
2025-12-27 13:43 | 73.2236 | FALSE | FALSE | -0.60556 | -0.8339 | -1.0295 | -1.3864 | 0.2826 |  |  | none | FALSE | 0 | 72.618 | FALSE | FALSE | 0.0346 |  | 73.4356 | 0 | 0.2826 | 0.05643 | 0.25257 | 0.89546 | 0.40876 | Normal | 74.2531 | -0.51852 | Day | 202512 | 2025-12-27 | 0.51852
2025-12-27 13:59 | 72.941 | FALSE | FALSE | -0.26062 | -0.35859 | -1.278 | -1.7219 | -0.2826 |  |  | none | FALSE | 0 | 72.6804 | FALSE | FALSE | 0.0882 |  | 73.4497 | 0 | -0.2826 | 0.01413 | 0.23331 | -1.2718 | 0.38465 | Normal | 74.219 | -1.3224 | Day | 202512 | 2025-12-27 | 1.3224
2025-12-27 14:14 | 72.941 | FALSE | FALSE | -0.26062 | -0.35859 | -1.278 | -1.7219 | 0 |  |  | none | FALSE | 0 | 72.6804 | FALSE | FALSE | 0.0882 |  | 73.4497 | 0 | 0 | 0 | 0.22459 | 0 | 0.38465 | Normal | 74.219 | -1.3224 | Day | 202512 | 2025-12-27 | 1.3224
2025-12-27 14:28 | 72.941 | FALSE | FALSE | -0.26062 | -0.35859 | -1.278 | -1.7219 | 0 |  |  | none | FALSE | 0 | 72.6804 | FALSE | FALSE | 0.0882 |  | 73.4497 | 0 | 0 | 0 | 0.22459 | 0 | 0.38465 | Normal | 74.219 | -1.3224 | Day | 202512 | 2025-12-27 | 1.3224
2025-12-27 14:43 | 72.6584 | FALSE | FALSE | -0.079309 | -0.10927 | -1.6053 | -2.1617 | -0.2826 |  |  | none | FALSE | 0 | 72.5791 | FALSE | FALSE | 0.1208 |  | 73.4214 | 0 | -0.2826 | -0.02826 | 0.22271 | -1.142 | 0.42116 | Normal | 74.2637 | -1.8117 | Day | 202512 | 2025-12-27 | 1.8117
2025-12-27 14:58 | 72.941 | FALSE | FALSE | -0.39917 | -0.55027 | -1.3318 | -1.7931 | 0.2826 |  |  | none | FALSE | 0 | 72.5418 | FALSE | FALSE | 0.0718 |  | 73.4073 | 0 | 0.2826 | -0.01413 | 0.23331 | 1.2718 | 0.43273 | Normal | 74.2728 | -1.0775 | Day | 202512 | 2025-12-27 | 1.0775
2025-12-27 15:13 | 72.941 | FALSE | FALSE | -0.45044 | -0.62138 | -1.3265 | -1.7861 | 0 |  |  | none | FALSE | 0 | 72.4906 | FALSE | FALSE | 0.0657 |  | 73.379 | 0 | 0 | -0.02826 | 0.22271 | 0.12689 | 0.44424 | Normal | 74.2675 | -0.98603 | Day | 202512 | 2025-12-27 | 0.98603
2025-12-27 15:28 | 72.6584 | FALSE | FALSE | -0.25117 | -0.34688 | -1.6359 | -2.2019 | -0.2826 |  |  | none | FALSE | 0 | 72.4072 | FALSE | FALSE | 0.0978 |  | 73.3508 | 0 | -0.2826 | -0.02826 | 0.22271 | -1.142 | 0.47177 | Normal | 74.2943 | -1.4676 | Day | 202512 | 2025-12-27 | 1.4676
2025-12-27 15:43 | 72.941 | FALSE | FALSE | -0.57618 | -0.79621 | -1.3392 | -1.8029 | 0.2826 |  |  | none | FALSE | 0 | 72.3648 | FALSE | FALSE | 0.0531 |  | 73.3225 | 0 | 0.2826 | -0.02826 | 0.22271 | 1.3958 | 0.47884 | Normal | 74.2802 | -0.79673 | Day | 202512 | 2025-12-27 | 0.79673
2025-12-27 15:58 | 72.6584 | FALSE | FALSE | -0.36749 | -0.50835 | -1.5827 | -2.1318 | -0.2826 |  |  | none | FALSE | 0 | 72.2909 | FALSE | FALSE | 0.0831 |  | 73.266 | 0 | -0.2826 | -0.05652 | 0.21697 | -1.042 | 0.48754 | Normal | 74.2411 | -1.2462 | Day | 202512 | 2025-12-27 | 1.2462
2025-12-27 16:13 | 72.3758 | FALSE | FALSE | -0.1998 | -0.27683 | -1.8389 | -2.4778 | -0.2826 |  |  | none | FALSE | 0 | 72.176 | FALSE | FALSE | 0.1072 |  | 73.1953 | 0 | -0.2826 | -0.07065 | 0.22224 | -0.95372 | 0.50967 | Normal | 74.2147 | -1.608 | Day | 202512 | 2025-12-27 | 1.608
2025-12-27 16:27 | 72.3758 | FALSE | FALSE | -0.25953 | -0.35988 | -1.7291 | -2.3333 | 0 |  |  | none | FALSE | 0 | 72.1163 | FALSE | FALSE | 0.0985 |  | 73.1106 | 0 | 0 | -0.08478 | 0.20706 | 0.40945 | 0.49715 | Normal | 74.1049 | -1.478 | Day | 202512 | 2025-12-27 | 1.478
2025-12-27 16:43 | 72.3758 | FALSE | FALSE | -0.28685 | -0.39791 | -1.5868 | -2.1454 | 0 |  |  | none | FALSE | 0 | 72.089 | FALSE | FALSE | 0.0925 |  | 73.0258 | 0 | 0 | -0.08478 | 0.20706 | 0.40945 | 0.46841 | Normal | 73.9626 | -1.3876 | Day | 202512 | 2025-12-27 | 1.3876
2025-12-27 16:58 | 72.3758 | FALSE | FALSE | -0.27513 | -0.38159 | -1.4055 | -1.905 | 0 |  |  | none | FALSE | 0 | 72.1007 | FALSE | FALSE | 0.0897 |  | 72.941 | 0 | 0 | -0.08478 | 0.20706 | 0.40945 | 0.42017 | Normal | 73.7813 | -1.3452 | Day | 202512 | 2025-12-27 | 1.3452
2025-12-27 17:13 | 72.941 | TRUE | FALSE | -0.78217 | -1.084 | -0.69739 | -0.94704 | 0.5652 |  |  | none | FALSE | 1 | 72.1588 | FALSE | FALSE | 0.0362 |  | 72.8986 | 0 | 0.5652 | -0.04239 | 0.2473 | 2.4569 | 0.36989 | Normal | 73.6384 | 0.1146 | Day | 202512 | 2025-12-27 | 0.1146
2025-12-27 17:27 | 72.941 | FALSE | FALSE | -0.75371 | -1.0441 | -0.61241 | -0.8326 | 0 |  |  | none | FALSE | 1 | 72.1873 | FALSE | FALSE | 0.0424 |  | 72.8704 | 0 | 0 | -0.02826 | 0.24084 | 0.11734 | 0.34153 | Normal | 73.5534 | 0.20686 | Day | 202512 | 2025-12-27 | 0.20686
2025-12-27 17:30 | 72.941 | FALSE | FALSE | -0.71465 | -0.98946 | -0.51683 | -0.70358 | 0 |  |  | none | FALSE | 1 | 72.2263 | FALSE | FALSE | 0.05 |  | 72.8421 | 0 | 0 | -0.02826 | 0.24084 | 0.11734 | 0.30787 | Normal | 73.4578 | 0.32127 | Day | 202512 | 2025-12-27 | 0.32127
2025-12-27 17:31 | 72.941 | FALSE | FALSE | -0.66101 | -0.91451 | -0.40667 | -0.55444 | 0 |  |  | none | FALSE | 1 | 72.28 | FALSE | FALSE | 0.0603 |  | 72.8138 | 0 | 0 | -0.02826 | 0.24084 | 0.11734 | 0.26692 | Normal | 73.3477 | 0.47644 | Day | 202512 | 2025-12-27 | 0.47644
2025-12-27 17:46 | 73.5062 | TRUE | FALSE | -1.2696 | -1.7576 | 0.086873 | 0.11832 | 0.5652 | 2025-12-27 19:59 | 2025-12-27 17:46 | upper | TRUE | 2 | 72.2366 | TRUE | FALSE | 0.2672 | 2.2938 | 72.828 | 1 | 0.5652 | 0.01413 | 0.26692 | 2.0646 | 0.29568 | Extreme triggered | 73.4193 | 2.2938 | Night | 202512 | 2025-12-27 | 2.2938
2025-12-27 18:01 | 73.7888 | FALSE | FALSE | -1.6491 | -2.286 | 0.18782 | 0.25519 | 0.2826 |  | 2025-12-27 17:46 | upper | TRUE | 2 | 72.1397 | FALSE | FALSE | 0.339 | 2.404 | 72.8704 | 2 | 0.2826 | 0.04239 | 0.26375 | 0.91074 | 0.36531 | Extreme/elevated | 73.601 | 2.5141 | Night | 202512 | 2025-12-27 | 2.5141
2025-12-27 18:16 | 73.7888 | FALSE | FALSE | -1.7159 | -2.3808 | 0.064493 | 0.087478 | 0 |  | 2025-12-27 17:46 | upper | TRUE | 2 | 72.0729 | FALSE | TRUE | 0.3723 | 2.3214 | 72.8986 | 3 | 0 | 0.02826 | 0.25771 | -0.10966 | 0.41285 | Persistent | 73.7243 | 2.1562 | Night | 202512 | 2025-12-27 | 2.1562
2025-12-27 18:30 | 73.7888 | FALSE | FALSE | -1.7647 | -2.4501 | -0.069075 | -0.093525 | 0 |  | 2025-12-27 17:46 | none | FALSE | 2 | 72.0241 | FALSE | FALSE | 0.409 | 2.2034 | 72.941 | 4 | 0 | 0.04239 | 0.2473 | -0.17141 | 0.45844 | Persistent | 73.8579 | 1.8493 | Night | 202512 | 2025-12-27 | 1.8493
2025-12-27 18:45 | 73.7888 | FALSE | FALSE | -1.7976 | -2.497 | -0.18677 | -0.25247 | 0 |  | 2025-12-27 17:46 | none | FALSE | 2 | 71.9912 | FALSE | FALSE | 0.4511 | 2.0874 | 72.9834 | 5 | 0 | 0.04239 | 0.2473 | -0.17141 | 0.49609 | Persistent | 73.9756 | 1.6235 | Night | 202512 | 2025-12-27 | 1.6235
2025-12-27 19:00 | 73.7888 | FALSE | FALSE | -1.818 | -2.5261 | -0.29198 | -0.39414 | 0 |  | 2025-12-27 17:46 | none | FALSE | 2 | 71.9708 | FALSE | FALSE | 0.4964 | 1.9806 | 73.0258 | 6 | 0 | 0.04239 | 0.2473 | -0.17141 | 0.5275 | Persistent | 74.0808 | 1.4465 | Night | 202512 | 2025-12-27 | 1.4465
2025-12-27 19:15 | 73.7888 | FALSE | TRUE | -1.7991 | -2.4991 | -0.38608 | -0.5205 | 0 |  | 2025-12-27 17:46 | none | FALSE | 1 | 71.9897 | FALSE | FALSE | 0.5148 | 1.8824 | 73.0823 | 7 | 0 | 0.05652 | 0.23555 | -0.23995 | 0.54629 | Confirmed/Materialized Shift | 74.1749 | 1.2933 | Night | 202512 | 2025-12-27 | 1.2933
2025-12-27 19:29 | 73.7888 | FALSE | TRUE | -1.7986 | -2.4984 | -0.47037 | -0.63342 | 0 |  | 2025-12-27 17:46 | none | FALSE | 1 | 71.9902 | FALSE | FALSE | 0.5066 | 1.7934 | 73.1247 | 8 | 0 | 0.04239 | 0.22968 | -0.18456 | 0.56724 | Confirmed/Materialized Shift | 74.2592 | 1.1708 | Night | 202512 | 2025-12-27 | 1.1708
2025-12-27 19:44 | 73.7888 | FALSE | TRUE | -1.7902 | -2.4864 | -0.54671 | -0.73547 | 0 |  | 2025-12-27 17:46 | none | FALSE | 1 | 71.9986 | FALSE | FALSE | 0.4995 | 1.7124 | 73.1671 | 9 | 0 | 0.04239 | 0.22968 | -0.18456 | 0.58422 | Confirmed/Materialized Shift | 74.3355 | 1.0642 | Night | 202512 | 2025-12-27 | 1.0642
2025-12-27 19:59 | 73.7888 | FALSE | FALSE | -1.7394 | -2.4141 | -0.60897 | -0.81854 | 0 |  |  | none | FALSE | 1 | 72.0494 | FALSE | FALSE | 0.0928 |  | 73.2236 | 0 | 0 | 0.05652 | 0.21697 | -0.26049 | 0.58709 | Persistence ends | 74.3978 | 0.96272 | Night | 202512 | 2025-12-27 | 0.96272
2025-12-27 20:14 | 73.7888 | FALSE | FALSE | -1.7151 | -2.3796 | -0.66948 | -0.89914 | 0 |  |  | none | FALSE | 0 | 72.0737 | FALSE | FALSE | 0.0585 |  | 73.266 | 0 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.59615 | Normal | 74.4583 | 0.87698 | Night | 202512 | 2025-12-27 | 0.87698
2025-12-27 20:29 | 73.7888 | FALSE | FALSE | -1.6444 | -2.2793 | -0.71181 | -0.95545 | 0 |  |  | none | FALSE | 0 | 72.1444 | FALSE | FALSE | 0.0528 |  | 73.3225 | 0 | 0 | 0.05652 | 0.19665 | -0.28742 | 0.58905 | Normal | 74.5006 | 0.79159 | Night | 202512 | 2025-12-27 | 0.79159
2025-12-27 20:44 | 73.5062 | FALSE | FALSE | -1.2194 | -1.6868 | -0.96503 | -1.2958 | -0.2826 |  |  | none | FALSE | 0 | 72.2868 | FALSE | FALSE | 0.0155 |  | 73.379 | 0 | -0.2826 | 0.05652 | 0.19665 | -1.7245 | 0.5461 | Normal | 74.4712 | 0.23287 | Night | 202512 | 2025-12-27 | 0.23287
2025-12-27 20:59 | 73.5062 | FALSE | FALSE | -1.056 | -1.4576 | -0.91472 | -1.2291 | 0 |  |  | none | FALSE | 0 | 72.4502 | FALSE | FALSE | 0.0096 |  | 73.4356 | 0 | 0 | 0.05652 | 0.19665 | -0.28742 | 0.49269 | Normal | 74.4209 | 0.1434 | Night | 202512 | 2025-12-27 | 0.1434
2025-12-27 21:14 | 73.5062 | FALSE | FALSE | -0.86391 | -1.1893 | -0.83565 | -1.1241 | 0 |  |  | none | FALSE | 0 | 72.6423 | FALSE | FALSE | 0.0022 |  | 73.4921 | 0 | 0 | 0.05652 | 0.19665 | -0.28742 | 0.42489 | Normal | 74.3419 | 0.033256 | Night | 202512 | 2025-12-27 | 0.033256
2025-12-27 21:29 | 73.2236 | FALSE | FALSE | -0.37281 | -0.51175 | -0.99453 | -1.34 | -0.2826 |  |  | none | FALSE | 0 | 72.8508 | FALSE | FALSE | 0.0606 |  | 73.5345 | 0 | -0.2826 | 0.04239 | 0.21058 | -1.5433 | 0.34184 | Normal | 74.2181 | -0.90938 | Night | 202512 | 2025-12-27 | 0.90938
2025-12-27 21:44 | 73.5062 | FALSE | FALSE | -0.56803 | -0.77879 | -0.68107 | -0.91805 | 0.2826 |  |  | none | FALSE | 0 | 72.9382 | FALSE | FALSE | 0.0121 |  | 73.5627 | 0 | 0.2826 | 0.02826 | 0.18107 | 1.4047 | 0.31228 | Normal | 74.1873 | -0.18099 | Night | 202512 | 2025-12-27 | 0.18099
2025-12-27 21:59 | 73.2236 | FALSE | FALSE | -0.223 | -0.30547 | -0.9295 | -1.2535 | -0.2826 |  |  | none | FALSE | 0 | 73.0006 | FALSE | FALSE | 0.0817 |  | 73.5768 | 0 | -0.2826 | 0.01413 | 0.19396 | -1.5299 | 0.28812 | Normal | 74.1531 | -1.226 | Night | 202512 | 2025-12-27 | 1.226
2025-12-27 22:14 | 73.2236 | FALSE | FALSE | -0.15451 | -0.21146 | -0.88927 | -1.1999 | 0 |  |  | none | FALSE | 0 | 73.0691 | FALSE | FALSE | 0.0939 |  | 73.591 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.26095 | Normal | 74.1129 | -1.4079 | Night | 202512 | 2025-12-27 | 1.4079
2025-12-27 22:28 | 73.2236 | FALSE | FALSE | -0.077844 | -0.10642 | -0.84086 | -1.1353 | 0 |  |  | none | FALSE | 0 | 73.1458 | FALSE | FALSE | 0.1107 |  | 73.6051 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.22968 | Normal | 74.0645 | -1.6611 | Night | 202512 | 2025-12-27 | 1.6611
2025-12-27 22:43 | 73.2236 | FALSE | FALSE | -0.12124 | -0.16585 | -0.856 | -1.1555 | 0 |  |  | none | FALSE | 0 | 73.1024 | FALSE | FALSE | 0.1003 |  | 73.591 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.24431 | Normal | 74.0796 | -1.5038 | Night | 202512 | 2025-12-27 | 1.5038
2025-12-27 22:59 | 72.941 | FALSE | FALSE | 0.049123 | 0.067301 | -1.1661 | -1.5735 | -0.2826 | 2025-12-28 05:56 | 2025-12-27 22:59 | lower | TRUE | 0 | 72.9901 | FALSE | FALSE | 0.2022 | 2.1759 | 73.5486 | 1 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.27923 | Extreme triggered | 74.1071 | -2.1759 | Night | 202512 | 2025-12-27 | 2.1759
2025-12-27 23:14 | 73.2236 | FALSE | FALSE | -0.26773 | -0.36697 | -0.86119 | -1.1624 | 0.2826 |  | 2025-12-27 22:59 | none | FALSE | 0 | 72.9559 | FALSE | FALSE | 0.1844 | 1.6137 | 73.5203 | 2 | 0.2826 | -0.02826 | 0.15614 | 1.9909 | 0.28223 | Extreme/elevated | 74.0848 | -1.0514 | Night | 202512 | 2025-12-27 | 1.0514
2025-12-27 23:28 | 72.941 | FALSE | FALSE | -0.068476 | -0.093966 | -1.1424 | -1.542 | -0.2826 |  | 2025-12-27 22:59 | none | FALSE | 0 | 72.8725 | FALSE | FALSE | 0.2897 | 1.667 | 73.4779 | 3 | -0.2826 | -0.04239 | 0.16593 | -1.4477 | 0.30271 | Persistent | 74.0834 | -1.7738 | Night | 202512 | 2025-12-27 | 1.7738
2025-12-27 23:43 | 72.941 | FALSE | FALSE | -0.13736 | -0.18868 | -1.1265 | -1.5209 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 72.8036 | FALSE | FALSE | 0.3329 | 1.6416 | 73.4356 | 4 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.31596 | Persistent | 74.0675 | -1.5652 | Night | 202512 | 2025-12-27 | 1.5652
2025-12-27 23:58 | 72.941 | FALSE | FALSE | -0.19357 | -0.26609 | -1.0979 | -1.4829 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 72.7474 | FALSE | FALSE | 0.3791 | 1.5934 | 73.3932 | 5 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.32287 | Persistent | 74.0389 | -1.4005 | Night | 202512 | 2025-12-27 | 1.4005
2025-12-28 00:13 | 72.941 | FALSE | FALSE | -0.23791 | -0.32724 | -1.0575 | -1.429 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 72.7031 | FALSE | FALSE | 0.4272 | 1.5387 | 73.3508 | 6 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.32384 | Persistent | 73.9985 | -1.2653 | Night | 202512 | 2025-12-28 | 1.2653
2025-12-28 00:28 | 72.6584 | FALSE | TRUE | -0.047207 | -0.065013 | -1.3189 | -1.7829 | -0.2826 |  | 2025-12-27 22:59 | none | FALSE | 0 | 72.6112 | FALSE | FALSE | 0.5241 | 1.5848 | 73.2943 | 7 | -0.2826 | -0.05652 | 0.17396 | -1.2996 | 0.34153 | Confirmed/Materialized Shift | 73.9773 | -1.8618 | Night | 202512 | 2025-12-28 | 1.8618
2025-12-28 00:43 | 72.6584 | FALSE | TRUE | -0.11834 | -0.16314 | -1.277 | -1.7272 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 72.5401 | FALSE | FALSE | 0.5107 | 1.5943 | 73.2377 | 8 | 0 | -0.05652 | 0.17396 | 0.32489 | 0.34883 | Confirmed/Materialized Shift | 73.9354 | -1.6608 | Night | 202512 | 2025-12-28 | 1.6608
2025-12-28 00:58 | 72.6584 | FALSE | TRUE | -0.17002 | -0.23455 | -1.2156 | -1.6456 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 72.4884 | FALSE | FALSE | 0.5006 | 1.5849 | 73.1812 | 9 | 0 | -0.05652 | 0.17396 | 0.32489 | 0.34642 | Confirmed/Materialized Shift | 73.874 | -1.5092 | Night | 202512 | 2025-12-28 | 1.5092
2025-12-28 01:13 | 72.3758 | FALSE | TRUE | 0.015144 | 0.02092 | -1.4544 | -1.9699 | -0.2826 |  | 2025-12-27 22:59 | lower | TRUE | 0 | 72.3909 | FALSE | TRUE | 0.5361 | 1.6306 | 73.1106 | 10 | -0.2826 | -0.07065 | 0.18049 | -1.1743 | 0.35981 | Confirmed/Materialized Shift | 73.8302 | -2.0421 | Night | 202512 | 2025-12-28 | 2.0421
2025-12-28 01:27 | 72.3758 | FALSE | TRUE | -0.052579 | -0.072701 | -1.3808 | -1.8721 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 72.3232 | FALSE | FALSE | 0.5236 | 1.6508 | 73.0399 | 11 | 0 | -0.07065 | 0.18049 | 0.39144 | 0.35834 | Confirmed/Materialized Shift | 73.7566 | -1.8533 | Night | 202512 | 2025-12-28 | 1.8533
2025-12-28 01:43 | 72.3758 | FALSE | TRUE | -0.13219 | -0.18297 | -1.3474 | -1.8276 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 72.2436 | FALSE | FALSE | 0.5095 | 1.6502 | 72.9834 | 12 | 0 | -0.05652 | 0.17396 | 0.32489 | 0.36989 | Confirmed/Materialized Shift | 73.7232 | -1.6426 | Night | 202512 | 2025-12-28 | 1.6426
2025-12-28 01:58 | 72.3758 | FALSE | TRUE | -0.19324 | -0.26771 | -1.2954 | -1.7583 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 72.1826 | FALSE | FALSE | 0.4987 | 1.6371 | 72.9269 | 13 | 0 | -0.05652 | 0.17396 | 0.32489 | 0.37215 | Confirmed/Materialized Shift | 73.6712 | -1.4808 | Night | 202512 | 2025-12-28 | 1.4808
2025-12-28 02:13 | 72.3758 | FALSE | TRUE | -0.23608 | -0.32725 | -1.2252 | -1.6646 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 72.1397 | FALSE | FALSE | 0.4903 | 1.6169 | 72.8704 | 14 | 0 | -0.05652 | 0.17396 | 0.32489 | 0.36531 | Confirmed/Materialized Shift | 73.601 | -1.3538 | Night | 202512 | 2025-12-28 | 1.3538
2025-12-28 02:27 | 72.095 | FALSE | TRUE | -0.068927 | -0.095697 | -1.5068 | -2.0472 | -0.2808 |  | 2025-12-27 22:59 | none | FALSE | 0 | 72.0261 | FALSE | FALSE | 0.5217 | 1.6308 | 72.8139 | 15 | -0.2808 | -0.05643 | 0.17384 | -1.2907 | 0.39392 | Confirmed/Materialized Shift | 73.6018 | -1.825 | Night | 202512 | 2025-12-28 | 1.825
2025-12-28 02:42 | 72.095 | FALSE | TRUE | -0.13116 | -0.18226 | -1.4279 | -1.9421 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 71.9638 | FALSE | FALSE | 0.5109 | 1.6328 | 72.7434 | 16 | 0 | -0.07056 | 0.15534 | 0.45424 | 0.38976 | Confirmed/Materialized Shift | 73.5229 | -1.6635 | Night | 202512 | 2025-12-28 | 1.6635
2025-12-28 02:57 | 72.095 | FALSE | TRUE | -0.20443 | -0.28437 | -1.3883 | -1.8893 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 71.8906 | FALSE | FALSE | 0.4991 | 1.6242 | 72.6869 | 17 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.39818 | Confirmed/Materialized Shift | 73.4833 | -1.4866 | Night | 202512 | 2025-12-28 | 1.4866
2025-12-28 03:12 | 72.095 | FALSE | TRUE | -0.26069 | -0.3629 | -1.3317 | -1.8136 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 71.8343 | FALSE | FALSE | 0.4897 | 1.6087 | 72.6305 | 18 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.39809 | Confirmed/Materialized Shift | 73.4267 | -1.3452 | Night | 202512 | 2025-12-28 | 1.3452
2025-12-28 03:27 | 72.095 | FALSE | TRUE | -0.29992 | -0.41774 | -1.2581 | -1.7151 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 71.7951 | FALSE | FALSE | 0.482 | 1.5888 | 72.5741 | 19 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.38949 | Confirmed/Materialized Shift | 73.3531 | -1.23 | Night | 202512 | 2025-12-28 | 1.23
2025-12-28 03:42 | 72.095 | FALSE | TRUE | -0.32094 | -0.44715 | -1.1662 | -1.5919 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 71.7741 | FALSE | FALSE | 0.4758 | 1.5662 | 72.5176 | 20 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.37179 | Confirmed/Materialized Shift | 73.2612 | -1.1368 | Night | 202512 | 2025-12-28 | 1.1368
2025-12-28 03:57 | 71.8124 | FALSE | TRUE | -0.12996 | -0.1813 | -1.4276 | -1.9492 | -0.2826 |  | 2025-12-27 22:59 | none | FALSE | 0 | 71.6824 | FALSE | FALSE | 0.5111 | 1.5709 | 72.4612 | 21 | -0.2826 | -0.05643 | 0.1477 | -1.5313 | 0.38938 | Confirmed/Materialized Shift | 73.24 | -1.6662 | Night | 202512 | 2025-12-28 | 1.6662
2025-12-28 04:12 | 71.8124 | FALSE | TRUE | -0.16456 | -0.22968 | -1.3211 | -1.8064 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 71.6478 | FALSE | FALSE | 0.5038 | 1.5703 | 72.3906 | 22 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.37141 | Confirmed/Materialized Shift | 73.1335 | -1.5569 | Night | 202512 | 2025-12-28 | 1.5569
2025-12-28 04:27 | 71.8124 | FALSE | TRUE | -0.21642 | -0.30227 | -1.2601 | -1.7244 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 71.596 | FALSE | FALSE | 0.4942 | 1.5635 | 72.3342 | 23 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.36912 | Confirmed/Materialized Shift | 73.0725 | -1.4137 | Night | 202512 | 2025-12-28 | 1.4137
2025-12-28 04:42 | 71.8124 | FALSE | TRUE | -0.24973 | -0.34897 | -1.1805 | -1.6173 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 71.5627 | FALSE | FALSE | 0.4868 | 1.5526 | 72.2778 | 24 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.35756 | Confirmed/Materialized Shift | 72.9929 | -1.3016 | Night | 202512 | 2025-12-28 | 1.3016
2025-12-28 04:57 | 71.8124 | FALSE | TRUE | -0.2626 | -0.36701 | -1.0805 | -1.4823 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 71.5498 | FALSE | FALSE | 0.4812 | 1.5392 | 72.2214 | 25 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.33578 | Confirmed/Materialized Shift | 72.8929 | -1.2179 | Night | 202512 | 2025-12-28 | 1.2179
2025-12-28 05:12 | 71.8124 | FALSE | TRUE | -0.2506 | -0.35018 | -0.95566 | -1.3133 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 71.5618 | FALSE | FALSE | 0.4779 | 1.525 | 72.1649 | 26 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.30156 | Confirmed/Materialized Shift | 72.7681 | -1.169 | Night | 202512 | 2025-12-28 | 1.169
2025-12-28 05:26 | 71.8124 | FALSE | TRUE | -0.26521 | -0.37067 | -0.88567 | -1.2183 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 71.5472 | FALSE | FALSE | 0.4719 | 1.5084 | 72.1226 | 27 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.28772 | Confirmed/Materialized Shift | 72.6981 | -1.0782 | Night | 202512 | 2025-12-28 | 1.0782
2025-12-28 05:41 | 71.8124 | FALSE | TRUE | -0.26445 | -0.36961 | -0.80031 | -1.1022 | 0 |  | 2025-12-27 22:59 | none | FALSE | 0 | 71.548 | FALSE | FALSE | 0.4671 | 1.4905 | 72.0803 | 28 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.26619 | Confirmed/Materialized Shift | 72.6127 | -1.0065 | Night | 202512 | 2025-12-28 | 1.0065
2025-12-28 05:56 | 71.8124 | FALSE | FALSE | -0.24411 | -0.34108 | -0.69537 | -0.95902 | 0 |  |  | none | FALSE | 0 | 71.5683 | FALSE | FALSE | 0.064 |  | 72.038 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.23487 | Persistence ends | 72.5078 | -0.96067 | Night | 202512 | 2025-12-28 | 0.96067
2025-12-28 06:11 | 71.5298 | TRUE | FALSE | -0.027505 | -0.038467 | -0.95936 | -1.3235 | -0.2826 |  |  | none | FALSE | 1 | 71.5023 | FALSE | FALSE | 0.1545 |  | 71.9957 | 0 | -0.2826 | -0.0423 | 0.10331 | -2.326 | 0.24672 | Normal | 72.4892 | -1.8885 | Night | 202512 | 2025-12-28 | 1.8885
2025-12-28 06:26 | 71.5298 | FALSE | FALSE | -0.077605 | -0.10861 | -0.92486 | -1.2765 | 0 |  |  | none | FALSE | 1 | 71.4522 | FALSE | FALSE | 0.1413 |  | 71.9534 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.25062 | Normal | 72.4547 | -1.6903 | Night | 202512 | 2025-12-28 | 1.6903
2025-12-28 06:41 | 71.5298 | FALSE | FALSE | -0.11256 | -0.15761 | -0.87522 | -1.2088 | 0 |  |  | none | FALSE | 1 | 71.4172 | FALSE | FALSE | 0.1315 |  | 71.9111 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.24694 | Normal | 72.405 | -1.5442 | Night | 202512 | 2025-12-28 | 1.5442
2025-12-28 06:56 | 71.5298 | FALSE | FALSE | -0.13166 | -0.1844 | -0.80972 | -1.1193 | 0 |  |  | none | FALSE | 1 | 71.3981 | FALSE | FALSE | 0.1246 |  | 71.8688 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.23535 | Normal | 72.3395 | -1.4406 | Night | 202512 | 2025-12-28 | 1.4406
2025-12-28 07:11 | 71.5298 | FALSE | FALSE | -0.13234 | -0.18536 | -0.7258 | -1.0045 | 0 |  |  | none | FALSE | 1 | 71.3975 | FALSE | FALSE | 0.1208 |  | 71.8265 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.21454 | Normal | 72.2556 | -1.3831 | Day | 202512 | 2025-12-28 | 1.3831
2025-12-28 07:26 | 71.5298 | FALSE | FALSE | -0.1606 | -0.22503 | -0.69754 | -0.96576 | 0 |  |  | none | FALSE | 1 | 71.3692 | FALSE | FALSE | 0.112 |  | 71.7983 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21454 | Normal | 72.2273 | -1.2514 | Day | 202512 | 2025-12-28 | 1.2514
2025-12-28 07:41 | 71.5298 | FALSE | FALSE | -0.18095 | -0.25362 | -0.66137 | -0.91614 | 0 |  |  | none | FALSE | 1 | 71.3488 | FALSE | FALSE | 0.1046 |  | 71.77 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21058 | Normal | 72.1912 | -1.1407 | Day | 202512 | 2025-12-28 | 1.1407
2025-12-28 07:56 | 71.5298 | FALSE | FALSE | -0.19293 | -0.27045 | -0.61683 | -0.85497 | 0 |  |  | none | FALSE | 1 | 71.3369 | FALSE | FALSE | 0.0984 |  | 71.7417 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.20244 | Normal | 72.1466 | -1.047 | Day | 202512 | 2025-12-28 | 1.047
2025-12-28 08:11 | 71.5298 | FALSE | FALSE | -0.19546 | -0.274 | -0.56284 | -0.78071 | 0 |  |  | none | FALSE | 1 | 71.3343 | FALSE | FALSE | 0.0932 |  | 71.7135 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18957 | Normal | 72.0926 | -0.96896 | Day | 202512 | 2025-12-28 | 0.96896
2025-12-28 08:25 | 71.5298 | FALSE | FALSE | -0.18641 | -0.26128 | -0.49727 | -0.69039 | 0 |  |  | none | FALSE | 1 | 71.3434 | FALSE | FALSE | 0.0892 |  | 71.6852 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.17092 | Normal | 72.0271 | -0.90938 | Day | 202512 | 2025-12-28 | 0.90938
2025-12-28 08:30 | 71.5298 | FALSE | FALSE | -0.16132 | -0.22604 | -0.41566 | -0.57774 | 0 |  |  | none | FALSE | 0 | 71.3685 | FALSE | FALSE | 0.0588 |  | 71.657 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.14424 | Normal | 71.9455 | -0.88163 | Day | 202512 | 2025-12-28 | 0.88163
2025-12-28 08:45 | 71.8124 | TRUE | FALSE | -0.44392 | -0.62201 | -0.13306 | -0.18494 | 0.2826 |  |  | none | FALSE | 1 | 71.3685 | FALSE | FALSE | 0.1004 |  | 71.657 | 0 | 0.2826 | 0 | 0.091688 | 3.0822 | 0.14424 | Normal | 71.9455 | 1.0775 | Day | 202512 | 2025-12-28 | 1.0775
2025-12-28 09:00 | 72.095 | TRUE | FALSE | -0.76696 | -1.0753 | 0.080837 | 0.11225 | 0.2826 | 2025-12-28 12:59 | 2025-12-28 09:00 | upper | TRUE | 2 | 71.328 | TRUE | FALSE | 0.279 | 2.4713 | 71.6711 | 1 | 0.2826 | 0.01413 | 0.11135 | 2.411 | 0.17153 | Extreme triggered | 72.0142 | 2.4713 | Day | 202512 | 2025-12-28 | 2.4713
2025-12-28 09:16 | 72.3758 | TRUE | FALSE | -1.1399 | -1.6002 | 0.21318 | 0.29541 | 0.2808 |  | 2025-12-28 09:00 | upper | TRUE | 3 | 71.2359 | TRUE | FALSE | 0.3947 | 2.6957 | 71.6993 | 2 | 0.2808 | 0.02817 | 0.12619 | 2.0019 | 0.23168 | Extreme/elevated | 72.1626 | 2.9202 | Day | 202512 | 2025-12-28 | 2.9202
2025-12-28 09:30 | 72.3758 | FALSE | FALSE | -1.2006 | -1.6869 | 0.096077 | 0.13292 | 0 |  | 2025-12-28 09:00 | upper | TRUE | 3 | 71.1752 | FALSE | TRUE | 0.4137 | 2.5798 | 71.7274 | 3 | 0 | 0.02817 | 0.12619 | -0.22323 | 0.27614 | Persistent | 72.2797 | 2.3479 | Day | 202512 | 2025-12-28 | 2.3479
2025-12-28 09:30 | 72.3758 | FALSE | FALSE | -1.2436 | -1.7483 | -0.0032317 | -0.004465 | 0 |  | 2025-12-28 09:00 | none | FALSE | 3 | 71.1322 | FALSE | FALSE | 0.4469 | 2.4322 | 71.7556 | 4 | 0 | 0.02817 | 0.12619 | -0.22323 | 0.31171 | Persistent | 72.379 | 1.9896 | Day | 202512 | 2025-12-28 | 1.9896
2025-12-28 09:45 | 72.6584 | FALSE | FALSE | -1.6035 | -2.2567 | 0.1175 | 0.16198 | 0.2826 |  | 2025-12-28 09:00 | upper | TRUE | 3 | 71.0549 | FALSE | TRUE | 0.5258 | 2.4091 | 71.7979 | 5 | 0.2826 | 0.0423 | 0.13813 | 1.7397 | 0.37149 | Persistent | 72.5409 | 2.3163 | Day | 202512 | 2025-12-28 | 2.3163
2025-12-28 10:00 | 72.941 | FALSE | FALSE | -1.9887 | -2.8029 | 0.18463 | 0.25376 | 0.2826 |  | 2025-12-28 09:00 | upper | TRUE | 3 | 70.9523 | FALSE | TRUE | 0.5892 | 2.4091 | 71.8543 | 6 | 0.2826 | 0.05643 | 0.1477 | 1.5313 | 0.45102 | Persistent | 72.7564 | 2.4094 | Day | 202512 | 2025-12-28 | 2.4094
2025-12-28 10:15 | 72.6584 | FALSE | TRUE | -1.7323 | -2.4423 | -0.20874 | -0.28646 | -0.2826 |  | 2025-12-28 09:00 | none | FALSE | 3 | 70.9261 | FALSE | FALSE | 0.5904 | 2.2892 | 71.8966 | 7 | -0.2826 | 0.0423 | 0.16579 | -1.9597 | 0.48525 | Confirmed/Materialized Shift | 72.8671 | 1.5698 | Day | 202512 | 2025-12-28 | 1.5698
2025-12-28 10:30 | 72.6584 | FALSE | TRUE | -1.7466 | -2.463 | -0.30767 | -0.42166 | 0 |  | 2025-12-28 09:00 | none | FALSE | 3 | 70.9118 | FALSE | FALSE | 0.5791 | 2.1782 | 71.9389 | 8 | 0 | 0.0423 | 0.16579 | -0.25514 | 0.51357 | Confirmed/Materialized Shift | 72.9661 | 1.4009 | Day | 202512 | 2025-12-28 | 1.4009
2025-12-28 10:45 | 72.941 | FALSE | TRUE | -2.0316 | -2.865 | -0.16859 | -0.23059 | 0.2826 |  | 2025-12-28 09:00 | none | FALSE | 3 | 70.9094 | FALSE | FALSE | 0.5986 | 2.1243 | 72.0095 | 9 | 0.2826 | 0.07056 | 0.15534 | 1.365 | 0.55004 | Confirmed/Materialized Shift | 73.1096 | 1.6935 | Day | 202512 | 2025-12-28 | 1.6935
2025-12-28 11:00 | 72.941 | FALSE | TRUE | -2.0114 | -2.8357 | -0.28948 | -0.39529 | 0 |  | 2025-12-28 09:00 | none | FALSE | 2 | 70.9296 | FALSE | FALSE | 0.5569 | 2.0616 | 72.0801 | 10 | 0 | 0.07056 | 0.15534 | -0.45424 | 0.57521 | Confirmed/Materialized Shift | 73.2305 | 1.4967 | Day | 202512 | 2025-12-28 | 1.4967
2025-12-28 11:15 | 73.2236 | FALSE | TRUE | -2.2856 | -3.2219 | -0.16786 | -0.22872 | 0.2826 |  | 2025-12-28 09:00 | none | FALSE | 1 | 70.938 | FALSE | FALSE | 0.5437 | 2.0311 | 72.1647 | 11 | 0.2826 | 0.08469 | 0.16132 | 1.2268 | 0.61335 | Confirmed/Materialized Shift | 73.3915 | 1.7263 | Day | 202512 | 2025-12-28 | 1.7263
2025-12-28 11:29 | 73.5062 | FALSE | TRUE | -2.5684 | -3.6206 | -0.083137 | -0.11297 | 0.2826 |  | 2025-12-28 09:00 | none | FALSE | 0 | 70.9378 | FALSE | FALSE | 0.525 | 2.018 | 72.2636 | 12 | 0.2826 | 0.09882 | 0.16582 | 1.1083 | 0.66288 | Confirmed/Materialized Shift | 73.5893 | 1.8746 | Day | 202512 | 2025-12-28 | 1.8746
2025-12-28 11:44 | 73.5062 | FALSE | TRUE | -2.5324 | -3.5681 | -0.24481 | -0.33194 | 0 |  | 2025-12-28 09:00 | none | FALSE | 0 | 70.9738 | FALSE | FALSE | 0.5098 | 1.9895 | 72.3624 | 13 | 0 | 0.09882 | 0.16582 | -0.59594 | 0.69431 | Confirmed/Materialized Shift | 73.751 | 1.6474 | Day | 202512 | 2025-12-28 | 1.6474
2025-12-28 11:59 | 73.7888 | FALSE | TRUE | -2.7821 | -3.9181 | -0.1552 | -0.20989 | 0.2826 |  | 2025-12-28 09:00 | none | FALSE | 0 | 71.0067 | FALSE | FALSE | 0.5192 | 1.9752 | 72.4753 | 14 | 0.2826 | 0.11295 | 0.16897 | 1.004 | 0.73433 | Confirmed/Materialized Shift | 73.944 | 1.7887 | Day | 202512 | 2025-12-28 | 1.7887
2025-12-28 12:05 | 74.0714 | FALSE | TRUE | -3.0301 | -4.2652 | -0.092122 | -0.12422 | 0.2826 |  | 2025-12-28 09:00 | none | FALSE | 0 | 71.0413 | FALSE | FALSE | 0.5255 | 1.969 | 72.6024 | 15 | 0.2826 | 0.12708 | 0.17083 | 0.91037 | 0.78055 | Confirmed/Materialized Shift | 74.1635 | 1.882 | Day | 202512 | 2025-12-28 | 1.882
2025-12-28 12:08 | 73.7888 | TRUE | TRUE | -2.6347 | -3.7027 | -0.4878 | -0.65673 | -0.2826 |  | 2025-12-28 09:00 | none | FALSE | 1 | 71.1541 | FALSE | FALSE | 0.5202 | 1.9319 | 72.7154 | 16 | -0.2826 | 0.11295 | 0.19224 | -2.0576 | 0.78061 | Confirmed/Materialized Shift | 74.2766 | 1.3751 | Day | 202512 | 2025-12-28 | 1.3751
2025-12-28 12:23 | 73.7888 | FALSE | TRUE | -2.487 | -3.488 | -0.56608 | -0.76132 | 0 |  | 2025-12-28 09:00 | none | FALSE | 1 | 71.3018 | FALSE | FALSE | 0.5125 | 1.8922 | 72.8283 | 17 | 0 | 0.11295 | 0.19224 | -0.58754 | 0.76328 | Confirmed/Materialized Shift | 74.3549 | 1.2584 | Day | 202512 | 2025-12-28 | 1.2584
2025-12-28 12:29 | 73.7888 | FALSE | TRUE | -2.3021 | -3.2204 | -0.60708 | -0.81602 | 0 |  | 2025-12-28 09:00 | none | FALSE | 1 | 71.4867 | FALSE | FALSE | 0.5063 | 1.8519 | 72.9413 | 18 | 0 | 0.11295 | 0.19224 | -0.58754 | 0.72731 | Confirmed/Materialized Shift | 74.3959 | 1.1653 | Day | 202512 | 2025-12-28 | 1.1653
2025-12-28 12:44 | 73.7888 | FALSE | TRUE | -2.074 | -2.892 | -0.60482 | -0.81299 | 0 |  | 2025-12-28 09:00 | none | FALSE | 1 | 71.7148 | FALSE | FALSE | 0.5017 | 1.8121 | 73.0542 | 19 | 0 | 0.11295 | 0.19224 | -0.58754 | 0.6697 | Confirmed/Materialized Shift | 74.3936 | 1.0969 | Day | 202512 | 2025-12-28 | 1.0969
2025-12-28 12:59 | 73.5062 | FALSE | FALSE | -1.5847 | -2.2034 | -0.85014 | -1.1433 | -0.2826 |  |  | none | FALSE | 1 | 71.9215 | FALSE | FALSE | 0.0688 |  | 73.1389 | 0 | -0.2826 | 0.08469 | 0.20697 | -1.7746 | 0.60871 | Persistence ends | 74.3563 | 0.60339 | Day | 202512 | 2025-12-28 | 0.60339
2025-12-28 13:14 | 73.5062 | FALSE | FALSE | -1.4193 | -1.9689 | -0.82583 | -1.111 | 0 |  |  | none | FALSE | 1 | 72.0869 | FALSE | FALSE | 0.0638 |  | 73.2095 | 0 | 0 | 0.07056 | 0.20234 | -0.34872 | 0.56128 | Normal | 74.332 | 0.52866 | Day | 202512 | 2025-12-28 | 0.52866
2025-12-28 13:29 | 73.5062 | FALSE | FALSE | -1.298 | -1.7976 | -0.81758 | -1.1 | 0 |  |  | none | FALSE | 1 | 72.2082 | FALSE | FALSE | 0.0588 |  | 73.266 | 0 | 0 | 0.05652 | 0.19665 | -0.28742 | 0.52889 | Normal | 74.3238 | 0.45417 | Day | 202512 | 2025-12-28 | 0.45417
2025-12-28 13:44 | 73.2236 | FALSE | FALSE | -0.88728 | -1.2266 | -1.0568 | -1.4228 | -0.2826 |  |  | none | FALSE | 1 | 72.3363 | FALSE | FALSE | 0.0402 |  | 73.3084 | 0 | -0.2826 | 0.04239 | 0.21058 | -1.5433 | 0.48603 | Normal | 74.2804 | -0.17443 | Day | 202512 | 2025-12-28 | 0.17443
2025-12-28 13:59 | 73.2236 | FALSE | FALSE | -0.74217 | -1.0239 | -0.99651 | -1.3426 | 0 |  |  | none | FALSE | 1 | 72.4814 | FALSE | FALSE | 0.0481 |  | 73.3508 | 0 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.43467 | Normal | 74.2201 | -0.29257 | Day | 202512 | 2025-12-28 | 0.29257
2025-12-28 14:14 | 73.2236 | FALSE | FALSE | -0.65381 | -0.90094 | -0.96467 | -1.3003 | 0 |  |  | none | FALSE | 1 | 72.5698 | FALSE | FALSE | 0.0542 |  | 73.379 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.40462 | Normal | 74.1883 | -0.38414 | Day | 202512 | 2025-12-28 | 0.38414
2025-12-28 14:28 | 73.2236 | FALSE | FALSE | -0.61703 | -0.84983 | -0.95615 | -1.289 | 0 |  |  | none | FALSE | 0 | 72.6066 | FALSE | FALSE | 0.0287 |  | 73.3932 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.3933 | Normal | 74.1798 | -0.43113 | Day | 202512 | 2025-12-28 | 0.43113
2025-12-28 14:43 | 73.2236 | FALSE | FALSE | -0.51475 | -0.70796 | -0.91039 | -1.228 | 0 |  |  | none | FALSE | 0 | 72.7088 | FALSE | FALSE | 0.037 |  | 73.4214 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.35629 | Normal | 74.134 | -0.55523 | Day | 202512 | 2025-12-28 | 0.55523
2025-12-28 14:59 | 73.2236 | FALSE | FALSE | -0.39847 | -0.54716 | -0.85063 | -1.1484 | 0 |  |  | none | FALSE | 0 | 72.8251 | FALSE | FALSE | 0.0483 |  | 73.4497 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.31228 | Normal | 74.0742 | -0.72397 | Day | 202512 | 2025-12-28 | 0.72397
2025-12-28 15:14 | 73.2236 | FALSE | FALSE | -0.34759 | -0.47696 | -0.82801 | -1.1182 | 0 |  |  | none | FALSE | 0 | 72.876 | FALSE | FALSE | 0.0545 |  | 73.4638 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.2939 | Normal | 74.0516 | -0.81732 | Day | 202512 | 2025-12-28 | 0.81732
2025-12-28 15:28 | 73.2236 | FALSE | FALSE | -0.29272 | -0.40137 | -0.8014 | -1.0826 | 0 |  |  | none | FALSE | 0 | 72.9309 | FALSE | FALSE | 0.062 |  | 73.4779 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.27353 | Normal | 74.025 | -0.92984 | Day | 202512 | 2025-12-28 | 0.92984
2025-12-28 15:43 | 73.2236 | FALSE | FALSE | -0.29272 | -0.40137 | -0.8014 | -1.0826 | 0 |  |  | none | FALSE | 0 | 72.9309 | FALSE | FALSE | 0.062 |  | 73.4779 | 0 | 0 | 0 | 0.15881 | 0 | 0.27353 | Normal | 74.025 | -0.92984 | Day | 202512 | 2025-12-28 | 0.92984
2025-12-28 15:58 | 73.2236 | FALSE | FALSE | -0.31826 | -0.43653 | -0.79868 | -1.079 | 0 |  |  | none | FALSE | 0 | 72.9053 | FALSE | FALSE | 0.0573 |  | 73.4638 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.27923 | Normal | 74.0223 | -0.86025 | Day | 202512 | 2025-12-28 | 0.86025
2025-12-28 16:13 | 72.941 | FALSE | FALSE | -0.11017 | -0.15127 | -1.0993 | -1.4847 | -0.2826 |  |  | none | FALSE | 0 | 72.8308 | FALSE | FALSE | 0.109 |  | 73.4356 | 0 | -0.2826 | -0.02826 | 0.15614 | -1.6289 | 0.30236 | Normal | 74.0403 | -1.6356 | Day | 202512 | 2025-12-28 | 1.6356
2025-12-28 16:28 | 72.941 | FALSE | FALSE | -0.16699 | -0.22946 | -1.0713 | -1.4475 | 0 |  |  | none | FALSE | 0 | 72.774 | FALSE | FALSE | 0.0974 |  | 73.3932 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.30957 | Normal | 74.0123 | -1.4606 | Day | 202512 | 2025-12-28 | 1.4606
2025-12-28 16:43 | 72.6584 | FALSE | FALSE | 0.048368 | 0.066525 | -1.2799 | -1.731 | -0.2826 | 2025-12-28 17:46 | 2025-12-28 16:43 | lower | TRUE | 0 | 72.7068 | FALSE | FALSE | 0.2009 | 2.1571 | 73.3225 | 1 | -0.2826 | -0.07065 | 0.12555 | -1.6882 | 0.30787 | Extreme triggered | 73.9383 | -2.1571 | Day | 202512 | 2025-12-28 | 2.1571
2025-12-28 16:58 | 72.3758 | FALSE | FALSE | 0.16822 | 0.23189 | -1.5839 | -2.1416 | -0.2826 |  | 2025-12-28 16:43 | lower | TRUE | 0 | 72.544 | FALSE | FALSE | 0.2793 | 2.3162 | 73.2519 | 2 | -0.2826 | -0.07065 | 0.12555 | -1.6882 | 0.35392 | Extreme/elevated | 73.9597 | -2.4753 | Day | 202512 | 2025-12-28 | 2.4753
2025-12-28 17:13 | 72.3758 | FALSE | FALSE | 0.043244 | 0.059714 | -1.5676 | -2.12 | 0 |  | 2025-12-28 16:43 | lower | TRUE | 0 | 72.419 | FALSE | TRUE | 0.3123 | 2.2486 | 73.1812 | 3 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.38108 | Persistent | 73.9434 | -2.1135 | Day | 202512 | 2025-12-28 | 2.1135
2025-12-28 17:28 | 72.095 | FALSE | FALSE | 0.15219 | 0.21065 | -1.8509 | -2.503 | -0.2808 |  | 2025-12-28 16:43 | lower | TRUE | 0 | 72.2472 | FALSE | TRUE | 0.3858 | 2.2761 | 73.0965 | 4 | -0.2808 | -0.08469 | 0.13273 | -1.4775 | 0.42467 | Persistent | 73.9459 | -2.3584 | Day | 202512 | 2025-12-28 | 2.3584
2025-12-28 17:30 | 72.095 | FALSE | FALSE | 0.021598 | 0.029949 | -1.8121 | -2.4518 | 0 |  | 2025-12-28 16:43 | lower | TRUE | 0 | 72.1166 | FALSE | TRUE | 0.4223 | 2.2305 | 73.0118 | 5 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.44762 | Persistent | 73.9071 | -2.0483 | Day | 202512 | 2025-12-28 | 2.0483
2025-12-28 17:31 | 72.095 | FALSE | FALSE | -0.10556 | -0.14664 | -1.7981 | -2.4334 | 0 |  | 2025-12-28 16:43 | none | FALSE | 0 | 71.9894 | FALSE | FALSE | 0.4614 | 2.1551 | 72.9413 | 6 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.47592 | Persistent | 73.8931 | -1.7782 | Day | 202512 | 2025-12-28 | 1.7782
2025-12-28 17:46 | 73.2236 | TRUE | FALSE | -1.221 | -1.6957 | -0.62806 | -0.85044 | 1.1286 |  |  | none | FALSE | 1 | 72.0026 | FALSE | FALSE | 0.0713 |  | 72.9271 | 0 | 1.1286 | -0.01413 | 0.2963 | 3.8567 | 0.46226 | Persistence ends | 73.8517 | 0.64133 | Night | 202512 | 2025-12-28 | 0.64133
2025-12-28 18:01 | 73.5062 | FALSE | FALSE | -1.5036 | -2.0882 | -0.34546 | -0.46778 | 0.2826 |  |  | none | FALSE | 1 | 72.0026 | FALSE | FALSE | 0.1121 |  | 72.9271 | 0 | 0.2826 | 0 | 0.30365 | 0.93067 | 0.46226 | Normal | 73.8517 | 1.2527 | Night | 202512 | 2025-12-28 | 1.2527
2025-12-28 18:16 | 73.7888 | FALSE | FALSE | -1.828 | -2.5402 | -0.16118 | -0.21795 | 0.2826 |  |  | none | FALSE | 1 | 71.9608 | FALSE | FALSE | 0.1403 |  | 72.9554 | 0 | 0.2826 | 0.02826 | 0.30227 | 0.84144 | 0.49729 | Normal | 73.95 | 1.6759 | Night | 202512 | 2025-12-28 | 1.6759
2025-12-28 18:30 | 73.7888 | FALSE | FALSE | -1.862 | -2.5887 | -0.25169 | -0.33994 | 0 |  |  | none | FALSE | 1 | 71.9268 | FALSE | FALSE | 0.1302 |  | 72.9837 | 0 | 0 | 0.02826 | 0.30227 | -0.093494 | 0.52842 | Normal | 74.0405 | 1.5237 | Night | 202512 | 2025-12-28 | 1.5237
2025-12-28 18:45 | 73.7888 | FALSE | FALSE | -1.8895 | -2.628 | -0.33572 | -0.45292 | 0 |  |  | none | FALSE | 1 | 71.8993 | FALSE | FALSE | 0.1217 |  | 73.0119 | 0 | 0 | 0.02826 | 0.30227 | -0.093494 | 0.5563 | Normal | 74.1245 | 1.3965 | Night | 202512 | 2025-12-28 | 1.3965
2025-12-28 19:00 | 73.7888 | FALSE | FALSE | -1.9114 | -2.6593 | -0.4142 | -0.5582 | 0 |  |  | none | FALSE | 1 | 71.8774 | FALSE | FALSE | 0.1144 |  | 73.0402 | 0 | 0 | 0.02826 | 0.30227 | -0.093494 | 0.58141 | Normal | 74.203 | 1.2876 | Night | 202512 | 2025-12-28 | 1.2876
2025-12-28 19:15 | 73.7888 | FALSE | FALSE | -1.9285 | -2.6837 | -0.48782 | -0.65676 | 0 |  |  | none | FALSE | 1 | 71.8603 | FALSE | FALSE | 0.1081 |  | 73.0684 | 0 | 0 | 0.02826 | 0.30227 | -0.093494 | 0.60409 | Normal | 74.2766 | 1.1925 | Night | 202512 | 2025-12-28 | 1.1925
2025-12-28 19:29 | 73.7888 | FALSE | FALSE | -1.9413 | -2.702 | -0.5571 | -0.74934 | 0 |  |  | none | FALSE | 1 | 71.8475 | FALSE | FALSE | 0.1024 |  | 73.0967 | 0 | 0 | 0.02826 | 0.30227 | -0.093494 | 0.6246 | Normal | 74.3459 | 1.1081 | Night | 202512 | 2025-12-28 | 1.1081
2025-12-28 19:44 | 73.7888 | FALSE | FALSE | -1.9502 | -2.7146 | -0.62247 | -0.83653 | 0 |  |  | none | FALSE | 1 | 71.8386 | FALSE | FALSE | 0.0974 |  | 73.125 | 0 | 0 | 0.02826 | 0.30227 | -0.093494 | 0.64316 | Normal | 74.4113 | 1.0322 | Night | 202512 | 2025-12-28 | 1.0322
2025-12-28 19:59 | 73.7888 | FALSE | FALSE | -1.9554 | -2.7222 | -0.68425 | -0.91879 | 0 |  |  | none | FALSE | 1 | 71.8334 | FALSE | FALSE | 0.0928 |  | 73.1532 | 0 | 0 | 0.02826 | 0.30227 | -0.093494 | 0.65992 | Normal | 74.4731 | 0.96312 | Night | 202512 | 2025-12-28 | 0.96312
2025-12-28 20:14 | 73.7888 | FALSE | FALSE | -1.9574 | -2.7249 | -0.74272 | -0.99652 | 0 |  |  | none | FALSE | 0 | 71.8314 | FALSE | FALSE | 0.06 |  | 73.1815 | 0 | 0 | 0.02826 | 0.30227 | -0.093494 | 0.67502 | Normal | 74.5315 | 0.89971 | Night | 202512 | 2025-12-28 | 0.89971
2025-12-28 20:29 | 73.7888 | FALSE | FALSE | -1.9562 | -2.7233 | -0.79808 | -1.07 | 0 |  |  | none | FALSE | 0 | 71.8326 | FALSE | FALSE | 0.0561 |  | 73.2097 | 0 | 0 | 0.02826 | 0.30227 | -0.093494 | 0.68857 | Normal | 74.5869 | 0.84096 | Night | 202512 | 2025-12-28 | 0.84096
2025-12-28 20:44 | 73.7888 | FALSE | FALSE | -1.9311 | -2.6873 | -0.85772 | -1.149 | 0 |  |  | none | FALSE | 0 | 71.8577 | FALSE | FALSE | 0.0513 |  | 73.2521 | 0 | 0 | 0.04239 | 0.29345 | -0.14446 | 0.6972 | Normal | 74.6465 | 0.76975 | Night | 202512 | 2025-12-28 | 0.76975
2025-12-28 20:59 | 73.7888 | FALSE | FALSE | -1.9003 | -2.6435 | -0.91179 | -1.2206 | 0 |  |  | none | FALSE | 0 | 71.8885 | FALSE | FALSE | 0.0469 |  | 73.2945 | 0 | 0 | 0.04239 | 0.29345 | -0.14446 | 0.70303 | Normal | 74.7006 | 0.70307 | Night | 202512 | 2025-12-28 | 0.70307
2025-12-28 21:14 | 73.7888 | FALSE | FALSE | -1.8269 | -2.5388 | -0.95142 | -1.273 | 0 |  |  | none | FALSE | 0 | 71.9619 | FALSE | FALSE | 0.042 |  | 73.351 | 0 | 0 | 0.05652 | 0.28361 | -0.19929 | 0.69459 | Normal | 74.7402 | 0.63024 | Night | 202512 | 2025-12-28 | 0.63024
2025-12-28 21:29 | 73.7888 | FALSE | FALSE | -1.6896 | -2.3434 | -0.95536 | -1.2782 | 0 |  |  | none | FALSE | 0 | 72.0992 | FALSE | FALSE | 0.037 |  | 73.4217 | 0 | 0 | 0.07065 | 0.27266 | -0.25912 | 0.66123 | Normal | 74.7442 | 0.55519 | Night | 202512 | 2025-12-28 | 0.55519
2025-12-28 21:44 | 73.7888 | FALSE | FALSE | -1.5318 | -2.1199 | -0.93885 | -1.2564 | 0 |  |  | none | FALSE | 0 | 72.257 | FALSE | FALSE | 0.032 |  | 73.4923 | 0 | 0 | 0.07065 | 0.27266 | -0.25912 | 0.61765 | Normal | 74.7276 | 0.47998 | Night | 202512 | 2025-12-28 | 0.47998
2025-12-28 21:59 | 73.7888 | FALSE | FALSE | -1.2621 | -1.7402 | -0.83857 | -1.1237 | 0 |  |  | none | FALSE | 0 | 72.5267 | FALSE | FALSE | 0.0269 |  | 73.577 | 0 | 0 | 0.08469 | 0.26057 | -0.32502 | 0.52517 | Normal | 74.6274 | 0.40324 | Night | 202512 | 2025-12-28 | 0.40324
2025-12-28 22:14 | 73.5062 | FALSE | FALSE | -0.64659 | -0.88745 | -0.92937 | -1.2486 | -0.2826 |  |  | none | FALSE | 0 | 72.8596 | FALSE | FALSE | 0.0239 |  | 73.6476 | 0 | -0.2826 | 0.07056 | 0.27278 | -1.2947 | 0.39399 | Normal | 74.4356 | -0.35887 | Night | 202512 | 2025-12-28 | 0.35887
2025-12-28 22:28 | 73.5062 | FALSE | FALSE | -0.098978 | -0.13483 | -0.52288 | -0.70631 | 0 |  |  | none | FALSE | 0 | 73.4072 | FALSE | FALSE | 0.0909 |  | 73.7181 | 0 | 0 | 0.07056 | 0.27278 | -0.25867 | 0.15546 | Normal | 74.0291 | -1.3633 | Night | 202512 | 2025-12-28 | 1.3633
2025-12-28 22:43 | 73.5062 | FALSE | FALSE | -0.0058732 | -0.0079907 | -0.45803 | -0.61926 | 0 |  |  | none | FALSE | 0 | 73.5003 | FALSE | FALSE | 0.13 |  | 73.7323 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.11598 | Normal | 73.9642 | -1.9494 | Night | 202512 | 2025-12-28 | 1.9494
2025-12-28 22:59 | 73.5062 | FALSE | FALSE | -0.0058732 | -0.0079907 | -0.45803 | -0.61926 | 0 |  |  | none | FALSE | 0 | 73.5003 | FALSE | FALSE | 0.13 |  | 73.7323 | 0 | 0 | 0 | 0.091688 | 0 | 0.11598 | Normal | 73.9642 | -1.9494 | Night | 202512 | 2025-12-28 | 1.9494
2025-12-28 23:14 | 73.5062 | FALSE | FALSE | -0.039147 | -0.053285 | -0.46305 | -0.626 | 0 |  |  | none | FALSE | 0 | 73.4671 | FALSE | FALSE | 0.1125 |  | 73.7181 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.12555 | Normal | 73.9692 | -1.6882 | Night | 202512 | 2025-12-28 | 1.6882
2025-12-28 23:28 | 73.2236 | TRUE | FALSE | 0.13444 | 0.18326 | -0.79814 | -1.0783 | -0.2826 | 2025-12-29 06:26 | 2025-12-28 23:28 | lower | TRUE | 1 | 73.358 | FALSE | FALSE | 0.2731 | 2.8102 | 73.6899 | 1 | -0.2826 | -0.02826 | 0.086982 | -2.924 | 0.16593 | Extreme triggered | 74.0217 | -2.8102 | Night | 202512 | 2025-12-28 | 2.8102
2025-12-28 23:43 | 73.2236 | FALSE | FALSE | 0.050115 | 0.068394 | -0.82595 | -1.1154 | 0 |  | 2025-12-28 23:28 | lower | TRUE | 1 | 73.2737 | FALSE | FALSE | 0.2934 | 2.5343 | 73.6616 | 2 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.19396 | Extreme/elevated | 74.0495 | -2.2584 | Night | 202512 | 2025-12-28 | 2.2584
2025-12-28 23:58 | 73.2236 | FALSE | FALSE | -0.019304 | -0.02637 | -0.83884 | -1.1326 | 0 |  | 2025-12-28 23:28 | none | FALSE | 1 | 73.2043 | FALSE | FALSE | 0.3273 | 2.3262 | 73.6334 | 3 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21454 | Persistent | 74.0624 | -1.91 | Night | 202512 | 2025-12-28 | 1.91
2025-12-29 00:13 | 73.2236 | FALSE | FALSE | -0.077844 | -0.10642 | -0.84086 | -1.1353 | 0 |  | 2025-12-28 23:28 | none | FALSE | 1 | 73.1458 | FALSE | FALSE | 0.3679 | 2.1599 | 73.6051 | 4 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22968 | Persistent | 74.0645 | -1.6611 | Night | 202512 | 2025-12-29 | 1.6611
2025-12-29 00:28 | 73.2236 | FALSE | FALSE | -0.12756 | -0.17452 | -0.83406 | -1.1262 | 0 |  | 2025-12-28 23:28 | none | FALSE | 1 | 73.096 | FALSE | FALSE | 0.4122 | 2.0218 | 73.5768 | 5 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.24041 | Persistent | 74.0577 | -1.4694 | Night | 202512 | 2025-12-29 | 1.4694
2025-12-29 00:43 | 73.2236 | FALSE | FALSE | -0.16961 | -0.23218 | -0.81959 | -1.1069 | 0 |  | 2025-12-28 23:28 | none | FALSE | 1 | 73.054 | FALSE | FALSE | 0.459 | 1.9039 | 73.5486 | 6 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.2473 | Persistent | 74.0432 | -1.3141 | Night | 202512 | 2025-12-29 | 1.3141
2025-12-29 00:58 | 72.941 | TRUE | TRUE | 0.015075 | 0.020663 | -1.1153 | -1.506 | -0.2826 |  | 2025-12-28 23:28 | lower | TRUE | 2 | 72.9561 | TRUE | TRUE | 0.5941 | 1.9254 | 73.5062 | 7 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.27506 | Confirmed/Materialized Shift | 74.0563 | -2.0548 | Night | 202512 | 2025-12-29 | 2.0548
2025-12-29 01:13 | 72.941 | FALSE | TRUE | -0.064992 | -0.089182 | -1.1106 | -1.4998 | 0 |  | 2025-12-28 23:28 | none | FALSE | 2 | 72.876 | FALSE | FALSE | 0.5757 | 1.9071 | 73.4638 | 8 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.2939 | Confirmed/Materialized Shift | 74.0516 | -1.7789 | Night | 202512 | 2025-12-29 | 1.7789
2025-12-29 01:27 | 72.941 | FALSE | TRUE | -0.13052 | -0.17927 | -1.0914 | -1.4742 | 0 |  | 2025-12-28 23:28 | none | FALSE | 2 | 72.8105 | FALSE | FALSE | 0.562 | 1.87 | 73.4214 | 9 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.30547 | Confirmed/Materialized Shift | 74.0324 | -1.5727 | Night | 202512 | 2025-12-29 | 1.5727
2025-12-29 01:43 | 72.941 | FALSE | TRUE | -0.18315 | -0.25172 | -1.0592 | -1.4314 | 0 |  | 2025-12-28 23:28 | none | FALSE | 2 | 72.7579 | FALSE | FALSE | 0.5512 | 1.824 | 73.379 | 10 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.31059 | Confirmed/Materialized Shift | 74.0002 | -1.4103 | Night | 202512 | 2025-12-29 | 1.4103
2025-12-29 01:58 | 72.6584 | FALSE | TRUE | -0.0040148 | -0.0055259 | -1.3322 | -1.8005 | -0.2826 |  | 2025-12-28 23:28 | none | FALSE | 1 | 72.6544 | FALSE | FALSE | 0.5611 | 1.8389 | 73.3225 | 11 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.33406 | Confirmed/Materialized Shift | 73.9906 | -1.988 | Night | 202512 | 2025-12-29 | 1.988
2025-12-29 02:13 | 72.6584 | FALSE | TRUE | -0.085243 | -0.11746 | -1.3004 | -1.7583 | 0 |  | 2025-12-28 23:28 | none | FALSE | 1 | 72.5732 | FALSE | FALSE | 0.5455 | 1.8318 | 73.266 | 12 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.34642 | Confirmed/Materialized Shift | 73.9588 | -1.7539 | Night | 202512 | 2025-12-29 | 1.7539
2025-12-29 02:27 | 72.6584 | FALSE | TRUE | -0.1466 | -0.20217 | -1.2487 | -1.6896 | 0 |  | 2025-12-28 23:28 | none | FALSE | 1 | 72.5118 | FALSE | FALSE | 0.5339 | 1.8124 | 73.2095 | 13 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.34883 | Confirmed/Materialized Shift | 73.9071 | -1.5797 | Night | 202512 | 2025-12-29 | 1.5797
2025-12-29 02:42 | 72.6584 | FALSE | TRUE | -0.18851 | -0.26012 | -1.1776 | -1.5949 | 0 |  | 2025-12-28 23:28 | none | FALSE | 1 | 72.4699 | FALSE | FALSE | 0.5251 | 1.7864 | 73.153 | 14 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.34153 | Confirmed/Materialized Shift | 73.836 | -1.448 | Night | 202512 | 2025-12-29 | 1.448
2025-12-29 02:57 | 72.6584 | FALSE | TRUE | -0.20965 | -0.28938 | -1.0857 | -1.4723 | 0 |  | 2025-12-28 23:28 | none | FALSE | 1 | 72.4487 | FALSE | FALSE | 0.5187 | 1.7575 | 73.0964 | 15 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.32384 | Confirmed/Materialized Shift | 73.7441 | -1.3526 | Night | 202512 | 2025-12-29 | 1.3526
2025-12-29 03:12 | 72.3758 | FALSE | TRUE | -0.028723 | -0.039701 | -1.3569 | -1.8404 | -0.2826 |  | 2025-12-28 23:28 | none | FALSE | 1 | 72.3471 | FALSE | FALSE | 0.5564 | 1.7675 | 73.0399 | 16 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.34642 | Confirmed/Materialized Shift | 73.7327 | -1.9171 | Night | 202512 | 2025-12-29 | 1.9171
2025-12-29 03:27 | 72.3758 | FALSE | TRUE | -0.1091 | -0.15097 | -1.3243 | -1.7968 | 0 |  | 2025-12-28 23:28 | none | FALSE | 0 | 72.2667 | FALSE | FALSE | 0.513 | 1.7632 | 72.9834 | 17 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.35834 | Confirmed/Materialized Shift | 73.7001 | -1.6955 | Night | 202512 | 2025-12-29 | 1.6955
2025-12-29 03:42 | 72.3758 | FALSE | TRUE | -0.1703 | -0.23585 | -1.2724 | -1.7277 | 0 |  | 2025-12-28 23:28 | none | FALSE | 0 | 72.2055 | FALSE | FALSE | 0.5019 | 1.7502 | 72.9269 | 18 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.36068 | Confirmed/Materialized Shift | 73.6482 | -1.5279 | Night | 202512 | 2025-12-29 | 1.5279
2025-12-29 03:57 | 72.3758 | FALSE | TRUE | -0.21269 | -0.29474 | -1.2018 | -1.6334 | 0 |  | 2025-12-28 23:28 | none | FALSE | 0 | 72.1631 | FALSE | FALSE | 0.4932 | 1.7316 | 72.8704 | 19 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.35362 | Confirmed/Materialized Shift | 73.5776 | -1.3985 | Night | 202512 | 2025-12-29 | 1.3985
2025-12-29 04:12 | 72.3758 | FALSE | TRUE | -0.23511 | -0.3259 | -1.1112 | -1.5121 | 0 |  | 2025-12-28 23:28 | none | FALSE | 0 | 72.1407 | FALSE | FALSE | 0.4868 | 1.7101 | 72.8138 | 20 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.33657 | Confirmed/Materialized Shift | 73.487 | -1.3015 | Night | 202512 | 2025-12-29 | 1.3015
2025-12-29 04:27 | 72.3758 | FALSE | TRUE | -0.27562 | -0.38228 | -1.0669 | -1.4527 | 0 |  | 2025-12-28 23:28 | none | FALSE | 0 | 72.1002 | FALSE | FALSE | 0.4786 | 1.6848 | 72.7714 | 21 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.33563 | Confirmed/Materialized Shift | 73.4427 | -1.1788 | Night | 202512 | 2025-12-29 | 1.1788
2025-12-29 04:42 | 72.095 | FALSE | TRUE | -0.080329 | -0.11155 | -1.3203 | -1.7985 | -0.2808 |  | 2025-12-28 23:28 | none | FALSE | 0 | 72.0147 | FALSE | FALSE | 0.518 | 1.6887 | 72.715 | 22 | -0.2808 | -0.05643 | 0.11579 | -1.9377 | 0.35017 | Confirmed/Materialized Shift | 73.4153 | -1.7706 | Night | 202512 | 2025-12-29 | 1.7706
2025-12-29 04:57 | 72.095 | FALSE | TRUE | -0.14603 | -0.20296 | -1.2732 | -1.7353 | 0 |  | 2025-12-28 23:28 | none | FALSE | 0 | 71.949 | FALSE | FALSE | 0.5059 | 1.6844 | 72.6586 | 23 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.3548 | Confirmed/Materialized Shift | 73.3682 | -1.5884 | Night | 202512 | 2025-12-29 | 1.5884
2025-12-29 05:12 | 72.095 | FALSE | TRUE | -0.1927 | -0.268 | -1.207 | -1.6466 | 0 |  | 2025-12-28 23:28 | none | FALSE | 0 | 71.9023 | FALSE | FALSE | 0.4966 | 1.6746 | 72.6021 | 24 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.34993 | Confirmed/Materialized Shift | 73.302 | -1.4493 | Night | 202512 | 2025-12-29 | 1.4493
2025-12-29 05:26 | 72.095 | FALSE | TRUE | -0.21952 | -0.30542 | -1.121 | -1.531 | 0 |  | 2025-12-28 23:28 | none | FALSE | 0 | 71.8755 | FALSE | FALSE | 0.4897 | 1.6614 | 72.5457 | 25 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.33512 | Confirmed/Materialized Shift | 73.216 | -1.3449 | Night | 202512 | 2025-12-29 | 1.3449
2025-12-29 05:41 | 72.095 | FALSE | TRUE | -0.22365 | -0.31118 | -1.0122 | -1.3846 | 0 |  | 2025-12-28 23:28 | none | FALSE | 0 | 71.8714 | FALSE | FALSE | 0.4851 | 1.6466 | 72.4893 | 26 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.30897 | Confirmed/Materialized Shift | 73.1072 | -1.2762 | Night | 202512 | 2025-12-29 | 1.2762
2025-12-29 05:56 | 72.095 | FALSE | TRUE | -0.2514 | -0.34993 | -0.95538 | -1.3078 | 0 |  | 2025-12-28 23:28 | none | FALSE | 0 | 71.8436 | FALSE | FALSE | 0.4778 | 1.6288 | 72.447 | 27 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.3017 | Confirmed/Materialized Shift | 73.0504 | -1.1667 | Night | 202512 | 2025-12-29 | 1.1667
2025-12-29 06:11 | 71.8124 | FALSE | TRUE | -0.04158 | -0.057935 | -1.1979 | -1.6407 | -0.2826 |  | 2025-12-28 23:28 | none | FALSE | 0 | 71.7708 | FALSE | FALSE | 0.5244 | 1.6373 | 72.3906 | 28 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.30987 | Confirmed/Materialized Shift | 73.0103 | -1.8658 | Night | 202512 | 2025-12-29 | 1.8658
2025-12-29 06:26 | 72.095 | TRUE | FALSE | -0.3222 | -0.44891 | -0.82872 | -1.1364 | 0.2826 |  |  | none | FALSE | 1 | 71.7728 | FALSE | FALSE | 0.0873 |  | 72.3483 | 0 | 0.2826 | -0.0423 | 0.13813 | 2.3521 | 0.28773 | Persistence ends | 72.9237 | -0.88021 | Night | 202512 | 2025-12-29 | 0.88021
2025-12-29 06:41 | 72.095 | FALSE | FALSE | -0.30202 | -0.42069 | -0.72394 | -0.99417 | 0 |  |  | none | FALSE | 1 | 71.793 | FALSE | FALSE | 0.0834 |  | 72.306 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.25649 | Normal | 72.8189 | -0.82248 | Night | 202512 | 2025-12-29 | 0.82248
2025-12-29 06:56 | 71.8124 | FALSE | FALSE | -0.0786 | -0.10957 | -0.98112 | -1.3478 | -0.2826 |  |  | none | FALSE | 1 | 71.7338 | FALSE | FALSE | 0.1421 |  | 72.2637 | 0 | -0.2826 | -0.0423 | 0.13813 | -1.7397 | 0.26493 | Normal | 72.7935 | -1.7033 | Night | 202512 | 2025-12-29 | 1.7033
2025-12-29 07:11 | 71.8124 | FALSE | FALSE | -0.12328 | -0.17197 | -0.9412 | -1.2937 | 0 |  |  | none | FALSE | 1 | 71.6891 | FALSE | FALSE | 0.131 |  | 72.2214 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.26612 | Normal | 72.7536 | -1.5367 | Night | 202512 | 2025-12-29 | 1.5367
2025-12-29 07:26 | 71.8124 | FALSE | FALSE | -0.15368 | -0.21446 | -0.887 | -1.2201 | 0 |  |  | none | FALSE | 1 | 71.6587 | FALSE | FALSE | 0.1225 |  | 72.1791 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.26017 | Normal | 72.6994 | -1.4093 | Day | 202512 | 2025-12-29 | 1.4093
2025-12-29 07:30 | 71.8124 | FALSE | FALSE | -0.16874 | -0.23553 | -0.81746 | -1.1255 | 0 |  |  | none | FALSE | 1 | 71.6437 | FALSE | FALSE | 0.1163 |  | 72.1368 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.24655 | Normal | 72.6299 | -1.3156 | Day | 202512 | 2025-12-29 | 1.3156
2025-12-29 07:45 | 71.8124 | FALSE | FALSE | -0.16569 | -0.23125 | -0.72981 | -1.006 | 0 |  |  | none | FALSE | 1 | 71.6467 | FALSE | FALSE | 0.1126 |  | 72.0945 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.22387 | Normal | 72.5422 | -1.2599 | Day | 202512 | 2025-12-29 | 1.2599
2025-12-29 08:00 | 71.8124 | FALSE | FALSE | -0.19021 | -0.26557 | -0.69799 | -0.9626 | 0 |  |  | none | FALSE | 1 | 71.6222 | FALSE | FALSE | 0.1048 |  | 72.0663 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.22205 | Normal | 72.5104 | -1.1434 | Day | 202512 | 2025-12-29 | 1.1434
2025-12-29 08:16 | 71.8124 | FALSE | FALSE | -0.20704 | -0.28914 | -0.65848 | -0.90861 | 0 |  |  | none | FALSE | 1 | 71.6054 | FALSE | FALSE | 0.0981 |  | 72.0381 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.21638 | Normal | 72.4709 | -1.0432 | Day | 202512 | 2025-12-29 | 1.0432
2025-12-29 08:30 | 72.095 | TRUE | FALSE | -0.47481 | -0.66296 | -0.33297 | -0.45973 | 0.2826 |  |  | none | FALSE | 2 | 71.6202 | TRUE | FALSE | 0.0806 |  | 72.0241 | 0 | 0.2826 | -0.01404 | 0.14407 | 2.059 | 0.20195 | Normal | 72.428 | 0.35118 | Day | 202512 | 2025-12-29 | 0.35118
2025-12-29 08:30 | 71.8124 | FALSE | FALSE | -0.19488 | -0.27211 | -0.5619 | -0.77637 | -0.2826 |  |  | none | FALSE | 1 | 71.6175 | FALSE | FALSE | 0.0932 |  | 71.9959 | 0 | -0.2826 | -0.02817 | 0.15598 | -1.6311 | 0.18919 | Normal | 72.3743 | -0.96996 | Day | 202512 | 2025-12-29 | 0.96996
2025-12-29 08:45 | 72.095 | FALSE | FALSE | -0.45081 | -0.62924 | -0.22455 | -0.3105 | 0.2826 |  |  | none | FALSE | 1 | 71.6442 | FALSE | FALSE | 0.0732 |  | 71.9819 | 0 | 0.2826 | -0.01404 | 0.17077 | 1.7371 | 0.16884 | Normal | 72.3196 | 0.67003 | Day | 202512 | 2025-12-29 | 0.67003
2025-12-29 09:00 | 72.3758 | FALSE | FALSE | -0.73161 | -1.0212 | 0.056246 | 0.077774 | 0.2808 | 2025-12-29 11:59 | 2025-12-29 09:00 | upper | TRUE | 1 | 71.6442 | FALSE | FALSE | 0.2413 | 2.3331 | 71.9819 | 1 | 0.2808 | 0 | 0.18308 | 1.5337 | 0.16884 | Extreme triggered | 72.3196 | 2.3331 | Day | 202512 | 2025-12-29 | 2.3331
2025-12-29 09:15 | 72.3758 | FALSE | FALSE | -0.75828 | -1.0588 | 0.0015041 | 0.0020782 | 0 |  | 2025-12-29 09:00 | upper | TRUE | 1 | 71.6175 | FALSE | FALSE | 0.2767 | 2.1705 | 71.9959 | 2 | 0 | 0.01404 | 0.17077 | -0.082216 | 0.18919 | Extreme/elevated | 72.3743 | 2.0079 | Day | 202512 | 2025-12-29 | 2.0079
2025-12-29 09:30 | 72.6584 | FALSE | FALSE | -1.1141 | -1.5572 | 0.15456 | 0.21318 | 0.2826 |  | 2025-12-29 09:00 | upper | TRUE | 1 | 71.5443 | FALSE | TRUE | 0.3763 | 2.3285 | 72.0241 | 3 | 0.2826 | 0.02817 | 0.18094 | 1.4062 | 0.23988 | Persistent | 72.5038 | 2.6443 | Day | 202512 | 2025-12-29 | 2.6443
2025-12-29 09:45 | 72.941 | FALSE | FALSE | -1.5059 | -2.1081 | 0.24329 | 0.33467 | 0.2826 |  | 2025-12-29 09:00 | upper | TRUE | 1 | 71.4351 | FALSE | TRUE | 0.4419 | 2.439 | 72.0664 | 4 | 0.2826 | 0.0423 | 0.18945 | 1.2684 | 0.31566 | Persistent | 72.6977 | 2.7707 | Day | 202512 | 2025-12-29 | 2.7707
2025-12-29 10:00 | 72.941 | FALSE | FALSE | -1.5752 | -2.2073 | 0.089414 | 0.12273 | 0 |  | 2025-12-29 09:00 | upper | TRUE | 1 | 71.3658 | FALSE | TRUE | 0.4637 | 2.3994 | 72.1087 | 5 | 0 | 0.0423 | 0.18945 | -0.22327 | 0.37145 | Persistent | 72.8516 | 2.2407 | Day | 202512 | 2025-12-29 | 2.2407
2025-12-29 10:15 | 73.2236 | FALSE | FALSE | -1.953 | -2.7403 | 0.16398 | 0.22444 | 0.2826 |  | 2025-12-29 09:00 | upper | TRUE | 1 | 71.2706 | FALSE | TRUE | 0.5292 | 2.3939 | 72.1651 | 6 | 0.2826 | 0.05643 | 0.19654 | 1.1508 | 0.44726 | Persistent | 73.0596 | 2.3666 | Day | 202512 | 2025-12-29 | 2.3666
2025-12-29 10:29 | 73.2236 | FALSE | TRUE | -2.0128 | -2.8265 | -0.0086763 | -0.011848 | 0 |  | 2025-12-29 09:00 | none | FALSE | 1 | 71.2108 | FALSE | FALSE | 0.5608 | 2.3352 | 72.2215 | 7 | 0 | 0.05643 | 0.19654 | -0.28712 | 0.50537 | Confirmed/Materialized Shift | 73.2323 | 1.9828 | Day | 202512 | 2025-12-29 | 1.9828
2025-12-29 10:44 | 73.5062 | FALSE | TRUE | -2.3417 | -3.2906 | 0.058222 | 0.079269 | 0.2826 |  | 2025-12-29 09:00 | upper | TRUE | 0 | 71.1645 | FALSE | TRUE | 0.5401 | 2.306 | 72.3062 | 8 | 0.2826 | 0.08469 | 0.18555 | 1.0666 | 0.57087 | Confirmed/Materialized Shift | 73.448 | 2.102 | Day | 202512 | 2025-12-29 | 2.102
2025-12-29 10:59 | 73.5062 | FALSE | TRUE | -2.3849 | -3.3534 | -0.12613 | -0.17129 | 0 |  | 2025-12-29 09:00 | none | FALSE | 0 | 71.1213 | FALSE | FALSE | 0.5199 | 2.2497 | 72.3768 | 9 | 0 | 0.07056 | 0.18038 | -0.39118 | 0.62777 | Confirmed/Materialized Shift | 73.6323 | 1.7991 | Day | 202512 | 2025-12-29 | 1.7991
2025-12-29 11:14 | 73.7888 | FALSE | TRUE | -2.7235 | -3.8323 | -0.068818 | -0.093176 | 0.2826 |  | 2025-12-29 09:00 | none | FALSE | 0 | 71.0653 | FALSE | FALSE | 0.5268 | 2.2149 | 72.4615 | 10 | 0.2826 | 0.08469 | 0.18555 | 1.0666 | 0.69807 | Confirmed/Materialized Shift | 73.8576 | 1.9014 | Day | 202512 | 2025-12-29 | 1.9014
2025-12-29 11:26 | 74.0714 | FALSE | TRUE | -3.0307 | -4.2662 | -0.036796 | -0.049652 | 0.2826 |  | 2025-12-29 09:00 | none | FALSE | 0 | 71.0407 | FALSE | FALSE | 0.5301 | 2.191 | 72.5744 | 11 | 0.2826 | 0.11295 | 0.16897 | 1.004 | 0.76688 | Confirmed/Materialized Shift | 74.1082 | 1.952 | Day | 202512 | 2025-12-29 | 1.952
2025-12-29 11:29 | 74.0714 | FALSE | TRUE | -3.0114 | -4.2378 | -0.24332 | -0.32742 | 0 |  | 2025-12-29 09:00 | none | FALSE | 0 | 71.06 | FALSE | FALSE | 0.5134 | 2.1501 | 72.6874 | 12 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.81367 | Confirmed/Materialized Shift | 74.3147 | 1.701 | Day | 202512 | 2025-12-29 | 1.701
2025-12-29 11:29 | 74.0714 | FALSE | TRUE | -2.9553 | -4.1556 | -0.41316 | -0.55469 | 0 |  | 2025-12-29 09:00 | none | FALSE | 0 | 71.1161 | FALSE | FALSE | 0.5006 | 2.1009 | 72.8003 | 13 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.84211 | Confirmed/Materialized Shift | 74.4846 | 1.5094 | Day | 202512 | 2025-12-29 | 1.5094
2025-12-29 11:44 | 74.0714 | FALSE | TRUE | -2.8662 | -4.0253 | -0.54997 | -0.73701 | 0 |  | 2025-12-29 09:00 | none | FALSE | 0 | 71.2052 | FALSE | FALSE | 0.4904 | 2.0477 | 72.9133 | 14 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.85404 | Confirmed/Materialized Shift | 74.6214 | 1.356 | Day | 202512 | 2025-12-29 | 1.356
2025-12-29 11:59 | 73.7888 | TRUE | FALSE | -2.4448 | -3.4268 | -0.89143 | -1.1937 | -0.2826 |  |  | none | FALSE | 1 | 71.344 | FALSE | FALSE | 0.0907 |  | 73.0121 | 0 | -0.2826 | 0.09882 | 0.18948 | -2.013 | 0.83407 | Persistence ends | 74.6802 | 0.93122 | Day | 202512 | 2025-12-29 | 0.93122
2025-12-29 12:14 | 73.5062 | FALSE | FALSE | -1.9908 | -2.7838 | -1.172 | -1.5694 | -0.2826 |  |  | none | FALSE | 1 | 71.5154 | FALSE | FALSE | 0.0631 |  | 73.0968 | 0 | -0.2826 | 0.08469 | 0.20697 | -1.7746 | 0.79071 | Normal | 74.6782 | 0.51778 | Day | 202512 | 2025-12-29 | 0.51778
2025-12-29 12:29 | 73.5062 | FALSE | FALSE | -1.794 | -2.5016 | -1.1445 | -1.5332 | 0 |  |  | none | FALSE | 1 | 71.7122 | FALSE | FALSE | 0.058 |  | 73.1815 | 0 | 0 | 0.08469 | 0.20697 | -0.40919 | 0.73462 | Normal | 74.6507 | 0.44203 | Day | 202512 | 2025-12-29 | 0.44203
2025-12-29 12:44 | 73.5062 | FALSE | FALSE | -1.6367 | -2.2773 | -1.1284 | -1.5119 | 0 |  |  | none | FALSE | 1 | 71.8695 | FALSE | FALSE | 0.0531 |  | 73.252 | 0 | 0 | 0.07056 | 0.20234 | -0.34872 | 0.69126 | Normal | 74.6346 | 0.36768 | Day | 202512 | 2025-12-29 | 0.36768
2025-12-29 12:59 | 73.2236 | FALSE | FALSE | -1.1069 | -1.5349 | -1.3049 | -1.7509 | -0.2826 |  |  | none | FALSE | 1 | 72.1167 | FALSE | FALSE | 0.0395 |  | 73.3226 | 0 | -0.2826 | 0.07056 | 0.20234 | -1.7454 | 0.60296 | Normal | 74.5285 | -0.16419 | Day | 202512 | 2025-12-29 | 0.16419
2025-12-29 13:14 | 73.2236 | FALSE | FALSE | -0.90553 | -1.2522 | -1.2164 | -1.6341 | 0 |  |  | none | FALSE | 1 | 72.3181 | FALSE | FALSE | 0.0481 |  | 73.379 | 0 | 0 | 0.05643 | 0.19654 | -0.28712 | 0.53048 | Normal | 74.44 | -0.293 | Day | 202512 | 2025-12-29 | 0.293
2025-12-29 13:28 | 73.2236 | FALSE | FALSE | -0.75679 | -1.0443 | -1.1524 | -1.5495 | 0 |  |  | none | FALSE | 1 | 72.4668 | FALSE | FALSE | 0.0562 |  | 73.4214 | 0 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.4773 | Normal | 74.376 | -0.41445 | Day | 202512 | 2025-12-29 | 0.41445
2025-12-29 13:43 | 72.941 | FALSE | FALSE | -0.34357 | -0.47325 | -1.3609 | -1.8316 | -0.2826 |  |  | none | FALSE | 1 | 72.5974 | FALSE | FALSE | 0.1082 |  | 73.4497 | 0 | -0.2826 | 0.02826 | 0.20296 | -1.5316 | 0.42613 | Normal | 74.3019 | -1.1937 | Day | 202512 | 2025-12-29 | 1.1937
2025-12-29 13:58 | 73.2236 | FALSE | FALSE | -0.52149 | -0.7173 | -1.0302 | -1.3874 | 0.2826 |  |  | none | FALSE | 1 | 72.7021 | FALSE | FALSE | 0.0723 |  | 73.4779 | 0 | 0.2826 | 0.02826 | 0.20296 | 1.2532 | 0.38792 | Normal | 74.2538 | -0.65566 | Day | 202512 | 2025-12-29 | 0.65566
2025-12-29 14:14 | 73.2236 | FALSE | FALSE | -0.47584 | -0.65409 | -1.0128 | -1.3643 | 0 |  |  | none | FALSE | 1 | 72.7478 | FALSE | FALSE | 0.0767 |  | 73.4921 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.37215 | Normal | 74.2364 | -0.72139 | Day | 202512 | 2025-12-29 | 0.72139
2025-12-29 14:28 | 72.941 | FALSE | FALSE | -0.19324 | -0.26563 | -1.2954 | -1.7449 | -0.2826 |  |  | none | FALSE | 0 | 72.7478 | FALSE | FALSE | 0.0987 |  | 73.4921 | 0 | -0.2826 | 0 | 0.20502 | -1.3784 | 0.37215 | Normal | 74.2364 | -1.4808 | Day | 202512 | 2025-12-29 | 1.4808
2025-12-29 14:43 | 72.941 | FALSE | FALSE | -0.23889 | -0.32859 | -1.3128 | -1.768 | 0 |  |  | none | FALSE | 0 | 72.7021 | FALSE | FALSE | 0.0923 |  | 73.4779 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.38792 | Normal | 74.2538 | -1.3842 | Day | 202512 | 2025-12-29 | 1.3842
2025-12-29 14:58 | 72.941 | FALSE | FALSE | -0.28227 | -0.38848 | -1.3279 | -1.7879 | 0 |  |  | none | FALSE | 0 | 72.6587 | FALSE | FALSE | 0.0866 |  | 73.4638 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.40254 | Normal | 74.2689 | -1.2988 | Day | 202512 | 2025-12-29 | 1.2988
2025-12-29 15:13 | 73.2236 | FALSE | FALSE | -0.58576 | -0.80641 | -1.0379 | -1.3977 | 0.2826 |  |  | none | FALSE | 0 | 72.6378 | FALSE | FALSE | 0.0371 |  | 73.4497 | 0 | 0.2826 | -0.01413 | 0.19396 | 1.5299 | 0.40592 | Normal | 74.2615 | -0.55696 | Day | 202512 | 2025-12-29 | 0.55696
2025-12-29 15:28 | 72.941 | FALSE | FALSE | -0.36191 | -0.49864 | -1.3227 | -1.7811 | -0.2826 |  |  | none | FALSE | 0 | 72.5791 | FALSE | FALSE | 0.076 |  | 73.4214 | 0 | -0.2826 | -0.02826 | 0.20296 | -1.2532 | 0.42116 | Normal | 74.2637 | -1.1407 | Day | 202512 | 2025-12-29 | 1.1407
2025-12-29 15:43 | 72.941 | FALSE | FALSE | -0.41175 | -0.5677 | -1.2878 | -1.7349 | 0 |  |  | none | FALSE | 0 | 72.5292 | FALSE | FALSE | 0.0687 |  | 73.379 | 0 | 0 | -0.04239 | 0.18957 | 0.22361 | 0.42489 | Normal | 74.2288 | -1.0309 | Day | 202512 | 2025-12-29 | 1.0309
2025-12-29 15:58 | 72.941 | FALSE | FALSE | -0.42357 | -0.58409 | -1.1866 | -1.6007 | 0 |  |  | none | FALSE | 0 | 72.5174 | FALSE | FALSE | 0.0632 |  | 73.3225 | 0 | 0 | -0.05652 | 0.17396 | 0.32489 | 0.40254 | Normal | 74.1276 | -0.94776 | Day | 202512 | 2025-12-29 | 0.94776
2025-12-29 16:13 | 72.941 | FALSE | FALSE | -0.41479 | -0.57191 | -1.0648 | -1.4388 | 0 |  |  | none | FALSE | 0 | 72.5262 | FALSE | FALSE | 0.0586 |  | 73.266 | 0 | 0 | -0.05652 | 0.17396 | 0.32489 | 0.36989 | Normal | 74.0058 | -0.87862 | Day | 202512 | 2025-12-29 | 0.87862
2025-12-29 16:27 | 72.6584 | FALSE | FALSE | -0.14673 | -0.20236 | -1.2206 | -1.6522 | -0.2826 |  |  | none | FALSE | 0 | 72.5117 | FALSE | FALSE | 0.1047 |  | 73.1953 | 0 | -0.2826 | -0.07065 | 0.18049 | -1.1743 | 0.34184 | Normal | 73.879 | -1.5708 | Day | 202512 | 2025-12-29 | 1.5708
2025-12-29 16:43 | 72.6584 | FALSE | FALSE | -0.12151 | -0.16752 | -1.0541 | -1.43 | 0 |  |  | none | FALSE | 0 | 72.5369 | FALSE | FALSE | 0.1058 |  | 73.1247 | 0 | 0 | -0.07065 | 0.18049 | 0.39144 | 0.2939 | Normal | 73.7125 | -1.5866 | Day | 202512 | 2025-12-29 | 1.5866
2025-12-29 16:58 | 72.3758 | FALSE | FALSE | 0.086873 | 0.11989 | -1.2696 | -1.7239 | -0.2826 | 2025-12-29 17:42 | 2025-12-29 16:58 | lower | TRUE | 0 | 72.4627 | FALSE | FALSE | 0.2101 | 2.2938 | 73.054 | 1 | -0.2826 | -0.07065 | 0.18049 | -1.1743 | 0.29568 | Extreme triggered | 73.6454 | -2.2938 | Day | 202512 | 2025-12-29 | 2.2938
2025-12-29 17:13 | 72.095 | FALSE | FALSE | 0.19613 | 0.27131 | -1.5808 | -2.1457 | -0.2808 |  | 2025-12-29 16:58 | lower | TRUE | 0 | 72.2911 | FALSE | FALSE | 0.2854 | 2.4302 | 72.9835 | 2 | -0.2808 | -0.07056 | 0.18038 | -1.1656 | 0.34617 | Extreme/elevated | 73.6758 | -2.5666 | Day | 202512 | 2025-12-29 | 2.5666
2025-12-29 17:27 | 72.3758 | FALSE | FALSE | -0.14606 | -0.20221 | -1.2484 | -1.6956 | 0.2808 |  | 2025-12-29 16:58 | none | FALSE | 0 | 72.2297 | FALSE | FALSE | 0.2768 | 2.1471 | 72.927 | 3 | 0.2808 | -0.05652 | 0.19638 | 1.7177 | 0.34861 | Persistent | 73.6242 | -1.581 | Day | 202512 | 2025-12-29 | 1.581
2025-12-29 17:42 | 72.6584 | FALSE | FALSE | -0.42429 | -0.58738 | -0.87663 | -1.1921 | 0.2826 |  |  | none | FALSE | 0 | 72.2341 | FALSE | FALSE | 0.0464 |  | 72.8846 | 0 | 0.2826 | -0.04239 | 0.21033 | 1.5452 | 0.32523 | Persistence ends | 73.535 | -0.69542 | Night | 202512 | 2025-12-29 | 0.69542
2025-12-29 17:57 | 72.6584 | FALSE | FALSE | -0.43951 | -0.60858 | -0.83533 | -1.1366 | 0 |  |  | none | FALSE | 0 | 72.2189 | FALSE | FALSE | 0.0414 |  | 72.8563 | 0 | 0 | -0.02826 | 0.2027 | 0.13942 | 0.31871 | Normal | 73.4937 | -0.62097 | Night | 202512 | 2025-12-29 | 0.62097
2025-12-29 18:12 | 72.941 | FALSE | FALSE | -0.7141 | -0.98869 | -0.51646 | -0.70308 | 0.2826 |  |  | none | FALSE | 0 | 72.2269 | FALSE | FALSE | 0.0214 |  | 72.8422 | 0 | 0.2826 | -0.01413 | 0.21429 | 1.3847 | 0.30764 | Normal | 73.4575 | 0.32122 | Night | 202512 | 2025-12-29 | 0.32122
2025-12-29 18:27 | 72.941 | FALSE | FALSE | -0.70385 | -0.97436 | -0.47795 | -0.65099 | 0 |  |  | none | FALSE | 0 | 72.2372 | FALSE | FALSE | 0.0255 |  | 72.8281 | 0 | 0 | -0.01413 | 0.21429 | 0.065939 | 0.29545 | Normal | 73.4189 | 0.3823 | Night | 202512 | 2025-12-29 | 0.3823
2025-12-29 18:30 | 72.6584 | FALSE | FALSE | -0.43752 | -0.6058 | -0.74856 | -1.0197 | -0.2826 |  |  | none | FALSE | 0 | 72.2209 | FALSE | FALSE | 0.035 |  | 72.8139 | 0 | -0.2826 | -0.01413 | 0.21429 | -1.2528 | 0.29652 | Normal | 73.407 | -0.52449 | Night | 202512 | 2025-12-29 | 0.52449
2025-12-29 18:31 | 72.941 | FALSE | FALSE | -0.70594 | -0.97728 | -0.42352 | -0.57728 | 0.2826 |  |  | none | FALSE | 0 | 72.2351 | FALSE | FALSE | 0.0333 |  | 72.7998 | 0 | 0.2826 | -0.01413 | 0.21429 | 1.3847 | 0.28236 | Normal | 73.3645 | 0.5001 | Night | 202512 | 2025-12-29 | 0.5001
2025-12-29 18:46 | 73.2236 | FALSE | FALSE | -0.98854 | -1.3685 | -0.14092 | -0.19208 | 0.2826 |  |  | none | FALSE | 0 | 72.2351 | FALSE | FALSE | 0.1001 |  | 72.7998 | 0 | 0.2826 | 0 | 0.22435 | 1.2596 | 0.28236 | Normal | 73.3645 | 1.5009 | Night | 202512 | 2025-12-29 | 1.5009
2025-12-29 19:01 | 73.5062 | FALSE | FALSE | -1.3234 | -1.8335 | 0.03285 | 0.044711 | 0.2826 | 2025-12-29 20:59 | 2025-12-29 19:01 | upper | TRUE | 0 | 72.1828 | FALSE | FALSE | 0.1973 | 2.1018 | 72.8281 | 1 | 0.2826 | 0.02826 | 0.22247 | 1.1433 | 0.32265 | Extreme triggered | 73.4733 | 2.1018 | Night | 202512 | 2025-12-29 | 2.1018
2025-12-29 19:16 | 73.7888 | FALSE | FALSE | -1.6933 | -2.3486 | 0.14345 | 0.19479 | 0.2826 |  | 2025-12-29 19:01 | upper | TRUE | 0 | 72.0955 | FALSE | FALSE | 0.2723 | 2.236 | 72.8704 | 2 | 0.2826 | 0.04239 | 0.22944 | 1.0469 | 0.38745 | Extreme/elevated | 73.6453 | 2.3702 | Night | 202512 | 2025-12-29 | 2.3702
2025-12-29 19:30 | 73.5062 | FALSE | FALSE | -1.4328 | -1.988 | -0.21783 | -0.29546 | -0.2826 |  | 2025-12-29 19:01 | none | FALSE | 0 | 72.0734 | FALSE | FALSE | 0.2696 | 1.9814 | 72.8987 | 3 | -0.2826 | 0.02826 | 0.24062 | -1.2919 | 0.41266 | Persistent | 73.724 | 1.4721 | Night | 202512 | 2025-12-29 | 1.4721
2025-12-29 19:45 | 73.5062 | FALSE | FALSE | -1.4512 | -2.014 | -0.26442 | -0.35843 | 0 |  | 2025-12-29 19:01 | none | FALSE | 0 | 72.055 | FALSE | FALSE | 0.3208 | 1.8319 | 72.9128 | 4 | 0 | 0.01413 | 0.23308 | -0.060623 | 0.42889 | Persistent | 73.7706 | 1.3835 | Night | 202512 | 2025-12-29 | 1.3835
2025-12-29 20:00 | 73.5062 | FALSE | FALSE | -1.4631 | -2.0309 | -0.33288 | -0.45082 | 0 |  | 2025-12-29 19:01 | none | FALSE | 0 | 72.0431 | FALSE | FALSE | 0.3696 | 1.7173 | 72.9411 | 5 | 0 | 0.02826 | 0.22247 | -0.12703 | 0.449 | Persistent | 73.8391 | 1.2586 | Night | 202512 | 2025-12-29 | 1.2586
2025-12-29 20:15 | 73.5062 | FALSE | FALSE | -1.4697 | -2.0403 | -0.39603 | -0.53588 | 0 |  | 2025-12-29 19:01 | none | FALSE | 0 | 72.0365 | FALSE | FALSE | 0.4196 | 1.6229 | 72.9694 | 6 | 0 | 0.02826 | 0.22247 | -0.12703 | 0.46644 | Persistent | 73.9022 | 1.151 | Night | 202512 | 2025-12-29 | 1.151
2025-12-29 20:29 | 73.5062 | FALSE | TRUE | -1.4716 | -2.0429 | -0.45443 | -0.61442 | 0 |  | 2025-12-29 19:01 | none | FALSE | 0 | 72.0346 | FALSE | FALSE | 0.4704 | 1.5419 | 72.9976 | 7 | 0 | 0.02826 | 0.22247 | -0.12703 | 0.48151 | Confirmed/Materialized Shift | 73.9606 | 1.0562 | Night | 202512 | 2025-12-29 | 1.0562
2025-12-29 20:44 | 73.7888 | FALSE | TRUE | -1.774 | -2.4633 | -0.27636 | -0.37313 | 0.2826 |  | 2025-12-29 19:01 | none | FALSE | 0 | 72.0148 | FALSE | FALSE | 0.4974 | 1.5318 | 73.04 | 8 | 0.2826 | 0.04239 | 0.22944 | 1.0469 | 0.51258 | Confirmed/Materialized Shift | 74.0652 | 1.4608 | Night | 202512 | 2025-12-29 | 1.4608
2025-12-29 20:59 | 73.5062 | FALSE | FALSE | -1.4526 | -2.0161 | -0.60502 | -0.81636 | -0.2826 |  |  | none | FALSE | 0 | 72.0536 | FALSE | FALSE | 0.0549 |  | 73.0824 | 0 | -0.2826 | 0.04239 | 0.22944 | -1.4164 | 0.51441 | Persistence ends | 74.1112 | 0.82387 | Night | 202512 | 2025-12-29 | 0.82387
2025-12-29 21:14 | 73.5062 | FALSE | FALSE | -1.4065 | -1.9508 | -0.64371 | -0.86812 | 0 |  |  | none | FALSE | 0 | 72.0997 | FALSE | FALSE | 0.0496 |  | 73.1248 | 0 | 0 | 0.04239 | 0.22944 | -0.18475 | 0.51256 | Normal | 74.1499 | 0.74414 | Night | 202512 | 2025-12-29 | 0.74414
2025-12-29 21:29 | 73.5062 | FALSE | FALSE | -1.2996 | -1.7998 | -0.64976 | -0.87621 | 0 |  |  | none | FALSE | 0 | 72.2066 | FALSE | FALSE | 0.0444 |  | 73.1813 | 0 | 0 | 0.05652 | 0.21673 | -0.26079 | 0.48733 | Normal | 74.156 | 0.66669 | Night | 202512 | 2025-12-29 | 0.66669
2025-12-29 21:44 | 73.5062 | FALSE | FALSE | -1.0927 | -1.5089 | -0.58399 | -0.78821 | 0 |  |  | none | FALSE | 0 | 72.4135 | FALSE | FALSE | 0.0405 |  | 73.2519 | 0 | 0 | 0.07056 | 0.20234 | -0.34872 | 0.41916 | Normal | 74.0902 | 0.60678 | Night | 202512 | 2025-12-29 | 0.60678
2025-12-29 21:59 | 73.5062 | FALSE | FALSE | -0.93361 | -1.2864 | -0.53797 | -0.72655 | 0 |  |  | none | FALSE | 0 | 72.5726 | FALSE | FALSE | 0.0358 |  | 73.3084 | 0 | 0 | 0.05652 | 0.19665 | -0.28742 | 0.36789 | Normal | 74.0442 | 0.53771 | Night | 202512 | 2025-12-29 | 0.53771
2025-12-29 22:14 | 73.5062 | FALSE | FALSE | -0.82857 | -1.1401 | -0.51771 | -0.69938 | 0 |  |  | none | FALSE | 0 | 72.6776 | FALSE | FALSE | 0.0308 |  | 73.3508 | 0 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.33657 | Normal | 74.0239 | 0.46181 | Night | 202512 | 2025-12-29 | 0.46181
2025-12-29 22:29 | 73.5062 | FALSE | FALSE | -0.70441 | -0.96757 | -0.47833 | -0.64652 | 0 |  |  | none | FALSE | 0 | 72.8018 | FALSE | FALSE | 0.0255 |  | 73.3932 | 0 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.29568 | Normal | 73.9845 | 0.3823 | Night | 202512 | 2025-12-29 | 0.3823
2025-12-29 22:44 | 73.5062 | FALSE | FALSE | -0.63795 | -0.87549 | -0.46839 | -0.63318 | 0 |  |  | none | FALSE | 0 | 72.8682 | FALSE | FALSE | 0.0204 |  | 73.4214 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.27659 | Normal | 73.9746 | 0.30652 | Night | 202512 | 2025-12-29 | 0.30652
2025-12-29 22:59 | 73.2236 | FALSE | FALSE | -0.30265 | -0.41503 | -0.72655 | -0.98248 | -0.2826 |  |  | none | FALSE | 0 | 72.921 | FALSE | FALSE | 0.0549 |  | 73.4356 | 0 | -0.2826 | 0.01413 | 0.19396 | -1.5299 | 0.2573 | Normal | 73.9501 | -0.82375 | Night | 202512 | 2025-12-29 | 0.82375
2025-12-29 23:14 | 73.2236 | FALSE | FALSE | -0.13894 | -0.19011 | -0.61936 | -0.83875 | 0 |  |  | none | FALSE | 0 | 73.0847 | FALSE | FALSE | 0.0845 |  | 73.4638 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.18957 | Normal | 73.843 | -1.2671 | Night | 202512 | 2025-12-29 | 1.2671
2025-12-29 23:28 | 73.2236 | FALSE | FALSE | -0.057937 | -0.079185 | -0.56662 | -0.76787 | 0 |  |  | none | FALSE | 0 | 73.1657 | FALSE | FALSE | 0.1086 |  | 73.4779 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.15614 | Normal | 73.7902 | -1.6289 | Night | 202512 | 2025-12-29 | 1.6289
2025-12-29 23:43 | 73.2236 | FALSE | FALSE | -0.057937 | -0.079185 | -0.56662 | -0.76787 | 0 |  |  | none | FALSE | 0 | 73.1657 | FALSE | FALSE | 0.1086 |  | 73.4779 | 0 | 0 | 0 | 0.15881 | 0 | 0.15614 | Normal | 73.7902 | -1.6289 | Night | 202512 | 2025-12-29 | 1.6289
2025-12-29 23:59 | 73.2236 | FALSE | FALSE | -0.091643 | -0.12531 | -0.57206 | -0.7752 | 0 |  |  | none | FALSE | 0 | 73.132 | FALSE | FALSE | 0.0965 |  | 73.4638 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.16593 | Normal | 73.7957 | -1.4477 | Night | 202512 | 2025-12-29 | 1.4477
2025-12-30 00:14 | 73.2236 | FALSE | FALSE | -0.098978 | -0.13535 | -0.52288 | -0.70902 | 0 |  |  | none | FALSE | 0 | 73.1246 | FALSE | FALSE | 0.0909 |  | 73.4356 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.15546 | Normal | 73.7465 | -1.3633 | Night | 202512 | 2025-12-30 | 1.3633
2025-12-30 00:28 | 73.2236 | FALSE | FALSE | -0.12505 | -0.17106 | -0.52069 | -0.70607 | 0 |  |  | none | FALSE | 0 | 73.0986 | FALSE | FALSE | 0.0817 |  | 73.4214 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.16143 | Normal | 73.7443 | -1.2254 | Night | 202512 | 2025-12-30 | 1.2254
2025-12-30 00:43 | 73.2236 | FALSE | FALSE | -0.14816 | -0.20275 | -0.51554 | -0.69914 | 0 |  |  | none | FALSE | 0 | 73.0754 | FALSE | FALSE | 0.0738 |  | 73.4073 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.16593 | Normal | 73.7391 | -1.1071 | Night | 202512 | 2025-12-30 | 1.1071
2025-12-30 00:58 | 73.2236 | FALSE | FALSE | -0.16857 | -0.23074 | -0.50769 | -0.68856 | 0 |  |  | none | FALSE | 0 | 73.055 | FALSE | FALSE | 0.0669 |  | 73.3932 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.16906 | Normal | 73.7313 | -1.0029 | Night | 202512 | 2025-12-30 | 1.0029
2025-12-30 01:13 | 72.941 | TRUE | FALSE | 0.034903 | 0.047828 | -0.8129 | -1.1022 | -0.2826 | 2025-12-30 03:13 | 2025-12-30 01:13 | lower | TRUE | 1 | 72.9759 | FALSE | FALSE | 0.231 | 2.1794 | 73.3649 | 1 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.1945 | Extreme triggered | 73.7539 | -2.1794 | Night | 202512 | 2025-12-30 | 2.1794
2025-12-30 01:28 | 72.941 | FALSE | FALSE | -0.030485 | -0.041812 | -0.82177 | -1.1141 | 0 |  | 2025-12-30 01:13 | none | FALSE | 1 | 72.9105 | FALSE | FALSE | 0.2667 | 2.0182 | 73.3366 | 2 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21306 | Extreme/elevated | 73.7628 | -1.8569 | Night | 202512 | 2025-12-30 | 1.8569
2025-12-30 01:43 | 72.941 | FALSE | FALSE | -0.051631 | -0.070835 | -0.75813 | -1.0287 | 0 |  | 2025-12-30 01:13 | none | FALSE | 1 | 72.8894 | FALSE | FALSE | 0.3163 | 1.9271 | 73.2943 | 3 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.20244 | Persistent | 73.6991 | -1.745 | Night | 202512 | 2025-12-30 | 1.745
2025-12-30 01:58 | 72.941 | FALSE | FALSE | -0.096174 | -0.13203 | -0.74615 | -1.0126 | 0 |  | 2025-12-30 01:13 | none | FALSE | 1 | 72.8448 | FALSE | FALSE | 0.36 | 1.8312 | 73.266 | 4 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21058 | Persistent | 73.6872 | -1.5433 | Night | 202512 | 2025-12-30 | 1.5433
2025-12-30 02:13 | 72.941 | FALSE | FALSE | -0.13234 | -0.18177 | -0.7258 | -0.98525 | 0 |  | 2025-12-30 01:13 | none | FALSE | 1 | 72.8087 | FALSE | FALSE | 0.4065 | 1.7415 | 73.2377 | 5 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21454 | Persistent | 73.6668 | -1.3831 | Night | 202512 | 2025-12-30 | 1.3831
2025-12-30 02:28 | 72.941 | FALSE | FALSE | -0.1606 | -0.22067 | -0.69754 | -0.94725 | 0 |  | 2025-12-30 01:13 | none | FALSE | 1 | 72.7804 | FALSE | FALSE | 0.4549 | 1.6599 | 73.2095 | 6 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21454 | Persistent | 73.6385 | -1.2514 | Night | 202512 | 2025-12-30 | 1.2514
2025-12-30 02:43 | 72.941 | FALSE | TRUE | -0.18095 | -0.2487 | -0.66137 | -0.89858 | 0 |  | 2025-12-30 01:13 | none | FALSE | 1 | 72.76 | FALSE | FALSE | 0.5046 | 1.5857 | 73.1812 | 7 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21058 | Confirmed/Materialized Shift | 73.6024 | -1.1407 | Night | 202512 | 2025-12-30 | 1.1407
2025-12-30 02:58 | 72.941 | FALSE | TRUE | -0.19293 | -0.2652 | -0.61683 | -0.83857 | 0 |  | 2025-12-30 01:13 | none | FALSE | 1 | 72.7481 | FALSE | FALSE | 0.4984 | 1.5183 | 73.153 | 8 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.20244 | Confirmed/Materialized Shift | 73.5578 | -1.047 | Night | 202512 | 2025-12-30 | 1.047
2025-12-30 03:13 | 72.941 | FALSE | FALSE | -0.19546 | -0.26869 | -0.56284 | -0.76573 | 0 |  |  | none | FALSE | 1 | 72.7455 | FALSE | FALSE | 0.0932 |  | 73.1247 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18957 | Persistence ends | 73.5038 | -0.96896 | Night | 202512 | 2025-12-30 | 0.96896
2025-12-30 03:27 | 72.941 | FALSE | FALSE | -0.18641 | -0.25621 | -0.49727 | -0.67712 | 0 |  |  | none | FALSE | 1 | 72.7546 | FALSE | FALSE | 0.0892 |  | 73.0964 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.17092 | Normal | 73.4383 | -0.90938 | Night | 202512 | 2025-12-30 | 0.90938
2025-12-30 03:42 | 72.941 | FALSE | FALSE | -0.16132 | -0.22165 | -0.41566 | -0.56663 | 0 |  |  | none | FALSE | 0 | 72.7797 | FALSE | FALSE | 0.0588 |  | 73.0682 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.14424 | Normal | 73.3567 | -0.88163 | Night | 202512 | 2025-12-30 | 0.88163
2025-12-30 03:57 | 72.941 | FALSE | FALSE | -0.17104 | -0.23505 | -0.39712 | -0.5415 | 0 |  |  | none | FALSE | 0 | 72.77 | FALSE | FALSE | 0.0531 |  | 73.054 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14204 | Normal | 73.3381 | -0.79582 | Night | 202512 | 2025-12-30 | 0.79582
2025-12-30 04:12 | 72.6584 | TRUE | FALSE | 0.044515 | 0.061228 | -0.69025 | -0.94105 | -0.2826 | 2025-12-30 08:00 | 2025-12-30 04:12 | lower | TRUE | 1 | 72.7029 | FALSE | FALSE | 0.2374 | 2.2757 | 73.0258 | 1 | -0.2826 | -0.02826 | 0.086982 | -2.924 | 0.16143 | Extreme triggered | 73.3486 | -2.2757 | Night | 202512 | 2025-12-30 | 2.2757
2025-12-30 04:27 | 72.6584 | FALSE | FALSE | -0.0088098 | -0.012126 | -0.68705 | -0.93673 | 0 |  | 2025-12-30 04:12 | none | FALSE | 1 | 72.6496 | FALSE | FALSE | 0.2728 | 2.1126 | 72.9975 | 2 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.17396 | Extreme/elevated | 73.3454 | -1.9494 | Night | 202512 | 2025-12-30 | 1.9494
2025-12-30 04:42 | 72.6584 | FALSE | FALSE | -0.051277 | -0.070622 | -0.673 | -0.91775 | 0 |  | 2025-12-30 04:12 | none | FALSE | 1 | 72.6071 | FALSE | FALSE | 0.3145 | 1.9806 | 72.9693 | 3 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18107 | Persistent | 73.3314 | -1.7168 | Night | 202512 | 2025-12-30 | 1.7168
2025-12-30 04:57 | 72.6584 | FALSE | FALSE | -0.08415 | -0.11595 | -0.64935 | -0.88579 | 0 |  | 2025-12-30 04:12 | none | FALSE | 1 | 72.5742 | FALSE | FALSE | 0.3599 | 1.8708 | 72.941 | 4 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18338 | Persistent | 73.3078 | -1.5411 | Night | 202512 | 2025-12-30 | 1.5411
2025-12-30 05:12 | 72.6584 | FALSE | FALSE | -0.1078 | -0.14858 | -0.61648 | -0.84132 | 0 |  | 2025-12-30 04:12 | none | FALSE | 1 | 72.5506 | FALSE | FALSE | 0.4079 | 1.7775 | 72.9127 | 5 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18107 | Persistent | 73.2749 | -1.4047 | Night | 202512 | 2025-12-30 | 1.4047
2025-12-30 05:27 | 72.6584 | FALSE | FALSE | -0.12185 | -0.16798 | -0.57401 | -0.78382 | 0 |  | 2025-12-30 04:12 | none | FALSE | 1 | 72.5366 | FALSE | FALSE | 0.4581 | 1.6979 | 72.8845 | 6 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.17396 | Persistent | 73.2324 | -1.2996 | Night | 202512 | 2025-12-30 | 1.2996
2025-12-30 05:42 | 72.6584 | FALSE | TRUE | -0.12505 | -0.1724 | -0.52069 | -0.71152 | 0 |  | 2025-12-30 04:12 | none | FALSE | 1 | 72.5334 | FALSE | FALSE | 0.5103 | 1.6304 | 72.8562 | 7 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.16143 | Confirmed/Materialized Shift | 73.1791 | -1.2254 | Night | 202512 | 2025-12-30 | 1.2254
2025-12-30 05:57 | 72.3758 | TRUE | TRUE | 0.096194 | 0.13273 | -0.77987 | -1.066 | -0.2826 |  | 2025-12-30 04:12 | lower | TRUE | 2 | 72.472 | TRUE | TRUE | 0.628 | 1.7469 | 72.8138 | 8 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.17092 | Confirmed/Materialized Shift | 73.1557 | -2.5628 | Night | 202512 | 2025-12-30 | 2.5628
2025-12-30 06:12 | 72.3758 | FALSE | TRUE | 0.021855 | 0.030187 | -0.79769 | -1.0901 | 0 |  | 2025-12-30 04:12 | lower | TRUE | 2 | 72.3977 | FALSE | TRUE | 0.598 | 1.7876 | 72.7856 | 9 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.19396 | Confirmed/Materialized Shift | 73.1735 | -2.1127 | Night | 202512 | 2025-12-30 | 2.1127
2025-12-30 06:26 | 72.3758 | FALSE | TRUE | -0.039654 | -0.05482 | -0.80267 | -1.0969 | 0 |  | 2025-12-30 04:12 | none | FALSE | 2 | 72.3361 | FALSE | FALSE | 0.5779 | 1.79 | 72.7573 | 10 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21058 | Confirmed/Materialized Shift | 73.1785 | -1.8117 | Night | 202512 | 2025-12-30 | 1.8117
2025-12-30 06:41 | 72.3758 | FALSE | TRUE | -0.091222 | -0.1262 | -0.79772 | -1.0902 | 0 |  | 2025-12-30 04:12 | none | FALSE | 1 | 72.2846 | FALSE | FALSE | 0.5345 | 1.7718 | 72.7291 | 11 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22224 | Confirmed/Materialized Shift | 73.1735 | -1.5895 | Night | 202512 | 2025-12-30 | 1.5895
2025-12-30 06:56 | 72.3758 | FALSE | TRUE | -0.13436 | -0.18599 | -0.78434 | -1.0721 | 0 |  | 2025-12-30 04:12 | none | FALSE | 1 | 72.2414 | FALSE | FALSE | 0.5229 | 1.742 | 72.7008 | 12 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22968 | Confirmed/Materialized Shift | 73.1601 | -1.415 | Night | 202512 | 2025-12-30 | 1.415
2025-12-30 07:11 | 72.3758 | FALSE | TRUE | -0.16989 | -0.23528 | -0.76335 | -1.0437 | 0 |  | 2025-12-30 04:12 | none | FALSE | 1 | 72.2059 | FALSE | FALSE | 0.5134 | 1.7059 | 72.6725 | 13 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.23331 | Confirmed/Materialized Shift | 73.1391 | -1.2718 | Night | 202512 | 2025-12-30 | 1.2718
2025-12-30 07:26 | 72.3758 | FALSE | TRUE | -0.19815 | -0.27453 | -0.73509 | -1.0054 | 0 |  | 2025-12-30 04:12 | none | FALSE | 1 | 72.1777 | FALSE | FALSE | 0.5053 | 1.6662 | 72.6443 | 14 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.23331 | Confirmed/Materialized Shift | 73.1109 | -1.1507 | Day | 202512 | 2025-12-30 | 1.1507
2025-12-30 07:30 | 72.3758 | FALSE | TRUE | -0.21914 | -0.30371 | -0.69956 | -0.95732 | 0 |  | 2025-12-30 04:12 | none | FALSE | 1 | 72.1567 | FALSE | FALSE | 0.4983 | 1.6249 | 72.616 | 15 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22968 | Confirmed/Materialized Shift | 73.0754 | -1.0459 | Day | 202512 | 2025-12-30 | 1.0459
2025-12-30 07:45 | 72.095 | TRUE | TRUE | -0.009536 | -0.013229 | -0.96696 | -1.3235 | -0.2808 |  | 2025-12-30 04:12 | none | FALSE | 2 | 72.0855 | TRUE | FALSE | 0.5879 | 1.6459 | 72.5737 | 16 | -0.2808 | -0.0423 | 0.10331 | -2.3086 | 0.24412 | Confirmed/Materialized Shift | 73.062 | -1.9609 | Day | 202512 | 2025-12-30 | 1.9609
2025-12-30 08:00 | 72.3758 | TRUE | FALSE | -0.29389 | -0.40771 | -0.63319 | -0.86727 | 0.2808 |  |  | none | FALSE | 3 | 72.0819 | TRUE | FALSE | 0.1345 |  | 72.5455 | 0 | 0.2808 | -0.02826 | 0.12596 | 2.4536 | 0.23177 | Persistence ends | 73.009 | -0.73198 | Day | 202512 | 2025-12-30 | 0.73198
2025-12-30 08:16 | 72.095 | FALSE | FALSE | -0.057802 | -0.080239 | -0.8741 | -1.1979 | -0.2808 |  |  | none | FALSE | 2 | 72.0372 | FALSE | FALSE | 0.1739 |  | 72.5032 | 0 | -0.2808 | -0.0423 | 0.13774 | -1.7315 | 0.23298 | Normal | 72.9691 | -1.7519 | Day | 202512 | 2025-12-30 | 1.7519
2025-12-30 08:30 | 72.3758 | FALSE | FALSE | -0.32139 | -0.44604 | -0.51957 | -0.71276 | 0.2808 |  |  | none | FALSE | 2 | 72.0544 | FALSE | FALSE | 0.0886 |  | 72.4749 | 0 | 0.2808 | -0.02826 | 0.15545 | 1.9881 | 0.21024 | Normal | 72.8954 | -0.47132 | Day | 202512 | 2025-12-30 | 0.47132
2025-12-30 08:30 | 72.3758 | FALSE | FALSE | -0.2894 | -0.40147 | -0.43106 | -0.59206 | 0 |  |  | none | FALSE | 2 | 72.0864 | FALSE | FALSE | 0.0834 |  | 72.4466 | 0 | 0 | -0.02826 | 0.15545 | 0.18179 | 0.18012 | Normal | 72.8069 | -0.39324 | Day | 202512 | 2025-12-30 | 0.39324
2025-12-30 08:45 | 72.3758 | FALSE | FALSE | -0.29049 | -0.40298 | -0.40389 | -0.55495 | 0 |  |  | none | FALSE | 2 | 72.0853 | FALSE | FALSE | 0.0789 |  | 72.4325 | 0 | 0 | -0.01413 | 0.1435 | 0.098465 | 0.1736 | Normal | 72.7797 | -0.32662 | Day | 202512 | 2025-12-30 | 0.32662
2025-12-30 09:00 | 72.6584 | FALSE | FALSE | -0.57309 | -0.79502 | -0.12129 | -0.16666 | 0.2826 |  |  | none | FALSE | 2 | 72.0853 | FALSE | FALSE | 0.1439 |  | 72.4325 | 0 | 0.2826 | 0 | 0.15813 | 1.7871 | 0.1736 | Normal | 72.7797 | 1.3013 | Day | 202512 | 2025-12-30 | 1.3013
2025-12-30 09:15 | 72.941 | FALSE | FALSE | -0.89859 | -1.2473 | 0.090149 | 0.12374 | 0.2826 | 2025-12-30 10:29 | 2025-12-30 09:15 | upper | TRUE | 2 | 72.0424 | FALSE | FALSE | 0.2774 | 2.446 | 72.4466 | 1 | 0.2826 | 0.01413 | 0.17029 | 1.5765 | 0.20211 | Extreme triggered | 72.8509 | 2.446 | Day | 202512 | 2025-12-30 | 2.446
2025-12-30 09:30 | 73.2236 | FALSE | FALSE | -1.2757 | -1.773 | 0.22175 | 0.30377 | 0.2826 |  | 2025-12-30 09:15 | upper | TRUE | 2 | 71.9479 | FALSE | FALSE | 0.3609 | 2.6438 | 72.4749 | 2 | 0.2826 | 0.02826 | 0.18048 | 1.4093 | 0.26348 | Extreme/elevated | 73.0018 | 2.8416 | Day | 202512 | 2025-12-30 | 2.8416
2025-12-30 09:45 | 72.941 | FALSE | FALSE | -1.0137 | -1.4093 | -0.1097 | -0.15018 | -0.2826 |  | 2025-12-30 09:15 | none | FALSE | 2 | 71.9273 | FALSE | FALSE | 0.3359 | 2.299 | 72.489 | 3 | -0.2826 | 0.01413 | 0.19341 | -1.5342 | 0.28084 | Persistent | 73.0507 | 1.6094 | Day | 202512 | 2025-12-30 | 1.6094
2025-12-30 10:00 | 72.941 | FALSE | FALSE | -1.0308 | -1.4335 | -0.15512 | -0.21222 | 0 |  | 2025-12-30 09:15 | none | FALSE | 1 | 71.9102 | FALSE | FALSE | 0.3556 | 2.0935 | 72.5032 | 4 | 0 | 0.01413 | 0.19341 | -0.073059 | 0.29649 | Persistent | 73.0961 | 1.4768 | Day | 202512 | 2025-12-30 | 1.4768
2025-12-30 10:15 | 72.941 | FALSE | FALSE | -1.0451 | -1.4536 | -0.19762 | -0.2702 | 0 |  | 2025-12-30 09:15 | none | FALSE | 0 | 71.8959 | FALSE | FALSE | 0.3766 | 1.9475 | 72.5173 | 5 | 0 | 0.01413 | 0.19341 | -0.073059 | 0.31067 | Persistent | 73.1386 | 1.3639 | Day | 202512 | 2025-12-30 | 1.3639
2025-12-30 10:29 | 72.6584 | FALSE | FALSE | -0.74764 | -1.0397 | -0.49366 | -0.67483 | -0.2826 |  |  | none | FALSE | 0 | 71.9108 | FALSE | FALSE | 0.0273 |  | 72.5314 | 0 | -0.2826 | 0.01413 | 0.19341 | -1.5342 | 0.31032 | Persistence ends | 73.1521 | 0.40922 | Day | 202512 | 2025-12-30 | 0.40922
2025-12-30 10:44 | 72.6584 | FALSE | FALSE | -0.73145 | -1.0169 | -0.50573 | -0.69123 | 0 |  |  | none | FALSE | 0 | 71.9269 | FALSE | FALSE | 0.0243 |  | 72.5455 | 0 | 0 | 0.01413 | 0.19341 | -0.073059 | 0.3093 | Normal | 73.1641 | 0.36489 | Day | 202512 | 2025-12-30 | 0.36489
2025-12-30 10:59 | 72.941 | FALSE | FALSE | -1.0045 | -1.3964 | -0.2701 | -0.36893 | 0.2826 |  |  | none | FALSE | 0 | 71.9365 | FALSE | FALSE | 0.0768 |  | 72.5738 | 0 | 0.2826 | 0.02826 | 0.20243 | 1.2564 | 0.31865 | Normal | 73.2111 | 1.1524 | Day | 202512 | 2025-12-30 | 1.1524
2025-12-30 11:14 | 72.941 | FALSE | FALSE | -0.98927 | -1.3749 | -0.31139 | -0.42509 | 0 |  |  | none | FALSE | 0 | 71.9517 | FALSE | FALSE | 0.0695 |  | 72.6021 | 0 | 0 | 0.02826 | 0.20243 | -0.1396 | 0.32516 | Normal | 73.2524 | 1.0424 | Day | 202512 | 2025-12-30 | 1.0424
2025-12-30 11:29 | 72.941 | FALSE | FALSE | -0.96868 | -1.3459 | -0.34732 | -0.47391 | 0 |  |  | none | FALSE | 0 | 71.9723 | FALSE | FALSE | 0.063 |  | 72.6303 | 0 | 0 | 0.02826 | 0.20243 | -0.1396 | 0.329 | Normal | 73.2883 | 0.94431 | Day | 202512 | 2025-12-30 | 0.94431
2025-12-30 11:44 | 73.2236 | FALSE | FALSE | -1.2479 | -1.7338 | -0.14615 | -0.1992 | 0.2826 |  |  | none | FALSE | 0 | 71.9757 | FALSE | FALSE | 0.1054 |  | 72.6727 | 0 | 0.2826 | 0.04239 | 0.21007 | 1.1435 | 0.34852 | Normal | 73.3698 | 1.5807 | Day | 202512 | 2025-12-30 | 1.5807
2025-12-30 11:59 | 73.2236 | FALSE | FALSE | -1.2321 | -1.7115 | -0.21512 | -0.29293 | 0 |  |  | none | FALSE | 0 | 71.9915 | FALSE | FALSE | 0.0937 |  | 72.7151 | 0 | 0 | 0.04239 | 0.21007 | -0.20179 | 0.36181 | Normal | 73.4387 | 1.4054 | Day | 202512 | 2025-12-30 | 1.4054
2025-12-30 12:14 | 73.2236 | FALSE | FALSE | -1.2052 | -1.6735 | -0.27299 | -0.37143 | 0 |  |  | none | FALSE | 0 | 72.0184 | FALSE | FALSE | 0.0841 |  | 72.7575 | 0 | 0 | 0.04239 | 0.21007 | -0.20179 | 0.36955 | Normal | 73.4966 | 1.2613 | Day | 202512 | 2025-12-30 | 1.2613
2025-12-30 12:29 | 73.2236 | FALSE | FALSE | -1.107 | -1.535 | -0.2876 | -0.39123 | 0 |  |  | none | FALSE | 0 | 72.1166 | FALSE | FALSE | 0.0783 |  | 72.8139 | 0 | 0 | 0.05643 | 0.19627 | -0.28752 | 0.34864 | Normal | 73.5112 | 1.1751 | Day | 202512 | 2025-12-30 | 1.1751
2025-12-30 12:44 | 73.2236 | FALSE | FALSE | -1.0554 | -1.4625 | -0.32086 | -0.43628 | 0 |  |  | none | FALSE | 0 | 72.1682 | FALSE | FALSE | 0.0712 |  | 72.8563 | 0 | 0 | 0.04239 | 0.18929 | -0.22394 | 0.34408 | Normal | 73.5445 | 1.0675 | Day | 202512 | 2025-12-30 | 1.0675
2025-12-30 12:59 | 73.5062 | FALSE | FALSE | -1.227 | -1.6976 | -0.06835 | -0.092899 | 0.2826 |  |  | none | FALSE | 0 | 72.2792 | FALSE | FALSE | 0.1193 |  | 72.9269 | 0 | 0.2826 | 0.07056 | 0.18038 | 1.1755 | 0.32384 | Normal | 73.5746 | 1.7889 | Day | 202512 | 2025-12-30 | 1.7889
2025-12-30 13:14 | 73.5062 | FALSE | FALSE | -1.1653 | -1.6108 | -0.11966 | -0.16252 | 0 |  |  | none | FALSE | 0 | 72.3409 | FALSE | FALSE | 0.1085 |  | 72.9834 | 0 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.32123 | Normal | 73.6259 | 1.6275 | Day | 202512 | 2025-12-30 | 1.6275
2025-12-30 13:28 | 73.5062 | FALSE | FALSE | -1.082 | -1.494 | -0.14945 | -0.20291 | 0 |  |  | none | FALSE | 0 | 72.4242 | FALSE | FALSE | 0.101 |  | 73.0399 | 0 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.30787 | Normal | 73.6557 | 1.5146 | Day | 202512 | 2025-12-30 | 1.5146
2025-12-30 13:43 | 73.5062 | FALSE | FALSE | -0.97423 | -1.3432 | -0.15469 | -0.21 | 0 |  |  | none | FALSE | 0 | 72.532 | FALSE | FALSE | 0.0968 |  | 73.0964 | 0 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.28223 | Normal | 73.6609 | 1.4519 | Day | 202512 | 2025-12-30 | 1.4519
2025-12-30 13:59 | 73.2236 | FALSE | FALSE | -0.62641 | -0.86286 | -0.42859 | -0.58191 | -0.2826 |  |  | none | FALSE | 0 | 72.5972 | FALSE | FALSE | 0.025 |  | 73.1247 | 0 | -0.2826 | 0.02826 | 0.18107 | -1.7168 | 0.26375 | Normal | 73.6522 | 0.37501 | Day | 202512 | 2025-12-30 | 0.37501
2025-12-30 14:14 | 73.2236 | FALSE | FALSE | -0.60667 | -0.83545 | -0.43711 | -0.59342 | 0 |  |  | none | FALSE | 0 | 72.6169 | FALSE | FALSE | 0.0217 |  | 73.1388 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.26095 | Normal | 73.6607 | 0.32489 | Day | 202512 | 2025-12-30 | 0.32489
2025-12-30 14:28 | 73.2236 | FALSE | FALSE | -0.60667 | -0.83545 | -0.43711 | -0.59342 | 0 |  |  | none | FALSE | 0 | 72.6169 | FALSE | FALSE | 0.0217 |  | 73.1388 | 0 | 0 | 0 | 0.15881 | 0 | 0.26095 | Normal | 73.6607 | 0.32489 | Day | 202512 | 2025-12-30 | 0.32489
2025-12-30 14:43 | 73.2236 | FALSE | FALSE | -0.58525 | -0.8057 | -0.44395 | -0.60263 | 0 |  |  | none | FALSE | 0 | 72.6384 | FALSE | FALSE | 0.0183 |  | 73.153 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.2573 | Normal | 73.6675 | 0.27458 | Day | 202512 | 2025-12-30 | 0.27458
2025-12-30 14:58 | 73.2236 | FALSE | FALSE | -0.56205 | -0.77352 | -0.44901 | -0.60947 | 0 |  |  | none | FALSE | 0 | 72.6615 | FALSE | FALSE | 0.0149 |  | 73.1671 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.25277 | Normal | 73.6726 | 0.22361 | Day | 202512 | 2025-12-30 | 0.22361
2025-12-30 15:13 | 73.2236 | FALSE | FALSE | -0.53699 | -0.73878 | -0.45221 | -0.61379 | 0 |  |  | none | FALSE | 0 | 72.6866 | FALSE | FALSE | 0.0114 |  | 73.1812 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.2473 | Normal | 73.6758 | 0.17141 | Day | 202512 | 2025-12-30 | 0.17141
2025-12-30 15:28 | 73.2236 | FALSE | FALSE | -0.4432 | -0.60896 | -0.41494 | -0.56349 | 0 |  |  | none | FALSE | 0 | 72.7804 | FALSE | FALSE | 0.0044 |  | 73.2095 | 0 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.21454 | Normal | 73.6385 | 0.065863 | Day | 202512 | 2025-12-30 | 0.065863
2025-12-30 15:43 | 72.941 | TRUE | FALSE | -0.08415 | -0.1155 | -0.64935 | -0.88238 | -0.2826 |  |  | none | FALSE | 1 | 72.8568 | FALSE | FALSE | 0.1313 |  | 73.2236 | 0 | -0.2826 | 0.01413 | 0.14424 | -2.0571 | 0.18338 | Normal | 73.5904 | -1.5411 | Day | 202512 | 2025-12-30 | 1.5411
2025-12-30 15:58 | 72.941 | FALSE | FALSE | -0.08415 | -0.1155 | -0.64935 | -0.88238 | 0 |  |  | none | FALSE | 1 | 72.8568 | FALSE | FALSE | 0.1313 |  | 73.2236 | 0 | 0 | 0 | 0.12967 | 0 | 0.18338 | Normal | 73.5904 | -1.5411 | Day | 202512 | 2025-12-30 | 1.5411
2025-12-30 16:13 | 72.941 | FALSE | FALSE | -0.08415 | -0.1155 | -0.64935 | -0.88238 | 0 |  |  | none | FALSE | 1 | 72.8568 | FALSE | FALSE | 0.1313 |  | 73.2236 | 0 | 0 | 0 | 0.12967 | 0 | 0.18338 | Normal | 73.5904 | -1.5411 | Day | 202512 | 2025-12-30 | 1.5411
2025-12-30 16:27 | 72.941 | FALSE | FALSE | -0.08415 | -0.1155 | -0.64935 | -0.88238 | 0 |  |  | none | FALSE | 1 | 72.8568 | FALSE | FALSE | 0.1313 |  | 73.2236 | 0 | 0 | 0 | 0.12967 | 0 | 0.18338 | Normal | 73.5904 | -1.5411 | Day | 202512 | 2025-12-30 | 1.5411
2025-12-30 16:43 | 72.6584 | TRUE | FALSE | 0.091523 | 0.12581 | -0.98236 | -1.334 | -0.2826 | 2025-12-30 17:13 | 2025-12-30 16:43 | lower | TRUE | 2 | 72.7499 | TRUE | FALSE | 0.275 | 2.411 | 73.1953 | 1 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.22271 | Extreme triggered | 73.6408 | -2.411 | Day | 202512 | 2025-12-30 | 2.411
2025-12-30 16:58 | 72.941 | TRUE | FALSE | -0.21914 | -0.30135 | -0.69956 | -0.94997 | 0.2826 |  | 2025-12-30 16:43 | none | FALSE | 3 | 72.7219 | TRUE | FALSE | 0.2697 | 1.7284 | 73.1812 | 2 | 0.2826 | -0.01413 | 0.14424 | 2.0571 | 0.22968 | Extreme/elevated | 73.6406 | -1.0459 | Day | 202512 | 2025-12-30 | 1.0459
2025-12-30 17:13 | 73.2236 | FALSE | FALSE | -0.50174 | -0.68995 | -0.41696 | -0.56621 | 0.2826 |  |  | none | FALSE | 3 | 72.7219 | FALSE | FALSE | 0.098 |  | 73.1812 | 0 | 0.2826 | 0 | 0.15881 | 1.7795 | 0.22968 | Persistence ends | 73.6406 | 0.18456 | Day | 202512 | 2025-12-30 | 0.18456
2025-12-30 17:27 | 73.2236 | FALSE | FALSE | -0.50174 | -0.68995 | -0.41696 | -0.56621 | 0 |  |  | none | FALSE | 3 | 72.7219 | FALSE | FALSE | 0.098 |  | 73.1812 | 0 | 0 | 0 | 0.15881 | 0 | 0.22968 | Normal | 73.6406 | 0.18456 | Day | 202512 | 2025-12-30 | 0.18456
2025-12-30 17:42 | 73.5062 | FALSE | FALSE | -0.79255 | -1.09 | -0.17083 | -0.23186 | 0.2826 |  |  | none | FALSE | 3 | 72.7137 | FALSE | FALSE | 0.1718 |  | 73.1953 | 0 | 0.2826 | 0.01413 | 0.17092 | 1.5708 | 0.24084 | Normal | 73.677 | 1.2907 | Night | 202512 | 2025-12-30 | 1.2907
2025-12-30 17:57 | 73.2236 | FALSE | FALSE | -0.50174 | -0.68995 | -0.41696 | -0.56621 | -0.2826 |  |  | none | FALSE | 3 | 72.7219 | FALSE | FALSE | 0.098 |  | 73.1812 | 0 | -0.2826 | -0.01413 | 0.17092 | -1.5708 | 0.22968 | Normal | 73.6406 | 0.18456 | Night | 202512 | 2025-12-30 | 0.18456
2025-12-30 18:12 | 73.2236 | FALSE | FALSE | -0.49046 | -0.67433 | -0.37742 | -0.5128 | 0 |  |  | none | FALSE | 2 | 72.7331 | FALSE | FALSE | 0.0745 |  | 73.1671 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.21697 | Normal | 73.601 | 0.26049 | Night | 202512 | 2025-12-30 | 0.26049
2025-12-30 18:27 | 73.2236 | FALSE | FALSE | -0.47553 | -0.65367 | -0.33423 | -0.45438 | 0 |  |  | none | FALSE | 2 | 72.7481 | FALSE | FALSE | 0.0804 |  | 73.153 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.20244 | Normal | 73.5578 | 0.34899 | Night | 202512 | 2025-12-30 | 0.34899
2025-12-30 18:42 | 73.5062 | FALSE | FALSE | -0.75813 | -1.0421 | -0.051631 | -0.070191 | 0.2826 |  |  | none | FALSE | 2 | 72.7481 | FALSE | FALSE | 0.1735 |  | 73.153 | 0 | 0.2826 | 0 | 0.18338 | 1.5411 | 0.20244 | Normal | 73.5578 | 1.745 | Night | 202512 | 2025-12-30 | 1.745
2025-12-30 18:42 | 73.5062 | FALSE | FALSE | -0.77306 | -1.0629 | -0.094825 | -0.12884 | 0 |  |  | none | FALSE | 2 | 72.7331 | FALSE | FALSE | 0.1613 |  | 73.1671 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.21697 | Normal | 73.601 | 1.563 | Night | 202512 | 2025-12-30 | 1.563
2025-12-30 18:57 | 73.2236 | FALSE | FALSE | -0.49046 | -0.67433 | -0.37742 | -0.5128 | -0.2826 |  |  | none | FALSE | 1 | 72.7331 | FALSE | FALSE | 0.0459 |  | 73.1671 | 0 | -0.2826 | 0 | 0.18338 | -1.5411 | 0.21697 | Normal | 73.601 | 0.26049 | Night | 202512 | 2025-12-30 | 0.26049
2025-12-30 19:12 | 73.2236 | FALSE | FALSE | -0.49046 | -0.67433 | -0.37742 | -0.5128 | 0 |  |  | none | FALSE | 0 | 72.7331 | FALSE | FALSE | 0.0174 |  | 73.1671 | 0 | 0 | 0 | 0.18338 | 0 | 0.21697 | Normal | 73.601 | 0.26049 | Night | 202512 | 2025-12-30 | 0.26049
2025-12-30 19:27 | 73.2236 | FALSE | FALSE | -0.49046 | -0.67433 | -0.37742 | -0.5128 | 0 |  |  | none | FALSE | 0 | 72.7331 | FALSE | FALSE | 0.0174 |  | 73.1671 | 0 | 0 | 0 | 0.18338 | 0 | 0.21697 | Normal | 73.601 | 0.26049 | Night | 202512 | 2025-12-30 | 0.26049
2025-12-30 19:42 | 73.2236 | FALSE | FALSE | -0.49046 | -0.67433 | -0.37742 | -0.5128 | 0 |  |  | none | FALSE | 0 | 72.7331 | FALSE | FALSE | 0.0174 |  | 73.1671 | 0 | 0 | 0 | 0.18338 | 0 | 0.21697 | Normal | 73.601 | 0.26049 | Night | 202512 | 2025-12-30 | 0.26049
2025-12-30 19:57 | 72.941 | FALSE | FALSE | -0.23252 | -0.3198 | -0.65642 | -0.89191 | -0.2826 |  |  | none | FALSE | 0 | 72.7085 | FALSE | FALSE | 0.0636 |  | 73.153 | 0 | -0.2826 | -0.01413 | 0.19396 | -1.3842 | 0.22224 | Normal | 73.5974 | -0.95372 | Night | 202512 | 2025-12-30 | 0.95372
2025-12-30 20:12 | 72.941 | FALSE | FALSE | -0.25508 | -0.35094 | -0.65072 | -0.88423 | 0 |  |  | none | FALSE | 0 | 72.6859 | FALSE | FALSE | 0.0582 |  | 73.1388 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.22645 | Normal | 73.5917 | -0.87356 | Night | 202512 | 2025-12-30 | 0.87356
2025-12-30 20:27 | 72.6584 | FALSE | FALSE | -0.028313 | -0.038983 | -0.96089 | -1.3052 | -0.2826 |  |  | none | FALSE | 0 | 72.6301 | FALSE | FALSE | 0.1257 |  | 73.1247 | 0 | -0.2826 | -0.01413 | 0.19396 | -1.3842 | 0.2473 | Normal | 73.6193 | -1.8855 | Night | 202512 | 2025-12-30 | 1.8855
2025-12-30 20:41 | 72.3758 | FALSE | FALSE | 0.12713 | 0.17535 | -1.3141 | -1.7833 | -0.2826 | 2026-01-02 16:04 | 2025-12-30 20:41 | lower | TRUE | 0 | 72.5029 | FALSE | FALSE | 0.219 | 2.4284 | 73.0964 | 1 | -0.2826 | -0.02826 | 0.20296 | -1.2532 | 0.29675 | Extreme triggered | 73.6899 | -2.4284 | Night | 202512 | 2025-12-30 | 2.4284
2025-12-30 20:56 | 72.3758 | FALSE | FALSE | 0.019231 | 0.026564 | -1.3655 | -1.8518 | 0 |  | 2025-12-30 20:41 | lower | TRUE | 0 | 72.395 | FALSE | FALSE | 0.2514 | 2.2428 | 73.0682 | 2 | 0 | -0.02826 | 0.20296 | 0.13924 | 0.33657 | Extreme/elevated | 73.7413 | -2.0571 | Night | 202512 | 2025-12-30 | 2.0571
2025-12-30 21:11 | 72.095 | FALSE | FALSE | 0.1299 | 0.17985 | -1.7318 | -2.3458 | -0.2808 |  | 2025-12-30 20:41 | lower | TRUE | 0 | 72.2249 | FALSE | TRUE | 0.3264 | 2.27 | 73.0259 | 3 | -0.2808 | -0.0423 | 0.21047 | -1.1332 | 0.40049 | Persistent | 73.8268 | -2.3243 | Night | 202512 | 2025-12-30 | 2.3243
2025-12-30 21:26 | 72.095 | FALSE | FALSE | 0.012636 | 0.017524 | -1.7928 | -2.4263 | 0 |  | 2025-12-30 20:41 | lower | TRUE | 0 | 72.1076 | FALSE | TRUE | 0.3638 | 2.2096 | 72.9977 | 4 | 0 | -0.02817 | 0.20284 | 0.13888 | 0.44503 | Persistent | 73.8878 | -2.0284 | Night | 202512 | 2025-12-30 | 2.0284
2025-12-30 21:41 | 72.095 | FALSE | FALSE | -0.11712 | -0.16272 | -1.8379 | -2.4859 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 71.9779 | FALSE | FALSE | 0.4031 | 2.1197 | 72.9554 | 5 | 0 | -0.0423 | 0.18945 | 0.22327 | 0.48876 | Persistent | 73.9329 | -1.7604 | Night | 202512 | 2025-12-30 | 1.7604
2025-12-30 21:56 | 71.8124 | FALSE | FALSE | -0.020487 | -0.028537 | -2.1654 | -2.9271 | -0.2826 |  | 2025-12-30 20:41 | none | FALSE | 0 | 71.7919 | FALSE | FALSE | 0.4737 | 2.0935 | 72.8848 | 6 | -0.2826 | -0.07056 | 0.18038 | -1.1755 | 0.54646 | Persistent | 73.9778 | -1.9625 | Night | 202512 | 2025-12-30 | 1.9625
2025-12-30 22:11 | 71.8124 | FALSE | TRUE | -0.17774 | -0.24812 | -2.1815 | -2.9482 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 71.6347 | FALSE | FALSE | 0.5132 | 2.0371 | 72.8143 | 7 | 0 | -0.07056 | 0.18038 | 0.39118 | 0.58981 | Confirmed/Materialized Shift | 73.9939 | -1.6987 | Night | 202512 | 2025-12-30 | 1.6987
2025-12-30 22:26 | 71.5298 | FALSE | TRUE | -0.07804 | -0.10922 | -2.4494 | -3.3109 | -0.2826 |  | 2025-12-30 20:41 | none | FALSE | 0 | 71.4518 | FALSE | FALSE | 0.5251 | 2.017 | 72.7155 | 8 | -0.2826 | -0.09882 | 0.16582 | -1.1083 | 0.63185 | Confirmed/Materialized Shift | 73.9792 | -1.8765 | Night | 202512 | 2025-12-30 | 1.8765
2025-12-30 22:41 | 71.5298 | FALSE | TRUE | -0.24377 | -0.34196 | -2.4457 | -3.3061 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 71.286 | FALSE | FALSE | 0.5092 | 1.9749 | 72.6308 | 9 | 0 | -0.08469 | 0.16132 | 0.52499 | 0.67237 | Confirmed/Materialized Shift | 73.9755 | -1.6374 | Night | 202512 | 2025-12-30 | 1.6374
2025-12-30 22:56 | 71.5298 | FALSE | TRUE | -0.38348 | -0.539 | -2.416 | -3.2673 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 71.1463 | FALSE | FALSE | 0.4968 | 1.9226 | 72.5461 | 10 | 0 | -0.08469 | 0.16132 | 0.52499 | 0.69988 | Confirmed/Materialized Shift | 73.9458 | -1.4521 | Night | 202512 | 2025-12-30 | 1.4521
2025-12-30 23:11 | 71.2472 | FALSE | TRUE | -0.27532 | -0.38793 | -2.6754 | -3.6192 | -0.2826 |  | 2025-12-30 20:41 | none | FALSE | 0 | 70.9719 | FALSE | FALSE | 0.5085 | 1.8957 | 72.4473 | 11 | -0.2826 | -0.09882 | 0.16582 | -1.1083 | 0.73769 | Confirmed/Materialized Shift | 73.9226 | -1.6268 | Night | 202512 | 2025-12-30 | 1.6268
2025-12-30 23:26 | 71.2472 | FALSE | TRUE | -0.39281 | -0.55438 | -2.567 | -3.4777 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 70.8544 | FALSE | FALSE | 0.4979 | 1.8601 | 72.3343 | 12 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.73996 | Confirmed/Materialized Shift | 73.8142 | -1.4692 | Night | 202512 | 2025-12-30 | 1.4692
2025-12-30 23:40 | 71.2472 | FALSE | TRUE | -0.47364 | -0.66923 | -2.422 | -3.2876 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 70.7736 | FALSE | FALSE | 0.4897 | 1.8206 | 72.2214 | 13 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.7239 | Confirmed/Materialized Shift | 73.6692 | -1.3457 | Night | 202512 | 2025-12-30 | 1.3457
2025-12-30 23:55 | 71.2472 | FALSE | TRUE | -0.5541 | -0.78382 | -2.3048 | -3.1335 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 70.6931 | FALSE | FALSE | 0.4816 | 1.778 | 72.1225 | 14 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.71472 | Confirmed/Materialized Shift | 73.552 | -1.2247 | Night | 202512 | 2025-12-30 | 1.2247
2025-12-31 00:10 | 70.9646 | FALSE | TRUE | -0.3751 | -0.53138 | -2.4651 | -3.3571 | -0.2826 |  | 2025-12-30 20:41 | none | FALSE | 0 | 70.5895 | FALSE | FALSE | 0.4981 | 1.7576 | 72.0096 | 15 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.71004 | Confirmed/Materialized Shift | 73.4297 | -1.4717 | Night | 202512 | 2025-12-31 | 1.4717
2025-12-31 00:25 | 70.9646 | FALSE | TRUE | -0.44002 | -0.62392 | -2.3041 | -3.1447 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 70.5246 | FALSE | FALSE | 0.4906 | 1.7327 | 71.8966 | 16 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.68603 | Confirmed/Materialized Shift | 73.2687 | -1.3586 | Night | 202512 | 2025-12-31 | 1.3586
2025-12-31 00:40 | 70.682 | FALSE | TRUE | -0.237 | -0.33643 | -2.4121 | -3.3 | -0.2826 |  | 2025-12-30 20:41 | none | FALSE | 0 | 70.445 | FALSE | FALSE | 0.5095 | 1.7273 | 71.7696 | 17 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.66228 | Confirmed/Materialized Shift | 73.0941 | -1.6421 | Night | 202512 | 2025-12-31 | 1.6421
2025-12-31 00:55 | 70.682 | FALSE | TRUE | -0.31413 | -0.44641 | -2.2633 | -3.1028 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 70.3679 | FALSE | FALSE | 0.5008 | 1.7154 | 71.6566 | 18 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.64437 | Confirmed/Materialized Shift | 72.9453 | -1.5125 | Night | 202512 | 2025-12-31 | 1.5125
2025-12-31 01:10 | 70.682 | FALSE | TRUE | -0.34656 | -0.49273 | -2.0699 | -2.8451 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 70.3354 | FALSE | FALSE | 0.4951 | 1.7002 | 71.5437 | 19 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.60411 | Confirmed/Materialized Shift | 72.7519 | -1.4263 | Night | 202512 | 2025-12-31 | 1.4263
2025-12-31 01:25 | 70.3994 | FALSE | TRUE | -0.16038 | -0.22833 | -2.223 | -3.061 | -0.2826 |  | 2025-12-30 20:41 | none | FALSE | 0 | 70.239 | FALSE | FALSE | 0.5154 | 1.7017 | 71.4307 | 20 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.59584 | Confirmed/Materialized Shift | 72.6224 | -1.7308 | Night | 202512 | 2025-12-31 | 1.7308
2025-12-31 01:40 | 70.3994 | FALSE | TRUE | -0.257 | -0.36639 | -2.122 | -2.926 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 70.1424 | FALSE | FALSE | 0.5045 | 1.6953 | 71.3319 | 21 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.59474 | Confirmed/Materialized Shift | 72.5214 | -1.5679 | Night | 202512 | 2025-12-31 | 1.5679
2025-12-31 01:55 | 70.1168 | FALSE | TRUE | -0.098932 | -0.1413 | -2.3032 | -3.1804 | -0.2826 |  | 2025-12-30 20:41 | none | FALSE | 0 | 70.0179 | FALSE | FALSE | 0.5224 | 1.7017 | 71.2189 | 22 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.60054 | Confirmed/Materialized Shift | 72.42 | -1.8353 | Night | 202512 | 2025-12-31 | 1.8353
2025-12-31 02:10 | 70.1168 | FALSE | TRUE | -0.21969 | -0.31431 | -2.2262 | -3.0772 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 69.8971 | FALSE | FALSE | 0.5094 | 1.6991 | 71.12 | 23 | 0 | -0.09891 | 0.13829 | 0.71522 | 0.61146 | Confirmed/Materialized Shift | 72.343 | -1.6407 | Night | 202512 | 2025-12-31 | 1.6407
2025-12-31 02:25 | 69.836 | FALSE | TRUE | -0.089397 | -0.12817 | -2.4316 | -3.3647 | -0.2808 |  | 2025-12-30 20:41 | none | FALSE | 0 | 69.7466 | FALSE | FALSE | 0.5239 | 1.7057 | 71.0071 | 24 | -0.2808 | -0.11295 | 0.14193 | -1.1826 | 0.63024 | Confirmed/Materialized Shift | 72.2676 | -1.8582 | Night | 202512 | 2025-12-31 | 1.8582
2025-12-31 02:39 | 69.836 | FALSE | TRUE | -0.19671 | -0.28248 | -2.313 | -3.2058 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 69.6393 | FALSE | FALSE | 0.5124 | 1.7049 | 70.8941 | 25 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.62742 | Confirmed/Materialized Shift | 72.149 | -1.6865 | Night | 202512 | 2025-12-31 | 1.6865
2025-12-31 02:54 | 69.5534 | FALSE | TRUE | -0.084405 | -0.1215 | -2.54 | -3.5232 | -0.2826 |  | 2025-12-30 20:41 | none | FALSE | 0 | 69.469 | FALSE | FALSE | 0.5248 | 1.7113 | 70.7812 | 26 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.65609 | Confirmed/Materialized Shift | 72.0934 | -1.8714 | Night | 202512 | 2025-12-31 | 1.8714
2025-12-31 03:09 | 69.2708 | FALSE | TRUE | 0.0011934 | 0.0017227 | -2.7654 | -3.8389 | -0.2826 |  | 2025-12-30 20:41 | lower | TRUE | 0 | 69.272 | FALSE | TRUE | 0.5334 | 1.7221 | 70.6541 | 27 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.69105 | Confirmed/Materialized Shift | 72.0362 | -2.0017 | Night | 202512 | 2025-12-31 | 2.0017
2025-12-31 03:25 | 69.2708 | FALSE | TRUE | -0.17806 | -0.25772 | -2.7188 | -3.7766 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 69.0927 | FALSE | FALSE | 0.5169 | 1.7232 | 70.5412 | 28 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.72421 | Confirmed/Materialized Shift | 71.9896 | -1.7541 | Night | 202512 | 2025-12-31 | 1.7541
2025-12-31 03:39 | 68.9882 | FALSE | TRUE | -0.10117 | -0.14686 | -2.9529 | -4.1046 | -0.2826 |  | 2025-12-30 20:41 | none | FALSE | 0 | 68.887 | FALSE | FALSE | 0.5245 | 1.7282 | 70.4141 | 29 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.76352 | Confirmed/Materialized Shift | 71.9411 | -1.8675 | Night | 202512 | 2025-12-31 | 1.8675
2025-12-31 03:54 | 68.9882 | FALSE | TRUE | -0.25999 | -0.37829 | -2.8576 | -3.9774 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 68.7282 | FALSE | FALSE | 0.5111 | 1.7261 | 70.287 | 30 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.77939 | Confirmed/Materialized Shift | 71.8458 | -1.6664 | Night | 202512 | 2025-12-31 | 1.6664
2025-12-31 04:09 | 68.9882 | FALSE | TRUE | -0.40699 | -0.59344 | -2.7787 | -3.8718 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 68.5812 | FALSE | FALSE | 0.4993 | 1.7185 | 70.174 | 31 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.79641 | Confirmed/Materialized Shift | 71.7669 | -1.489 | Night | 202512 | 2025-12-31 | 1.489
2025-12-31 04:24 | 68.7056 | FALSE | TRUE | -0.2959 | -0.43254 | -2.9786 | -4.1552 | -0.2826 |  | 2025-12-30 20:41 | none | FALSE | 0 | 68.4097 | FALSE | FALSE | 0.5092 | 1.716 | 70.047 | 32 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.81863 | Confirmed/Materialized Shift | 71.6842 | -1.6385 | Night | 202512 | 2025-12-31 | 1.6385
2025-12-31 04:39 | 68.7056 | FALSE | TRUE | -0.42527 | -0.62283 | -2.8538 | -3.9881 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 68.2803 | FALSE | FALSE | 0.4987 | 1.7089 | 69.9199 | 33 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.81978 | Confirmed/Materialized Shift | 71.5594 | -1.4812 | Night | 202512 | 2025-12-31 | 1.4812
2025-12-31 04:54 | 68.7056 | FALSE | TRUE | -0.51269 | -0.75182 | -2.6871 | -3.7638 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 68.1929 | FALSE | FALSE | 0.4906 | 1.6986 | 69.7928 | 34 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.79994 | Confirmed/Materialized Shift | 71.3927 | -1.3591 | Night | 202512 | 2025-12-31 | 1.3591
2025-12-31 05:09 | 68.423 | FALSE | TRUE | -0.36898 | -0.54219 | -2.8544 | -4.0047 | -0.2826 |  | 2025-12-30 20:41 | none | FALSE | 0 | 68.054 | FALSE | FALSE | 0.5028 | 1.6941 | 69.6657 | 35 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.80585 | Confirmed/Materialized Shift | 71.2774 | -1.5421 | Night | 202512 | 2025-12-31 | 1.5421
2025-12-31 05:24 | 68.1404 | FALSE | TRUE | -0.24324 | -0.35825 | -3.0115 | -4.2324 | -0.2826 |  | 2025-12-30 20:41 | none | FALSE | 0 | 67.8972 | FALSE | FALSE | 0.5134 | 1.6943 | 69.5245 | 36 | -0.2826 | -0.14121 | 0.14488 | -0.97592 | 0.81367 | Confirmed/Materialized Shift | 71.1519 | -1.7011 | Night | 202512 | 2025-12-31 | 1.7011
2025-12-31 05:38 | 68.1404 | FALSE | TRUE | -0.3866 | -0.5706 | -2.9007 | -4.0831 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 67.7538 | FALSE | FALSE | 0.502 | 1.6899 | 69.3974 | 37 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.82182 | Confirmed/Materialized Shift | 71.0411 | -1.5296 | Night | 202512 | 2025-12-31 | 1.5296
2025-12-31 05:54 | 68.1404 | FALSE | TRUE | -0.48832 | -0.72181 | -2.7482 | -3.8768 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 67.6521 | FALSE | FALSE | 0.4931 | 1.6821 | 69.2703 | 38 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.80913 | Confirmed/Materialized Shift | 70.8886 | -1.3965 | Night | 202512 | 2025-12-31 | 1.3965
2025-12-31 06:09 | 67.8596 | FALSE | TRUE | -0.32235 | -0.4773 | -2.8616 | -4.0463 | -0.2808 |  | 2025-12-30 20:41 | none | FALSE | 0 | 67.5372 | FALSE | FALSE | 0.5063 | 1.6799 | 69.1292 | 39 | -0.2808 | -0.14112 | 0.14479 | -0.96473 | 0.79599 | Confirmed/Materialized Shift | 70.7212 | -1.595 | Night | 202512 | 2025-12-31 | 1.595
2025-12-31 06:24 | 67.8596 | FALSE | TRUE | -0.42778 | -0.63439 | -2.7131 | -3.8443 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 67.4318 | FALSE | FALSE | 0.497 | 1.6743 | 69.0022 | 40 | 0 | -0.12699 | 0.14404 | 0.88163 | 0.78521 | Confirmed/Materialized Shift | 70.5727 | -1.4552 | Night | 202512 | 2025-12-31 | 1.4552
2026-01-02 13:13 | 71.8124 | TRUE | TRUE | -4.6622 | -6.943 | 0.81681 | 1.1505 | 3.9528 |  | 2025-12-30 20:41 | upper | TRUE | 1 | 67.1502 | FALSE | TRUE | 0.6185 | 1.7029 | 69.0729 | 41 | 3.9528 | 0.07065 | 0.92456 | 4.1989 | 0.96135 | Confirmed/Materialized Shift | 70.9956 | 2.8497 | Day | 202601 | 2026-01-02 | 2.8497
2026-01-02 13:13 | 71.8124 | FALSE | TRUE | -4.8946 | -7.3144 | 0.41485 | 0.58104 | 0 |  | 2025-12-30 20:41 | upper | TRUE | 1 | 66.9178 | FALSE | TRUE | 0.5866 | 1.7188 | 69.1577 | 42 | 0 | 0.08478 | 0.92103 | -0.092049 | 1.1199 | Confirmed/Materialized Shift | 71.3976 | 2.3704 | Day | 202601 | 2026-01-02 | 2.3704
2026-01-02 13:28 | 71.8124 | FALSE | TRUE | -5.0753 | -7.6049 | 0.064589 | 0.090022 | 0 |  | 2025-12-30 20:41 | upper | TRUE | 1 | 66.7371 | FALSE | TRUE | 0.5653 | 1.7266 | 69.2425 | 43 | 0 | 0.08478 | 0.92103 | -0.092049 | 1.2527 | Confirmed/Materialized Shift | 71.7478 | 2.0516 | Day | 202601 | 2026-01-02 | 2.0516
2026-01-02 13:43 | 72.095 | FALSE | TRUE | -5.5435 | -8.3297 | -0.064328 | -0.089147 | 0.2826 |  | 2025-12-30 20:41 | none | FALSE | 1 | 66.5515 | FALSE | FALSE | 0.5588 | 1.7318 | 69.3554 | 44 | 0.2826 | 0.11295 | 0.91787 | 0.18483 | 1.402 | Confirmed/Materialized Shift | 72.1593 | 1.9541 | Day | 202601 | 2026-01-02 | 1.9541
2026-01-02 13:58 | 72.3758 | FALSE | TRUE | -6.0024 | -9.0435 | -0.21562 | -0.29703 | 0.2808 |  | 2025-12-30 20:41 | none | FALSE | 1 | 66.3734 | FALSE | FALSE | 0.5527 | 1.7346 | 69.4824 | 45 | 0.2808 | 0.12699 | 0.9182 | 0.16751 | 1.5545 | Confirmed/Materialized Shift | 72.5914 | 1.8613 | Day | 202601 | 2026-01-02 | 1.8613
2026-01-02 14:13 | 72.6584 | FALSE | TRUE | -6.4394 | -9.7244 | -0.39788 | -0.54463 | 0.2826 |  | 2025-12-30 20:41 | none | FALSE | 1 | 66.219 | FALSE | FALSE | 0.5464 | 1.7353 | 69.6376 | 46 | 0.2826 | 0.15525 | 0.91362 | 0.13939 | 1.7093 | Confirmed/Materialized Shift | 73.0563 | 1.7672 | Day | 202601 | 2026-01-02 | 1.7672
2026-01-02 14:28 | 72.6584 | FALSE | TRUE | -6.52 | -9.8582 | -0.81728 | -1.1123 | 0 |  | 2025-12-30 20:41 | none | FALSE | 1 | 66.1384 | FALSE | FALSE | 0.5322 | 1.7315 | 69.807 | 47 | 0 | 0.16938 | 0.90866 | -0.18641 | 1.8343 | Confirmed/Materialized Shift | 73.4757 | 1.5545 | Day | 202601 | 2026-01-02 | 1.5545
2026-01-02 14:43 | 72.941 | FALSE | TRUE | -6.8651 | -10.3897 | -0.96418 | -1.3046 | 0.2826 |  | 2025-12-30 20:41 | none | FALSE | 1 | 66.0759 | FALSE | FALSE | 0.5291 | 1.7268 | 69.9905 | 48 | 0.2826 | 0.18351 | 0.90809 | 0.10912 | 1.9573 | Confirmed/Materialized Shift | 73.9052 | 1.5074 | Day | 202601 | 2026-01-02 | 1.5074
2026-01-02 14:58 | 73.2236 | FALSE | TRUE | -7.1595 | -10.8372 | -1.1169 | -1.5024 | 0.2826 |  | 2025-12-30 20:41 | none | FALSE | 1 | 66.0641 | FALSE | FALSE | 0.5259 | 1.7214 | 70.2023 | 49 | 0.2826 | 0.21177 | 0.90159 | 0.078561 | 2.0691 | Confirmed/Materialized Shift | 74.3405 | 1.4602 | Day | 202601 | 2026-01-02 | 1.4602
2026-01-02 15:13 | 73.2236 | FALSE | TRUE | -7.1162 | -10.7646 | -1.4971 | -2.0036 | 0 |  | 2025-12-30 20:41 | none | FALSE | 1 | 66.1074 | FALSE | FALSE | 0.5156 | 1.713 | 70.4141 | 50 | 0 | 0.21177 | 0.90159 | -0.23488 | 2.1533 | Confirmed/Materialized Shift | 74.7207 | 1.3047 | Day | 202601 | 2026-01-02 | 1.3047
2026-01-02 15:28 | 73.2236 | FALSE | TRUE | -7.0241 | -10.6105 | -1.8286 | -2.4364 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 66.1995 | FALSE | FALSE | 0.4783 | 1.7025 | 70.6258 | 51 | 0 | 0.21177 | 0.90159 | -0.23488 | 2.2132 | Confirmed/Materialized Shift | 75.0522 | 1.1738 | Day | 202601 | 2026-01-02 | 1.1738
2026-01-02 15:43 | 73.5062 | FALSE | TRUE | -7.1481 | -10.772 | -1.8674 | -2.4776 | 0.2826 |  | 2025-12-30 20:41 | none | FALSE | 0 | 66.3581 | FALSE | FALSE | 0.4781 | 1.6923 | 70.8659 | 52 | 0.2826 | 0.24003 | 0.89411 | 0.047612 | 2.2539 | Confirmed/Materialized Shift | 75.3736 | 1.1715 | Day | 202601 | 2026-01-02 | 1.1715
2026-01-02 15:58 | 73.5062 | FALSE | TRUE | -6.9349 | -10.4172 | -2.1343 | -2.8216 | 0 |  | 2025-12-30 20:41 | none | FALSE | 0 | 66.5713 | FALSE | FALSE | 0.4706 | 1.6803 | 71.1059 | 53 | 0 | 0.24003 | 0.89411 | -0.26846 | 2.2673 | Confirmed/Materialized Shift | 75.6405 | 1.0587 | Day | 202601 | 2026-01-02 | 1.0587
2026-01-02 16:04 | 73.5062 | FALSE | FALSE | -6.668 | -9.9764 | -2.3475 | -3.0948 | 0 |  |  | none | FALSE | 0 | 66.8382 | FALSE | FALSE | 0.0639 |  | 71.3459 | 0 | 0 | 0.24003 | 0.89411 | -0.26846 | 2.2539 | Persistence ends | 75.8537 | 0.95847 | Day | 202601 | 2026-01-02 | 0.95847
2026-01-02 16:07 | 73.5062 | FALSE | FALSE | -6.2915 | -9.3603 | -2.4793 | -3.2629 | 0 |  |  | none | FALSE | 0 | 67.2147 | FALSE | FALSE | 0.058 |  | 71.6001 | 0 | 0 | 0.25416 | 0.88762 | -0.28634 | 2.1927 | Normal | 75.9855 | 0.8693 | Day | 202601 | 2026-01-02 | 0.8693
2026-01-02 16:21 | 72.095 | FALSE | FALSE | -4.3714 | -6.4547 | -3.777 | -4.9781 | -1.4112 |  |  | none | FALSE | 0 | 67.7236 | FALSE | FALSE | 0.0097 |  | 71.7978 | 0 | -1.4112 | 0.19773 | 0.95673 | -1.6817 | 2.0371 | Normal | 75.872 | 0.14588 | Day | 202601 | 2026-01-02 | 0.14588
2026-01-02 16:21 | 72.095 | FALSE | FALSE | -3.7922 | -5.5521 | -3.5933 | -4.7476 | 0 |  |  | none | FALSE | 0 | 68.3028 | FALSE | FALSE | 0.0036 |  | 71.9955 | 0 | 0 | 0.19773 | 0.95673 | -0.20667 | 1.8464 | Normal | 75.6883 | 0.053862 | Day | 202601 | 2026-01-02 | 0.053862
2026-01-02 16:22 | 71.8124 | FALSE | FALSE | -2.854 | -4.1387 | -3.5875 | -4.7579 | -0.2826 |  |  | none | FALSE | 0 | 68.9584 | FALSE | FALSE | 0.0152 |  | 72.1792 | 0 | -0.2826 | 0.1836 | 0.96187 | -0.48468 | 1.6104 | Normal | 75.3999 | -0.22774 | Day | 202601 | 2026-01-02 | 0.22774
2026-01-02 16:37 | 72.3758 | FALSE | FALSE | -2.4685 | -3.5311 | -2.5268 | -3.3735 | 0.5634 |  |  | none | FALSE | 0 | 69.9073 | FALSE | FALSE | 0.0016 |  | 72.405 | 0 | 0.5634 | 0.22581 | 0.95894 | 0.35204 | 1.2488 | Normal | 74.9026 | -0.02335 | Day | 202601 | 2026-01-02 | 0.02335
2026-01-02 16:52 | 72.6584 | FALSE | FALSE | -1.3019 | -1.8245 | -1.2749 | -1.7243 | 0.2826 |  |  | none | FALSE | 0 | 71.3565 | FALSE | FALSE | 0.0014 |  | 72.6449 | 0 | 0.2826 | 0.23994 | 0.95752 | 0.044553 | 0.64418 | Normal | 73.9333 | 0.020957 | Day | 202601 | 2026-01-02 | 0.020957
2026-01-02 17:07 | 72.941 | FALSE | FALSE | -1.4722 | -2.0599 | -0.99282 | -1.3429 | 0.2826 |  |  | none | FALSE | 0 | 71.4688 | FALSE | FALSE | 0.0259 |  | 72.7013 | 0 | 0.2826 | 0.05643 | 0.3949 | 0.57273 | 0.61625 | Normal | 73.9338 | 0.38892 | Day | 202601 | 2026-01-02 | 0.38892
2026-01-02 17:21 | 72.941 | FALSE | FALSE | -1.3457 | -1.8796 | -0.97924 | -1.3247 | 0 |  |  | none | FALSE | 0 | 71.5953 | FALSE | FALSE | 0.021 |  | 72.7578 | 0 | 0 | 0.05643 | 0.3949 | -0.1429 | 0.58124 | Normal | 73.9202 | 0.31526 | Day | 202601 | 2026-01-02 | 0.31526
2026-01-02 17:36 | 73.2236 | FALSE | FALSE | -1.4852 | -2.0703 | -0.69464 | -0.93975 | 0.2826 |  |  | none | FALSE | 0 | 71.7384 | FALSE | FALSE | 0.0484 |  | 72.8283 | 0 | 0.2826 | 0.07056 | 0.39782 | 0.53301 | 0.54496 | Normal | 73.9182 | 0.72533 | Day | 202601 | 2026-01-02 | 0.72533
2026-01-02 17:51 | 73.2236 | FALSE | FALSE | -1.3849 | -1.9278 | -0.70719 | -0.95656 | 0 |  |  | none | FALSE | 0 | 71.8387 | FALSE | FALSE | 0.0432 |  | 72.8847 | 0 | 0 | 0.05643 | 0.3949 | -0.1429 | 0.52302 | Normal | 73.9308 | 0.64787 | Night | 202601 | 2026-01-02 | 0.64787
2026-01-02 18:06 | 72.941 | FALSE | FALSE | -1.0463 | -1.4553 | -0.99033 | -1.3395 | -0.2826 |  |  | none | FALSE | 0 | 71.8947 | FALSE | FALSE | 0.0037 |  | 72.913 | 0 | -0.2826 | 0.02826 | 0.39813 | -0.78079 | 0.50916 | Normal | 73.9313 | 0.054973 | Night | 202601 | 2026-01-02 | 0.054973
2026-01-02 18:20 | 73.2236 | FALSE | FALSE | -1.3023 | -1.8107 | -0.73761 | -0.99729 | 0.2826 |  |  | none | FALSE | 0 | 71.9213 | FALSE | FALSE | 0.0369 |  | 72.9413 | 0 | 0.2826 | 0.02826 | 0.39813 | 0.63883 | 0.50997 | Normal | 73.9612 | 0.55362 | Night | 202601 | 2026-01-02 | 0.55362
2026-01-02 18:35 | 73.2236 | FALSE | FALSE | -1.2723 | -1.7683 | -0.76419 | -1.0329 | 0 |  |  | none | FALSE | 0 | 71.9513 | FALSE | FALSE | 0.0333 |  | 72.9695 | 0 | 0 | 0.02826 | 0.39813 | -0.070981 | 0.50913 | Normal | 73.9878 | 0.49903 | Night | 202601 | 2026-01-02 | 0.49903
2026-01-02 18:35 | 73.2236 | FALSE | FALSE | -1.2644 | -1.757 | -0.78448 | -1.06 | 0 |  |  | none | FALSE | 0 | 71.9592 | FALSE | FALSE | 0.0312 |  | 72.9837 | 0 | 0 | 0.01413 | 0.39362 | -0.035897 | 0.51221 | Normal | 74.0081 | 0.46844 | Night | 202601 | 2026-01-02 | 0.46844
2026-01-02 18:50 | 72.941 | FALSE | FALSE | -0.98973 | -1.3756 | -1.0468 | -1.4148 | -0.2826 |  |  | none | FALSE | 0 | 71.9513 | FALSE | FALSE | 0.0037 |  | 72.9695 | 0 | -0.2826 | -0.01413 | 0.39362 | -0.68205 | 0.50913 | Normal | 73.9878 | -0.056037 | Night | 202601 | 2026-01-02 | 0.056037
2026-01-02 19:05 | 72.941 | FALSE | FALSE | -0.99683 | -1.3856 | -1.0256 | -1.3866 | 0 |  |  | none | FALSE | 0 | 71.9442 | FALSE | FALSE | 0.0019 |  | 72.9554 | 0 | 0 | -0.01413 | 0.39362 | 0.035897 | 0.50562 | Normal | 73.9666 | -0.02848 | Night | 202601 | 2026-01-02 | 0.02848
2026-01-02 19:21 | 72.941 | FALSE | FALSE | -1.0031 | -1.3943 | -1.0036 | -1.3572 | 0 |  |  | none | FALSE | 0 | 71.9379 | FALSE | FALSE | 0 |  | 72.9413 | 0 | 0 | -0.01413 | 0.39362 | 0.035897 | 0.50166 | Normal | 73.9446 | -0.00053821 | Night | 202601 | 2026-01-02 | 0.00053821
2026-01-02 19:35 | 72.6584 | FALSE | FALSE | -0.73355 | -1.0199 | -1.2145 | -1.6441 | -0.2826 |  |  | none | FALSE | 0 | 71.9248 | FALSE | FALSE | 0.0329 |  | 72.8989 | 0 | -0.2826 | -0.04239 | 0.39148 | -0.6136 | 0.48702 | Normal | 73.8729 | -0.49378 | Night | 202601 | 2026-01-02 | 0.49378
2026-01-02 19:50 | 72.3758 | FALSE | FALSE | -0.49012 | -0.68181 | -1.4232 | -1.9285 | -0.2826 |  |  | none | FALSE | 0 | 71.8857 | FALSE | FALSE | 0.065 |  | 72.8424 | 0 | -0.2826 | -0.05652 | 0.39495 | -0.57242 | 0.47834 | Normal | 73.799 | -0.97537 | Night | 202601 | 2026-01-02 | 0.97537
2026-01-02 20:05 | 72.3758 | FALSE | FALSE | -0.51454 | -0.71602 | -1.3346 | -1.8106 | 0 |  |  | none | FALSE | 0 | 71.8613 | FALSE | FALSE | 0.0591 |  | 72.7858 | 0 | 0 | -0.05652 | 0.39495 | 0.14311 | 0.46229 | Normal | 73.7104 | -0.88698 | Night | 202601 | 2026-01-02 | 0.88698
2026-01-02 20:20 | 72.095 | FALSE | FALSE | -0.28808 | -0.40118 | -1.5286 | -2.0763 | -0.2808 |  |  | none | FALSE | 0 | 71.8069 | FALSE | FALSE | 0.091 |  | 72.7153 | 0 | -0.2808 | -0.07056 | 0.39782 | -0.52848 | 0.45418 | Normal | 73.6236 | -1.3657 | Night | 202601 | 2026-01-02 | 1.3657
2026-01-02 20:35 | 72.095 | FALSE | FALSE | -0.28808 | -0.40118 | -1.5286 | -2.0763 | 0 |  |  | none | FALSE | 0 | 71.8069 | FALSE | FALSE | 0.091 |  | 72.7153 | 0 | 0 | 0 | 0.24225 | 0 | 0.45418 | Normal | 73.6236 | -1.3657 | Night | 202601 | 2026-01-02 | 1.3657
2026-01-02 20:50 | 72.095 | FALSE | FALSE | -0.28808 | -0.40118 | -1.5286 | -2.0763 | 0 |  |  | none | FALSE | 0 | 71.8069 | FALSE | FALSE | 0.091 |  | 72.7153 | 0 | 0 | 0 | 0.24225 | 0 | 0.45418 | Normal | 73.6236 | -1.3657 | Night | 202601 | 2026-01-02 | 1.3657
2026-01-02 21:05 | 71.8124 | FALSE | FALSE | -0.0054775 | -0.007628 | -1.8112 | -2.4601 | -0.2826 |  |  | none | FALSE | 0 | 71.8069 | FALSE | FALSE | 0.1325 |  | 72.7153 | 0 | -0.2826 | 0 | 0.24225 | -1.1666 | 0.45418 | Normal | 73.6236 | -1.9879 | Night | 202601 | 2026-01-02 | 1.9879
2026-01-02 21:20 | 71.8124 | FALSE | FALSE | -0.10973 | -0.15304 | -1.8592 | -2.5236 | 0 |  |  | none | FALSE | 0 | 71.7027 | FALSE | FALSE | 0.1185 |  | 72.6871 | 0 | 0 | -0.02817 | 0.20284 | 0.13888 | 0.49222 | Normal | 73.6716 | -1.7771 | Night | 202601 | 2026-01-02 | 1.7771
2026-01-02 21:34 | 71.5298 | FALSE | FALSE | -0.011559 | -0.016162 | -2.2133 | -3.0014 | -0.2826 |  |  | none | FALSE | 0 | 71.5182 | FALSE | FALSE | 0.1319 |  | 72.6307 | 0 | -0.2826 | -0.05643 | 0.19654 | -1.1508 | 0.55622 | Normal | 73.7431 | -1.9792 | Night | 202601 | 2026-01-02 | 1.9792
2026-01-02 21:49 | 71.5298 | FALSE | FALSE | -0.17443 | -0.24446 | -2.2351 | -3.03 | 0 |  |  | none | FALSE | 0 | 71.3554 | FALSE | FALSE | 0.114 |  | 72.5601 | 0 | 0 | -0.07056 | 0.18038 | 0.39118 | 0.60238 | Normal | 73.7649 | -1.7104 | Night | 202601 | 2026-01-02 | 1.7104
2026-01-02 22:04 | 71.2472 | FALSE | FALSE | -0.096 | -0.13492 | -2.5525 | -3.4586 | -0.2826 |  |  | none | FALSE | 0 | 71.1512 | FALSE | FALSE | 0.1237 |  | 72.4754 | 0 | -0.2826 | -0.08469 | 0.18555 | -1.0666 | 0.66211 | Normal | 73.7997 | -1.855 | Night | 202601 | 2026-01-02 | 1.855
2026-01-02 22:19 | 71.2472 | FALSE | FALSE | -0.25342 | -0.35696 | -2.5122 | -3.406 | 0 |  |  | none | FALSE | 0 | 70.9938 | FALSE | FALSE | 0.1089 |  | 72.3766 | 0 | 0 | -0.09882 | 0.16582 | 0.59594 | 0.69141 | Normal | 73.7594 | -1.6335 | Night | 202601 | 2026-01-02 | 1.6335
2026-01-02 22:34 | 71.2472 | FALSE | FALSE | -0.37959 | -0.53563 | -2.4408 | -3.3123 | 0 |  |  | none | FALSE | 0 | 70.8676 | FALSE | FALSE | 0.0974 |  | 72.2778 | 0 | 0 | -0.09882 | 0.16582 | 0.59594 | 0.70509 | Normal | 73.688 | -1.4616 | Night | 202601 | 2026-01-02 | 1.4616
2026-01-02 22:49 | 70.9646 | FALSE | FALSE | -0.2749 | -0.38889 | -2.7036 | -3.67 | -0.2826 |  |  | none | FALSE | 0 | 70.6897 | FALSE | FALSE | 0.1087 |  | 72.179 | 0 | -0.2826 | -0.09882 | 0.16582 | -1.1083 | 0.74464 | Normal | 73.6682 | -1.6308 | Night | 202601 | 2026-01-02 | 1.6308
2026-01-02 23:04 | 70.682 | FALSE | FALSE | -0.17671 | -0.25063 | -2.9165 | -3.9627 | -0.2826 |  |  | none | FALSE | 0 | 70.5053 | FALSE | FALSE | 0.1181 |  | 72.0519 | 0 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.7733 | Normal | 73.5985 | -1.7715 | Night | 202601 | 2026-01-02 | 1.7715
2026-01-02 23:19 | 70.682 | FALSE | FALSE | -0.31604 | -0.44914 | -2.8017 | -3.8126 | 0 |  |  | none | FALSE | 0 | 70.366 | FALSE | FALSE | 0.1063 |  | 71.9248 | 0 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.77943 | Normal | 73.4837 | -1.5945 | Night | 202601 | 2026-01-02 | 1.5945
2026-01-02 23:34 | 70.3994 | FALSE | FALSE | -0.19085 | -0.27184 | -2.9593 | -4.034 | -0.2826 |  |  | none | FALSE | 0 | 70.2085 | FALSE | FALSE | 0.1172 |  | 71.7836 | 0 | -0.2826 | -0.14121 | 0.14488 | -0.97592 | 0.78753 | Normal | 73.3587 | -1.7577 | Night | 202601 | 2026-01-02 | 1.7577
2026-01-02 23:49 | 70.3994 | FALSE | FALSE | -0.33478 | -0.47782 | -2.849 | -3.8895 | 0 |  |  | none | FALSE | 0 | 70.0646 | FALSE | FALSE | 0.1053 |  | 71.6565 | 0 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.79595 | Normal | 73.2484 | -1.5794 | Night | 202601 | 2026-01-02 | 1.5794
2026-01-03 00:04 | 70.3994 | FALSE | FALSE | -0.43569 | -0.62274 | -2.6958 | -3.688 | 0 |  |  | none | FALSE | 0 | 69.9637 | FALSE | FALSE | 0.0962 |  | 71.5294 | 0 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.78287 | Normal | 73.0952 | -1.4435 | Night | 202601 | 2026-01-03 | 1.4435
2026-01-03 00:19 | 70.3994 | FALSE | FALSE | -0.49132 | -0.70282 | -2.4972 | -3.4257 | 0 |  |  | none | FALSE | 0 | 69.9081 | FALSE | FALSE | 0.0895 |  | 71.4024 | 0 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.74714 | Normal | 72.8966 | -1.3424 | Night | 202601 | 2026-01-03 | 1.3424
2026-01-03 00:33 | 70.3994 | FALSE | FALSE | -0.54485 | -0.77997 | -2.3249 | -3.1968 | 0 |  |  | none | FALSE | 0 | 69.8546 | FALSE | FALSE | 0.0827 |  | 71.2894 | 0 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.71743 | Normal | 72.7243 | -1.2406 | Night | 202601 | 2026-01-03 | 1.2406
2026-01-03 00:49 | 70.1168 | FALSE | FALSE | -0.37076 | -0.53158 | -2.4901 | -3.4295 | -0.2826 |  |  | none | FALSE | 0 | 69.746 | FALSE | FALSE | 0.0988 |  | 71.1765 | 0 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.71521 | Normal | 72.6069 | -1.4816 | Night | 202601 | 2026-01-03 | 1.4816
2026-01-03 01:04 | 70.1168 | FALSE | FALSE | -0.44108 | -0.63304 | -2.3345 | -3.2222 | 0 |  |  | none | FALSE | 0 | 69.6757 | FALSE | FALSE | 0.091 |  | 71.0635 | 0 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.69389 | Normal | 72.4513 | -1.3643 | Night | 202601 | 2026-01-03 | 1.3643
2026-01-03 01:19 | 70.1168 | FALSE | FALSE | -0.51215 | -0.73579 | -2.2077 | -3.0526 | 0 |  |  | none | FALSE | 0 | 69.6047 | FALSE | FALSE | 0.0831 |  | 70.9646 | 0 | 0 | -0.09891 | 0.13829 | 0.71522 | 0.67997 | Normal | 72.3245 | -1.2468 | Night | 202601 | 2026-01-03 | 1.2468
2026-01-03 01:33 | 70.1168 | FALSE | FALSE | -0.55133 | -0.79253 | -2.0491 | -2.8394 | 0 |  |  | none | FALSE | 0 | 69.5655 | FALSE | FALSE | 0.0768 |  | 70.8657 | 0 | 0 | -0.09891 | 0.13829 | 0.71522 | 0.65011 | Normal | 72.1659 | -1.1519 | Night | 202601 | 2026-01-03 | 1.1519
2026-01-03 01:48 | 69.836 | FALSE | FALSE | -0.325 | -0.46755 | -2.1585 | -2.9981 | -0.2808 |  |  | none | FALSE | 0 | 69.511 | FALSE | FALSE | 0.0984 |  | 70.7527 | 0 | -0.2808 | -0.11295 | 0.14193 | -1.1826 | 0.62087 | Normal | 71.9945 | -1.4765 | Night | 202601 | 2026-01-03 | 1.4765
2026-01-03 02:03 | 69.836 | FALSE | FALSE | -0.38264 | -0.55092 | -2.0185 | -2.8091 | 0 |  |  | none | FALSE | 0 | 69.4534 | FALSE | FALSE | 0.0908 |  | 70.6539 | 0 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.60028 | Normal | 71.8545 | -1.3626 | Night | 202601 | 2026-01-03 | 1.3626
2026-01-03 02:18 | 69.836 | FALSE | FALSE | -0.40273 | -0.58003 | -1.8409 | -2.5684 | 0 |  |  | none | FALSE | 0 | 69.4333 | FALSE | FALSE | 0.0855 |  | 70.5551 | 0 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.56092 | Normal | 71.6769 | -1.282 | Night | 202601 | 2026-01-03 | 1.282
2026-01-03 02:33 | 69.5534 | FALSE | FALSE | -0.20556 | -0.29641 | -2.0113 | -2.8105 | -0.2826 |  |  | none | FALSE | 0 | 69.3478 | FALSE | FALSE | 0.1086 |  | 70.4563 | 0 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.55422 | Normal | 71.5647 | -1.6291 | Night | 202601 | 2026-01-03 | 1.6291
2026-01-03 02:48 | 69.5534 | FALSE | FALSE | -0.25259 | -0.36449 | -1.8607 | -2.6055 | 0 |  |  | none | FALSE | 0 | 69.3008 | FALSE | FALSE | 0.1015 |  | 70.3575 | 0 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.52833 | Normal | 71.4141 | -1.5219 | Night | 202601 | 2026-01-03 | 1.5219
2026-01-03 03:03 | 69.5534 | FALSE | FALSE | -0.30813 | -0.44499 | -1.7469 | -2.45 | 0 |  |  | none | FALSE | 0 | 69.2453 | FALSE | FALSE | 0.0933 |  | 70.2728 | 0 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.51375 | Normal | 71.3003 | -1.4002 | Night | 202601 | 2026-01-03 | 1.4002
2026-01-03 03:18 | 69.5534 | FALSE | FALSE | -0.33207 | -0.47972 | -1.6014 | -2.2506 | 0 |  |  | none | FALSE | 0 | 69.2213 | FALSE | FALSE | 0.0875 |  | 70.1881 | 0 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.48338 | Normal | 71.1548 | -1.313 | Night | 202601 | 2026-01-03 | 1.313
2026-01-03 03:33 | 69.2708 | FALSE | FALSE | -0.095036 | -0.13738 | -1.732 | -2.4393 | -0.2826 |  |  | none | FALSE | 0 | 69.1758 | FALSE | FALSE | 0.1195 |  | 70.0893 | 0 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.45675 | Normal | 71.0028 | -1.7919 | Night | 202601 | 2026-01-03 | 1.7919
2026-01-03 03:48 | 69.2708 | FALSE | FALSE | -0.15166 | -0.21942 | -1.6192 | -2.2841 | 0 |  |  | none | FALSE | 0 | 69.1191 | FALSE | FALSE | 0.1105 |  | 70.0046 | 0 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.44272 | Normal | 70.89 | -1.6574 | Night | 202601 | 2026-01-03 | 1.6574
2026-01-03 04:03 | 69.2708 | FALSE | FALSE | -0.21983 | -0.31837 | -1.5463 | -2.1834 | 0 |  |  | none | FALSE | 0 | 69.051 | FALSE | FALSE | 0.1001 |  | 69.934 | 0 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.44152 | Normal | 70.8171 | -1.5021 | Night | 202601 | 2026-01-03 | 1.5021
2026-01-03 04:18 | 69.2708 | FALSE | FALSE | -0.26386 | -0.38237 | -1.4492 | -2.0492 | 0 |  |  | none | FALSE | 0 | 69.0069 | FALSE | FALSE | 0.0923 |  | 69.8635 | 0 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.42826 | Normal | 70.72 | -1.3839 | Night | 202601 | 2026-01-03 | 1.3839
2026-01-03 04:32 | 68.9882 | FALSE | FALSE | -0.097229 | -0.14113 | -1.7066 | -2.4141 | -0.2826 |  |  | none | FALSE | 0 | 68.891 | FALSE | FALSE | 0.119 |  | 69.7929 | 0 | -0.2826 | -0.07056 | 0.12539 | -1.6911 | 0.45096 | Normal | 70.6948 | -1.7844 | Night | 202601 | 2026-01-03 | 1.7844
2026-01-03 04:47 | 68.9882 | FALSE | FALSE | -0.18857 | -0.27408 | -1.6568 | -2.3453 | 0 |  |  | none | FALSE | 0 | 68.7996 | FALSE | FALSE | 0.1061 |  | 69.7223 | 0 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.46135 | Normal | 70.645 | -1.5913 | Night | 202601 | 2026-01-03 | 1.5913
2026-01-03 05:02 | 68.9882 | FALSE | FALSE | -0.25695 | -0.37385 | -1.5841 | -2.2446 | 0 |  |  | none | FALSE | 0 | 68.7312 | FALSE | FALSE | 0.0961 |  | 69.6518 | 0 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.46026 | Normal | 70.5723 | -1.4417 | Night | 202601 | 2026-01-03 | 1.4417
2026-01-03 05:17 | 68.9882 | FALSE | FALSE | -0.30221 | -0.43999 | -1.4882 | -2.1117 | 0 |  |  | none | FALSE | 0 | 68.686 | FALSE | FALSE | 0.0883 |  | 69.5812 | 0 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.44761 | Normal | 70.4764 | -1.3248 | Night | 202601 | 2026-01-03 | 1.3248
2026-01-03 05:32 | 68.7056 | FALSE | FALSE | -0.098856 | -0.14409 | -1.6807 | -2.3878 | -0.2826 |  |  | none | FALSE | 0 | 68.6067 | FALSE | FALSE | 0.1185 |  | 69.4965 | 0 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.44489 | Normal | 70.3863 | -1.7778 | Night | 202601 | 2026-01-03 | 1.7778
2026-01-03 05:47 | 68.7056 | FALSE | FALSE | -0.18597 | -0.27141 | -1.6267 | -2.3129 | 0 |  |  | none | FALSE | 0 | 68.5196 | FALSE | FALSE | 0.106 |  | 69.426 | 0 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.45317 | Normal | 70.3323 | -1.5896 | Night | 202601 | 2026-01-03 | 1.5896
2026-01-03 06:02 | 68.7056 | FALSE | FALSE | -0.24978 | -0.36488 | -1.5494 | -2.2054 | 0 |  |  | none | FALSE | 0 | 68.4558 | FALSE | FALSE | 0.0963 |  | 69.3554 | 0 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.44979 | Normal | 70.255 | -1.4447 | Night | 202601 | 2026-01-03 | 1.4447
2026-01-03 06:17 | 68.7056 | FALSE | FALSE | -0.28974 | -0.4235 | -1.4482 | -2.0643 | 0 |  |  | none | FALSE | 0 | 68.4159 | FALSE | FALSE | 0.0889 |  | 69.2848 | 0 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.43449 | Normal | 70.1538 | -1.3332 | Night | 202601 | 2026-01-03 | 1.3332
2026-01-03 06:32 | 68.7056 | FALSE | FALSE | -0.30316 | -0.44319 | -1.3205 | -1.8857 | 0 |  |  | none | FALSE | 0 | 68.4024 | FALSE | FALSE | 0.0835 |  | 69.2143 | 0 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.40592 | Normal | 70.0261 | -1.2532 | Night | 202601 | 2026-01-03 | 1.2532
2026-01-03 06:47 | 68.7056 | FALSE | FALSE | -0.33443 | -0.48914 | -1.2388 | -1.7711 | 0 |  |  | none | FALSE | 0 | 68.3712 | FALSE | FALSE | 0.0766 |  | 69.1578 | 0 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.3933 | Normal | 69.9444 | -1.1497 | Night | 202601 | 2026-01-03 | 1.1497
2026-01-03 07:02 | 68.423 | FALSE | FALSE | -0.11981 | -0.1754 | -1.448 | -2.0724 | -0.2826 |  |  | none | FALSE | 0 | 68.3032 | FALSE | FALSE | 0.113 |  | 69.0871 | 0 | -0.2826 | -0.07065 | 0.12555 | -1.6882 | 0.39196 | Normal | 69.871 | -1.6943 | Night | 202601 | 2026-01-03 | 1.6943
2026-01-03 07:17 | 68.423 | FALSE | FALSE | -0.16039 | -0.23496 | -1.3473 | -1.9311 | 0 |  |  | none | FALSE | 0 | 68.2626 | FALSE | FALSE | 0.105 |  | 69.0165 | 0 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.37692 | Normal | 69.7703 | -1.5745 | Day | 202601 | 2026-01-03 | 1.5745
2026-01-03 07:30 | 68.423 | FALSE | FALSE | -0.21691 | -0.31802 | -1.2908 | -1.8516 | 0 |  |  | none | FALSE | 0 | 68.2061 | FALSE | FALSE | 0.095 |  | 68.9599 | 0 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.37692 | Normal | 69.7138 | -1.4245 | Day | 202601 | 2026-01-03 | 1.4245
2026-01-03 07:45 | 68.423 | FALSE | FALSE | -0.25537 | -0.37462 | -1.2162 | -1.7464 | 0 |  |  | none | FALSE | 0 | 68.1676 | FALSE | FALSE | 0.0871 |  | 68.9034 | 0 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.36789 | Normal | 69.6392 | -1.3059 | Day | 202601 | 2026-01-03 | 1.3059
2026-01-03 08:00 | 68.423 | FALSE | FALSE | -0.27437 | -0.40261 | -1.1222 | -1.6136 | 0 |  |  | none | FALSE | 0 | 68.1486 | FALSE | FALSE | 0.0809 |  | 68.8469 | 0 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.34914 | Normal | 69.5452 | -1.2141 | Day | 202601 | 2026-01-03 | 1.2141
2026-01-03 08:16 | 68.423 | FALSE | FALSE | -0.27049 | -0.39689 | -1.0053 | -1.4479 | 0 |  |  | none | FALSE | 0 | 68.1525 | FALSE | FALSE | 0.0768 |  | 68.7904 | 0 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.31894 | Normal | 69.4283 | -1.1519 | Day | 202601 | 2026-01-03 | 1.1519
2026-01-03 08:30 | 68.7056 | TRUE | FALSE | -0.54051 | -0.79294 | -0.65355 | -0.94226 | 0.2826 |  |  | none | FALSE | 1 | 68.1651 | FALSE | FALSE | 0.0412 |  | 68.7621 | 0 | 0.2826 | -0.02826 | 0.12638 | 2.4597 | 0.29851 | Normal | 69.3591 | -0.18934 | Day | 202601 | 2026-01-03 | 0.18934
2026-01-03 08:45 | 68.7056 | FALSE | FALSE | -0.5188 | -0.76085 | -0.57532 | -0.83042 | 0 |  |  | none | FALSE | 1 | 68.1868 | FALSE | FALSE | 0.0355 |  | 68.7339 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.27353 | Normal | 69.2809 | -0.10332 | Day | 202601 | 2026-01-03 | 0.10332
2026-01-03 08:45 | 68.9882 | TRUE | FALSE | -0.76983 | -1.1285 | -0.23289 | -0.33644 | 0.2826 |  |  | none | FALSE | 2 | 68.2184 | TRUE | FALSE | 0.1285 |  | 68.7197 | 0 | 0.2826 | -0.01413 | 0.14424 | 2.0571 | 0.25068 | Normal | 69.2211 | 1.071 | Day | 202601 | 2026-01-03 | 1.071
2026-01-03 09:00 | 69.2708 | FALSE | FALSE | -1.0524 | -1.5427 | 0.049714 | 0.07182 | 0.2826 | 2026-01-03 11:58 | 2026-01-03 09:00 | upper | TRUE | 2 | 68.2184 | FALSE | FALSE | 0.2608 | 2.1983 | 68.7197 | 1 | 0.2826 | 0 | 0.15881 | 1.7795 | 0.25068 | Extreme triggered | 69.2211 | 2.1983 | Day | 202601 | 2026-01-03 | 2.1983
2026-01-03 09:15 | 69.5534 | FALSE | FALSE | -1.4212 | -2.0859 | 0.18967 | 0.27344 | 0.2826 |  | 2026-01-03 09:00 | upper | TRUE | 2 | 68.1322 | FALSE | FALSE | 0.3458 | 2.4072 | 68.748 | 2 | 0.2826 | 0.02826 | 0.15614 | 1.6289 | 0.30787 | Extreme/elevated | 69.3637 | 2.6161 | Day | 202601 | 2026-01-03 | 2.6161
2026-01-03 09:30 | 69.836 | FALSE | FALSE | -1.8258 | -2.6846 | 0.26547 | 0.38158 | 0.2826 |  | 2026-01-03 09:00 | upper | TRUE | 2 | 68.0102 | FALSE | TRUE | 0.4073 | 2.4983 | 68.7904 | 3 | 0.2826 | 0.04239 | 0.16593 | 1.4477 | 0.39008 | Persistent | 69.5705 | 2.6806 | Day | 202601 | 2026-01-03 | 2.6806
2026-01-03 09:44 | 70.3994 | TRUE | FALSE | -2.5989 | -3.8331 | 0.47805 | 0.68369 | 0.5634 |  | 2026-01-03 09:00 | upper | TRUE | 3 | 67.8005 | TRUE | TRUE | 0.5077 | 2.5991 | 68.8609 | 4 | 0.5634 | 0.07056 | 0.20221 | 2.4373 | 0.53021 | Persistent | 69.9214 | 2.9016 | Day | 202601 | 2026-01-03 | 2.9016
2026-01-03 09:59 | 70.3994 | FALSE | FALSE | -2.7322 | -4.0377 | 0.20362 | 0.29008 | 0 |  | 2026-01-03 09:00 | upper | TRUE | 3 | 67.6672 | FALSE | TRUE | 0.5262 | 2.5437 | 68.9315 | 5 | 0 | 0.07056 | 0.20221 | -0.34895 | 0.63214 | Persistent | 70.1958 | 2.3221 | Day | 202601 | 2026-01-03 | 2.3221
2026-01-03 10:14 | 70.9646 | TRUE | FALSE | -3.4707 | -5.1422 | 0.36962 | 0.52358 | 0.5652 |  | 2026-01-03 09:00 | upper | TRUE | 4 | 67.4939 | TRUE | TRUE | 0.6223 | 2.5326 | 69.0444 | 6 | 0.5652 | 0.11295 | 0.21286 | 2.1246 | 0.77526 | Persistent | 70.595 | 2.4768 | Day | 202601 | 2026-01-03 | 2.4768
2026-01-03 10:30 | 71.5298 | FALSE | TRUE | -4.2406 | -6.302 | 0.44772 | 0.62986 | 0.5652 |  | 2026-01-03 09:00 | upper | TRUE | 4 | 67.2892 | FALSE | TRUE | 0.6791 | 2.5239 | 69.1857 | 7 | 0.5652 | 0.14121 | 0.23359 | 1.8151 | 0.94821 | Confirmed/Materialized Shift | 71.0821 | 2.4722 | Day | 202601 | 2026-01-03 | 2.4722
2026-01-03 10:44 | 71.8124 | FALSE | TRUE | -4.6847 | -6.9789 | 0.25806 | 0.36065 | 0.2826 |  | 2026-01-03 09:00 | upper | TRUE | 3 | 67.1277 | FALSE | TRUE | 0.6346 | 2.4876 | 69.341 | 8 | 0.2826 | 0.15534 | 0.23314 | 0.54585 | 1.1067 | Confirmed/Materialized Shift | 71.5543 | 2.2332 | Day | 202601 | 2026-01-03 | 2.2332
2026-01-03 10:59 | 72.095 | FALSE | TRUE | -5.0925 | -7.6004 | 0.076602 | 0.10636 | 0.2826 |  | 2026-01-03 09:00 | upper | TRUE | 3 | 67.0025 | FALSE | TRUE | 0.6231 | 2.4402 | 69.5105 | 9 | 0.2826 | 0.16947 | 0.23179 | 0.48807 | 1.254 | Confirmed/Materialized Shift | 72.0184 | 2.0611 | Day | 202601 | 2026-01-03 | 2.0611
2026-01-03 11:14 | 72.3758 | FALSE | TRUE | -5.4639 | -8.1658 | -0.10026 | -0.13834 | 0.2808 |  | 2026-01-03 09:00 | none | FALSE | 2 | 66.9119 | FALSE | FALSE | 0.5857 | 2.389 | 69.694 | 10 | 0.2808 | 0.18351 | 0.22948 | 0.42396 | 1.391 | Confirmed/Materialized Shift | 72.4761 | 1.9279 | Day | 202601 | 2026-01-03 | 1.9279
2026-01-03 11:24 | 72.3758 | FALSE | TRUE | -5.4827 | -8.1962 | -0.48609 | -0.66714 | 0 |  | 2026-01-03 09:00 | none | FALSE | 2 | 66.8931 | FALSE | FALSE | 0.5688 | 2.324 | 69.8775 | 11 | 0 | 0.18351 | 0.22948 | -0.79968 | 1.4922 | Confirmed/Materialized Shift | 72.8619 | 1.6742 | Day | 202601 | 2026-01-03 | 1.6742
2026-01-03 11:25 | 72.6584 | FALSE | TRUE | -5.7157 | -8.5381 | -0.57737 | -0.78838 | 0.2826 |  | 2026-01-03 09:00 | none | FALSE | 2 | 66.9427 | FALSE | FALSE | 0.566 | 2.2664 | 70.0893 | 12 | 0.2826 | 0.21177 | 0.20224 | 0.35022 | 1.5733 | Confirmed/Materialized Shift | 73.2358 | 1.633 | Day | 202601 | 2026-01-03 | 1.633
2026-01-03 11:27 | 72.941 | FALSE | TRUE | -5.9142 | -8.8236 | -0.66251 | -0.90011 | 0.2826 |  | 2026-01-03 09:00 | none | FALSE | 2 | 67.0268 | FALSE | FALSE | 0.5636 | 2.2149 | 70.3152 | 13 | 0.2826 | 0.2259 | 0.19646 | 0.28861 | 1.6442 | Confirmed/Materialized Shift | 73.6035 | 1.5971 | Day | 202601 | 2026-01-03 | 1.5971
2026-01-03 11:42 | 72.6584 | TRUE | TRUE | -5.4521 | -8.1125 | -1.1892 | -1.6103 | -0.2826 |  | 2026-01-03 09:00 | none | FALSE | 2 | 67.2063 | TRUE | FALSE | 0.5427 | 2.1484 | 70.5269 | 14 | -0.2826 | 0.21177 | 0.22206 | -2.2263 | 1.6603 | Confirmed/Materialized Shift | 73.8476 | 1.2838 | Day | 202601 | 2026-01-03 | 1.2838
2026-01-03 11:58 | 72.095 | TRUE | FALSE | -4.6203 | -6.8474 | -1.8513 | -2.5036 | -0.5634 |  |  | none | FALSE | 3 | 67.4747 | TRUE | FALSE | 0.1428 |  | 70.7105 | 0 | -0.5634 | 0.1836 | 0.27882 | -2.6792 | 1.6179 | Persistence ends | 73.9463 | 0.85572 | Day | 202601 | 2026-01-03 | 0.85572
2026-01-03 12:13 | 72.095 | FALSE | FALSE | -4.3042 | -6.3492 | -1.9024 | -2.5709 | 0 |  |  | none | FALSE | 2 | 67.7908 | FALSE | FALSE | 0.1087 |  | 70.8941 | 0 | 0 | 0.1836 | 0.27882 | -0.6585 | 1.5516 | Normal | 73.9974 | 0.77393 | Day | 202601 | 2026-01-03 | 0.77393
2026-01-03 12:24 | 72.095 | FALSE | FALSE | -3.9339 | -5.7714 | -1.8993 | -2.5668 | 0 |  |  | none | FALSE | 2 | 68.1611 | FALSE | FALSE | 0.1036 |  | 71.0777 | 0 | 0 | 0.1836 | 0.27882 | -0.6585 | 1.4583 | Normal | 73.9943 | 0.69757 | Day | 202601 | 2026-01-03 | 0.69757
2026-01-03 12:31 | 71.8124 | FALSE | FALSE | -3.2874 | -4.7974 | -2.1288 | -2.879 | -0.2826 |  |  | none | FALSE | 2 | 68.525 | FALSE | FALSE | 0.0857 |  | 71.2331 | 0 | -0.2826 | 0.15534 | 0.29635 | -1.4778 | 1.3541 | Normal | 73.9412 | 0.42785 | Day | 202601 | 2026-01-03 | 0.42785
2026-01-03 12:46 | 72.6584 | FALSE | FALSE | -3.7281 | -5.4086 | -1.2728 | -1.7216 | 0.846 |  |  | none | FALSE | 2 | 68.9303 | FALSE | FALSE | 0.1226 |  | 71.4307 | 0 | 0.846 | 0.19764 | 0.33132 | 1.9569 | 1.2502 | Normal | 73.9312 | 0.98197 | Day | 202601 | 2026-01-03 | 0.98197
2026-01-03 13:01 | 73.2236 | FALSE | FALSE | -3.923 | -5.6608 | -0.76072 | -1.0282 | 0.5652 |  |  | none | FALSE | 2 | 69.3006 | FALSE | FALSE | 0.1472 |  | 71.6425 | 0 | 0.5652 | 0.21177 | 0.34102 | 1.0364 | 1.1709 | Normal | 73.9843 | 1.3503 | Day | 202601 | 2026-01-03 | 1.3503
2026-01-03 13:16 | 73.5062 | FALSE | FALSE | -3.8525 | -5.5309 | -0.5486 | -0.74081 | 0.2826 |  |  | none | FALSE | 2 | 69.6537 | FALSE | FALSE | 0.1572 |  | 71.8542 | 0 | 0.2826 | 0.21177 | 0.34102 | 0.2077 | 1.1003 | Normal | 74.0548 | 1.5014 | Day | 202601 | 2026-01-03 | 1.5014
2026-01-03 13:24 | 73.5062 | FALSE | FALSE | -3.4885 | -4.9823 | -0.57989 | -0.78273 | 0 |  |  | none | FALSE | 2 | 70.0177 | FALSE | FALSE | 0.1525 |  | 72.0519 | 0 | 0 | 0.19764 | 0.34377 | -0.57491 | 1.0171 | Normal | 74.0861 | 1.4299 | Day | 202601 | 2026-01-03 | 1.4299
2026-01-03 13:39 | 73.2236 | FALSE | FALSE | -2.8113 | -3.9927 | -0.80667 | -1.0897 | -0.2826 |  |  | none | FALSE | 2 | 70.4123 | FALSE | FALSE | 0.131 |  | 72.2213 | 0 | -0.2826 | 0.16938 | 0.3593 | -1.2579 | 0.9045 | Normal | 74.0303 | 1.1082 | Day | 202601 | 2026-01-03 | 1.1082
2026-01-03 13:54 | 73.2236 | FALSE | FALSE | -2.5047 | -3.5417 | -0.78243 | -1.0573 | 0 |  |  | none | FALSE | 1 | 70.7189 | FALSE | FALSE | 0.0984 |  | 72.3625 | 0 | 0 | 0.14121 | 0.34871 | -0.40494 | 0.82178 | Normal | 74.006 | 1.0479 | Day | 202601 | 2026-01-03 | 1.0479
2026-01-03 14:09 | 73.2236 | FALSE | FALSE | -2.1207 | -2.9825 | -0.68084 | -0.92125 | 0 |  |  | none | FALSE | 0 | 71.1029 | FALSE | FALSE | 0.0685 |  | 72.5037 | 0 | 0 | 0.14121 | 0.34871 | -0.40494 | 0.70038 | Normal | 73.9044 | 1.0279 | Day | 202601 | 2026-01-03 | 1.0279
2026-01-03 14:24 | 73.2236 | FALSE | FALSE | -1.8394 | -2.5767 | -0.62544 | -0.84692 | 0 |  |  | none | FALSE | 0 | 71.3842 | FALSE | FALSE | 0.0657 |  | 72.6166 | 0 | 0 | 0.11295 | 0.33519 | -0.33698 | 0.6162 | Normal | 73.849 | 0.98501 | Day | 202601 | 2026-01-03 | 0.98501
2026-01-03 14:39 | 73.2236 | FALSE | FALSE | -1.6701 | -2.334 | -0.62555 | -0.84706 | 0 |  |  | none | FALSE | 0 | 71.5535 | FALSE | FALSE | 0.0607 |  | 72.7013 | 0 | 0 | 0.08469 | 0.31846 | -0.26594 | 0.57391 | Normal | 73.8491 | 0.91002 | Day | 202601 | 2026-01-03 | 0.91002
2026-01-03 14:42 | 73.2236 | FALSE | FALSE | -1.5415 | -2.1504 | -0.63806 | -0.86386 | 0 |  |  | none | FALSE | 0 | 71.6821 | FALSE | FALSE | 0.0553 |  | 72.7719 | 0 | 0 | 0.07056 | 0.31547 | -0.22367 | 0.54488 | Normal | 73.8617 | 0.829 | Day | 202601 | 2026-01-03 | 0.829
2026-01-03 14:43 | 73.2236 | FALSE | FALSE | -1.4539 | -2.0258 | -0.66334 | -0.89778 | 0 |  |  | none | FALSE | 0 | 71.7697 | FALSE | FALSE | 0.0498 |  | 72.8283 | 0 | 0 | 0.05643 | 0.31178 | -0.18099 | 0.52931 | Normal | 73.8869 | 0.74678 | Day | 202601 | 2026-01-03 | 0.74678
2026-01-03 14:45 | 73.2236 | FALSE | FALSE | -1.4031 | -1.9536 | -0.6973 | -0.94331 | 0 |  |  | none | FALSE | 0 | 71.8205 | FALSE | FALSE | 0.0448 |  | 72.8707 | 0 | 0 | 0.04239 | 0.30744 | -0.13788 | 0.5251 | Normal | 73.9209 | 0.67205 | Day | 202601 | 2026-01-03 | 0.67205
2026-01-03 15:01 | 72.3758 | TRUE | FALSE | -0.55528 | -0.77315 | -1.5451 | -2.0902 | -0.8478 |  |  | none | FALSE | 1 | 71.8205 | FALSE | FALSE | 0.0914 |  | 72.8707 | 0 | -0.8478 | 0 | 0.36639 | -2.314 | 0.5251 | Normal | 73.9209 | -0.94251 | Day | 202601 | 2026-01-03 | 0.94251
2026-01-03 15:16 | 71.8124 | FALSE | FALSE | -0.13363 | -0.18643 | -2.1656 | -2.9274 | -0.5634 |  |  | none | FALSE | 1 | 71.6788 | FALSE | FALSE | 0.1464 |  | 72.8284 | 0 | -0.5634 | -0.0423 | 0.3806 | -1.3691 | 0.57482 | Normal | 73.978 | -1.7675 | Day | 202601 | 2026-01-03 | 1.7675
2026-01-03 15:17 | 71.8124 | FALSE | FALSE | -0.27448 | -0.38369 | -2.1936 | -2.9641 | 0 |  |  | none | FALSE | 1 | 71.5379 | FALSE | FALSE | 0.1322 |  | 72.772 | 0 | 0 | -0.05643 | 0.37308 | 0.15126 | 0.61703 | Normal | 74.006 | -1.5552 | Day | 202601 | 2026-01-03 | 1.5552
2026-01-03 15:29 | 72.941 | TRUE | FALSE | -1.39 | -1.9426 | -1.0802 | -1.4593 | 1.1286 |  |  | none | FALSE | 2 | 71.551 | TRUE | FALSE | 0.0739 |  | 72.7861 | 0 | 1.1286 | 0.01413 | 0.45295 | 2.4605 | 0.61753 | Normal | 74.0212 | 0.25082 | Day | 202601 | 2026-01-03 | 0.25082
2026-01-03 15:42 | 73.2236 | FALSE | FALSE | -1.5859 | -2.2138 | -0.82381 | -1.1125 | 0.2826 |  |  | none | FALSE | 2 | 71.6377 | FALSE | FALSE | 0.0993 |  | 72.8425 | 0 | 0.2826 | 0.05643 | 0.43534 | 0.51953 | 0.60243 | Normal | 74.0474 | 0.63253 | Day | 202601 | 2026-01-03 | 0.63253
2026-01-03 15:57 | 73.7888 | FALSE | FALSE | -2.0832 | -2.9052 | -0.36005 | -0.48558 | 0.5652 |  |  | none | FALSE | 2 | 71.7056 | FALSE | FALSE | 0.1512 |  | 72.9272 | 0 | 0.5652 | 0.08469 | 0.44959 | 1.0688 | 0.61081 | Normal | 74.1489 | 1.4105 | Day | 202601 | 2026-01-03 | 1.4105
2026-01-03 16:08 | 74.0714 | FALSE | FALSE | -2.3027 | -3.2086 | -0.21205 | -0.28545 | 0.2826 |  |  | none | FALSE | 2 | 71.7687 | FALSE | FALSE | 0.168 |  | 73.026 | 0 | 0.2826 | 0.09882 | 0.45123 | 0.40729 | 0.6287 | Normal | 74.2834 | 1.6627 | Day | 202601 | 2026-01-03 | 1.6627
2026-01-03 16:11 | 73.7888 | FALSE | FALSE | -1.8268 | -2.5386 | -0.49896 | -0.67166 | -0.2826 |  |  | none | FALSE | 2 | 71.962 | FALSE | FALSE | 0.1333 |  | 73.1249 | 0 | -0.2826 | 0.09882 | 0.45123 | -0.84529 | 0.58145 | Normal | 74.2878 | 1.1419 | Day | 202601 | 2026-01-03 | 1.1419
2026-01-03 16:26 | 73.2236 | FALSE | FALSE | -1.2129 | -1.6844 | -1.072 | -1.4429 | -0.5652 |  |  | none | FALSE | 2 | 72.0107 | FALSE | FALSE | 0.0654 |  | 73.1531 | 0 | -0.5652 | 0.02826 | 0.4384 | -1.3537 | 0.57123 | Normal | 74.2956 | 0.12337 | Day | 202601 | 2026-01-03 | 0.12337
2026-01-03 16:41 | 72.095 | TRUE | FALSE | -0.2338 | -0.32535 | -2.2372 | -3.0097 | -1.1286 |  |  | none | FALSE | 3 | 71.8612 | TRUE | FALSE | 0.1938 |  | 73.0967 | 0 | -1.1286 | -0.05643 | 0.4898 | -2.189 | 0.61775 | Normal | 74.3322 | -1.6215 | Day | 202601 | 2026-01-03 | 1.6215
2026-01-03 16:42 | 72.095 | FALSE | FALSE | -0.36556 | -0.50964 | -2.2278 | -2.9975 | 0 |  |  | none | FALSE | 2 | 71.7294 | FALSE | FALSE | 0.1529 |  | 73.0261 | 0 | 0 | -0.07056 | 0.48354 | 0.14592 | 0.64835 | Normal | 74.3228 | -1.4362 | Day | 202601 | 2026-01-03 | 1.4362
2026-01-03 16:57 | 72.095 | FALSE | FALSE | -0.479 | -0.66885 | -2.2002 | -2.9614 | 0 |  |  | none | FALSE | 2 | 71.616 | FALSE | FALSE | 0.1428 |  | 72.9556 | 0 | 0 | -0.07056 | 0.48354 | 0.14592 | 0.66979 | Normal | 74.2952 | -1.2848 | Day | 202601 | 2026-01-03 | 1.2848
2026-01-03 17:12 | 72.095 | FALSE | FALSE | -0.58216 | -0.81407 | -2.1905 | -2.9487 | 0 |  |  | none | FALSE | 2 | 71.5128 | FALSE | FALSE | 0.1345 |  | 72.8992 | 0 | 0 | -0.05643 | 0.48114 | 0.11728 | 0.69316 | Normal | 74.2855 | -1.1601 | Day | 202601 | 2026-01-03 | 1.1601
2026-01-03 17:27 | 72.095 | FALSE | FALSE | -0.6744 | -0.94427 | -2.1698 | -2.9218 | 0 |  |  | none | FALSE | 1 | 71.4206 | FALSE | FALSE | 0.0987 |  | 72.8427 | 0 | 0 | -0.05643 | 0.48114 | 0.11728 | 0.71106 | Normal | 74.2648 | -1.0516 | Day | 202601 | 2026-01-03 | 1.0516
2026-01-03 17:42 | 72.095 | FALSE | FALSE | -0.75653 | -1.0605 | -2.1391 | -2.8816 | 0 |  |  | none | FALSE | 1 | 71.3385 | FALSE | FALSE | 0.0922 |  | 72.7863 | 0 | 0 | -0.05643 | 0.48114 | 0.11728 | 0.72391 | Normal | 74.2341 | -0.95494 | Night | 202601 | 2026-01-03 | 0.95494
2026-01-03 17:42 | 72.095 | FALSE | FALSE | -0.82908 | -1.1634 | -2.0988 | -2.8288 | 0 |  |  | none | FALSE | 1 | 71.2659 | FALSE | FALSE | 0.0864 |  | 72.7299 | 0 | 0 | -0.05643 | 0.48114 | 0.11728 | 0.73197 | Normal | 74.1938 | -0.86733 | Night | 202601 | 2026-01-03 | 0.86733
2026-01-03 17:42 | 72.095 | FALSE | FALSE | -0.89237 | -1.2533 | -2.0492 | -2.7638 | 0 |  |  | none | FALSE | 1 | 71.2026 | FALSE | FALSE | 0.081 |  | 72.6734 | 0 | 0 | -0.05643 | 0.48114 | 0.11728 | 0.7354 | Normal | 74.1442 | -0.78655 | Night | 202601 | 2026-01-03 | 0.78655
2026-01-03 17:57 | 72.941 | FALSE | FALSE | -1.7356 | -2.4374 | -1.1722 | -1.5816 | 0.846 |  |  | none | FALSE | 1 | 71.2054 | FALSE | FALSE | 0.0544 |  | 72.6593 | 0 | 0.846 | -0.01413 | 0.52183 | 1.6483 | 0.72694 | Normal | 74.1132 | 0.38752 | Night | 202601 | 2026-01-03 | 0.38752
2026-01-03 18:12 | 72.941 | FALSE | FALSE | -1.732 | -2.4323 | -1.1403 | -1.5393 | 0 |  |  | none | FALSE | 1 | 71.209 | FALSE | FALSE | 0.056 |  | 72.6452 | 0 | 0 | -0.01413 | 0.52183 | 0.027078 | 0.71808 | Normal | 74.0813 | 0.41197 | Night | 202601 | 2026-01-03 | 0.41197
2026-01-03 18:27 | 73.2236 | FALSE | FALSE | -2.0146 | -2.8291 | -0.85774 | -1.1578 | 0.2826 |  |  | none | FALSE | 0 | 71.209 | FALSE | FALSE | 0.0537 |  | 72.6452 | 0 | 0.2826 | 0 | 0.52604 | 0.53722 | 0.71808 | Normal | 74.0813 | 0.80552 | Night | 202601 | 2026-01-03 | 0.80552
2026-01-03 18:41 | 73.2236 | FALSE | FALSE | -1.9887 | -2.7917 | -0.91661 | -1.2363 | 0 |  |  | none | FALSE | 0 | 71.2349 | FALSE | FALSE | 0.0492 |  | 72.6876 | 0 | 0 | 0.04239 | 0.48683 | -0.087074 | 0.72632 | Normal | 74.1402 | 0.73802 | Night | 202601 | 2026-01-03 | 0.73802
2026-01-03 18:56 | 73.2236 | FALSE | FALSE | -1.8756 | -2.6288 | -0.94465 | -1.2737 | 0 |  |  | none | FALSE | 0 | 71.348 | FALSE | FALSE | 0.044 |  | 72.7581 | 0 | 0 | 0.07056 | 0.46577 | -0.15149 | 0.70506 | Normal | 74.1682 | 0.66019 | Night | 202601 | 2026-01-03 | 0.66019
2026-01-03 19:11 | 73.2236 | FALSE | FALSE | -1.7458 | -2.4424 | -0.95594 | -1.2887 | 0 |  |  | none | FALSE | 0 | 71.4778 | FALSE | FALSE | 0.039 |  | 72.8287 | 0 | 0 | 0.07056 | 0.46577 | -0.15149 | 0.67543 | Normal | 74.1795 | 0.58469 | Night | 202601 | 2026-01-03 | 0.58469
2026-01-03 19:26 | 73.2236 | FALSE | FALSE | -1.7425 | -2.4377 | -0.98089 | -1.3219 | 0 |  |  | none | FALSE | 0 | 71.4811 | FALSE | FALSE | 0.0373 |  | 72.8428 | 0 | 0 | 0.01413 | 0.39362 | -0.035897 | 0.68084 | Normal | 74.2045 | 0.5593 | Night | 202601 | 2026-01-03 | 0.5593
2026-01-03 19:41 | 73.2236 | FALSE | FALSE | -1.7425 | -2.4377 | -0.98089 | -1.3219 | 0 |  |  | none | FALSE | 0 | 71.4811 | FALSE | FALSE | 0.0373 |  | 72.8428 | 0 | 0 | 0 | 0.38852 | 0 | 0.68084 | Normal | 74.2045 | 0.5593 | Night | 202601 | 2026-01-03 | 0.5593
2026-01-03 19:56 | 72.941 | FALSE | FALSE | -1.4291 | -1.9984 | -1.1479 | -1.5494 | -0.2826 |  |  | none | FALSE | 0 | 71.5119 | FALSE | FALSE | 0.0145 |  | 72.8004 | 0 | -0.2826 | -0.04239 | 0.36938 | -0.6503 | 0.64425 | Normal | 74.0889 | 0.21821 | Night | 202601 | 2026-01-03 | 0.21821
2026-01-03 20:11 | 72.941 | FALSE | FALSE | -1.342 | -1.8744 | -0.94783 | -1.2828 | 0 |  |  | none | FALSE | 0 | 71.599 | FALSE | FALSE | 0.023 |  | 72.7439 | 0 | 0 | -0.05652 | 0.36162 | 0.1563 | 0.57246 | Normal | 73.8888 | 0.3443 | Night | 202601 | 2026-01-03 | 0.3443
2026-01-03 20:26 | 72.941 | FALSE | FALSE | -1.2795 | -1.7855 | -0.80052 | -1.0856 | 0 |  |  | none | FALSE | 0 | 71.6615 | FALSE | FALSE | 0.0307 |  | 72.7015 | 0 | 0 | -0.04239 | 0.35782 | 0.11847 | 0.52 | Normal | 73.7415 | 0.46056 | Night | 202601 | 2026-01-03 | 0.46056
2026-01-03 20:41 | 72.941 | FALSE | FALSE | -1.2712 | -1.7737 | -0.76396 | -1.0365 | 0 |  |  | none | FALSE | 0 | 71.6698 | FALSE | FALSE | 0.0332 |  | 72.6874 | 0 | 0 | -0.01413 | 0.33601 | 0.042052 | 0.50879 | Normal | 73.705 | 0.49848 | Night | 202601 | 2026-01-03 | 0.49848
2026-01-03 20:56 | 72.941 | FALSE | FALSE | -1.195 | -1.6656 | -0.77234 | -1.0478 | 0 |  |  | none | FALSE | 0 | 71.746 | FALSE | FALSE | 0.0286 |  | 72.7297 | 0 | 0 | 0.0423 | 0.21022 | -0.20122 | 0.49183 | Normal | 73.7133 | 0.42966 | Night | 202601 | 2026-01-03 | 0.42966
2026-01-03 21:11 | 72.941 | FALSE | FALSE | -1.1096 | -1.5447 | -0.77154 | -1.0467 | 0 |  |  | none | FALSE | 0 | 71.8314 | FALSE | FALSE | 0.024 |  | 72.772 | 0 | 0 | 0.0423 | 0.21022 | -0.20122 | 0.47028 | Normal | 73.7125 | 0.3594 | Night | 202601 | 2026-01-03 | 0.3594
2026-01-03 21:26 | 72.941 | FALSE | FALSE | -1.0137 | -1.4093 | -0.76021 | -1.0315 | 0 |  |  | none | FALSE | 0 | 71.9273 | FALSE | FALSE | 0.019 |  | 72.8143 | 0 | 0 | 0.0423 | 0.21022 | -0.20122 | 0.44347 | Normal | 73.7012 | 0.28575 | Night | 202601 | 2026-01-03 | 0.28575
2026-01-03 21:40 | 72.941 | FALSE | FALSE | -0.90514 | -1.2565 | -0.7363 | -0.99936 | 0 |  |  | none | FALSE | 0 | 72.0359 | FALSE | FALSE | 0.0137 |  | 72.8566 | 0 | 0 | 0.0423 | 0.21022 | -0.20122 | 0.41036 | Normal | 73.6773 | 0.20572 | Night | 202601 | 2026-01-03 | 0.20572
2026-01-03 21:55 | 72.941 | FALSE | FALSE | -0.78066 | -1.0818 | -0.69642 | -0.94574 | 0 |  |  | none | FALSE | 0 | 72.1603 | FALSE | FALSE | 0.0076 |  | 72.8989 | 0 | 0 | 0.0423 | 0.21022 | -0.20122 | 0.36927 | Normal | 73.6374 | 0.11406 | Night | 202601 | 2026-01-03 | 0.11406
2026-01-03 22:10 | 72.6584 | FALSE | FALSE | -0.37805 | -0.52304 | -0.91535 | -1.2441 | -0.2826 |  |  | none | FALSE | 0 | 72.2803 | FALSE | FALSE | 0.0554 |  | 72.927 | 0 | -0.2826 | 0.02817 | 0.22236 | -1.3976 | 0.32335 | Normal | 73.5738 | -0.83083 | Night | 202601 | 2026-01-03 | 0.83083
2026-01-03 22:25 | 72.941 | FALSE | FALSE | -0.48642 | -0.67134 | -0.54312 | -0.73909 | 0.2826 |  |  | none | FALSE | 0 | 72.4546 | FALSE | FALSE | 0.0073 |  | 72.9694 | 0 | 0.2826 | 0.0423 | 0.22934 | 1.0478 | 0.25738 | Normal | 73.4841 | -0.11015 | Night | 202601 | 2026-01-03 | 0.11015
2026-01-03 22:40 | 72.6584 | FALSE | FALSE | -0.0088098 | -0.012126 | -0.68705 | -0.93673 | -0.2826 |  |  | none | FALSE | 0 | 72.6496 | FALSE | FALSE | 0.13 |  | 72.9975 | 0 | -0.2826 | 0.02817 | 0.24052 | -1.2921 | 0.17396 | Normal | 73.3454 | -1.9494 | Night | 202601 | 2026-01-03 | 1.9494
2026-01-03 22:55 | 72.6584 | FALSE | FALSE | -0.054158 | -0.074593 | -0.70414 | -0.95981 | 0 |  |  | none | FALSE | 0 | 72.6042 | FALSE | FALSE | 0.1143 |  | 72.9834 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.18957 | Normal | 73.3625 | -1.7143 | Night | 202601 | 2026-01-03 | 1.7143
2026-01-03 23:10 | 72.6584 | FALSE | FALSE | -0.095058 | -0.131 | -0.71678 | -0.97687 | 0 |  |  | none | FALSE | 0 | 72.5633 | FALSE | FALSE | 0.1021 |  | 72.9693 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.20296 | Normal | 73.3752 | -1.5316 | Night | 202601 | 2026-01-03 | 1.5316
2026-01-03 23:25 | 72.6584 | FALSE | FALSE | -0.12744 | -0.1757 | -0.69264 | -0.94428 | 0 |  |  | none | FALSE | 0 | 72.531 | FALSE | FALSE | 0.0919 |  | 72.941 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.20502 | Normal | 73.351 | -1.3784 | Night | 202601 | 2026-01-03 | 1.3784
2026-01-03 23:40 | 72.6584 | FALSE | FALSE | -0.15158 | -0.20905 | -0.66026 | -0.90053 | 0 |  |  | none | FALSE | 0 | 72.5068 | FALSE | FALSE | 0.0835 |  | 72.9127 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.20296 | Normal | 73.3187 | -1.2532 | Night | 202601 | 2026-01-03 | 1.2532
2026-01-03 23:55 | 72.6584 | FALSE | FALSE | -0.16722 | -0.23067 | -0.61938 | -0.84524 | 0 |  |  | none | FALSE | 0 | 72.4912 | FALSE | FALSE | 0.0766 |  | 72.8845 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.19665 | Normal | 73.2778 | -1.1497 | Night | 202601 | 2026-01-03 | 1.1497
2026-01-04 00:10 | 72.6584 | FALSE | FALSE | -0.17349 | -0.23934 | -0.56913 | -0.7772 | 0 |  |  | none | FALSE | 0 | 72.4849 | FALSE | FALSE | 0.071 |  | 72.8562 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.18565 | Normal | 73.2275 | -1.0655 | Night | 202601 | 2026-01-04 | 1.0655
2026-01-04 00:25 | 72.6584 | FALSE | FALSE | -0.16857 | -0.23254 | -0.50769 | -0.69388 | 0 |  |  | none | FALSE | 0 | 72.4898 | FALSE | FALSE | 0.0669 |  | 72.828 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.16906 | Normal | 73.1661 | -1.0029 | Night | 202601 | 2026-01-04 | 1.0029
2026-01-04 00:39 | 72.6584 | FALSE | FALSE | -0.14864 | -0.205 | -0.43124 | -0.59002 | 0 |  |  | none | FALSE | 0 | 72.5098 | FALSE | FALSE | 0.065 |  | 72.7997 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.14497 | Normal | 73.0896 | -0.97468 | Night | 202601 | 2026-01-04 | 0.97468
2026-01-04 00:54 | 72.3758 | TRUE | FALSE | 0.057513 | 0.079401 | -0.73377 | -1.0037 | -0.2826 | 2026-01-04 04:09 | 2026-01-04 00:54 | lower | TRUE | 1 | 72.4333 | FALSE | FALSE | 0.2417 | 2.3402 | 72.7714 | 1 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.16906 | Extreme triggered | 73.1096 | -2.3402 | Night | 202601 | 2026-01-04 | 2.3402
2026-01-04 01:10 | 72.3758 | FALSE | FALSE | -0.0039263 | -0.0054251 | -0.73869 | -1.0103 | 0 |  | 2026-01-04 00:54 | none | FALSE | 1 | 72.3719 | FALSE | FALSE | 0.2748 | 2.1595 | 72.7432 | 2 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.18565 | Extreme/elevated | 73.1145 | -1.9789 | Night | 202601 | 2026-01-04 | 1.9789
2026-01-04 01:25 | 72.3758 | FALSE | FALSE | -0.054176 | -0.074909 | -0.73242 | -1.0018 | 0 |  | 2026-01-04 00:54 | none | FALSE | 1 | 72.3216 | FALSE | FALSE | 0.315 | 2.0145 | 72.7149 | 3 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.19665 | Persistent | 73.1082 | -1.7245 | Night | 202601 | 2026-01-04 | 1.7245
2026-01-04 01:39 | 72.3758 | FALSE | FALSE | -0.095058 | -0.13151 | -0.71678 | -0.98064 | 0 |  | 2026-01-04 00:54 | none | FALSE | 1 | 72.2807 | FALSE | FALSE | 0.3593 | 1.8938 | 72.6867 | 4 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.20296 | Persistent | 73.0926 | -1.5316 | Night | 202601 | 2026-01-04 | 1.5316
2026-01-04 01:54 | 72.3758 | FALSE | FALSE | -0.12744 | -0.17639 | -0.69264 | -0.94793 | 0 |  | 2026-01-04 00:54 | none | FALSE | 1 | 72.2484 | FALSE | FALSE | 0.4062 | 1.7907 | 72.6584 | 5 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.20502 | Persistent | 73.0684 | -1.3784 | Night | 202601 | 2026-01-04 | 1.3784
2026-01-04 02:09 | 72.095 | FALSE | FALSE | 0.062177 | 0.086169 | -0.98002 | -1.3411 | -0.2808 |  | 2026-01-04 00:54 | lower | TRUE | 1 | 72.1572 | FALSE | TRUE | 0.5228 | 1.8708 | 72.6161 | 6 | -0.2808 | -0.0423 | 0.13813 | -1.7266 | 0.22946 | Persistent | 73.075 | -2.271 | Night | 202601 | 2026-01-04 | 2.271
2026-01-04 02:24 | 72.095 | FALSE | TRUE | -0.0090736 | -0.012587 | -0.96667 | -1.3231 | 0 |  | 2026-01-04 00:54 | none | FALSE | 1 | 72.0859 | FALSE | FALSE | 0.5594 | 1.8839 | 72.5738 | 7 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.24394 | Confirmed/Materialized Shift | 73.0617 | -1.9628 | Night | 202601 | 2026-01-04 | 1.9628
2026-01-04 02:39 | 72.095 | FALSE | TRUE | -0.063863 | -0.088661 | -0.93686 | -1.2828 | 0 |  | 2026-01-04 00:54 | none | FALSE | 1 | 72.0311 | FALSE | FALSE | 0.5449 | 1.8665 | 72.5315 | 8 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.25018 | Confirmed/Materialized Shift | 73.0319 | -1.7447 | Night | 202601 | 2026-01-04 | 1.7447
2026-01-04 02:54 | 72.095 | FALSE | TRUE | -0.10343 | -0.14367 | -0.89183 | -1.2219 | 0 |  | 2026-01-04 00:54 | none | FALSE | 1 | 71.9916 | FALSE | FALSE | 0.5342 | 1.8352 | 72.4892 | 9 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.24882 | Confirmed/Materialized Shift | 72.9868 | -1.5843 | Night | 202601 | 2026-01-04 | 1.5843
2026-01-04 03:09 | 72.095 | FALSE | TRUE | -0.15453 | -0.2148 | -0.88659 | -1.2148 | 0 |  | 2026-01-04 00:54 | none | FALSE | 1 | 71.9405 | FALSE | FALSE | 0.5223 | 1.7923 | 72.461 | 10 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.26028 | Confirmed/Materialized Shift | 72.9816 | -1.4063 | Night | 202601 | 2026-01-04 | 1.4063
2026-01-04 03:24 | 72.095 | FALSE | TRUE | -0.16938 | -0.23549 | -0.81684 | -1.1203 | 0 |  | 2026-01-04 00:54 | none | FALSE | 0 | 71.9256 | FALSE | FALSE | 0.4875 | 1.7487 | 72.4187 | 11 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.24655 | Confirmed/Materialized Shift | 72.9118 | -1.313 | Night | 202601 | 2026-01-04 | 1.313
2026-01-04 03:39 | 72.095 | FALSE | TRUE | -0.20423 | -0.28408 | -0.79535 | -1.0912 | 0 |  | 2026-01-04 00:54 | none | FALSE | 0 | 71.8908 | FALSE | FALSE | 0.4788 | 1.7015 | 72.3906 | 12 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.24989 | Confirmed/Materialized Shift | 72.8903 | -1.1827 | Night | 202601 | 2026-01-04 | 1.1827
2026-01-04 03:54 | 72.095 | FALSE | TRUE | -0.23234 | -0.32332 | -0.76712 | -1.0528 | 0 |  | 2026-01-04 00:54 | none | FALSE | 0 | 71.8627 | FALSE | FALSE | 0.4713 | 1.653 | 72.3624 | 13 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.24987 | Confirmed/Materialized Shift | 72.8621 | -1.0701 | Night | 202601 | 2026-01-04 | 1.0701
2026-01-04 04:09 | 72.095 | FALSE | FALSE | -0.25373 | -0.35318 | -0.73217 | -1.0053 | 0 |  |  | none | FALSE | 0 | 71.8413 | FALSE | FALSE | 0.0647 |  | 72.3342 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.24647 | Persistence ends | 72.8272 | -0.97057 | Night | 202601 | 2026-01-04 | 0.97057
2026-01-04 04:24 | 72.095 | FALSE | FALSE | -0.26809 | -0.37325 | -0.69019 | -0.94826 | 0 |  |  | none | FALSE | 0 | 71.8269 | FALSE | FALSE | 0.0587 |  | 72.306 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.23957 | Normal | 72.7852 | -0.88095 | Night | 202601 | 2026-01-04 | 0.88095
2026-01-04 04:38 | 71.8124 | TRUE | FALSE | -0.045853 | -0.063892 | -0.94855 | -1.3037 | -0.2826 |  |  | none | FALSE | 1 | 71.7665 | FALSE | FALSE | 0.1496 |  | 72.2638 | 0 | -0.2826 | -0.0423 | 0.10331 | -2.326 | 0.2486 | Normal | 72.761 | -1.8156 | Night | 202601 | 2026-01-04 | 1.8156
2026-01-04 04:53 | 71.8124 | FALSE | FALSE | -0.090726 | -0.1265 | -0.90883 | -1.2497 | 0 |  |  | none | FALSE | 1 | 71.7217 | FALSE | FALSE | 0.1377 |  | 72.2215 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.24989 | Normal | 72.7212 | -1.6369 | Night | 202601 | 2026-01-04 | 1.6369
2026-01-04 05:08 | 71.8124 | FALSE | FALSE | -0.12036 | -0.16788 | -0.85386 | -1.175 | 0 |  |  | none | FALSE | 1 | 71.692 | FALSE | FALSE | 0.129 |  | 72.1792 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.24355 | Normal | 72.6663 | -1.5058 | Night | 202601 | 2026-01-04 | 1.5058
2026-01-04 05:23 | 71.8124 | FALSE | FALSE | -0.13348 | -0.18622 | -0.78238 | -1.0777 | 0 |  |  | none | FALSE | 1 | 71.6789 | FALSE | FALSE | 0.123 |  | 72.1368 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.22897 | Normal | 72.5948 | -1.417 | Night | 202601 | 2026-01-04 | 1.417
2026-01-04 05:38 | 71.8124 | FALSE | FALSE | -0.12658 | -0.17658 | -0.69088 | -0.9529 | 0 |  |  | none | FALSE | 1 | 71.6858 | FALSE | FALSE | 0.1206 |  | 72.0945 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.20437 | Normal | 72.5033 | -1.3806 | Night | 202601 | 2026-01-04 | 1.3806
2026-01-04 05:53 | 71.8124 | FALSE | FALSE | -0.15078 | -0.2104 | -0.65874 | -0.90897 | 0 |  |  | none | FALSE | 1 | 71.6616 | FALSE | FALSE | 0.1122 |  | 72.0664 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.20238 | Normal | 72.4711 | -1.255 | Night | 202601 | 2026-01-04 | 1.255
2026-01-04 06:08 | 71.8124 | FALSE | FALSE | -0.16651 | -0.2324 | -0.61813 | -0.85341 | 0 |  |  | none | FALSE | 1 | 71.6459 | FALSE | FALSE | 0.1053 |  | 72.0382 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.19616 | Normal | 72.4305 | -1.1512 | Night | 202601 | 2026-01-04 | 1.1512
2026-01-04 06:23 | 71.8124 | FALSE | FALSE | -0.17292 | -0.24137 | -0.5682 | -0.78501 | 0 |  |  | none | FALSE | 1 | 71.6395 | FALSE | FALSE | 0.0997 |  | 72.01 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.18528 | Normal | 72.3806 | -1.0667 | Night | 202601 | 2026-01-04 | 1.0667
2026-01-04 06:38 | 71.8124 | FALSE | FALSE | -0.16821 | -0.23479 | -0.50715 | -0.70127 | 0 |  |  | none | FALSE | 1 | 71.6442 | FALSE | FALSE | 0.0955 |  | 71.9819 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.16884 | Normal | 72.3196 | -1.0037 | Night | 202601 | 2026-01-04 | 1.0037
2026-01-04 06:53 | 71.5298 | TRUE | FALSE | 0.067934 | 0.094883 | -0.75161 | -1.0398 | -0.2826 | 2026-01-04 08:37 | 2026-01-04 06:53 | lower | TRUE | 2 | 71.5977 | TRUE | FALSE | 0.2741 | 2.3975 | 71.9396 | 1 | -0.2826 | -0.0423 | 0.10331 | -2.326 | 0.17092 | Extreme triggered | 72.2814 | -2.3975 | Night | 202601 | 2026-01-04 | 2.3975
2026-01-04 07:08 | 71.5298 | FALSE | FALSE | 0.0023623 | 0.0033024 | -0.76066 | -1.0522 | 0 |  | 2026-01-04 06:53 | lower | TRUE | 1 | 71.5322 | FALSE | FALSE | 0.277 | 2.205 | 71.9113 | 2 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18957 | Extreme/elevated | 72.2905 | -2.0125 | Night | 202601 | 2026-01-04 | 2.0125
2026-01-04 07:23 | 71.5298 | FALSE | FALSE | -0.051631 | -0.072234 | -0.75813 | -1.0488 | 0 |  | 2026-01-04 06:53 | none | FALSE | 1 | 71.4782 | FALSE | FALSE | 0.3163 | 2.0516 | 71.883 | 3 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.20244 | Persistent | 72.2879 | -1.745 | Day | 202601 | 2026-01-04 | 1.745
2026-01-04 07:37 | 71.5298 | FALSE | FALSE | -0.096174 | -0.13463 | -0.74615 | -1.0324 | 0 |  | 2026-01-04 06:53 | none | FALSE | 1 | 71.4336 | FALSE | FALSE | 0.36 | 1.9245 | 71.8548 | 4 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21058 | Persistent | 72.276 | -1.5433 | Day | 202601 | 2026-01-04 | 1.5433
2026-01-04 07:52 | 71.5298 | FALSE | FALSE | -0.13234 | -0.18536 | -0.7258 | -1.0045 | 0 |  | 2026-01-04 06:53 | none | FALSE | 1 | 71.3975 | FALSE | FALSE | 0.4065 | 1.8163 | 71.8265 | 5 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21454 | Persistent | 72.2556 | -1.3831 | Day | 202601 | 2026-01-04 | 1.3831
2026-01-04 08:07 | 71.5298 | FALSE | FALSE | -0.1606 | -0.22503 | -0.69754 | -0.96576 | 0 |  | 2026-01-04 06:53 | none | FALSE | 1 | 71.3692 | FALSE | FALSE | 0.4549 | 1.7221 | 71.7983 | 6 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21454 | Persistent | 72.2273 | -1.2514 | Day | 202601 | 2026-01-04 | 1.2514
2026-01-04 08:22 | 71.5298 | FALSE | TRUE | -0.18095 | -0.25362 | -0.66137 | -0.91614 | 0 |  | 2026-01-04 06:53 | none | FALSE | 1 | 71.3488 | FALSE | FALSE | 0.5046 | 1.6391 | 71.77 | 7 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21058 | Confirmed/Materialized Shift | 72.1912 | -1.1407 | Day | 202601 | 2026-01-04 | 1.1407
2026-01-04 08:37 | 71.5298 | FALSE | TRUE | -0.19293 | -0.27045 | -0.61683 | -0.85497 | 0 |  | 2026-01-04 06:53 | none | FALSE | 1 | 71.3369 | FALSE | FALSE | 0.4984 | 1.565 | 71.7417 | 8 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.20244 | Confirmed/Materialized Shift | 72.1466 | -1.047 | Day | 202601 | 2026-01-04 | 1.047
2026-01-04 08:37 | 71.8124 | TRUE | FALSE | -0.45609 | -0.63917 | -0.28653 | -0.39741 | 0.2826 |  |  | none | FALSE | 2 | 71.3563 | TRUE | FALSE | 0.0876 |  | 71.7276 | 0 | 0.2826 | -0.01413 | 0.11135 | 2.6647 | 0.18565 | Persistence ends | 72.0989 | 0.45666 | Day | 202601 | 2026-01-04 | 0.45666
2026-01-04 08:52 | 71.8124 | FALSE | FALSE | -0.43076 | -0.60346 | -0.23294 | -0.32333 | 0 |  |  | none | FALSE | 2 | 71.3816 | FALSE | FALSE | 0.0969 |  | 71.7135 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.16593 | Normal | 72.0453 | 0.59611 | Day | 202601 | 2026-01-04 | 0.59611
2026-01-04 09:07 | 71.8124 | FALSE | FALSE | -0.39712 | -0.55608 | -0.17104 | -0.23762 | 0 |  |  | none | FALSE | 1 | 71.4153 | FALSE | FALSE | 0.0816 |  | 71.6994 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14204 | Normal | 71.9834 | 0.79582 | Day | 202601 | 2026-01-04 | 0.79582
2026-01-04 09:23 | 71.8124 | FALSE | FALSE | -0.39712 | -0.55608 | -0.17104 | -0.23762 | 0 |  |  | none | FALSE | 1 | 71.4153 | FALSE | FALSE | 0.0816 |  | 71.6994 | 0 | 0 | 0 | 0.091688 | 0 | 0.14204 | Normal | 71.9834 | 0.79582 | Day | 202601 | 2026-01-04 | 0.79582
2026-01-04 09:30 | 71.8124 | FALSE | FALSE | -0.39712 | -0.55608 | -0.17104 | -0.23762 | 0 |  |  | none | FALSE | 1 | 71.4153 | FALSE | FALSE | 0.0816 |  | 71.6994 | 0 | 0 | 0 | 0.091688 | 0 | 0.14204 | Normal | 71.9834 | 0.79582 | Day | 202601 | 2026-01-04 | 0.79582
2026-01-04 09:45 | 71.8124 | FALSE | FALSE | -0.39712 | -0.55608 | -0.17104 | -0.23762 | 0 |  |  | none | FALSE | 1 | 71.4153 | FALSE | FALSE | 0.0816 |  | 71.6994 | 0 | 0 | 0 | 0.091688 | 0 | 0.14204 | Normal | 71.9834 | 0.79582 | Day | 202601 | 2026-01-04 | 0.79582
2026-01-04 10:00 | 72.095 | TRUE | FALSE | -0.71336 | -0.99937 | 0.049657 | 0.068924 | 0.2826 | 2026-01-04 13:23 | 2026-01-04 10:00 | upper | TRUE | 2 | 71.3816 | TRUE | FALSE | 0.2676 | 2.2993 | 71.7135 | 1 | 0.2826 | 0.01413 | 0.11135 | 2.411 | 0.16593 | Extreme triggered | 72.0453 | 2.2993 | Day | 202601 | 2026-01-04 | 2.2993
2026-01-04 10:15 | 72.3758 | TRUE | FALSE | -1.0781 | -1.5121 | 0.19021 | 0.2635 | 0.2808 |  | 2026-01-04 10:00 | upper | TRUE | 3 | 71.2977 | TRUE | FALSE | 0.3905 | 2.5781 | 71.7417 | 2 | 0.2808 | 0.02817 | 0.12619 | 2.0019 | 0.22197 | Extreme/elevated | 72.1856 | 2.8569 | Day | 202601 | 2026-01-04 | 2.8569
2026-01-04 10:30 | 72.6584 | FALSE | FALSE | -1.4789 | -2.0778 | 0.26994 | 0.37291 | 0.2826 |  | 2026-01-04 10:00 | upper | TRUE | 3 | 71.1795 | FALSE | TRUE | 0.45 | 2.6831 | 71.784 | 3 | 0.2826 | 0.0423 | 0.13813 | 1.7397 | 0.30225 | Persistent | 72.3885 | 2.8931 | Day | 202601 | 2026-01-04 | 2.8931
2026-01-04 10:45 | 72.941 | FALSE | FALSE | -1.8966 | -2.6697 | 0.30457 | 0.41931 | 0.2826 |  | 2026-01-04 10:00 | upper | TRUE | 3 | 71.0444 | FALSE | TRUE | 0.4986 | 2.7036 | 71.8404 | 4 | 0.2826 | 0.05643 | 0.1477 | 1.5313 | 0.39802 | Persistent | 72.6364 | 2.7652 | Day | 202601 | 2026-01-04 | 2.7652
2026-01-04 11:00 | 73.2236 | FALSE | FALSE | -2.3203 | -3.2725 | 0.30501 | 0.41828 | 0.2826 |  | 2026-01-04 10:00 | upper | TRUE | 2 | 70.9033 | FALSE | TRUE | 0.5165 | 2.684 | 71.9109 | 5 | 0.2826 | 0.07056 | 0.15534 | 1.365 | 0.50382 | Persistent | 72.9186 | 2.6054 | Day | 202601 | 2026-01-04 | 2.6054
2026-01-04 11:15 | 73.5062 | FALSE | FALSE | -2.743 | -3.8763 | 0.27814 | 0.37983 | 0.2826 |  | 2026-01-04 10:00 | upper | TRUE | 2 | 70.7632 | FALSE | TRUE | 0.5634 | 2.6452 | 71.9956 | 6 | 0.2826 | 0.08469 | 0.16132 | 1.2268 | 0.61621 | Persistent | 73.2281 | 2.4514 | Day | 202601 | 2026-01-04 | 2.4514
2026-01-04 11:29 | 73.5062 | FALSE | TRUE | -2.7946 | -3.9522 | 0.028835 | 0.039244 | 0 |  | 2026-01-04 10:00 | upper | TRUE | 2 | 70.7116 | FALSE | TRUE | 0.5933 | 2.559 | 72.0945 | 7 | 0 | 0.09882 | 0.13817 | -0.71522 | 0.69145 | Confirmed/Materialized Shift | 73.4774 | 2.0417 | Day | 202601 | 2026-01-04 | 2.0417
2026-01-04 11:44 | 73.5062 | FALSE | TRUE | -2.8041 | -3.9661 | -0.17831 | -0.24199 | 0 |  | 2026-01-04 10:00 | none | FALSE | 2 | 70.7021 | FALSE | FALSE | 0.5745 | 2.4592 | 72.1933 | 8 | 0 | 0.09882 | 0.13817 | -0.71522 | 0.74561 | Confirmed/Materialized Shift | 73.6845 | 1.7609 | Day | 202601 | 2026-01-04 | 1.7609
2026-01-04 11:59 | 73.5062 | FALSE | TRUE | -2.7803 | -3.931 | -0.35206 | -0.47667 | 0 |  | 2026-01-04 10:00 | none | FALSE | 2 | 70.7259 | FALSE | FALSE | 0.5605 | 2.3583 | 72.2921 | 9 | 0 | 0.09882 | 0.13817 | -0.71522 | 0.78308 | Confirmed/Materialized Shift | 73.8583 | 1.5504 | Day | 202601 | 2026-01-04 | 1.5504
2026-01-04 12:15 | 73.5062 | FALSE | TRUE | -2.7277 | -3.8538 | -0.49709 | -0.67171 | 0 |  | 2026-01-04 10:00 | none | FALSE | 2 | 70.7785 | FALSE | FALSE | 0.5494 | 2.2608 | 72.3909 | 10 | 0 | 0.09882 | 0.13817 | -0.71522 | 0.80619 | Confirmed/Materialized Shift | 74.0033 | 1.3834 | Day | 202601 | 2026-01-04 | 1.3834
2026-01-04 12:29 | 73.5062 | FALSE | TRUE | -2.6488 | -3.7381 | -0.61583 | -0.83083 | 0 |  | 2026-01-04 10:00 | none | FALSE | 1 | 70.8574 | FALSE | FALSE | 0.5116 | 2.1685 | 72.4897 | 11 | 0 | 0.09882 | 0.13817 | -0.71522 | 0.81615 | Confirmed/Materialized Shift | 74.122 | 1.2454 | Day | 202601 | 2026-01-04 | 1.2454
2026-01-04 12:44 | 73.7888 | FALSE | TRUE | -2.851 | -4.019 | -0.4788 | -0.6447 | 0.2826 |  | 2026-01-04 10:00 | none | FALSE | 0 | 70.9378 | FALSE | FALSE | 0.495 | 2.1065 | 72.6027 | 12 | 0.2826 | 0.11295 | 0.14193 | 1.1953 | 0.83246 | Confirmed/Materialized Shift | 74.2676 | 1.4248 | Day | 202601 | 2026-01-04 | 1.4248
2026-01-04 12:59 | 73.7888 | FALSE | TRUE | -2.7381 | -3.8537 | -0.59179 | -0.79563 | 0 |  | 2026-01-04 10:00 | none | FALSE | 0 | 71.0507 | FALSE | FALSE | 0.4859 | 2.0436 | 72.7156 | 13 | 0 | 0.11295 | 0.14193 | -0.79582 | 0.83248 | Confirmed/Materialized Shift | 74.3806 | 1.2891 | Day | 202601 | 2026-01-04 | 1.2891
2026-01-04 13:05 | 74.0714 | FALSE | TRUE | -2.9005 | -4.0754 | -0.44314 | -0.5947 | 0.2826 |  | 2026-01-04 10:00 | none | FALSE | 0 | 71.1709 | FALSE | FALSE | 0.498 | 2.0026 | 72.8427 | 14 | 0.2826 | 0.12708 | 0.14414 | 1.0789 | 0.83591 | Confirmed/Materialized Shift | 74.5145 | 1.4699 | Day | 202601 | 2026-01-04 | 1.4699
2026-01-04 13:08 | 74.0714 | FALSE | TRUE | -2.7997 | -3.9281 | -0.5682 | -0.76125 | 0 |  | 2026-01-04 10:00 | none | FALSE | 0 | 71.2717 | FALSE | FALSE | 0.4883 | 1.9575 | 72.9557 | 15 | 0 | 0.11295 | 0.14193 | -0.79582 | 0.84196 | Confirmed/Materialized Shift | 74.6396 | 1.3252 | Day | 202601 | 2026-01-04 | 1.3252
2026-01-04 13:23 | 73.7888 | TRUE | FALSE | -2.3669 | -3.314 | -0.89831 | -1.2028 | -0.2826 |  |  | none | FALSE | 1 | 71.4219 | FALSE | FALSE | 0.0885 |  | 73.0545 | 0 | -0.2826 | 0.09882 | 0.16582 | -2.3002 | 0.81631 | Persistence ends | 74.6871 | 0.89955 | Day | 202601 | 2026-01-04 | 0.89955
2026-01-04 13:29 | 73.5062 | FALSE | FALSE | -1.9011 | -2.655 | -1.1671 | -1.5629 | -0.2826 |  |  | none | FALSE | 1 | 71.6051 | FALSE | FALSE | 0.0605 |  | 73.1392 | 0 | -0.2826 | 0.08469 | 0.18555 | -1.9794 | 0.76704 | Normal | 74.6733 | 0.47849 | Day | 202601 | 2026-01-04 | 0.47849
2026-01-04 13:29 | 73.5062 | FALSE | FALSE | -1.6898 | -2.3529 | -1.1251 | -1.5076 | 0 |  |  | none | FALSE | 1 | 71.8164 | FALSE | FALSE | 0.0553 |  | 73.2239 | 0 | 0 | 0.08469 | 0.18555 | -0.45642 | 0.70373 | Normal | 74.6313 | 0.40119 | Day | 202601 | 2026-01-04 | 0.40119
2026-01-04 13:44 | 73.5062 | FALSE | FALSE | -1.4419 | -2.0008 | -1.0466 | -1.4038 | 0 |  |  | none | FALSE | 1 | 72.0643 | FALSE | FALSE | 0.0498 |  | 73.3086 | 0 | 0 | 0.08469 | 0.18555 | -0.45642 | 0.62212 | Normal | 74.5528 | 0.31769 | Day | 202601 | 2026-01-04 | 0.31769
2026-01-04 13:59 | 73.2236 | FALSE | FALSE | -0.87279 | -1.2063 | -1.1838 | -1.591 | -0.2826 |  |  | none | FALSE | 1 | 72.3508 | FALSE | FALSE | 0.0487 |  | 73.3791 | 0 | -0.2826 | 0.07056 | 0.20234 | -1.7454 | 0.51415 | Normal | 74.4074 | -0.30248 | Day | 202601 | 2026-01-04 | 0.30248
2026-01-04 14:14 | 72.941 | FALSE | FALSE | -0.38164 | -0.52597 | -1.3425 | -1.8072 | -0.2826 |  |  | none | FALSE | 1 | 72.5594 | FALSE | FALSE | 0.1029 |  | 73.4214 | 0 | -0.2826 | 0.0423 | 0.21047 | -1.5437 | 0.43103 | Normal | 74.2835 | -1.1146 | Day | 202601 | 2026-01-04 | 1.1146
2026-01-04 14:29 | 72.3758 | TRUE | FALSE | 0.18356 | 0.25298 | -1.9077 | -2.5681 | -0.5652 | 2026-01-04 15:59 | 2026-01-04 14:29 | lower | TRUE | 2 | 72.5594 | TRUE | FALSE | 0.276 | 2.4259 | 73.4214 | 1 | -0.5652 | 0 | 0.24258 | -2.3299 | 0.43103 | Extreme triggered | 74.2835 | -2.4259 | Day | 202601 | 2026-01-04 | 2.4259
2026-01-04 14:44 | 72.3758 | FALSE | FALSE | 0.10959 | 0.15118 | -1.9534 | -2.628 | 0 |  | 2026-01-04 14:29 | lower | TRUE | 2 | 72.4854 | FALSE | FALSE | 0.3206 | 2.3318 | 73.4073 | 2 | 0 | -0.01413 | 0.23331 | 0.060564 | 0.46095 | Extreme/elevated | 74.3292 | -2.2377 | Day | 202601 | 2026-01-04 | 2.2377
2026-01-04 14:59 | 72.095 | FALSE | FALSE | 0.19335 | 0.26747 | -2.3466 | -3.1523 | -0.2808 |  | 2026-01-04 14:29 | lower | TRUE | 2 | 72.2884 | FALSE | TRUE | 0.3858 | 2.3409 | 73.365 | 3 | -0.2808 | -0.0423 | 0.22958 | -1.0389 | 0.53832 | Persistent | 74.4416 | -2.3592 | Day | 202601 | 2026-01-04 | 2.3592
2026-01-04 15:14 | 72.095 | FALSE | FALSE | -0.0034382 | -0.0047692 | -2.4306 | -3.2614 | 0 |  | 2026-01-04 14:29 | none | FALSE | 2 | 72.0916 | FALSE | FALSE | 0.4187 | 2.2543 | 73.3086 | 4 | 0 | -0.05643 | 0.21687 | 0.2602 | 0.6085 | Persistent | 74.5256 | -1.9943 | Day | 202601 | 2026-01-04 | 1.9943
2026-01-04 15:29 | 72.3758 | FALSE | FALSE | -0.40539 | -0.56327 | -2.1579 | -2.8952 | 0.2808 |  | 2026-01-04 14:29 | none | FALSE | 1 | 71.9704 | FALSE | FALSE | 0.4054 | 2.0769 | 73.252 | 5 | 0.2808 | -0.05652 | 0.21673 | 1.5564 | 0.64082 | Persistent | 74.5337 | -1.3674 | Day | 202601 | 2026-01-04 | 1.3674
2026-01-04 15:44 | 72.3758 | FALSE | FALSE | -0.51338 | -0.7144 | -2.1528 | -2.8886 | 0 |  | 2026-01-04 14:29 | none | FALSE | 1 | 71.8624 | FALSE | FALSE | 0.4534 | 1.9357 | 73.1955 | 6 | 0 | -0.05652 | 0.21673 | 0.26079 | 0.66655 | Persistent | 74.5286 | -1.2298 | Day | 202601 | 2026-01-04 | 1.2298
2026-01-04 15:59 | 72.941 | TRUE | FALSE | -1.1031 | -1.5355 | -1.5556 | -2.0881 | 0.5652 |  |  | none | FALSE | 2 | 71.8379 | TRUE | FALSE | 0.0798 |  | 73.1673 | 0 | 0.5652 | -0.02826 | 0.2575 | 2.3047 | 0.66467 | Persistence ends | 74.4966 | -0.34041 | Day | 202601 | 2026-01-04 | 0.34041
2026-01-04 16:14 | 72.941 | FALSE | FALSE | -1.125 | -1.5665 | -1.521 | -2.0427 | 0 |  |  | none | FALSE | 2 | 71.816 | FALSE | FALSE | 0.0771 |  | 73.139 | 0 | 0 | -0.02826 | 0.2575 | 0.10975 | 0.6615 | Normal | 74.462 | -0.29932 | Day | 202601 | 2026-01-04 | 0.29932
2026-01-04 16:28 | 72.941 | FALSE | FALSE | -1.1444 | -1.5939 | -1.4838 | -1.9937 | 0 |  |  | none | FALSE | 2 | 71.7966 | FALSE | FALSE | 0.0744 |  | 73.1107 | 0 | 0 | -0.02826 | 0.2575 | 0.10975 | 0.65705 | Normal | 74.4248 | -0.25834 | Day | 202601 | 2026-01-04 | 0.25834
2026-01-04 16:43 | 72.941 | FALSE | FALSE | -1.1611 | -1.6175 | -1.444 | -1.9413 | 0 |  |  | none | FALSE | 2 | 71.7799 | FALSE | FALSE | 0.0716 |  | 73.0825 | 0 | 0 | -0.02826 | 0.2575 | 0.10975 | 0.65127 | Normal | 74.385 | -0.21724 | Day | 202601 | 2026-01-04 | 0.21724
2026-01-04 16:58 | 72.941 | FALSE | FALSE | -1.1612 | -1.6177 | -1.3594 | -1.8295 | 0 |  |  | none | FALSE | 1 | 71.7798 | FALSE | FALSE | 0.0391 |  | 73.0401 | 0 | 0 | -0.04239 | 0.24709 | 0.17156 | 0.63013 | Normal | 74.3004 | -0.15725 | Day | 202601 | 2026-01-04 | 0.15725
2026-01-04 17:13 | 72.6584 | FALSE | FALSE | -0.89445 | -1.2464 | -1.5448 | -2.0818 | -0.2826 |  |  | none | FALSE | 1 | 71.764 | FALSE | FALSE | 0.0641 |  | 72.9836 | 0 | -0.2826 | -0.05652 | 0.25255 | -0.89518 | 0.60981 | Normal | 74.2032 | -0.53323 | Day | 202601 | 2026-01-04 | 0.53323
2026-01-04 17:28 | 72.6584 | FALSE | FALSE | -0.85884 | -1.1962 | -1.3679 | -1.8478 | 0 |  |  | none | FALSE | 1 | 71.7996 | FALSE | FALSE | 0.0591 |  | 72.9129 | 0 | 0 | -0.07065 | 0.24018 | 0.29415 | 0.55668 | Normal | 74.0263 | -0.45721 | Day | 202601 | 2026-01-04 | 0.45721
2026-01-04 17:43 | 72.3758 | FALSE | FALSE | -0.54139 | -0.75367 | -1.4461 | -1.9589 | -0.2826 |  |  | none | FALSE | 1 | 71.8344 | FALSE | FALSE | 0.0893 |  | 72.8281 | 0 | -0.2826 | -0.08478 | 0.24409 | -0.81044 | 0.49687 | Normal | 73.8219 | -0.91039 | Night | 202601 | 2026-01-04 | 0.91039
2026-01-04 17:43 | 72.3758 | FALSE | FALSE | -0.52124 | -0.7254 | -1.2846 | -1.744 | 0 |  |  | none | FALSE | 1 | 71.8546 | FALSE | FALSE | 0.0849 |  | 72.7575 | 0 | 0 | -0.07065 | 0.24018 | 0.29415 | 0.45146 | Normal | 73.6604 | -0.84545 | Night | 202601 | 2026-01-04 | 0.84545
2026-01-04 17:44 | 72.3758 | FALSE | FALSE | -0.5201 | -0.72381 | -1.1704 | -1.5914 | 0 |  |  | none | FALSE | 1 | 71.8557 | FALSE | FALSE | 0.0799 |  | 72.701 | 0 | 0 | -0.05652 | 0.23532 | 0.24018 | 0.42264 | Normal | 73.5462 | -0.76939 | Night | 202601 | 2026-01-04 | 0.76939
2026-01-04 17:59 | 73.2236 | TRUE | FALSE | -1.3334 | -1.8548 | -0.25988 | -0.35366 | 0.8478 |  |  | none | FALSE | 1 | 71.8902 | FALSE | FALSE | 0.1184 |  | 72.6868 | 0 | 0.8478 | -0.01413 | 0.31042 | 2.7767 | 0.39832 | Normal | 73.4835 | 1.3476 | Night | 202601 | 2026-01-04 | 1.3476
2026-01-04 18:14 | 73.2236 | FALSE | FALSE | -1.2946 | -1.7998 | -0.19283 | -0.26265 | 0 |  |  | none | FALSE | 1 | 71.929 | FALSE | FALSE | 0.1273 |  | 72.6727 | 0 | 0 | -0.01413 | 0.31042 | 0.045519 | 0.37186 | Normal | 73.4164 | 1.4814 | Night | 202601 | 2026-01-04 | 1.4814
2026-01-04 18:29 | 73.5062 | FALSE | FALSE | -1.616 | -2.2479 | 0.022716 | 0.030914 | 0.2826 | 2026-01-04 19:28 | 2026-01-04 18:29 | upper | TRUE | 1 | 71.8902 | FALSE | FALSE | 0.2228 | 2.057 | 72.6868 | 1 | 0.2826 | 0.01413 | 0.31042 | 0.86487 | 0.39832 | Extreme triggered | 73.4835 | 2.057 | Night | 202601 | 2026-01-04 | 2.057
2026-01-04 18:43 | 73.2236 | FALSE | FALSE | -1.3478 | -1.8751 | -0.30251 | -0.41143 | -0.2826 |  | 2026-01-04 18:29 | none | FALSE | 1 | 71.8758 | FALSE | FALSE | 0.2273 | 1.6619 | 72.701 | 2 | -0.2826 | 0.01413 | 0.31042 | -0.95591 | 0.41257 | Extreme/elevated | 73.5261 | 1.2668 | Night | 202601 | 2026-01-04 | 1.2668
2026-01-04 18:58 | 73.2236 | FALSE | FALSE | -1.322 | -1.8386 | -0.3615 | -0.49127 | 0 |  | 2026-01-04 18:29 | none | FALSE | 1 | 71.9016 | FALSE | FALSE | 0.2761 | 1.4883 | 72.7434 | 3 | 0 | 0.04239 | 0.27904 | -0.15191 | 0.42087 | Persistent | 73.5851 | 1.1411 | Night | 202601 | 2026-01-04 | 1.1411
2026-01-04 19:13 | 73.2236 | FALSE | FALSE | -1.287 | -1.7891 | -0.41131 | -0.55859 | 0 |  | 2026-01-04 18:29 | none | FALSE | 1 | 71.9366 | FALSE | FALSE | 0.3259 | 1.374 | 72.7857 | 4 | 0 | 0.04239 | 0.27904 | -0.15191 | 0.42458 | Persistent | 73.6349 | 1.0312 | Night | 202601 | 2026-01-04 | 1.0312
2026-01-04 19:28 | 73.2236 | FALSE | FALSE | -1.1861 | -1.6466 | -0.42331 | -0.57478 | 0 |  |  | none | FALSE | 1 | 72.0375 | FALSE | FALSE | 0.0918 |  | 72.8422 | 0 | 0 | 0.05643 | 0.2688 | -0.20993 | 0.40236 | Persistence ends | 73.6469 | 0.94795 | Night | 202601 | 2026-01-04 | 0.94795
2026-01-04 19:42 | 73.2236 | FALSE | FALSE | -1.0648 | -1.4756 | -0.41479 | -0.56328 | 0 |  |  | none | FALSE | 1 | 72.1588 | FALSE | FALSE | 0.0871 |  | 72.8986 | 0 | 0 | 0.05643 | 0.2688 | -0.20993 | 0.36989 | Normal | 73.6384 | 0.87862 | Night | 202601 | 2026-01-04 | 0.87862
2026-01-04 19:57 | 73.2236 | FALSE | FALSE | -0.99281 | -1.3745 | -0.42761 | -0.58059 | 0 |  |  | none | FALSE | 1 | 72.2308 | FALSE | FALSE | 0.0816 |  | 72.941 | 0 | 0 | 0.04239 | 0.26375 | -0.16072 | 0.3551 | Normal | 73.6512 | 0.79582 | Night | 202601 | 2026-01-04 | 0.79582
2026-01-04 20:12 | 72.941 | FALSE | FALSE | -0.63036 | -0.87174 | -0.68688 | -0.93291 | -0.2826 |  |  | none | FALSE | 1 | 72.3106 | FALSE | FALSE | 0.0343 |  | 72.9693 | 0 | -0.2826 | 0.02826 | 0.27353 | -1.1365 | 0.32931 | Normal | 73.6279 | -0.085816 | Night | 202601 | 2026-01-04 | 0.085816
2026-01-04 20:27 | 72.941 | FALSE | FALSE | -0.63036 | -0.87174 | -0.68688 | -0.93291 | 0 |  |  | none | FALSE | 0 | 72.3106 | FALSE | FALSE | 0.0057 |  | 72.9693 | 0 | 0 | 0 | 0.24258 | 0 | 0.32931 | Normal | 73.6279 | -0.085816 | Night | 202601 | 2026-01-04 | 0.085816
2026-01-04 20:42 | 72.941 | FALSE | FALSE | -0.63036 | -0.87174 | -0.68688 | -0.93291 | 0 |  |  | none | FALSE | 0 | 72.3106 | FALSE | FALSE | 0.0057 |  | 72.9693 | 0 | 0 | 0 | 0.24258 | 0 | 0.32931 | Normal | 73.6279 | -0.085816 | Night | 202601 | 2026-01-04 | 0.085816
2026-01-04 20:57 | 72.941 | FALSE | FALSE | -0.63036 | -0.87174 | -0.68688 | -0.93291 | 0 |  |  | none | FALSE | 0 | 72.3106 | FALSE | FALSE | 0.0057 |  | 72.9693 | 0 | 0 | 0 | 0.24258 | 0 | 0.32931 | Normal | 73.6279 | -0.085816 | Night | 202601 | 2026-01-04 | 0.085816
2026-01-04 21:12 | 72.941 | FALSE | FALSE | -0.63036 | -0.87174 | -0.68688 | -0.93291 | 0 |  |  | none | FALSE | 0 | 72.3106 | FALSE | FALSE | 0.0057 |  | 72.9693 | 0 | 0 | 0 | 0.24258 | 0 | 0.32931 | Normal | 73.6279 | -0.085816 | Night | 202601 | 2026-01-04 | 0.085816
2026-01-04 21:27 | 72.941 | FALSE | FALSE | -0.63036 | -0.87174 | -0.68688 | -0.93291 | 0 |  |  | none | FALSE | 0 | 72.3106 | FALSE | FALSE | 0.0057 |  | 72.9693 | 0 | 0 | 0 | 0.24258 | 0 | 0.32931 | Normal | 73.6279 | -0.085816 | Night | 202601 | 2026-01-04 | 0.085816
2026-01-04 21:42 | 72.941 | FALSE | FALSE | -0.60008 | -0.82951 | -0.68486 | -0.93019 | 0 |  |  | none | FALSE | 0 | 72.3409 | FALSE | FALSE | 0.0088 |  | 72.9834 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.32123 | Normal | 73.6259 | -0.13196 | Night | 202601 | 2026-01-04 | 0.13196
2026-01-04 21:57 | 72.941 | FALSE | FALSE | -0.56803 | -0.78487 | -0.68107 | -0.92509 | 0 |  |  | none | FALSE | 0 | 72.373 | FALSE | FALSE | 0.0121 |  | 72.9975 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.31228 | Normal | 73.6221 | -0.18099 | Night | 202601 | 2026-01-04 | 0.18099
2026-01-04 22:12 | 72.6584 | FALSE | FALSE | -0.223 | -0.30786 | -0.9295 | -1.2631 | -0.2826 |  |  | none | FALSE | 0 | 72.4354 | FALSE | FALSE | 0.0817 |  | 73.0117 | 0 | -0.2826 | 0.01413 | 0.23331 | -1.2718 | 0.28812 | Normal | 73.5879 | -1.226 | Night | 202601 | 2026-01-04 | 1.226
2026-01-04 22:27 | 72.6584 | FALSE | FALSE | -0.15451 | -0.21311 | -0.88927 | -1.2091 | 0 |  |  | none | FALSE | 0 | 72.5039 | FALSE | FALSE | 0.0939 |  | 73.0258 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.26095 | Normal | 73.5477 | -1.4079 | Night | 202601 | 2026-01-04 | 1.4079
2026-01-04 22:41 | 72.6584 | FALSE | FALSE | -0.077844 | -0.10725 | -0.84086 | -1.144 | 0 |  |  | none | FALSE | 0 | 72.5806 | FALSE | FALSE | 0.1107 |  | 73.0399 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.22968 | Normal | 73.4993 | -1.6611 | Night | 202601 | 2026-01-04 | 1.6611
2026-01-04 22:56 | 72.6584 | FALSE | FALSE | -0.12756 | -0.17587 | -0.83406 | -1.1349 | 0 |  |  | none | FALSE | 0 | 72.5308 | FALSE | FALSE | 0.098 |  | 73.0117 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.24041 | Normal | 73.4925 | -1.4694 | Night | 202601 | 2026-01-04 | 1.4694
2026-01-04 23:11 | 72.6584 | FALSE | FALSE | -0.16961 | -0.23399 | -0.81959 | -1.1154 | 0 |  |  | none | FALSE | 0 | 72.4888 | FALSE | FALSE | 0.0876 |  | 72.9834 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.2473 | Normal | 73.478 | -1.3141 | Night | 202601 | 2026-01-04 | 1.3141
2026-01-04 23:27 | 72.3758 | FALSE | FALSE | 0.049714 | 0.068642 | -1.0524 | -1.4333 | -0.2826 | 2026-01-05 04:55 | 2026-01-04 23:27 | lower | TRUE | 0 | 72.4255 | FALSE | FALSE | 0.2037 | 2.1983 | 72.9269 | 1 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.25068 | Extreme triggered | 73.4282 | -2.1983 | Night | 202601 | 2026-01-04 | 2.1983
2026-01-04 23:41 | 72.3758 | FALSE | FALSE | -0.029081 | -0.040197 | -1.0464 | -1.4252 | 0 |  | 2026-01-04 23:27 | none | FALSE | 0 | 72.3467 | FALSE | FALSE | 0.2404 | 2.0451 | 72.8845 | 2 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.26888 | Extreme/elevated | 73.4222 | -1.8918 | Night | 202601 | 2026-01-04 | 1.8918
2026-01-04 23:56 | 72.3758 | FALSE | FALSE | -0.092177 | -0.12752 | -1.0248 | -1.3961 | 0 |  | 2026-01-04 23:27 | none | FALSE | 0 | 72.2836 | FALSE | FALSE | 0.2828 | 1.92 | 72.8421 | 3 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27923 | Persistent | 73.4006 | -1.6699 | Night | 202601 | 2026-01-04 | 1.6699
2026-01-05 00:11 | 72.3758 | FALSE | FALSE | -0.1413 | -0.19561 | -0.9891 | -1.3482 | 0 |  | 2026-01-04 23:27 | none | FALSE | 0 | 72.2345 | FALSE | FALSE | 0.3286 | 1.815 | 72.7997 | 4 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.2826 | Persistent | 73.3649 | -1.5 | Night | 202601 | 2026-01-05 | 1.5
2026-01-05 00:26 | 72.3758 | FALSE | FALSE | -0.17696 | -0.2451 | -0.93998 | -1.2821 | 0 |  | 2026-01-04 23:27 | none | FALSE | 0 | 72.1988 | FALSE | FALSE | 0.3768 | 1.7253 | 72.7573 | 5 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27923 | Persistent | 73.3158 | -1.3663 | Night | 202601 | 2026-01-05 | 1.3663
2026-01-05 00:41 | 72.3758 | FALSE | FALSE | -0.19864 | -0.27521 | -0.87688 | -1.1971 | 0 |  | 2026-01-04 23:27 | none | FALSE | 0 | 72.1772 | FALSE | FALSE | 0.4269 | 1.6479 | 72.7149 | 6 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.26888 | Persistent | 73.2527 | -1.2612 | Night | 202601 | 2026-01-05 | 1.2612
2026-01-05 00:56 | 72.095 | FALSE | TRUE | 0.013754 | 0.019073 | -1.1132 | -1.5206 | -0.2808 |  | 2026-01-04 23:27 | lower | TRUE | 0 | 72.1088 | FALSE | TRUE | 0.5367 | 1.7054 | 72.6585 | 7 | -0.2808 | -0.05643 | 0.11579 | -1.9377 | 0.27487 | Confirmed/Materialized Shift | 73.2082 | -2.05 | Night | 202601 | 2026-01-05 | 2.05
2026-01-05 01:11 | 72.095 | FALSE | TRUE | -0.065939 | -0.091545 | -1.1083 | -1.514 | 0 |  | 2026-01-04 23:27 | none | FALSE | 0 | 72.0291 | FALSE | FALSE | 0.5184 | 1.7141 | 72.6162 | 8 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.29356 | Confirmed/Materialized Shift | 73.2033 | -1.7754 | Night | 202601 | 2026-01-05 | 1.7754
2026-01-05 01:26 | 72.095 | FALSE | TRUE | -0.13116 | -0.18226 | -1.0889 | -1.488 | 0 |  | 2026-01-04 23:27 | none | FALSE | 0 | 71.9638 | FALSE | FALSE | 0.5047 | 1.6981 | 72.5739 | 9 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.30503 | Confirmed/Materialized Shift | 73.1839 | -1.57 | Night | 202601 | 2026-01-05 | 1.57
2026-01-05 01:40 | 72.095 | FALSE | TRUE | -0.18352 | -0.2552 | -1.0567 | -1.4445 | 0 |  | 2026-01-04 23:27 | none | FALSE | 0 | 71.9115 | FALSE | FALSE | 0.4939 | 1.6691 | 72.5316 | 10 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.31006 | Confirmed/Materialized Shift | 73.1517 | -1.4081 | Night | 202601 | 2026-01-05 | 1.4081
2026-01-05 01:55 | 72.095 | FALSE | TRUE | -0.22365 | -0.31118 | -1.0122 | -1.3846 | 0 |  | 2026-01-04 23:27 | none | FALSE | 0 | 71.8714 | FALSE | FALSE | 0.4851 | 1.6334 | 72.4893 | 11 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.30897 | Confirmed/Materialized Shift | 73.1072 | -1.2762 | Night | 202601 | 2026-01-05 | 1.2762
2026-01-05 02:11 | 72.095 | FALSE | TRUE | -0.2514 | -0.34993 | -0.95538 | -1.3078 | 0 |  | 2026-01-04 23:27 | none | FALSE | 0 | 71.8436 | FALSE | FALSE | 0.4778 | 1.5945 | 72.447 | 12 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.3017 | Confirmed/Materialized Shift | 73.0504 | -1.1667 | Night | 202601 | 2026-01-05 | 1.1667
2026-01-05 02:26 | 72.095 | FALSE | TRUE | -0.26586 | -0.37013 | -0.88524 | -1.213 | 0 |  | 2026-01-04 23:27 | none | FALSE | 0 | 71.8291 | FALSE | FALSE | 0.4717 | 1.5546 | 72.4047 | 13 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.28777 | Confirmed/Materialized Shift | 72.9802 | -1.0762 | Night | 202601 | 2026-01-05 | 1.0762
2026-01-05 02:40 | 71.8124 | FALSE | TRUE | -0.039595 | -0.055167 | -1.1113 | -1.5239 | -0.2826 |  | 2026-01-04 23:27 | none | FALSE | 0 | 71.7728 | FALSE | FALSE | 0.5242 | 1.5766 | 72.3483 | 14 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.28773 | Confirmed/Materialized Shift | 72.9237 | -1.8624 | Night | 202601 | 2026-01-05 | 1.8624
2026-01-05 02:55 | 71.8124 | FALSE | TRUE | -0.072137 | -0.10055 | -1.031 | -1.4154 | 0 |  | 2026-01-04 23:27 | none | FALSE | 0 | 71.7403 | FALSE | FALSE | 0.5159 | 1.5874 | 72.2918 | 15 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.27578 | Confirmed/Materialized Shift | 72.8434 | -1.7384 | Night | 202601 | 2026-01-05 | 1.7384
2026-01-05 03:10 | 71.8124 | FALSE | TRUE | -0.12571 | -0.17537 | -0.99997 | -1.3734 | 0 |  | 2026-01-04 23:27 | none | FALSE | 0 | 71.6867 | FALSE | FALSE | 0.5036 | 1.5853 | 72.2495 | 16 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.28142 | Confirmed/Materialized Shift | 72.8124 | -1.5533 | Night | 202601 | 2026-01-05 | 1.5533
2026-01-05 03:25 | 71.8124 | FALSE | TRUE | -0.16579 | -0.2314 | -0.95545 | -1.313 | 0 |  | 2026-01-04 23:27 | none | FALSE | 0 | 71.6466 | FALSE | FALSE | 0.4939 | 1.5749 | 72.2072 | 17 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.28031 | Confirmed/Materialized Shift | 72.7678 | -1.4086 | Night | 202601 | 2026-01-05 | 1.4086
2026-01-05 03:40 | 71.8124 | FALSE | TRUE | -0.19219 | -0.26835 | -0.89725 | -1.234 | 0 |  | 2026-01-04 23:27 | none | FALSE | 0 | 71.6202 | FALSE | FALSE | 0.4863 | 1.5593 | 72.1649 | 18 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.27236 | Confirmed/Materialized Shift | 72.7097 | -1.2943 | Night | 202601 | 2026-01-05 | 1.2943
2026-01-05 03:55 | 71.8124 | FALSE | TRUE | -0.20367 | -0.28441 | -0.82413 | -1.1346 | 0 |  | 2026-01-04 23:27 | none | FALSE | 0 | 71.6087 | FALSE | FALSE | 0.4805 | 1.5408 | 72.1226 | 19 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.25695 | Confirmed/Materialized Shift | 72.6365 | -1.2074 | Night | 202601 | 2026-01-05 | 1.2074
2026-01-05 04:10 | 71.8124 | FALSE | TRUE | -0.19724 | -0.27542 | -0.7331 | -1.0105 | 0 |  | 2026-01-04 23:27 | none | FALSE | 0 | 71.6152 | FALSE | FALSE | 0.4768 | 1.5213 | 72.0803 | 20 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.23259 | Confirmed/Materialized Shift | 72.5455 | -1.152 | Night | 202601 | 2026-01-05 | 1.152
2026-01-05 04:25 | 71.8124 | FALSE | TRUE | -0.21825 | -0.30485 | -0.69777 | -0.96231 | 0 |  | 2026-01-04 23:27 | none | FALSE | 0 | 71.5941 | FALSE | FALSE | 0.4698 | 1.4987 | 72.0522 | 21 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.22901 | Confirmed/Materialized Shift | 72.5102 | -1.047 | Night | 202601 | 2026-01-05 | 1.047
2026-01-05 04:39 | 71.5298 | TRUE | TRUE | -0.0074193 | -0.010373 | -0.96754 | -1.3346 | -0.2826 |  | 2026-01-04 23:27 | none | FALSE | 1 | 71.5224 | FALSE | FALSE | 0.5599 | 1.5201 | 72.0099 | 22 | -0.2826 | -0.0423 | 0.10331 | -2.326 | 0.24374 | Confirmed/Materialized Shift | 72.4973 | -1.9696 | Night | 202601 | 2026-01-05 | 1.9696
2026-01-05 04:55 | 71.8124 | TRUE | FALSE | -0.29365 | -0.41059 | -0.63223 | -0.8727 | 0.2826 |  |  | none | FALSE | 2 | 71.5188 | TRUE | FALSE | 0.1059 |  | 71.9817 | 0 | 0.2826 | -0.02817 | 0.12619 | 2.4627 | 0.23147 | Persistence ends | 72.4446 | -0.73137 | Night | 202601 | 2026-01-05 | 0.73137
2026-01-05 05:10 | 71.8124 | FALSE | FALSE | -0.28819 | -0.40292 | -0.57043 | -0.78807 | 0 |  |  | none | FALSE | 2 | 71.5242 | FALSE | FALSE | 0.101 |  | 71.9535 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.21465 | Normal | 72.3828 | -0.65743 | Night | 202601 | 2026-01-05 | 0.65743
2026-01-05 05:25 | 71.8124 | FALSE | FALSE | -0.27126 | -0.37916 | -0.49716 | -0.68754 | 0 |  |  | none | FALSE | 2 | 71.5411 | FALSE | FALSE | 0.0963 |  | 71.9253 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.1921 | Normal | 72.3096 | -0.58797 | Night | 202601 | 2026-01-05 | 0.58797
2026-01-05 05:39 | 71.8124 | FALSE | FALSE | -0.23809 | -0.33264 | -0.40765 | -0.56445 | 0 |  |  | none | FALSE | 2 | 71.5743 | FALSE | FALSE | 0.0922 |  | 71.8972 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.16143 | Normal | 72.22 | -0.52517 | Night | 202601 | 2026-01-05 | 0.52517
2026-01-05 05:54 | 71.8124 | FALSE | FALSE | -0.24028 | -0.33571 | -0.38158 | -0.52854 | 0 |  |  | none | FALSE | 2 | 71.5721 | FALSE | FALSE | 0.0874 |  | 71.883 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.15546 | Normal | 72.194 | -0.45445 | Night | 202601 | 2026-01-05 | 0.45445
2026-01-05 06:09 | 71.5298 | TRUE | FALSE | -0.0068632 | -0.0095958 | -0.65684 | -0.90992 | -0.2826 |  |  | none | FALSE | 3 | 71.5229 | TRUE | FALSE | 0.2163 |  | 71.8548 | 0 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.16593 | Normal | 72.1866 | -1.9586 | Night | 202601 | 2026-01-05 | 1.9586
2026-01-05 06:24 | 71.5298 | FALSE | FALSE | -0.045106 | -0.063099 | -0.63857 | -0.88483 | 0 |  |  | none | FALSE | 3 | 71.4847 | FALSE | FALSE | 0.2015 |  | 71.8265 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.17092 | Normal | 72.1684 | -1.7361 | Night | 202601 | 2026-01-05 | 1.7361
2026-01-05 06:39 | 71.8124 | TRUE | FALSE | -0.31761 | -0.44425 | -0.31761 | -0.44034 | 0.2826 |  |  | none | FALSE | 4 | 71.4948 | TRUE | FALSE | 0.1143 |  | 71.8124 | 0 | 0.2826 | -0.01413 | 0.14424 | 2.0571 | 0.15881 | Normal | 72.13 | 0 | Night | 202601 | 2026-01-05 | 0
2026-01-05 06:54 | 71.5298 | FALSE | FALSE | -0.057937 | -0.081062 | -0.56662 | -0.78591 | -0.2826 |  |  | none | FALSE | 4 | 71.4719 | FALSE | FALSE | 0.2229 |  | 71.7841 | 0 | -0.2826 | -0.02826 | 0.15614 | -1.6289 | 0.15614 | Normal | 72.0964 | -1.6289 | Night | 202601 | 2026-01-05 | 1.6289
2026-01-05 07:09 | 71.5298 | FALSE | FALSE | -0.069603 | -0.097402 | -0.52176 | -0.72415 | 0 |  |  | none | FALSE | 3 | 71.4602 | FALSE | FALSE | 0.1877 |  | 71.7559 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.14784 | Normal | 72.0516 | -1.5292 | Night | 202601 | 2026-01-05 | 1.5292
2026-01-05 07:24 | 71.5298 | FALSE | FALSE | -0.067916 | -0.095038 | -0.46356 | -0.64389 | 0 |  |  | none | FALSE | 2 | 71.4619 | FALSE | FALSE | 0.1564 |  | 71.7276 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.13287 | Normal | 71.9934 | -1.4888 | Day | 202601 | 2026-01-05 | 1.4888
2026-01-05 07:30 | 71.5298 | FALSE | FALSE | -0.092897 | -0.13004 | -0.46028 | -0.63936 | 0 |  |  | none | FALSE | 2 | 71.4369 | FALSE | FALSE | 0.1457 |  | 71.7135 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.13829 | Normal | 71.9901 | -1.3283 | Day | 202601 | 2026-01-05 | 1.3283
2026-01-05 07:45 | 71.5298 | FALSE | FALSE | -0.11452 | -0.16036 | -0.45364 | -0.63021 | 0 |  |  | none | FALSE | 2 | 71.4153 | FALSE | FALSE | 0.1367 |  | 71.6994 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.14204 | Normal | 71.9834 | -1.1937 | Day | 202601 | 2026-01-05 | 1.1937
2026-01-05 08:00 | 71.5298 | FALSE | FALSE | -0.13306 | -0.18636 | -0.44392 | -0.61678 | 0 |  |  | none | FALSE | 2 | 71.3967 | FALSE | FALSE | 0.129 |  | 71.6852 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.14424 | Normal | 71.9737 | -1.0775 | Day | 202601 | 2026-01-05 | 1.0775
2026-01-05 08:15 | 71.5298 | FALSE | FALSE | -0.14864 | -0.20824 | -0.43124 | -0.59927 | 0 |  |  | none | FALSE | 2 | 71.3812 | FALSE | FALSE | 0.1221 |  | 71.6711 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.14497 | Normal | 71.961 | -0.97468 | Day | 202601 | 2026-01-05 | 0.97468
2026-01-05 08:30 | 71.5298 | FALSE | FALSE | -0.16132 | -0.22604 | -0.41566 | -0.57774 | 0 |  |  | none | FALSE | 1 | 71.3685 | FALSE | FALSE | 0.0873 |  | 71.657 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.14424 | Normal | 71.9455 | -0.88163 | Day | 202601 | 2026-01-05 | 0.88163
2026-01-05 08:45 | 71.5298 | FALSE | FALSE | -0.17104 | -0.2397 | -0.39712 | -0.55212 | 0 |  |  | none | FALSE | 1 | 71.3588 | FALSE | FALSE | 0.0816 |  | 71.6428 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.14204 | Normal | 71.9269 | -0.79582 | Day | 202601 | 2026-01-05 | 0.79582
2026-01-05 08:45 | 71.5298 | FALSE | FALSE | -0.17768 | -0.24901 | -0.3755 | -0.52221 | 0 |  |  | none | FALSE | 0 | 71.3521 | FALSE | FALSE | 0.0477 |  | 71.6287 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.13829 | Normal | 71.9053 | -0.71522 | Day | 202601 | 2026-01-05 | 0.71522
2026-01-05 09:00 | 71.5298 | FALSE | FALSE | -0.18096 | -0.25362 | -0.35052 | -0.48764 | 0 |  |  | none | FALSE | 0 | 71.3488 | FALSE | FALSE | 0.0425 |  | 71.6146 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.13287 | Normal | 71.8803 | -0.63808 | Day | 202601 | 2026-01-05 | 0.63808
2026-01-05 09:15 | 71.8124 | FALSE | FALSE | -0.46028 | -0.64508 | -0.092897 | -0.12919 | 0.2826 |  |  | none | FALSE | 0 | 71.3521 | FALSE | FALSE | 0.0886 |  | 71.6287 | 0 | 0.2826 | 0.01413 | 0.14424 | 1.8612 | 0.13829 | Normal | 71.9053 | 1.3283 | Day | 202601 | 2026-01-05 | 1.3283
2026-01-05 09:30 | 71.8124 | FALSE | FALSE | -0.46028 | -0.64508 | -0.092897 | -0.12919 | 0 |  |  | none | FALSE | 0 | 71.3521 | FALSE | FALSE | 0.0886 |  | 71.6287 | 0 | 0 | 0 | 0.12967 | 0 | 0.13829 | Normal | 71.9053 | 1.3283 | Day | 202601 | 2026-01-05 | 1.3283
2026-01-05 09:44 | 71.8124 | FALSE | FALSE | -0.46028 | -0.64508 | -0.092897 | -0.12919 | 0 |  |  | none | FALSE | 0 | 71.3521 | FALSE | FALSE | 0.0886 |  | 71.6287 | 0 | 0 | 0 | 0.12967 | 0 | 0.13829 | Normal | 71.9053 | 1.3283 | Day | 202601 | 2026-01-05 | 1.3283
2026-01-05 09:59 | 72.095 | FALSE | FALSE | -0.79029 | -1.1083 | 0.11403 | 0.15842 | 0.2826 | 2026-01-05 13:01 | 2026-01-05 09:59 | upper | TRUE | 0 | 71.3047 | FALSE | FALSE | 0.2354 | 2.6745 | 71.6428 | 1 | 0.2826 | 0.01413 | 0.14424 | 1.8612 | 0.16906 | Extreme triggered | 71.981 | 2.6745 | Day | 202601 | 2026-01-05 | 2.6745
2026-01-05 10:15 | 72.095 | FALSE | FALSE | -0.82595 | -1.1589 | 0.050115 | 0.06956 | 0 |  | 2026-01-05 09:59 | upper | TRUE | 0 | 71.2691 | FALSE | FALSE | 0.2648 | 2.4664 | 71.657 | 2 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.19396 | Extreme/elevated | 72.0449 | 2.2584 | Day | 202601 | 2026-01-05 | 2.2584
2026-01-05 10:30 | 72.3758 | FALSE | FALSE | -1.1915 | -1.6738 | 0.18983 | 0.26297 | 0.2808 |  | 2026-01-05 09:59 | upper | TRUE | 0 | 71.1843 | FALSE | TRUE | 0.3553 | 2.5636 | 71.6851 | 3 | 0.2808 | 0.02817 | 0.15598 | 1.6196 | 0.25042 | Persistent | 72.186 | 2.758 | Day | 202601 | 2026-01-05 | 2.758
2026-01-05 10:44 | 72.941 | TRUE | FALSE | -1.9315 | -2.7201 | 0.43909 | 0.60563 | 0.5652 |  | 2026-01-05 09:59 | upper | TRUE | 1 | 71.0095 | FALSE | TRUE | 0.4689 | 2.7169 | 71.7557 | 4 | 0.5652 | 0.07056 | 0.18038 | 2.7423 | 0.3731 | Persistent | 72.5019 | 3.1769 | Day | 202601 | 2026-01-05 | 3.1769
2026-01-05 10:59 | 73.2236 | FALSE | FALSE | -2.3678 | -3.3418 | 0.39857 | 0.5473 | 0.2826 |  | 2026-01-05 09:59 | upper | TRUE | 1 | 70.8558 | FALSE | TRUE | 0.5016 | 2.7355 | 71.8404 | 5 | 0.2826 | 0.08469 | 0.18555 | 1.0666 | 0.49232 | Persistent | 72.825 | 2.8096 | Day | 202601 | 2026-01-05 | 2.8096
2026-01-05 11:14 | 73.2236 | FALSE | FALSE | -2.4751 | -3.4984 | 0.15025 | 0.20561 | 0 |  | 2026-01-05 09:59 | upper | TRUE | 1 | 70.7485 | FALSE | TRUE | 0.522 | 2.656 | 71.9109 | 6 | 0 | 0.07056 | 0.18038 | -0.39118 | 0.5812 | Persistent | 73.0734 | 2.2585 | Day | 202601 | 2026-01-05 | 2.2585
2026-01-05 11:29 | 73.5062 | FALSE | TRUE | -2.8437 | -4.0244 | 0.14913 | 0.20329 | 0.2826 |  | 2026-01-05 09:59 | upper | TRUE | 1 | 70.6625 | FALSE | TRUE | 0.5767 | 2.5939 | 72.0098 | 7 | 0.2826 | 0.09882 | 0.16582 | 1.1083 | 0.67365 | Confirmed/Materialized Shift | 73.3571 | 2.2214 | Day | 202601 | 2026-01-05 | 2.2214
2026-01-05 11:44 | 73.5062 | FALSE | TRUE | -2.8799 | -4.0776 | -0.084633 | -0.11501 | 0 |  | 2026-01-05 09:59 | none | FALSE | 1 | 70.6263 | FALSE | FALSE | 0.5543 | 2.5054 | 72.1086 | 8 | 0 | 0.09882 | 0.16582 | -0.59594 | 0.74112 | Confirmed/Materialized Shift | 73.5908 | 1.8858 | Day | 202601 | 2026-01-05 | 1.8858
2026-01-05 11:59 | 73.5062 | FALSE | TRUE | -2.8789 | -4.0761 | -0.28128 | -0.3812 | 0 |  | 2026-01-05 09:59 | none | FALSE | 1 | 70.6273 | FALSE | FALSE | 0.5382 | 2.4097 | 72.2074 | 9 | 0 | 0.09882 | 0.16582 | -0.59594 | 0.79004 | Confirmed/Materialized Shift | 73.7875 | 1.644 | Day | 202601 | 2026-01-05 | 1.644
2026-01-05 12:14 | 73.5062 | FALSE | TRUE | -2.8474 | -4.0298 | -0.44744 | -0.60503 | 0 |  | 2026-01-05 09:59 | none | FALSE | 1 | 70.6588 | FALSE | FALSE | 0.5257 | 2.3144 | 72.3062 | 10 | 0 | 0.09882 | 0.16582 | -0.59594 | 0.82371 | Confirmed/Materialized Shift | 73.9536 | 1.4568 | Day | 202601 | 2026-01-05 | 1.4568
2026-01-05 12:29 | 73.7888 | FALSE | TRUE | -3.1005 | -4.3862 | -0.3613 | -0.48725 | 0.2826 |  | 2026-01-05 09:59 | none | FALSE | 1 | 70.6883 | FALSE | FALSE | 0.5341 | 2.2478 | 72.4192 | 11 | 0.2826 | 0.11295 | 0.16897 | 1.004 | 0.86546 | Confirmed/Materialized Shift | 74.1501 | 1.5825 | Day | 202601 | 2026-01-05 | 1.5825
2026-01-05 12:43 | 74.0714 | FALSE | TRUE | -3.3517 | -4.7394 | -0.3014 | -0.40526 | 0.2826 |  | 2026-01-05 09:59 | none | FALSE | 1 | 70.7197 | FALSE | FALSE | 0.5399 | 2.1997 | 72.5463 | 12 | 0.2826 | 0.12708 | 0.17083 | 0.91037 | 0.91327 | Confirmed/Materialized Shift | 74.3728 | 1.67 | Day | 202601 | 2026-01-05 | 1.67
2026-01-05 12:44 | 73.7888 | TRUE | TRUE | -2.9708 | -4.195 | -0.71162 | -0.95519 | -0.2826 |  | 2026-01-05 09:59 | none | FALSE | 2 | 70.818 | TRUE | FALSE | 0.5389 | 2.1249 | 72.6592 | 13 | -0.2826 | 0.11295 | 0.19224 | -2.0576 | 0.92061 | Confirmed/Materialized Shift | 74.5004 | 1.227 | Day | 202601 | 2026-01-05 | 1.227
2026-01-05 12:46 | 73.7888 | FALSE | TRUE | -2.8432 | -4.0076 | -0.80995 | -1.0857 | 0 |  | 2026-01-05 09:59 | none | FALSE | 1 | 70.9456 | FALSE | FALSE | 0.5028 | 2.0526 | 72.7722 | 14 | 0 | 0.11295 | 0.19224 | -0.58754 | 0.91329 | Confirmed/Materialized Shift | 74.5987 | 1.1132 | Day | 202601 | 2026-01-05 | 1.1132
2026-01-05 13:01 | 73.5062 | FALSE | FALSE | -2.3913 | -3.3626 | -1.1209 | -1.5019 | -0.2826 |  |  | none | FALSE | 1 | 71.1149 | FALSE | FALSE | 0.0768 |  | 72.871 | 0 | -0.2826 | 0.09882 | 0.2105 | -1.812 | 0.87804 | Persistence ends | 74.6271 | 0.72345 | Day | 202601 | 2026-01-05 | 0.72345
2026-01-05 13:16 | 72.941 | TRUE | FALSE | -1.6381 | -2.2974 | -1.6392 | -2.1979 | -0.5652 |  |  | none | FALSE | 2 | 71.3029 | TRUE | FALSE | 0.0572 |  | 72.9415 | 0 | -0.5652 | 0.07056 | 0.25722 | -2.4717 | 0.81933 | Normal | 74.5802 | -0.00065908 | Day | 202601 | 2026-01-05 | 0.00065908
2026-01-05 13:31 | 72.941 | FALSE | FALSE | -1.4271 | -1.9956 | -1.5693 | -2.1062 | 0 |  |  | none | FALSE | 2 | 71.5139 | FALSE | FALSE | 0.0635 |  | 73.0121 | 0 | 0 | 0.07056 | 0.25722 | -0.27432 | 0.74911 | Normal | 74.5103 | -0.094913 | Day | 202601 | 2026-01-05 | 0.094913
2026-01-05 13:43 | 72.3758 | TRUE | FALSE | -0.75804 | -1.0585 | -2.087 | -2.8027 | -0.5652 |  |  | none | FALSE | 3 | 71.6178 | TRUE | FALSE | 0.148 |  | 73.0403 | 0 | -0.5652 | 0.02817 | 0.2884 | -2.0574 | 0.71126 | Normal | 74.4628 | -0.93422 | Day | 202601 | 2026-01-05 | 0.93422
2026-01-05 13:58 | 72.095 | FALSE | FALSE | -0.41661 | -0.58122 | -2.3354 | -3.1377 | -0.2808 |  |  | none | FALSE | 3 | 71.6784 | FALSE | FALSE | 0.1787 |  | 73.0544 | 0 | -0.2808 | 0.01413 | 0.29657 | -0.99448 | 0.68801 | Normal | 74.4304 | -1.3945 | Day | 202601 | 2026-01-05 | 1.3945
2026-01-05 14:13 | 72.095 | FALSE | FALSE | -0.35372 | -0.49305 | -2.3008 | -3.0926 | 0 |  |  | none | FALSE | 3 | 71.7413 | FALSE | FALSE | 0.1835 |  | 73.0685 | 0 | 0 | 0.01413 | 0.29657 | -0.047645 | 0.66363 | Normal | 74.3958 | -1.467 | Day | 202601 | 2026-01-05 | 1.467
2026-01-05 14:28 | 72.095 | FALSE | FALSE | -0.35372 | -0.49305 | -2.3008 | -3.0926 | 0 |  |  | none | FALSE | 3 | 71.7413 | FALSE | FALSE | 0.1835 |  | 73.0685 | 0 | 0 | 0 | 0.28976 | 0 | 0.66363 | Normal | 74.3958 | -1.467 | Day | 202601 | 2026-01-05 | 1.467
2026-01-05 14:43 | 72.095 | FALSE | FALSE | -0.35372 | -0.49305 | -2.3008 | -3.0926 | 0 |  |  | none | FALSE | 3 | 71.7413 | FALSE | FALSE | 0.1835 |  | 73.0685 | 0 | 0 | 0 | 0.28976 | 0 | 0.66363 | Normal | 74.3958 | -1.467 | Day | 202601 | 2026-01-05 | 1.467
2026-01-05 14:58 | 72.095 | FALSE | FALSE | -0.40406 | -0.56361 | -2.323 | -3.1216 | 0 |  |  | none | FALSE | 2 | 71.6909 | FALSE | FALSE | 0.151 |  | 73.0545 | 0 | 0 | -0.01404 | 0.28214 | 0.049763 | 0.68177 | Normal | 74.418 | -1.4073 | Day | 202601 | 2026-01-05 | 1.4073
2026-01-05 15:13 | 71.8124 | FALSE | FALSE | -0.28673 | -0.40088 | -2.6581 | -3.5693 | -0.2826 |  |  | none | FALSE | 2 | 71.5257 | FALSE | FALSE | 0.1645 |  | 72.9981 | 0 | -0.2826 | -0.05643 | 0.25268 | -0.89508 | 0.7362 | Normal | 74.4705 | -1.6105 | Day | 202601 | 2026-01-05 | 1.6105
2026-01-05 15:28 | 72.6584 | TRUE | FALSE | -1.1645 | -1.6288 | -1.7873 | -2.4008 | 0.846 |  |  | none | FALSE | 3 | 71.4939 | TRUE | FALSE | 0.1138 |  | 72.9698 | 0 | 0.846 | -0.02826 | 0.31595 | 2.7671 | 0.73793 | Normal | 74.4457 | -0.42199 | Day | 202601 | 2026-01-05 | 0.42199
2026-01-05 15:43 | 72.941 | FALSE | FALSE | -1.4564 | -2.0373 | -1.4857 | -1.9962 | 0.2826 |  |  | none | FALSE | 2 | 71.4846 | FALSE | FALSE | 0.0585 |  | 72.9557 | 0 | 0.2826 | -0.01413 | 0.32351 | 0.91722 | 0.73552 | Normal | 74.4267 | -0.019945 | Day | 202601 | 2026-01-05 | 0.019945
2026-01-05 15:58 | 72.6584 | FALSE | FALSE | -1.1981 | -1.6766 | -1.7079 | -2.2966 | -0.2826 |  |  | none | FALSE | 2 | 71.4603 | FALSE | FALSE | 0.0805 |  | 72.9133 | 0 | -0.2826 | -0.04239 | 0.3209 | -0.74855 | 0.72649 | Normal | 74.3663 | -0.35084 | Day | 202601 | 2026-01-05 | 0.35084
2026-01-05 16:13 | 72.941 | FALSE | FALSE | -1.4821 | -2.0741 | -1.3702 | -1.8439 | 0.2826 |  |  | none | FALSE | 1 | 71.4589 | FALSE | FALSE | 0.0338 |  | 72.885 | 0 | 0.2826 | -0.02826 | 0.32899 | 0.94491 | 0.71308 | Normal | 74.3112 | 0.078504 | Day | 202601 | 2026-01-05 | 0.078504
2026-01-05 16:28 | 72.941 | FALSE | FALSE | -1.4807 | -2.072 | -1.3122 | -1.7672 | 0 |  |  | none | FALSE | 1 | 71.4603 | FALSE | FALSE | 0.0366 |  | 72.8568 | 0 | 0 | -0.02826 | 0.32899 | 0.0859 | 0.69821 | Normal | 74.2532 | 0.12065 | Day | 202601 | 2026-01-05 | 0.12065
2026-01-05 16:42 | 72.941 | FALSE | FALSE | -1.4761 | -2.0655 | -1.2511 | -1.6863 | 0 |  |  | none | FALSE | 1 | 71.4649 | FALSE | FALSE | 0.0396 |  | 72.8285 | 0 | 0 | -0.02826 | 0.32899 | 0.0859 | 0.68179 | Normal | 74.1921 | 0.16501 | Day | 202601 | 2026-01-05 | 0.16501
2026-01-05 16:57 | 73.2236 | FALSE | FALSE | -1.7252 | -2.4129 | -0.87845 | -1.1855 | 0.2826 |  |  | none | FALSE | 1 | 71.4984 | FALSE | FALSE | 0.0719 |  | 72.8002 | 0 | 0.2826 | -0.02826 | 0.32899 | 0.94491 | 0.65091 | Normal | 74.1021 | 0.65042 | Day | 202601 | 2026-01-05 | 0.65042
2026-01-05 17:12 | 72.941 | FALSE | FALSE | -1.3571 | -1.8959 | -0.96257 | -1.3025 | -0.2826 |  |  | none | FALSE | 1 | 71.5839 | FALSE | FALSE | 0.0513 |  | 72.7437 | 0 | -0.2826 | -0.05652 | 0.32513 | -0.69535 | 0.57993 | Normal | 73.9036 | 0.34018 | Day | 202601 | 2026-01-05 | 0.34018
2026-01-05 17:27 | 72.941 | FALSE | FALSE | -1.2961 | -1.809 | -0.81671 | -1.1073 | 0 |  |  | none | FALSE | 1 | 71.6449 | FALSE | FALSE | 0.0588 |  | 72.7013 | 0 | 0 | -0.04239 | 0.3209 | 0.1321 | 0.52819 | Normal | 73.7577 | 0.45376 | Day | 202601 | 2026-01-05 | 0.45376
2026-01-05 17:42 | 72.941 | FALSE | FALSE | -1.2156 | -1.6948 | -0.65148 | -0.88526 | 0 |  |  | none | FALSE | 1 | 71.7254 | FALSE | FALSE | 0.0689 |  | 72.6589 | 0 | 0 | -0.04239 | 0.3209 | 0.1321 | 0.46677 | Normal | 73.5925 | 0.60428 | Day | 202601 | 2026-01-05 | 0.60428
2026-01-05 17:57 | 72.941 | FALSE | FALSE | -1.1669 | -1.6258 | -0.54628 | -0.74337 | 0 |  |  | none | FALSE | 0 | 71.7741 | FALSE | FALSE | 0.0483 |  | 72.6307 | 0 | 0 | -0.02826 | 0.31595 | 0.089444 | 0.4283 | Normal | 73.4873 | 0.72454 | Night | 202601 | 2026-01-05 | 0.72454
2026-01-05 18:12 | 72.941 | FALSE | FALSE | -1.1669 | -1.6258 | -0.54628 | -0.74337 | 0 |  |  | none | FALSE | 0 | 71.7741 | FALSE | FALSE | 0.0483 |  | 72.6307 | 0 | 0 | 0 | 0.28957 | 0 | 0.4283 | Normal | 73.4873 | 0.72454 | Night | 202601 | 2026-01-05 | 0.72454
2026-01-05 18:27 | 72.941 | FALSE | FALSE | -1.1669 | -1.6258 | -0.54628 | -0.74337 | 0 |  |  | none | FALSE | 0 | 71.7741 | FALSE | FALSE | 0.0483 |  | 72.6307 | 0 | 0 | 0 | 0.28957 | 0 | 0.4283 | Normal | 73.4873 | 0.72454 | Night | 202601 | 2026-01-05 | 0.72454
2026-01-05 18:30 | 72.941 | FALSE | FALSE | -1.1405 | -1.5885 | -0.57643 | -0.78407 | 0 |  |  | none | FALSE | 0 | 71.8005 | FALSE | FALSE | 0.0438 |  | 72.6589 | 0 | 0 | 0.02826 | 0.25729 | -0.10984 | 0.42924 | Normal | 73.5174 | 0.65711 | Night | 202601 | 2026-01-05 | 0.65711
2026-01-05 18:31 | 72.941 | FALSE | FALSE | -1.0639 | -1.4802 | -0.58441 | -0.79485 | 0 |  |  | none | FALSE | 0 | 71.8771 | FALSE | FALSE | 0.0388 |  | 72.7012 | 0 | 0 | 0.0423 | 0.24699 | -0.17126 | 0.41209 | Normal | 73.5254 | 0.58182 | Night | 202601 | 2026-01-05 | 0.58182
2026-01-05 18:46 | 72.941 | FALSE | FALSE | -0.97621 | -1.3565 | -0.58129 | -0.79063 | 0 |  |  | none | FALSE | 0 | 71.9648 | FALSE | FALSE | 0.0338 |  | 72.7435 | 0 | 0 | 0.0423 | 0.24699 | -0.17126 | 0.38938 | Normal | 73.5223 | 0.50712 | Night | 202601 | 2026-01-05 | 0.50712
2026-01-05 19:01 | 73.5062 | FALSE | FALSE | -1.4791 | -2.0536 | -0.094918 | -0.12896 | 0.5652 |  |  | none | FALSE | 0 | 72.0271 | FALSE | FALSE | 0.1173 |  | 72.8141 | 0 | 0.5652 | 0.07056 | 0.27288 | 1.8127 | 0.39351 | Normal | 73.6011 | 1.7588 | Night | 202601 | 2026-01-05 | 1.7588
2026-01-05 19:16 | 73.7888 | FALSE | FALSE | -1.7148 | -2.3793 | 0.065182 | 0.088413 | 0.2826 | 2026-01-05 20:59 | 2026-01-05 19:16 | upper | TRUE | 0 | 72.074 | FALSE | FALSE | 0.201 | 2.158 | 72.8988 | 1 | 0.2826 | 0.08469 | 0.27633 | 0.71622 | 0.41241 | Extreme triggered | 73.7236 | 2.158 | Night | 202601 | 2026-01-05 | 2.158
2026-01-05 19:30 | 73.7888 | FALSE | FALSE | -1.6305 | -2.2596 | -0.019839 | -0.026879 | 0 |  | 2026-01-05 19:16 | none | FALSE | 0 | 72.1583 | FALSE | FALSE | 0.2444 | 2.055 | 72.9835 | 2 | 0 | 0.08469 | 0.27633 | -0.30649 | 0.41258 | Extreme/elevated | 73.8086 | 1.9519 | Night | 202601 | 2026-01-05 | 1.9519
2026-01-05 19:45 | 73.7888 | FALSE | FALSE | -1.4048 | -1.9407 | 0.0082284 | 0.011153 | 0 |  | 2026-01-05 19:16 | upper | TRUE | 0 | 72.384 | FALSE | TRUE | 0.3063 | 2.0445 | 73.0823 | 3 | 0 | 0.09882 | 0.26348 | -0.37505 | 0.34914 | Persistent | 73.7806 | 2.0236 | Night | 202601 | 2026-01-05 | 2.0236
2026-01-05 20:00 | 73.7888 | FALSE | FALSE | -1.3858 | -1.914 | -0.085809 | -0.11615 | 0 |  | 2026-01-05 19:16 | none | FALSE | 0 | 72.403 | FALSE | FALSE | 0.3464 | 1.9751 | 73.1388 | 4 | 0 | 0.05652 | 0.19665 | -0.28742 | 0.36789 | Persistent | 73.8746 | 1.7668 | Night | 202601 | 2026-01-05 | 1.7668
2026-01-05 20:15 | 73.7888 | FALSE | FALSE | -1.3915 | -1.922 | -0.17633 | -0.23839 | 0 |  | 2026-01-05 19:16 | none | FALSE | 0 | 72.3973 | FALSE | FALSE | 0.3891 | 1.8901 | 73.1812 | 5 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.39196 | Persistent | 73.9651 | 1.5501 | Night | 202601 | 2026-01-05 | 1.5501
2026-01-05 20:29 | 73.7888 | FALSE | FALSE | -1.3393 | -1.8485 | -0.23712 | -0.32032 | 0 |  | 2026-01-05 19:16 | none | FALSE | 0 | 72.4495 | FALSE | FALSE | 0.4361 | 1.8081 | 73.2377 | 6 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.3941 | Persistent | 74.0259 | 1.3983 | Night | 202601 | 2026-01-05 | 1.3983
2026-01-05 20:44 | 73.7888 | FALSE | TRUE | -1.3205 | -1.8222 | -0.30316 | -0.40916 | 0 |  | 2026-01-05 19:16 | none | FALSE | 0 | 72.4683 | FALSE | FALSE | 0.4835 | 1.7288 | 73.2801 | 7 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.40592 | Confirmed/Materialized Shift | 74.092 | 1.2532 | Night | 202601 | 2026-01-05 | 1.2532
2026-01-05 20:59 | 73.5062 | FALSE | FALSE | -0.99923 | -1.3781 | -0.60359 | -0.81446 | -0.2826 |  |  | none | FALSE | 0 | 72.507 | FALSE | FALSE | 0.0329 |  | 73.3084 | 0 | -0.2826 | 0.02826 | 0.18107 | -1.7168 | 0.40071 | Persistence ends | 74.1098 | 0.49368 | Night | 202601 | 2026-01-05 | 0.49368
2026-01-05 21:14 | 73.5062 | FALSE | FALSE | -0.95615 | -1.3179 | -0.61703 | -0.83244 | 0 |  |  | none | FALSE | 0 | 72.55 | FALSE | FALSE | 0.0287 |  | 73.3366 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.3933 | Normal | 74.1232 | 0.43113 | Night | 202601 | 2026-01-05 | 0.43113
2026-01-05 21:29 | 73.5062 | FALSE | FALSE | -0.94362 | -1.3004 | -0.63276 | -0.85348 | 0 |  |  | none | FALSE | 0 | 72.5626 | FALSE | FALSE | 0.0263 |  | 73.3508 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.3941 | Normal | 74.139 | 0.3944 | Night | 202601 | 2026-01-05 | 0.3944
2026-01-05 21:44 | 73.5062 | FALSE | FALSE | -0.89373 | -1.2308 | -0.63939 | -0.86235 | 0 |  |  | none | FALSE | 0 | 72.6125 | FALSE | FALSE | 0.0221 |  | 73.379 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.38328 | Normal | 74.1456 | 0.33179 | Night | 202601 | 2026-01-05 | 0.33179
2026-01-05 21:59 | 73.5062 | FALSE | FALSE | -0.83869 | -1.1541 | -0.64087 | -0.86432 | 0 |  |  | none | FALSE | 0 | 72.6675 | FALSE | FALSE | 0.0178 |  | 73.4073 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.36989 | Normal | 74.1471 | 0.2674 | Night | 202601 | 2026-01-05 | 0.2674
2026-01-05 22:14 | 73.2236 | FALSE | FALSE | -0.51475 | -0.70796 | -0.91039 | -1.228 | -0.2826 |  |  | none | FALSE | 0 | 72.7088 | FALSE | FALSE | 0.037 |  | 73.4214 | 0 | -0.2826 | 0.01413 | 0.17092 | -1.7361 | 0.35629 | Normal | 74.134 | -0.55523 | Night | 202601 | 2026-01-05 | 0.55523
2026-01-05 22:29 | 73.2236 | FALSE | FALSE | -0.47111 | -0.64755 | -0.89501 | -1.2075 | 0 |  |  | none | FALSE | 0 | 72.7525 | FALSE | FALSE | 0.0414 |  | 73.4356 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.34153 | Normal | 74.1186 | -0.62059 | Night | 202601 | 2026-01-05 | 0.62059
2026-01-05 22:44 | 73.2236 | FALSE | FALSE | -0.42484 | -0.58358 | -0.877 | -1.1835 | 0 |  |  | none | FALSE | 0 | 72.7988 | FALSE | FALSE | 0.0463 |  | 73.4497 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.32546 | Normal | 74.1006 | -0.69465 | Night | 202601 | 2026-01-05 | 0.69465
2026-01-05 22:59 | 73.2236 | FALSE | FALSE | -0.37553 | -0.5155 | -0.85595 | -1.1554 | 0 |  |  | none | FALSE | 0 | 72.8481 | FALSE | FALSE | 0.052 |  | 73.4638 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.30787 | Normal | 74.0796 | -0.78023 | Night | 202601 | 2026-01-05 | 0.78023
2026-01-05 23:14 | 73.2236 | FALSE | FALSE | -0.32264 | -0.44257 | -0.83132 | -1.1226 | 0 |  |  | none | FALSE | 0 | 72.901 | FALSE | FALSE | 0.0588 |  | 73.4779 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.28849 | Normal | 74.0549 | -0.88163 | Night | 202601 | 2026-01-05 | 0.88163
2026-01-05 23:28 | 73.2236 | FALSE | FALSE | -0.26537 | -0.36373 | -0.80231 | -1.0838 | 0 |  |  | none | FALSE | 0 | 72.9582 | FALSE | FALSE | 0.0671 |  | 73.4921 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.26692 | Normal | 74.0259 | -1.0058 | Night | 202601 | 2026-01-05 | 1.0058
2026-01-05 23:43 | 72.941 | FALSE | FALSE | 0.017231 | 0.023618 | -1.0849 | -1.4656 | -0.2826 | 2026-01-06 06:12 | 2026-01-05 23:43 | lower | TRUE | 0 | 72.9582 | FALSE | FALSE | 0.1948 | 2.0646 | 73.4921 | 1 | -0.2826 | 0 | 0.18338 | -1.5411 | 0.26692 | Extreme triggered | 74.0259 | -2.0646 | Night | 202601 | 2026-01-05 | 2.0646
2026-01-05 23:59 | 72.941 | FALSE | FALSE | -0.064992 | -0.089182 | -1.1106 | -1.4998 | 0 |  | 2026-01-05 23:43 | none | FALSE | 0 | 72.876 | FALSE | FALSE | 0.2329 | 1.9217 | 73.4638 | 2 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.2939 | Extreme/elevated | 74.0516 | -1.7789 | Night | 202601 | 2026-01-05 | 1.7789
2026-01-06 00:14 | 72.941 | FALSE | FALSE | -0.13052 | -0.17927 | -1.0914 | -1.4742 | 0 |  | 2026-01-05 23:43 | none | FALSE | 0 | 72.8105 | FALSE | FALSE | 0.2763 | 1.8054 | 73.4214 | 3 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.30547 | Persistent | 74.0324 | -1.5727 | Night | 202601 | 2026-01-06 | 1.5727
2026-01-06 00:28 | 72.941 | FALSE | FALSE | -0.18315 | -0.25172 | -1.0592 | -1.4314 | 0 |  | 2026-01-05 23:43 | none | FALSE | 0 | 72.7579 | FALSE | FALSE | 0.3226 | 1.7066 | 73.379 | 4 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.31059 | Persistent | 74.0002 | -1.4103 | Night | 202601 | 2026-01-06 | 1.4103
2026-01-06 00:43 | 72.941 | FALSE | FALSE | -0.22351 | -0.30736 | -1.0148 | -1.3722 | 0 |  | 2026-01-05 23:43 | none | FALSE | 0 | 72.7175 | FALSE | FALSE | 0.3709 | 1.6209 | 73.3366 | 5 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.30957 | Persistent | 73.9558 | -1.278 | Night | 202601 | 2026-01-06 | 1.278
2026-01-06 00:58 | 72.941 | FALSE | FALSE | -0.25147 | -0.34595 | -0.95797 | -1.2963 | 0 |  | 2026-01-05 23:43 | none | FALSE | 0 | 72.6895 | FALSE | FALSE | 0.4207 | 1.5455 | 73.2943 | 6 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.30236 | Persistent | 73.899 | -1.1683 | Night | 202601 | 2026-01-06 | 1.1683
2026-01-06 01:13 | 72.6584 | FALSE | TRUE | -0.041849 | -0.05763 | -1.2005 | -1.6254 | -0.2826 |  | 2026-01-05 23:43 | none | FALSE | 0 | 72.6166 | FALSE | FALSE | 0.5244 | 1.5911 | 73.2377 | 7 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.31059 | Confirmed/Materialized Shift | 73.8589 | -1.8653 | Night | 202601 | 2026-01-06 | 1.8653
2026-01-06 01:28 | 72.6584 | FALSE | TRUE | -0.092932 | -0.12807 | -1.1386 | -1.5428 | 0 |  | 2026-01-05 23:43 | none | FALSE | 0 | 72.5655 | FALSE | FALSE | 0.5132 | 1.6045 | 73.1812 | 8 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.30787 | Confirmed/Materialized Shift | 73.797 | -1.6981 | Night | 202601 | 2026-01-06 | 1.6981
2026-01-06 01:43 | 72.3758 | FALSE | TRUE | 0.08903 | 0.12286 | -1.3805 | -1.8717 | -0.2826 |  | 2026-01-05 23:43 | lower | TRUE | 0 | 72.4648 | FALSE | TRUE | 0.5517 | 1.6791 | 73.1106 | 9 | -0.2826 | -0.07065 | 0.12555 | -1.6882 | 0.32287 | Confirmed/Materialized Shift | 73.7563 | -2.2757 | Night | 202601 | 2026-01-06 | 2.2757
2026-01-06 01:58 | 72.3758 | FALSE | TRUE | -0.01762 | -0.02435 | -1.3741 | -1.8632 | 0 |  | 2026-01-05 23:43 | none | FALSE | 0 | 72.3582 | FALSE | FALSE | 0.53 | 1.7061 | 73.054 | 10 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.34793 | Confirmed/Materialized Shift | 73.7499 | -1.9494 | Night | 202601 | 2026-01-06 | 1.9494
2026-01-06 02:13 | 72.3758 | FALSE | TRUE | -0.10255 | -0.1419 | -1.346 | -1.8258 | 0 |  | 2026-01-05 23:43 | none | FALSE | 0 | 72.2732 | FALSE | FALSE | 0.5145 | 1.7071 | 72.9975 | 11 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.36214 | Confirmed/Materialized Shift | 73.7218 | -1.7168 | Night | 202601 | 2026-01-06 | 1.7168
2026-01-06 02:27 | 72.3758 | FALSE | TRUE | -0.1683 | -0.23308 | -1.2987 | -1.7628 | 0 |  | 2026-01-05 23:43 | none | FALSE | 0 | 72.2075 | FALSE | FALSE | 0.5027 | 1.6933 | 72.941 | 12 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.36675 | Confirmed/Materialized Shift | 73.6745 | -1.5411 | Night | 202601 | 2026-01-06 | 1.5411
2026-01-06 02:43 | 72.095 | FALSE | TRUE | 0.00053097 | 0.00073648 | -1.5503 | -2.1052 | -0.2808 |  | 2026-01-05 23:43 | lower | TRUE | 0 | 72.0955 | FALSE | TRUE | 0.5334 | 1.717 | 72.8704 | 13 | -0.2808 | -0.07056 | 0.12539 | -1.6767 | 0.38745 | Confirmed/Materialized Shift | 73.6453 | -2.0014 | Night | 202601 | 2026-01-06 | 2.0014
2026-01-06 02:58 | 72.095 | FALSE | TRUE | -0.083168 | -0.11549 | -1.4929 | -2.0288 | 0 |  | 2026-01-05 23:43 | none | FALSE | 0 | 72.0118 | FALSE | FALSE | 0.5193 | 1.7221 | 72.7999 | 14 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.39402 | Confirmed/Materialized Shift | 73.5879 | -1.7889 | Night | 202601 | 2026-01-06 | 1.7889
2026-01-06 03:13 | 72.095 | FALSE | TRUE | -0.17278 | -0.24023 | -1.4697 | -1.9978 | 0 |  | 2026-01-05 23:43 | none | FALSE | 0 | 71.9222 | FALSE | FALSE | 0.5053 | 1.7126 | 72.7434 | 15 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.41061 | Confirmed/Materialized Shift | 73.5647 | -1.5792 | Night | 202601 | 2026-01-06 | 1.5792
2026-01-06 03:27 | 72.095 | FALSE | TRUE | -0.24523 | -0.34132 | -1.4293 | -1.9439 | 0 |  | 2026-01-05 23:43 | none | FALSE | 0 | 71.8498 | FALSE | FALSE | 0.4943 | 1.6939 | 72.687 | 16 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.41863 | Confirmed/Materialized Shift | 73.5243 | -1.4142 | Night | 202601 | 2026-01-06 | 1.4142
2026-01-06 03:42 | 71.8124 | FALSE | TRUE | -0.079378 | -0.11066 | -1.6875 | -2.2959 | -0.2826 |  | 2026-01-05 23:43 | none | FALSE | 0 | 71.733 | FALSE | FALSE | 0.5214 | 1.7014 | 72.6165 | 17 | -0.2826 | -0.07056 | 0.12539 | -1.6911 | 0.44172 | Confirmed/Materialized Shift | 73.4999 | -1.8203 | Night | 202601 | 2026-01-06 | 1.8203
2026-01-06 03:57 | 71.8124 | FALSE | TRUE | -0.17094 | -0.2386 | -1.6379 | -2.23 | 0 |  | 2026-01-05 23:43 | none | FALSE | 0 | 71.6415 | FALSE | FALSE | 0.5081 | 1.697 | 72.5459 | 18 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.45222 | Confirmed/Materialized Shift | 73.4503 | -1.622 | Night | 202601 | 2026-01-06 | 1.622
2026-01-06 04:12 | 71.8124 | FALSE | TRUE | -0.23907 | -0.33402 | -1.5649 | -2.1327 | 0 |  | 2026-01-05 23:43 | none | FALSE | 0 | 71.5733 | FALSE | FALSE | 0.498 | 1.685 | 72.4753 | 19 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.451 | Confirmed/Materialized Shift | 73.3773 | -1.4699 | Night | 202601 | 2026-01-06 | 1.4699
2026-01-06 04:27 | 71.8124 | FALSE | TRUE | -0.28358 | -0.39646 | -1.4683 | -2.0037 | 0 |  | 2026-01-05 23:43 | none | FALSE | 0 | 71.5288 | FALSE | FALSE | 0.4902 | 1.6684 | 72.4048 | 20 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.43798 | Confirmed/Materialized Shift | 73.2807 | -1.3525 | Night | 202601 | 2026-01-06 | 1.3525
2026-01-06 04:42 | 71.5298 | FALSE | TRUE | -0.1159 | -0.16229 | -1.7247 | -2.3544 | -0.2826 |  | 2026-01-05 23:43 | none | FALSE | 0 | 71.4139 | FALSE | FALSE | 0.5165 | 1.6722 | 72.3342 | 21 | -0.2826 | -0.07056 | 0.12539 | -1.6911 | 0.46016 | Confirmed/Materialized Shift | 73.2545 | -1.7481 | Night | 202601 | 2026-01-06 | 1.7481
2026-01-06 04:57 | 71.5298 | FALSE | TRUE | -0.20675 | -0.28987 | -1.6745 | -2.2874 | 0 |  | 2026-01-05 23:43 | none | FALSE | 0 | 71.3231 | FALSE | FALSE | 0.504 | 1.6671 | 72.2637 | 22 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.4703 | Confirmed/Materialized Shift | 73.2043 | -1.5604 | Night | 202601 | 2026-01-06 | 1.5604
2026-01-06 05:12 | 71.5298 | FALSE | TRUE | -0.27509 | -0.38606 | -1.6017 | -2.1901 | 0 |  | 2026-01-05 23:43 | none | FALSE | 0 | 71.2547 | FALSE | FALSE | 0.4942 | 1.6561 | 72.1931 | 23 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.46919 | Confirmed/Materialized Shift | 73.1315 | -1.4137 | Night | 202601 | 2026-01-06 | 1.4137
2026-01-06 05:27 | 71.5298 | FALSE | TRUE | -0.32076 | -0.45044 | -1.5062 | -2.0623 | 0 |  | 2026-01-05 23:43 | none | FALSE | 0 | 71.209 | FALSE | FALSE | 0.4865 | 1.6412 | 72.1225 | 24 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.45675 | Confirmed/Materialized Shift | 73.036 | -1.2977 | Night | 202601 | 2026-01-06 | 1.2977
2026-01-06 05:42 | 71.5298 | FALSE | TRUE | -0.34179 | -0.48013 | -1.3862 | -1.901 | 0 |  | 2026-01-05 23:43 | none | FALSE | 0 | 71.188 | FALSE | FALSE | 0.4806 | 1.6239 | 72.052 | 25 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.43199 | Confirmed/Materialized Shift | 72.916 | -1.2088 | Night | 202601 | 2026-01-06 | 1.2088
2026-01-06 05:57 | 71.5298 | FALSE | TRUE | -0.33356 | -0.4685 | -1.2368 | -1.6997 | 0 |  | 2026-01-05 23:43 | none | FALSE | 0 | 71.1962 | FALSE | FALSE | 0.4767 | 1.6056 | 71.9814 | 26 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.39259 | Confirmed/Materialized Shift | 72.7666 | -1.1504 | Night | 202601 | 2026-01-06 | 1.1504
2026-01-06 06:12 | 71.8124 | TRUE | FALSE | -0.59335 | -0.83313 | -0.84679 | -1.1654 | 0.2826 |  |  | none | FALSE | 1 | 71.2191 | FALSE | FALSE | 0.052 |  | 71.9391 | 0 | 0.2826 | -0.0423 | 0.13813 | 2.3521 | 0.36003 | Persistence ends | 72.6592 | -0.35197 | Night | 202601 | 2026-01-06 | 0.35197
2026-01-06 06:26 | 71.8124 | FALSE | FALSE | -0.55231 | -0.77506 | -0.72115 | -0.99423 | 0 |  |  | none | FALSE | 1 | 71.2601 | FALSE | FALSE | 0.0462 |  | 71.8968 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.31837 | Normal | 72.5336 | -0.26517 | Night | 202601 | 2026-01-06 | 0.26517
2026-01-06 06:26 | 71.8124 | FALSE | FALSE | -0.53981 | -0.75739 | -0.65231 | -0.90017 | 0 |  |  | none | FALSE | 1 | 71.2726 | FALSE | FALSE | 0.0412 |  | 71.8687 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.29803 | Normal | 72.4647 | -0.18874 | Night | 202601 | 2026-01-06 | 0.18874
2026-01-06 06:27 | 71.8124 | FALSE | FALSE | -0.51824 | -0.7269 | -0.5744 | -0.79351 | 0 |  |  | none | FALSE | 1 | 71.2942 | FALSE | FALSE | 0.0354 |  | 71.8405 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.27316 | Normal | 72.3868 | -0.1028 | Night | 202601 | 2026-01-06 | 0.1028
2026-01-06 06:42 | 71.8124 | FALSE | FALSE | -0.48481 | -0.6797 | -0.48463 | -0.67034 | 0 |  |  | none | FALSE | 1 | 71.3276 | FALSE | FALSE | 0.0286 |  | 71.8123 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.24236 | Normal | 72.297 | 0.00037135 | Night | 202601 | 2026-01-06 | 0.00037135
2026-01-06 06:47 | 71.8124 | FALSE | FALSE | -0.43418 | -0.60828 | -0.37766 | -0.52314 | 0 |  |  | none | FALSE | 1 | 71.3782 | FALSE | FALSE | 0.0379 |  | 71.7841 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.20296 | Normal | 72.1901 | 0.13924 | Night | 202601 | 2026-01-06 | 0.13924
2026-01-06 06:47 | 71.8124 | FALSE | FALSE | -0.42154 | -0.59046 | -0.33676 | -0.46675 | 0 |  |  | none | FALSE | 1 | 71.3909 | FALSE | FALSE | 0.0435 |  | 71.77 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.18957 | Normal | 72.1492 | 0.22361 | Night | 202601 | 2026-01-06 | 0.22361
2026-01-06 06:50 | 72.095 | TRUE | FALSE | -0.70414 | -0.98631 | -0.054158 | -0.075064 | 0.2826 |  |  | none | FALSE | 2 | 71.3909 | TRUE | FALSE | 0.1714 |  | 71.77 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.18957 | Normal | 72.1492 | 1.7143 | Night | 202601 | 2026-01-06 | 1.7143
2026-01-06 06:55 | 71.5298 | TRUE | FALSE | -0.14902 | -0.20877 | -0.57292 | -0.79459 | -0.5652 |  |  | none | FALSE | 3 | 71.3808 | TRUE | FALSE | 0.164 |  | 71.7417 | 0 | -0.5652 | -0.02826 | 0.18107 | -2.9654 | 0.18049 | Normal | 72.1027 | -1.1743 | Night | 202601 | 2026-01-06 | 1.1743
2026-01-06 06:55 | 71.5298 | FALSE | FALSE | -0.14816 | -0.20756 | -0.51554 | -0.71558 | 0 |  |  | none | FALSE | 3 | 71.3816 | FALSE | FALSE | 0.1595 |  | 71.7135 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.16593 | Normal | 72.0453 | -1.1071 | Night | 202601 | 2026-01-06 | 1.1071
2026-01-06 06:55 | 71.5298 | FALSE | FALSE | -0.16857 | -0.23622 | -0.50769 | -0.70475 | 0 |  |  | none | FALSE | 2 | 71.3612 | FALSE | FALSE | 0.124 |  | 71.6994 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.16906 | Normal | 72.0375 | -1.0029 | Night | 202601 | 2026-01-06 | 1.0029
2026-01-06 07:10 | 71.8124 | FALSE | FALSE | -0.45117 | -0.63223 | -0.22509 | -0.31246 | 0.2826 |  |  | none | FALSE | 2 | 71.3612 | FALSE | FALSE | 0.1017 |  | 71.6994 | 0 | 0.2826 | 0 | 0.18338 | 1.5411 | 0.16906 | Normal | 72.0375 | 0.66862 | Night | 202601 | 2026-01-06 | 0.66862
2026-01-06 07:25 | 71.8124 | FALSE | FALSE | -0.45117 | -0.63223 | -0.22509 | -0.31246 | 0 |  |  | none | FALSE | 2 | 71.3612 | FALSE | FALSE | 0.1017 |  | 71.6994 | 0 | 0 | 0 | 0.18338 | 0 | 0.16906 | Normal | 72.0375 | 0.66862 | Day | 202601 | 2026-01-06 | 0.66862
2026-01-06 07:30 | 71.8124 | FALSE | FALSE | -0.45117 | -0.63223 | -0.22509 | -0.31246 | 0 |  |  | none | FALSE | 2 | 71.3612 | FALSE | FALSE | 0.1017 |  | 71.6994 | 0 | 0 | 0 | 0.18338 | 0 | 0.16906 | Normal | 72.0375 | 0.66862 | Day | 202601 | 2026-01-06 | 0.66862
2026-01-06 07:45 | 72.095 | FALSE | FALSE | -0.73869 | -1.0352 | -0.0039263 | -0.0054457 | 0.2826 |  |  | none | FALSE | 2 | 71.3563 | FALSE | FALSE | 0.1891 |  | 71.7276 | 0 | 0.2826 | 0.02826 | 0.18107 | 1.4047 | 0.18565 | Normal | 72.0989 | 1.9789 | Day | 202601 | 2026-01-06 | 1.9789
2026-01-06 07:57 | 71.8124 | FALSE | FALSE | -0.43162 | -0.60468 | -0.29032 | -0.40265 | -0.2826 |  |  | none | FALSE | 2 | 71.3808 | FALSE | FALSE | 0.0832 |  | 71.7417 | 0 | -0.2826 | 0.01413 | 0.19396 | -1.5299 | 0.18049 | Normal | 72.1027 | 0.39144 | Day | 202601 | 2026-01-06 | 0.39144
2026-01-06 07:57 | 72.095 | FALSE | FALSE | -0.70414 | -0.98631 | -0.054158 | -0.075064 | 0.2826 |  |  | none | FALSE | 2 | 71.3909 | FALSE | FALSE | 0.1714 |  | 71.77 | 0 | 0.2826 | 0.02826 | 0.20296 | 1.2532 | 0.18957 | Normal | 72.1492 | 1.7143 | Day | 202601 | 2026-01-06 | 1.7143
2026-01-06 08:12 | 72.095 | FALSE | FALSE | -0.68465 | -0.95875 | -0.091185 | -0.12632 | 0 |  |  | none | FALSE | 1 | 71.4104 | FALSE | FALSE | 0.1306 |  | 71.7983 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.19396 | Normal | 72.1862 | 1.5299 | Day | 202601 | 2026-01-06 | 1.5299
2026-01-06 08:27 | 72.3758 | FALSE | FALSE | -0.98019 | -1.3729 | 0.09027 | 0.12488 | 0.2808 | 2026-01-06 11:29 | 2026-01-06 08:27 | upper | TRUE | 0 | 71.3956 | FALSE | FALSE | 0.2175 | 2.4057 | 71.8406 | 1 | 0.2808 | 0.0423 | 0.21047 | 1.1332 | 0.22248 | Extreme triggered | 72.2855 | 2.4057 | Day | 202601 | 2026-01-06 | 2.4057
2026-01-06 08:30 | 72.3758 | FALSE | FALSE | -0.97296 | -1.3626 | 0.012895 | 0.01782 | 0 |  | 2026-01-06 08:27 | upper | TRUE | 0 | 71.4028 | FALSE | FALSE | 0.2512 | 2.2297 | 71.8829 | 2 | 0 | 0.0423 | 0.21047 | -0.20097 | 0.24002 | Extreme/elevated | 72.3629 | 2.0537 | Day | 202601 | 2026-01-06 | 2.0537
2026-01-06 08:45 | 72.6584 | FALSE | FALSE | -1.3235 | -1.8554 | 0.14291 | 0.19708 | 0.2826 |  | 2026-01-06 08:27 | upper | TRUE | 0 | 71.3349 | FALSE | TRUE | 0.337 | 2.3146 | 71.9252 | 3 | 0.2826 | 0.0423 | 0.21047 | 1.1417 | 0.29516 | Persistent | 72.5155 | 2.4842 | Day | 202601 | 2026-01-06 | 2.4842
2026-01-06 09:00 | 73.2236 | TRUE | FALSE | -2.0523 | -2.8837 | 0.40339 | 0.55396 | 0.5652 |  | 2026-01-06 08:27 | upper | TRUE | 1 | 71.1713 | FALSE | TRUE | 0.4557 | 2.4805 | 71.9957 | 4 | 0.5652 | 0.07056 | 0.24032 | 2.0582 | 0.41224 | Persistent | 72.8202 | 2.9785 | Day | 202601 | 2026-01-06 | 2.9785
2026-01-06 09:15 | 73.2236 | FALSE | FALSE | -2.1418 | -3.0131 | 0.17287 | 0.23664 | 0 |  | 2026-01-06 08:27 | upper | TRUE | 1 | 71.0818 | FALSE | TRUE | 0.471 | 2.4547 | 72.0663 | 5 | 0 | 0.07056 | 0.24032 | -0.2936 | 0.49222 | Persistent | 73.0507 | 2.3512 | Day | 202601 | 2026-01-06 | 2.3512
2026-01-06 09:30 | 73.5062 | FALSE | FALSE | -2.5222 | -3.5532 | 0.18824 | 0.25674 | 0.2826 |  | 2026-01-06 08:27 | upper | TRUE | 1 | 70.984 | FALSE | TRUE | 0.5263 | 2.4327 | 72.151 | 6 | 0.2826 | 0.08469 | 0.24423 | 0.81033 | 0.58349 | Persistent | 73.318 | 2.3226 | Day | 202601 | 2026-01-06 | 2.3226
2026-01-06 09:45 | 73.2236 | FALSE | TRUE | -2.2506 | -3.1711 | -0.24653 | -0.33555 | -0.2826 |  | 2026-01-06 08:27 | none | FALSE | 1 | 70.973 | FALSE | FALSE | 0.5356 | 2.3144 | 72.2215 | 7 | -0.2826 | 0.07056 | 0.25722 | -1.373 | 0.62429 | Confirmed/Materialized Shift | 73.4701 | 1.6051 | Day | 202601 | 2026-01-06 | 1.6051
2026-01-06 10:00 | 73.2236 | FALSE | TRUE | -2.2408 | -3.1568 | -0.37776 | -0.51325 | 0 |  | 2026-01-06 08:27 | none | FALSE | 1 | 70.9828 | FALSE | FALSE | 0.5234 | 2.203 | 72.2921 | 8 | 0 | 0.07056 | 0.25722 | -0.27432 | 0.65463 | Confirmed/Materialized Shift | 73.6014 | 1.4229 | Day | 202601 | 2026-01-06 | 1.4229
2026-01-06 10:15 | 73.5062 | FALSE | TRUE | -2.5243 | -3.5563 | -0.26552 | -0.35993 | 0.2826 |  | 2026-01-06 08:27 | none | FALSE | 1 | 70.9819 | FALSE | FALSE | 0.5365 | 2.1382 | 72.3768 | 9 | 0.2826 | 0.08469 | 0.26088 | 0.75864 | 0.69747 | Confirmed/Materialized Shift | 73.7717 | 1.6193 | Day | 202601 | 2026-01-06 | 1.6193
2026-01-06 10:29 | 73.5062 | FALSE | TRUE | -2.5342 | -3.5707 | -0.41651 | -0.56345 | 0 |  | 2026-01-06 08:27 | none | FALSE | 1 | 70.972 | FALSE | FALSE | 0.5243 | 2.0679 | 72.4474 | 10 | 0 | 0.07056 | 0.25722 | -0.27432 | 0.73768 | Confirmed/Materialized Shift | 73.9227 | 1.4354 | Day | 202601 | 2026-01-06 | 1.4354
2026-01-06 10:44 | 73.7888 | FALSE | TRUE | -2.7532 | -3.8757 | -0.29616 | -0.39975 | 0.2826 |  | 2026-01-06 08:27 | none | FALSE | 1 | 71.0356 | FALSE | FALSE | 0.536 | 2.0264 | 72.5603 | 11 | 0.2826 | 0.11295 | 0.21299 | 0.79653 | 0.76233 | Confirmed/Materialized Shift | 74.085 | 1.6115 | Day | 202601 | 2026-01-06 | 1.6115
2026-01-06 10:56 | 74.0714 | FALSE | TRUE | -2.9695 | -4.1764 | -0.20146 | -0.27124 | 0.2826 |  | 2026-01-06 08:27 | none | FALSE | 1 | 71.1019 | FALSE | FALSE | 0.545 | 2.003 | 72.6874 | 12 | 0.2826 | 0.12708 | 0.21447 | 0.72514 | 0.79274 | Confirmed/Materialized Shift | 74.2729 | 1.7459 | Day | 202601 | 2026-01-06 | 1.7459
2026-01-06 10:59 | 73.7888 | FALSE | TRUE | -2.5484 | -3.5772 | -0.57144 | -0.76847 | -0.2826 |  | 2026-01-06 08:27 | none | FALSE | 1 | 71.2404 | FALSE | FALSE | 0.5131 | 1.9464 | 72.8003 | 13 | -0.2826 | 0.11295 | 0.23188 | -1.7058 | 0.77995 | Confirmed/Materialized Shift | 74.3602 | 1.2673 | Day | 202601 | 2026-01-06 | 1.2673
2026-01-06 11:14 | 74.0714 | FALSE | TRUE | -2.7438 | -3.8467 | -0.42752 | -0.57386 | 0.2826 |  | 2026-01-06 08:27 | none | FALSE | 0 | 71.3276 | FALSE | FALSE | 0.4974 | 1.9117 | 72.9133 | 14 | 0.2826 | 0.11295 | 0.23188 | 0.73161 | 0.79282 | Confirmed/Materialized Shift | 74.4989 | 1.4608 | Day | 202601 | 2026-01-06 | 1.4608
2026-01-06 11:29 | 73.7888 | FALSE | TRUE | -2.3192 | -3.245 | -0.76582 | -1.0272 | -0.2826 |  | 2026-01-06 08:27 | none | FALSE | 0 | 71.4696 | FALSE | FALSE | 0.4671 | 1.8514 | 73.0121 | 15 | -0.2826 | 0.09882 | 0.24723 | -1.5428 | 0.77126 | Confirmed/Materialized Shift | 74.5546 | 1.0071 | Day | 202601 | 2026-01-06 | 1.0071
2026-01-06 11:29 | 73.7888 | FALSE | FALSE | -2.1483 | -2.9988 | -0.79258 | -1.0627 | 0 |  |  | none | FALSE | 0 | 71.6405 | FALSE | FALSE | 0.0615 |  | 73.1109 | 0 | 0 | 0.09882 | 0.24723 | -0.39971 | 0.73523 | Persistence ends | 74.5814 | 0.922 | Day | 202601 | 2026-01-06 | 0.922
2026-01-06 11:44 | 73.7888 | FALSE | FALSE | -2.0115 | -2.8024 | -0.82509 | -1.1058 | 0 |  |  | none | FALSE | 0 | 71.7773 | FALSE | FALSE | 0.0558 |  | 73.1956 | 0 | 0 | 0.08469 | 0.24423 | -0.34676 | 0.70914 | Normal | 74.6139 | 0.83649 | Day | 202601 | 2026-01-06 | 0.83649
2026-01-06 11:59 | 73.5062 | FALSE | FALSE | -1.4903 | -2.0695 | -1.0385 | -1.3932 | -0.2826 |  |  | none | FALSE | 0 | 72.0159 | FALSE | FALSE | 0.0238 |  | 73.2803 | 0 | -0.2826 | 0.08469 | 0.24423 | -1.5039 | 0.63222 | Normal | 74.5447 | 0.35731 | Day | 202601 | 2026-01-06 | 0.35731
2026-01-06 12:14 | 73.5062 | FALSE | FALSE | -1.2924 | -1.7896 | -0.98168 | -1.3179 | 0 |  |  | none | FALSE | 0 | 72.2138 | FALSE | FALSE | 0.0182 |  | 73.3509 | 0 | 0 | 0.07056 | 0.24032 | -0.2936 | 0.56851 | Normal | 74.4879 | 0.27324 | Day | 202601 | 2026-01-06 | 0.27324
2026-01-06 12:29 | 73.5062 | FALSE | FALSE | -1.0568 | -1.4587 | -0.88728 | -1.1927 | 0 |  |  | none | FALSE | 0 | 72.4494 | FALSE | FALSE | 0.0116 |  | 73.4214 | 0 | 0 | 0.07056 | 0.24032 | -0.2936 | 0.48603 | Normal | 74.3935 | 0.17443 | Day | 202601 | 2026-01-06 | 0.17443
2026-01-06 12:44 | 73.5062 | FALSE | FALSE | -0.86659 | -1.193 | -0.81007 | -1.09 | 0 |  |  | none | FALSE | 0 | 72.6396 | FALSE | FALSE | 0.0045 |  | 73.4779 | 0 | 0 | 0.05652 | 0.23555 | -0.23995 | 0.41916 | Normal | 74.3163 | 0.06742 | Day | 202601 | 2026-01-06 | 0.06742
2026-01-06 12:59 | 73.5062 | FALSE | FALSE | -0.63036 | -0.86498 | -0.68688 | -0.9258 | 0 |  |  | none | FALSE | 0 | 72.8758 | FALSE | FALSE | 0.0057 |  | 73.5345 | 0 | 0 | 0.05652 | 0.23555 | -0.23995 | 0.32931 | Normal | 74.1931 | -0.085816 | Day | 202601 | 2026-01-06 | 0.085816
2026-01-06 13:14 | 73.2236 | FALSE | FALSE | -0.19864 | -0.27202 | -0.87688 | -1.1834 | -0.2826 |  |  | none | FALSE | 0 | 73.025 | FALSE | FALSE | 0.0841 |  | 73.5627 | 0 | -0.2826 | 0.02826 | 0.24084 | -1.2907 | 0.26888 | Normal | 74.1005 | -1.2612 | Day | 202601 | 2026-01-06 | 1.2612
2026-01-06 13:28 | 73.2236 | FALSE | FALSE | -0.19864 | -0.27202 | -0.87688 | -1.1834 | 0 |  |  | none | FALSE | 0 | 73.025 | FALSE | FALSE | 0.0841 |  | 73.5627 | 0 | 0 | 0 | 0.20502 | 0 | 0.26888 | Normal | 74.1005 | -1.2612 | Day | 202601 | 2026-01-06 | 1.2612
2026-01-06 13:44 | 73.2236 | FALSE | FALSE | -0.19864 | -0.27202 | -0.87688 | -1.1834 | 0 |  |  | none | FALSE | 0 | 73.025 | FALSE | FALSE | 0.0841 |  | 73.5627 | 0 | 0 | 0 | 0.20502 | 0 | 0.26888 | Normal | 74.1005 | -1.2612 | Day | 202601 | 2026-01-06 | 1.2612
2026-01-06 13:59 | 72.941 | FALSE | FALSE | -0.011956 | -0.016393 | -1.1989 | -1.617 | -0.2826 |  |  | none | FALSE | 0 | 72.929 | FALSE | FALSE | 0.1307 |  | 73.5345 | 0 | -0.2826 | -0.02826 | 0.20296 | -1.2532 | 0.30271 | Normal | 74.1399 | -1.9605 | Day | 202601 | 2026-01-06 | 1.9605
2026-01-06 14:14 | 72.941 | FALSE | FALSE | -0.06835 | -0.093794 | -1.227 | -1.6544 | 0 |  |  | none | FALSE | 0 | 72.8726 | FALSE | FALSE | 0.1193 |  | 73.5203 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.32384 | Normal | 74.168 | -1.7889 | Day | 202601 | 2026-01-06 | 1.7889
2026-01-06 14:28 | 72.941 | FALSE | FALSE | -0.12093 | -0.16606 | -1.2513 | -1.6866 | 0 |  |  | none | FALSE | 0 | 72.8201 | FALSE | FALSE | 0.1098 |  | 73.5062 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.34306 | Normal | 74.1923 | -1.6475 | Day | 202601 | 2026-01-06 | 1.6475
2026-01-06 14:43 | 72.941 | FALSE | FALSE | -0.19426 | -0.26704 | -1.2681 | -1.7089 | 0 |  |  | none | FALSE | 0 | 72.7467 | FALSE | FALSE | 0.0979 |  | 73.4779 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.3656 | Normal | 74.2091 | -1.4686 | Day | 202601 | 2026-01-06 | 1.4686
2026-01-06 14:58 | 72.941 | FALSE | FALSE | -0.26062 | -0.35859 | -1.278 | -1.7219 | 0 |  |  | none | FALSE | 0 | 72.6804 | FALSE | FALSE | 0.0882 |  | 73.4497 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.38465 | Normal | 74.219 | -1.3224 | Day | 202601 | 2026-01-06 | 1.3224
2026-01-06 15:13 | 73.2236 | FALSE | FALSE | -0.56048 | -0.77133 | -0.95612 | -1.2889 | 0.2826 |  |  | none | FALSE | 0 | 72.6631 | FALSE | FALSE | 0.0348 |  | 73.4214 | 0 | 0.2826 | -0.02826 | 0.18107 | 1.7168 | 0.37915 | Normal | 74.1797 | -0.52175 | Day | 202601 | 2026-01-06 | 0.52175
2026-01-06 15:28 | 73.2236 | FALSE | FALSE | -0.54224 | -0.74605 | -0.8531 | -1.1516 | 0 |  |  | none | FALSE | 0 | 72.6814 | FALSE | FALSE | 0.0297 |  | 73.379 | 0 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.34883 | Normal | 74.0767 | -0.44557 | Day | 202601 | 2026-01-06 | 0.44557
2026-01-06 15:43 | 73.2236 | FALSE | FALSE | -0.54597 | -0.75122 | -0.80031 | -1.0811 | 0 |  |  | none | FALSE | 0 | 72.6776 | FALSE | FALSE | 0.0252 |  | 73.3508 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.33657 | Normal | 74.0239 | -0.37784 | Day | 202601 | 2026-01-06 | 0.37784
2026-01-06 15:58 | 72.941 | FALSE | FALSE | -0.25147 | -0.34595 | -0.95797 | -1.2963 | -0.2826 |  |  | none | FALSE | 0 | 72.6895 | FALSE | FALSE | 0.0779 |  | 73.2943 | 0 | -0.2826 | -0.05652 | 0.14784 | -1.5292 | 0.30236 | Normal | 73.899 | -1.1683 | Day | 202601 | 2026-01-06 | 1.1683
2026-01-06 16:13 | 73.2236 | FALSE | FALSE | -0.51608 | -0.7098 | -0.60086 | -0.8139 | 0.2826 |  |  | none | FALSE | 0 | 72.7075 | FALSE | FALSE | 0.0101 |  | 73.266 | 0 | 0.2826 | -0.02826 | 0.15614 | 1.9909 | 0.27923 | Normal | 73.8245 | -0.15181 | Day | 202601 | 2026-01-06 | 0.15181
2026-01-06 16:28 | 72.941 | FALSE | FALSE | -0.23606 | -0.32469 | -0.80126 | -1.0866 | -0.2826 |  |  | none | FALSE | 0 | 72.7049 | FALSE | FALSE | 0.0726 |  | 73.2236 | 0 | -0.2826 | -0.04239 | 0.16593 | -1.4477 | 0.25933 | Normal | 73.7423 | -1.0897 | Day | 202601 | 2026-01-06 | 1.0897
2026-01-06 16:43 | 72.941 | FALSE | FALSE | -0.21914 | -0.30135 | -0.69956 | -0.94997 | 0 |  |  | none | FALSE | 0 | 72.7219 | FALSE | FALSE | 0.0697 |  | 73.1812 | 0 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.22968 | Normal | 73.6406 | -1.0459 | Day | 202601 | 2026-01-06 | 1.0459
2026-01-06 16:58 | 72.6584 | FALSE | FALSE | -0.0081981 | -0.011284 | -0.96904 | -1.3161 | -0.2826 |  |  | none | FALSE | 0 | 72.6502 | FALSE | FALSE | 0.1311 |  | 73.1388 | 0 | -0.2826 | -0.04239 | 0.16593 | -1.4477 | 0.24431 | Normal | 73.6274 | -1.9664 | Day | 202601 | 2026-01-06 | 1.9664
2026-01-06 17:13 | 72.3758 | FALSE | FALSE | 0.1413 | 0.19485 | -1.2717 | -1.7267 | -0.2826 | 2026-01-06 18:12 | 2026-01-06 17:13 | lower | TRUE | 0 | 72.5171 | FALSE | FALSE | 0.2238 | 2.5 | 73.0823 | 1 | -0.2826 | -0.05652 | 0.17396 | -1.2996 | 0.2826 | Extreme triggered | 73.6475 | -2.5 | Day | 202601 | 2026-01-06 | 2.5
2026-01-06 17:27 | 72.095 | FALSE | FALSE | 0.23419 | 0.32379 | -1.5993 | -2.1702 | -0.2808 |  | 2026-01-06 17:13 | lower | TRUE | 0 | 72.3292 | FALSE | FALSE | 0.2934 | 2.5931 | 73.0117 | 2 | -0.2808 | -0.07056 | 0.18038 | -1.1656 | 0.34127 | Extreme/elevated | 73.6943 | -2.6862 | Day | 202601 | 2026-01-06 | 2.6862
2026-01-06 17:42 | 72.3758 | FALSE | FALSE | -0.11778 | -0.163 | -1.2766 | -1.7333 | 0.2808 |  | 2026-01-06 17:13 | none | FALSE | 0 | 72.258 | FALSE | FALSE | 0.2822 | 2.2828 | 72.9552 | 3 | 0.2808 | -0.05652 | 0.19638 | 1.7177 | 0.3486 | Persistent | 73.6524 | -1.6621 | Day | 202601 | 2026-01-06 | 1.6621
2026-01-06 17:57 | 72.3758 | FALSE | FALSE | -0.16949 | -0.23473 | -1.2153 | -1.6514 | 0 |  | 2026-01-06 17:13 | none | FALSE | 0 | 72.2063 | FALSE | FALSE | 0.3293 | 2.0897 | 72.8987 | 4 | 0 | -0.05652 | 0.19638 | 0.28781 | 0.3462 | Persistent | 73.5911 | -1.5104 | Night | 202601 | 2026-01-06 | 1.5104
2026-01-06 18:12 | 72.6584 | FALSE | FALSE | -0.47059 | -0.65189 | -0.89467 | -1.2164 | 0.2826 |  |  | none | FALSE | 0 | 72.1878 | FALSE | FALSE | 0.0414 |  | 72.8704 | 0 | 0.2826 | -0.02826 | 0.2027 | 1.5336 | 0.34131 | Persistence ends | 73.5531 | -0.62125 | Night | 202601 | 2026-01-06 | 0.62125
2026-01-06 18:27 | 72.6584 | FALSE | FALSE | -0.48392 | -0.67049 | -0.85148 | -1.1583 | 0 |  |  | none | FALSE | 0 | 72.1745 | FALSE | FALSE | 0.0367 |  | 72.8422 | 0 | 0 | -0.02826 | 0.2027 | 0.13942 | 0.33385 | Normal | 73.5099 | -0.55049 | Night | 202601 | 2026-01-06 | 0.55049
2026-01-06 18:30 | 72.6584 | FALSE | FALSE | -0.49174 | -0.68139 | -0.80278 | -1.0928 | 0 |  |  | none | FALSE | 0 | 72.1667 | FALSE | FALSE | 0.032 |  | 72.8139 | 0 | 0 | -0.02826 | 0.2027 | 0.13942 | 0.32363 | Normal | 73.4612 | -0.48055 | Night | 202601 | 2026-01-06 | 0.48055
2026-01-06 18:31 | 72.6584 | FALSE | FALSE | -0.50653 | -0.70203 | -0.78931 | -1.0747 | 0 |  |  | none | FALSE | 0 | 72.1519 | FALSE | FALSE | 0.0291 |  | 72.7998 | 0 | 0 | -0.01413 | 0.19368 | 0.072955 | 0.32396 | Normal | 73.4477 | -0.43645 | Night | 202601 | 2026-01-06 | 0.43645
2026-01-06 18:46 | 73.2236 | TRUE | FALSE | -1.0824 | -1.5004 | -0.26305 | -0.35796 | 0.5652 |  |  | none | FALSE | 1 | 72.1412 | FALSE | FALSE | 0.1098 |  | 72.8139 | 0 | 0.5652 | 0.01413 | 0.23308 | 2.3643 | 0.33637 | Normal | 73.4867 | 1.218 | Night | 202601 | 2026-01-06 | 1.218
2026-01-06 19:01 | 73.5062 | FALSE | FALSE | -1.4034 | -1.9464 | -0.075374 | -0.10244 | 0.2826 |  |  | none | FALSE | 1 | 72.1028 | FALSE | FALSE | 0.1483 |  | 72.8422 | 0 | 0.2826 | 0.02826 | 0.24062 | 1.057 | 0.3697 | Normal | 73.5816 | 1.7961 | Night | 202601 | 2026-01-06 | 1.7961
2026-01-06 19:16 | 73.5062 | FALSE | FALSE | -1.4321 | -1.9869 | -0.16055 | -0.21794 | 0 |  |  | none | FALSE | 1 | 72.0741 | FALSE | FALSE | 0.135 |  | 72.8704 | 0 | 0 | 0.02826 | 0.24062 | -0.11745 | 0.39816 | Normal | 73.6668 | 1.5968 | Night | 202601 | 2026-01-06 | 1.5968
2026-01-06 19:30 | 73.5062 | FALSE | FALSE | -1.453 | -2.0165 | -0.23795 | -0.32268 | 0 |  |  | none | FALSE | 1 | 72.0532 | FALSE | FALSE | 0.1244 |  | 72.8987 | 0 | 0 | 0.02826 | 0.24062 | -0.11745 | 0.42273 | Normal | 73.7442 | 1.4371 | Night | 202601 | 2026-01-06 | 1.4371
2026-01-06 19:45 | 73.5062 | FALSE | FALSE | -1.4705 | -2.0414 | -0.2838 | -0.3846 | 0 |  |  | none | FALSE | 1 | 72.0357 | FALSE | FALSE | 0.1188 |  | 72.9128 | 0 | 0 | 0.01413 | 0.23308 | -0.060623 | 0.43858 | Normal | 73.79 | 1.3529 | Night | 202601 | 2026-01-06 | 1.3529
2026-01-06 20:00 | 73.5062 | FALSE | FALSE | -1.4861 | -2.0634 | -0.32761 | -0.44371 | 0 |  |  | none | FALSE | 1 | 72.0201 | FALSE | FALSE | 0.1137 |  | 72.927 | 0 | 0 | 0.01413 | 0.23308 | -0.060623 | 0.45342 | Normal | 73.8338 | 1.2775 | Night | 202601 | 2026-01-06 | 1.2775
2026-01-06 20:15 | 73.5062 | FALSE | FALSE | -1.4998 | -2.0829 | -0.36958 | -0.50027 | 0 |  |  | none | FALSE | 1 | 72.0064 | FALSE | FALSE | 0.1092 |  | 72.9411 | 0 | 0 | 0.01413 | 0.23308 | -0.060623 | 0.46734 | Normal | 73.8758 | 1.2092 | Night | 202601 | 2026-01-06 | 1.2092
2026-01-06 20:29 | 73.5062 | FALSE | FALSE | -1.5051 | -2.0904 | -0.4314 | -0.58347 | 0 |  |  | none | FALSE | 1 | 72.0011 | FALSE | FALSE | 0.1025 |  | 72.9694 | 0 | 0 | 0.02826 | 0.22247 | -0.12703 | 0.48413 | Normal | 73.9376 | 1.1089 | Night | 202601 | 2026-01-06 | 1.1089
2026-01-06 20:44 | 73.5062 | FALSE | FALSE | -1.5146 | -2.1038 | -0.46912 | -0.63415 | 0 |  |  | none | FALSE | 1 | 71.9916 | FALSE | FALSE | 0.0988 |  | 72.9835 | 0 | 0 | 0.01413 | 0.21429 | -0.065939 | 0.49592 | Normal | 73.9753 | 1.054 | Night | 202601 | 2026-01-06 | 1.054
2026-01-06 20:59 | 73.5062 | FALSE | FALSE | -1.513 | -2.1017 | -0.52413 | -0.70799 | 0 |  |  | none | FALSE | 1 | 71.9932 | FALSE | FALSE | 0.0933 |  | 73.0117 | 0 | 0 | 0.02826 | 0.2027 | -0.13942 | 0.50929 | Normal | 74.0303 | 0.97087 | Night | 202601 | 2026-01-06 | 0.97087
2026-01-06 21:15 | 73.5062 | FALSE | FALSE | -1.5076 | -2.094 | -0.57523 | -0.77648 | 0 |  |  | none | FALSE | 0 | 71.9986 | FALSE | FALSE | 0.0597 |  | 73.04 | 0 | 0 | 0.02826 | 0.2027 | -0.13942 | 0.52071 | Normal | 74.0814 | 0.89531 | Night | 202601 | 2026-01-06 | 0.89531
2026-01-06 21:29 | 73.5062 | FALSE | FALSE | -1.4689 | -2.039 | -0.62123 | -0.83806 | 0 |  |  | none | FALSE | 0 | 72.0373 | FALSE | FALSE | 0.0541 |  | 73.0824 | 0 | 0 | 0.04239 | 0.18929 | -0.22394 | 0.52252 | Normal | 74.1274 | 0.81109 | Night | 202601 | 2026-01-06 | 0.81109
2026-01-06 21:44 | 73.7888 | FALSE | FALSE | -1.6707 | -2.3166 | -0.39915 | -0.53803 | 0.2826 |  |  | none | FALSE | 0 | 72.1181 | FALSE | FALSE | 0.0819 |  | 73.153 | 0 | 0.2826 | 0.07065 | 0.18019 | 1.1763 | 0.51746 | Normal | 74.188 | 1.2286 | Night | 202601 | 2026-01-06 | 1.2286
2026-01-06 21:59 | 73.5062 | FALSE | FALSE | -1.1995 | -1.6589 | -0.63428 | -0.8555 | -0.2826 |  |  | none | FALSE | 0 | 72.3067 | FALSE | FALSE | 0.0411 |  | 73.2236 | 0 | -0.2826 | 0.07056 | 0.18038 | -1.9579 | 0.45844 | Normal | 74.1405 | 0.61644 | Night | 202601 | 2026-01-06 | 0.61644
2026-01-06 22:14 | 73.5062 | FALSE | FALSE | -1.0584 | -1.4609 | -0.60621 | -0.81796 | 0 |  |  | none | FALSE | 0 | 72.4478 | FALSE | FALSE | 0.0362 |  | 73.2801 | 0 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.41614 | Normal | 74.1124 | 0.54327 | Night | 202601 | 2026-01-06 | 0.54327
2026-01-06 22:29 | 73.5062 | FALSE | FALSE | -0.88918 | -1.2245 | -0.55006 | -0.74275 | 0 |  |  | none | FALSE | 0 | 72.617 | FALSE | FALSE | 0.0314 |  | 73.3366 | 0 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.35981 | Normal | 74.0563 | 0.47125 | Night | 202601 | 2026-01-06 | 0.47125
2026-01-06 22:44 | 73.5062 | FALSE | FALSE | -0.77485 | -1.0654 | -0.52051 | -0.70314 | 0 |  |  | none | FALSE | 0 | 72.7313 | FALSE | FALSE | 0.0262 |  | 73.379 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.32384 | Normal | 74.0267 | 0.39269 | Night | 202601 | 2026-01-06 | 0.39269
2026-01-06 22:59 | 73.2236 | FALSE | FALSE | -0.37478 | -0.51446 | -0.74216 | -1.0034 | -0.2826 |  |  | none | FALSE | 0 | 72.8488 | FALSE | FALSE | 0.0439 |  | 73.4073 | 0 | -0.2826 | 0.02826 | 0.18107 | -1.7168 | 0.27923 | Normal | 73.9658 | -0.65784 | Night | 202601 | 2026-01-06 | 0.65784
2026-01-06 23:14 | 73.2236 | FALSE | FALSE | -0.23252 | -0.31856 | -0.65642 | -0.8885 | 0 |  |  | none | FALSE | 0 | 72.9911 | FALSE | FALSE | 0.0636 |  | 73.4356 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.22224 | Normal | 73.88 | -0.95372 | Night | 202601 | 2026-01-06 | 0.95372
2026-01-06 23:28 | 73.2236 | FALSE | FALSE | -0.036377 | -0.049703 | -0.5168 | -0.70083 | 0 |  |  | none | FALSE | 0 | 73.1872 | FALSE | FALSE | 0.1158 |  | 73.4638 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.13829 | Normal | 73.7404 | -1.737 | Night | 202601 | 2026-01-06 | 1.737
2026-01-06 23:44 | 73.2236 | FALSE | FALSE | -0.036377 | -0.049703 | -0.5168 | -0.70083 | 0 |  |  | none | FALSE | 0 | 73.1872 | FALSE | FALSE | 0.1158 |  | 73.4638 | 0 | 0 | 0 | 0.12967 | 0 | 0.13829 | Normal | 73.7404 | -1.737 | Night | 202601 | 2026-01-06 | 1.737
2026-01-06 23:59 | 73.2236 | FALSE | FALSE | -0.069603 | -0.095146 | -0.52176 | -0.70752 | 0 |  |  | none | FALSE | 0 | 73.154 | FALSE | FALSE | 0.1019 |  | 73.4497 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14784 | Normal | 73.7454 | -1.5292 | Night | 202601 | 2026-01-06 | 1.5292
2026-01-07 00:14 | 73.2236 | FALSE | FALSE | -0.098978 | -0.13535 | -0.52288 | -0.70902 | 0 |  |  | none | FALSE | 0 | 73.1246 | FALSE | FALSE | 0.0909 |  | 73.4356 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.15546 | Normal | 73.7465 | -1.3633 | Night | 202601 | 2026-01-07 | 1.3633
2026-01-07 00:28 | 73.2236 | FALSE | FALSE | -0.12505 | -0.17106 | -0.52069 | -0.70607 | 0 |  |  | none | FALSE | 0 | 73.0986 | FALSE | FALSE | 0.0817 |  | 73.4214 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.16143 | Normal | 73.7443 | -1.2254 | Night | 202601 | 2026-01-07 | 1.2254
2026-01-07 00:43 | 72.941 | TRUE | FALSE | 0.067509 | 0.092468 | -0.83681 | -1.1342 | -0.2826 | 2026-01-07 00:58 | 2026-01-07 00:43 | lower | TRUE | 1 | 73.0085 | FALSE | FALSE | 0.2424 | 2.351 | 73.3932 | 1 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.19233 | Extreme triggered | 73.7778 | -2.351 | Night | 202601 | 2026-01-07 | 2.351
2026-01-07 00:58 | 73.2236 | TRUE | FALSE | -0.23249 | -0.31851 | -0.54335 | -0.73657 | 0.2826 |  |  | none | FALSE | 2 | 72.9911 | TRUE | FALSE | 0.1106 |  | 73.379 | 0 | 0.2826 | -0.01413 | 0.14424 | 2.0571 | 0.19396 | Persistence ends | 73.7669 | -0.80136 | Night | 202601 | 2026-01-07 | 0.80136
2026-01-07 01:13 | 72.941 | FALSE | FALSE | -0.019304 | -0.026473 | -0.83884 | -1.137 | -0.2826 |  |  | none | FALSE | 2 | 72.9217 | FALSE | FALSE | 0.1845 |  | 73.3508 | 0 | -0.2826 | -0.02826 | 0.15614 | -1.6289 | 0.21454 | Normal | 73.7798 | -1.91 | Night | 202601 | 2026-01-07 | 1.91
2026-01-07 01:28 | 72.941 | FALSE | FALSE | -0.077844 | -0.10684 | -0.84086 | -1.1397 | 0 |  |  | none | FALSE | 2 | 72.8632 | FALSE | FALSE | 0.1679 |  | 73.3225 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.22968 | Normal | 73.7819 | -1.6611 | Night | 202601 | 2026-01-07 | 1.6611
2026-01-07 01:43 | 72.941 | FALSE | FALSE | -0.12756 | -0.17519 | -0.83406 | -1.1305 | 0 |  |  | none | FALSE | 2 | 72.8134 | FALSE | FALSE | 0.1551 |  | 73.2943 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.24041 | Normal | 73.7751 | -1.4694 | Night | 202601 | 2026-01-07 | 1.4694
2026-01-07 01:58 | 72.6584 | FALSE | FALSE | 0.0464 | 0.063819 | -1.1405 | -1.5454 | -0.2826 | 2026-01-07 07:45 | 2026-01-07 01:58 | lower | TRUE | 2 | 72.7048 | FALSE | FALSE | 0.2589 | 2.1696 | 73.2519 | 1 | -0.2826 | -0.04239 | 0.16593 | -1.4477 | 0.27353 | Extreme triggered | 73.7989 | -2.1696 | Night | 202601 | 2026-01-07 | 2.1696
2026-01-07 02:13 | 72.941 | FALSE | FALSE | -0.26753 | -0.36812 | -0.83273 | -1.1288 | 0.2826 |  | 2026-01-07 01:58 | none | FALSE | 2 | 72.6735 | FALSE | FALSE | 0.2399 | 1.5985 | 73.2236 | 2 | 0.2826 | -0.02826 | 0.18107 | 1.7168 | 0.27506 | Extreme/elevated | 73.7737 | -1.0274 | Night | 202601 | 2026-01-07 | 1.0274
2026-01-07 02:28 | 72.6584 | FALSE | FALSE | -0.064992 | -0.089529 | -1.1106 | -1.5055 | -0.2826 |  | 2026-01-07 01:58 | none | FALSE | 2 | 72.5934 | FALSE | FALSE | 0.3472 | 1.6586 | 73.1812 | 3 | -0.2826 | -0.04239 | 0.18957 | -1.2671 | 0.2939 | Persistent | 73.769 | -1.7789 | Night | 202601 | 2026-01-07 | 1.7789
2026-01-07 02:43 | 72.6584 | FALSE | FALSE | -0.092177 | -0.12702 | -1.0248 | -1.3908 | 0 |  | 2026-01-07 01:58 | none | FALSE | 2 | 72.5662 | FALSE | FALSE | 0.397 | 1.6614 | 73.1247 | 4 | 0 | -0.05652 | 0.17396 | 0.32489 | 0.27923 | Persistent | 73.6832 | -1.6699 | Night | 202601 | 2026-01-07 | 1.6699
2026-01-07 02:58 | 72.6584 | FALSE | FALSE | -0.1413 | -0.19485 | -0.9891 | -1.343 | 0 |  | 2026-01-07 01:58 | none | FALSE | 2 | 72.5171 | FALSE | FALSE | 0.4429 | 1.6292 | 73.0823 | 5 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.2826 | Persistent | 73.6475 | -1.5 | Night | 202601 | 2026-01-07 | 1.5
2026-01-07 03:13 | 72.6584 | FALSE | FALSE | -0.17696 | -0.24414 | -0.93998 | -1.2772 | 0 |  | 2026-01-07 01:58 | none | FALSE | 1 | 72.4814 | FALSE | FALSE | 0.4625 | 1.5853 | 73.0399 | 6 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.27923 | Persistent | 73.5984 | -1.3663 | Night | 202601 | 2026-01-07 | 1.3663
2026-01-07 03:27 | 72.3758 | FALSE | TRUE | 0.019788 | 0.027333 | -1.1954 | -1.6248 | -0.2826 |  | 2026-01-07 01:58 | lower | TRUE | 0 | 72.3956 | FALSE | TRUE | 0.5378 | 1.6542 | 72.9834 | 7 | -0.2826 | -0.05652 | 0.17396 | -1.2996 | 0.2939 | Confirmed/Materialized Shift | 73.5712 | -2.0673 | Night | 202601 | 2026-01-07 | 2.0673
2026-01-07 03:42 | 72.3758 | FALSE | TRUE | -0.042425 | -0.058653 | -1.1446 | -1.5568 | 0 |  | 2026-01-07 01:58 | none | FALSE | 0 | 72.3334 | FALSE | FALSE | 0.5238 | 1.6796 | 72.9269 | 8 | 0 | -0.05652 | 0.17396 | 0.32489 | 0.29675 | Confirmed/Materialized Shift | 73.5204 | -1.857 | Night | 202601 | 2026-01-07 | 1.857
2026-01-07 03:57 | 72.3758 | FALSE | TRUE | -0.11587 | -0.16036 | -1.1332 | -1.5416 | 0 |  | 2026-01-07 01:58 | none | FALSE | 0 | 72.2599 | FALSE | FALSE | 0.5086 | 1.6739 | 72.8845 | 9 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.31228 | Confirmed/Materialized Shift | 73.509 | -1.6289 | Night | 202601 | 2026-01-07 | 1.6289
2026-01-07 04:12 | 72.3758 | FALSE | TRUE | -0.17618 | -0.24401 | -1.1088 | -1.5088 | 0 |  | 2026-01-07 01:58 | none | FALSE | 0 | 72.1996 | FALSE | FALSE | 0.4968 | 1.6517 | 72.8421 | 10 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.32123 | Confirmed/Materialized Shift | 73.4846 | -1.4516 | Night | 202601 | 2026-01-07 | 1.4516
2026-01-07 04:27 | 72.095 | FALSE | TRUE | -0.0066336 | -0.0092021 | -1.388 | -1.8888 | -0.2808 |  | 2026-01-07 01:58 | none | FALSE | 0 | 72.0884 | FALSE | FALSE | 0.5321 | 1.6816 | 72.7857 | 11 | -0.2808 | -0.05643 | 0.17384 | -1.2907 | 0.34865 | Confirmed/Materialized Shift | 73.483 | -1.981 | Night | 202601 | 2026-01-07 | 1.981
2026-01-07 04:42 | 72.095 | FALSE | TRUE | -0.09574 | -0.13297 | -1.3642 | -1.8571 | 0 |  | 2026-01-07 01:58 | none | FALSE | 0 | 71.9993 | FALSE | FALSE | 0.5158 | 1.6863 | 72.7292 | 12 | 0 | -0.05643 | 0.17384 | 0.3246 | 0.36499 | Confirmed/Materialized Shift | 73.4592 | -1.7377 | Night | 202601 | 2026-01-07 | 1.7377
2026-01-07 04:57 | 72.095 | FALSE | TRUE | -0.16562 | -0.23026 | -1.3212 | -1.7996 | 0 |  | 2026-01-07 01:58 | none | FALSE | 0 | 71.9294 | FALSE | FALSE | 0.5036 | 1.6762 | 72.6728 | 13 | 0 | -0.05643 | 0.17384 | 0.3246 | 0.37171 | Confirmed/Materialized Shift | 73.4162 | -1.5544 | Night | 202601 | 2026-01-07 | 1.5544
2026-01-07 05:12 | 72.095 | FALSE | TRUE | -0.21734 | -0.30237 | -1.2601 | -1.7178 | 0 |  | 2026-01-07 01:58 | none | FALSE | 0 | 71.8777 | FALSE | FALSE | 0.4941 | 1.6573 | 72.6164 | 14 | 0 | -0.05643 | 0.17384 | 0.3246 | 0.36935 | Confirmed/Materialized Shift | 73.3551 | -1.4116 | Night | 202601 | 2026-01-07 | 1.4116
2026-01-07 05:27 | 72.095 | FALSE | TRUE | -0.25052 | -0.34869 | -1.1804 | -1.6109 | 0 |  | 2026-01-07 01:58 | none | FALSE | 0 | 71.8445 | FALSE | FALSE | 0.4866 | 1.6334 | 72.5599 | 15 | 0 | -0.05643 | 0.17384 | 0.3246 | 0.35773 | Confirmed/Materialized Shift | 73.2754 | -1.2997 | Night | 202601 | 2026-01-07 | 1.2997
2026-01-07 05:42 | 72.095 | FALSE | TRUE | -0.29797 | -0.41502 | -1.1433 | -1.561 | 0 |  | 2026-01-07 01:58 | none | FALSE | 0 | 71.797 | FALSE | FALSE | 0.4782 | 1.6046 | 72.5176 | 16 | 0 | -0.0423 | 0.16579 | 0.25514 | 0.36031 | Confirmed/Materialized Shift | 73.2383 | -1.173 | Night | 202601 | 2026-01-07 | 1.173
2026-01-07 05:57 | 72.095 | FALSE | TRUE | -0.29603 | -0.4123 | -1.0284 | -1.4065 | 0 |  | 2026-01-07 01:58 | none | FALSE | 0 | 71.799 | FALSE | FALSE | 0.4737 | 1.5753 | 72.4612 | 17 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.33112 | Confirmed/Materialized Shift | 73.1234 | -1.106 | Night | 202601 | 2026-01-07 | 1.106
2026-01-07 06:12 | 71.8124 | FALSE | TRUE | -0.089758 | -0.12515 | -1.2745 | -1.7438 | -0.2826 |  | 2026-01-07 01:58 | none | FALSE | 0 | 71.7226 | FALSE | FALSE | 0.5158 | 1.5843 | 72.4048 | 18 | -0.2826 | -0.05643 | 0.1477 | -1.5313 | 0.34107 | Confirmed/Materialized Shift | 73.0869 | -1.7368 | Night | 202601 | 2026-01-07 | 1.7368
2026-01-07 06:26 | 71.8124 | FALSE | TRUE | -0.14614 | -0.20392 | -1.218 | -1.6679 | 0 |  | 2026-01-07 01:58 | none | FALSE | 0 | 71.6663 | FALSE | FALSE | 0.5048 | 1.5836 | 72.3483 | 19 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.34105 | Confirmed/Materialized Shift | 73.0304 | -1.5715 | Night | 202601 | 2026-01-07 | 1.5715
2026-01-07 06:41 | 71.8124 | FALSE | TRUE | -0.18257 | -0.25488 | -1.1416 | -1.5648 | 0 |  | 2026-01-07 01:58 | none | FALSE | 0 | 71.6298 | FALSE | FALSE | 0.4966 | 1.5769 | 72.2919 | 20 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.33105 | Confirmed/Materialized Shift | 72.954 | -1.4485 | Night | 202601 | 2026-01-07 | 1.4485
2026-01-07 06:56 | 71.8124 | FALSE | TRUE | -0.23432 | -0.32736 | -1.1088 | -1.5205 | 0 |  | 2026-01-07 01:58 | none | FALSE | 0 | 71.5781 | FALSE | FALSE | 0.4868 | 1.5638 | 72.2496 | 21 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.33577 | Confirmed/Materialized Shift | 72.9212 | -1.3021 | Night | 202601 | 2026-01-07 | 1.3021
2026-01-07 07:11 | 71.8124 | FALSE | TRUE | -0.23335 | -0.32601 | -0.99493 | -1.3665 | 0 |  | 2026-01-07 01:58 | none | FALSE | 0 | 71.579 | FALSE | FALSE | 0.4827 | 1.5491 | 72.1932 | 22 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.30707 | Confirmed/Materialized Shift | 72.8073 | -1.2401 | Night | 202601 | 2026-01-07 | 1.2401
2026-01-07 07:26 | 71.8124 | FALSE | TRUE | -0.25699 | -0.35915 | -0.93397 | -1.2839 | 0 |  | 2026-01-07 01:58 | none | FALSE | 0 | 71.5554 | FALSE | FALSE | 0.4758 | 1.5311 | 72.1509 | 23 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.29774 | Confirmed/Materialized Shift | 72.7464 | -1.1369 | Day | 202601 | 2026-01-07 | 1.1369
2026-01-07 07:30 | 71.8124 | FALSE | TRUE | -0.26681 | -0.37292 | -0.85919 | -1.1823 | 0 |  | 2026-01-07 01:58 | none | FALSE | 0 | 71.5456 | FALSE | FALSE | 0.4701 | 1.5112 | 72.1086 | 24 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.2815 | Confirmed/Materialized Shift | 72.6716 | -1.0522 | Day | 202601 | 2026-01-07 | 1.0522
2026-01-07 07:45 | 71.8124 | FALSE | FALSE | -0.26017 | -0.36361 | -0.76795 | -1.0581 | 0 |  |  | none | FALSE | 0 | 71.5522 | FALSE | FALSE | 0.0659 |  | 72.0663 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.25703 | Persistence ends | 72.5804 | -0.98778 | Day | 202601 | 2026-01-07 | 0.98778
2026-01-07 08:00 | 71.8124 | FALSE | FALSE | -0.23168 | -0.32366 | -0.65486 | -0.90366 | 0 |  |  | none | FALSE | 0 | 71.5807 | FALSE | FALSE | 0.0636 |  | 72.024 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.22163 | Normal | 72.4673 | -0.95468 | Day | 202601 | 2026-01-07 | 0.95468
2026-01-07 08:15 | 71.8124 | FALSE | FALSE | -0.23672 | -0.33072 | -0.60356 | -0.83346 | 0 |  |  | none | FALSE | 0 | 71.5757 | FALSE | FALSE | 0.0582 |  | 71.9958 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.21007 | Normal | 72.416 | -0.87315 | Day | 202601 | 2026-01-07 | 0.87315
2026-01-07 08:30 | 71.8124 | FALSE | FALSE | -0.23187 | -0.32392 | -0.54237 | -0.74959 | 0 |  |  | none | FALSE | 0 | 71.5805 | FALSE | FALSE | 0.0535 |  | 71.9677 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.19356 | Normal | 72.3548 | -0.80209 | Day | 202601 | 2026-01-07 | 0.80209
2026-01-07 08:30 | 72.095 | TRUE | FALSE | -0.48399 | -0.67585 | -0.20121 | -0.27831 | 0.2826 |  |  | none | FALSE | 1 | 71.611 | FALSE | FALSE | 0.0836 |  | 71.9536 | 0 | 0.2826 | -0.01404 | 0.11113 | 2.6694 | 0.1713 | Normal | 72.2962 | 0.8254 | Day | 202601 | 2026-01-07 | 0.8254
2026-01-07 08:45 | 72.095 | FALSE | FALSE | -0.44392 | -0.61956 | -0.13306 | -0.18422 | 0 |  |  | none | FALSE | 1 | 71.6511 | FALSE | FALSE | 0.1004 |  | 71.9396 | 0 | 0 | -0.01404 | 0.11113 | 0.12634 | 0.14424 | Normal | 72.2281 | 1.0775 | Day | 202601 | 2026-01-07 | 1.0775
2026-01-07 09:00 | 72.3758 | TRUE | FALSE | -0.76479 | -1.068 | 0.079594 | 0.11009 | 0.2808 | 2026-01-07 11:29 | 2026-01-07 09:00 | upper | TRUE | 2 | 71.611 | TRUE | FALSE | 0.2786 | 2.4647 | 71.9536 | 1 | 0.2808 | 0.01404 | 0.11113 | 2.4005 | 0.1713 | Extreme triggered | 72.2962 | 2.4647 | Day | 202601 | 2026-01-07 | 2.4647
2026-01-07 09:15 | 72.6584 | TRUE | FALSE | -1.1396 | -1.5935 | 0.21359 | 0.29483 | 0.2826 |  | 2026-01-07 09:00 | upper | TRUE | 3 | 71.5188 | TRUE | FALSE | 0.3948 | 2.6936 | 71.9818 | 2 | 0.2826 | 0.02817 | 0.12619 | 2.0162 | 0.23151 | Extreme/elevated | 72.4448 | 2.9226 | Day | 202601 | 2026-01-07 | 2.9226
2026-01-07 09:30 | 72.941 | FALSE | FALSE | -1.5477 | -2.1678 | 0.28615 | 0.39385 | 0.2826 |  | 2026-01-07 09:00 | upper | TRUE | 3 | 71.3933 | FALSE | TRUE | 0.451 | 2.7648 | 72.0241 | 3 | 0.2826 | 0.0423 | 0.13813 | 1.7397 | 0.31538 | Persistent | 72.6548 | 2.9073 | Day | 202601 | 2026-01-07 | 2.9073
2026-01-07 09:45 | 73.2236 | FALSE | FALSE | -1.9715 | -2.767 | 0.31465 | 0.43156 | 0.2826 |  | 2026-01-07 09:00 | upper | TRUE | 3 | 71.2521 | FALSE | TRUE | 0.4983 | 2.7635 | 72.0805 | 4 | 0.2826 | 0.05643 | 0.1477 | 1.5313 | 0.41422 | Persistent | 72.909 | 2.7596 | Day | 202601 | 2026-01-07 | 2.7596
2026-01-07 10:00 | 73.2236 | FALSE | FALSE | -2.0603 | -2.8952 | 0.11303 | 0.1546 | 0 |  | 2026-01-07 09:00 | upper | TRUE | 3 | 71.1633 | FALSE | TRUE | 0.5202 | 2.6573 | 72.1369 | 5 | 0 | 0.05643 | 0.1477 | -0.38207 | 0.48681 | Persistent | 73.1106 | 2.2322 | Day | 202601 | 2026-01-07 | 2.2322
2026-01-07 10:15 | 73.2236 | FALSE | FALSE | -2.1178 | -2.9784 | -0.057322 | -0.078222 | 0 |  | 2026-01-07 09:00 | none | FALSE | 3 | 71.1058 | FALSE | FALSE | 0.5549 | 2.5302 | 72.1934 | 6 | 0 | 0.05643 | 0.1477 | -0.38207 | 0.54378 | Persistent | 73.2809 | 1.8946 | Day | 202601 | 2026-01-07 | 1.8946
2026-01-07 10:29 | 73.7888 | TRUE | TRUE | -2.8094 | -3.958 | 0.21212 | 0.2883 | 0.5652 |  | 2026-01-07 09:00 | upper | TRUE | 4 | 70.9794 | TRUE | TRUE | 0.6694 | 2.5011 | 72.2781 | 7 | 0.5652 | 0.08469 | 0.18555 | 2.5896 | 0.64931 | Confirmed/Materialized Shift | 73.5767 | 2.3267 | Day | 202601 | 2026-01-07 | 2.3267
2026-01-07 10:44 | 73.7888 | FALSE | TRUE | -2.8542 | -4.0237 | -0.030345 | -0.041108 | 0 |  | 2026-01-07 09:00 | none | FALSE | 4 | 70.9346 | FALSE | FALSE | 0.6448 | 2.4332 | 72.3769 | 8 | 0 | 0.09882 | 0.16582 | -0.59594 | 0.72113 | Confirmed/Materialized Shift | 73.8191 | 1.9579 | Day | 202601 | 2026-01-07 | 1.9579
2026-01-07 10:59 | 73.7888 | FALSE | TRUE | -2.8596 | -4.0316 | -0.23339 | -0.31529 | 0 |  | 2026-01-07 09:00 | none | FALSE | 3 | 70.9292 | FALSE | FALSE | 0.5989 | 2.3515 | 72.4757 | 9 | 0 | 0.09882 | 0.16582 | -0.59594 | 0.77324 | Confirmed/Materialized Shift | 74.0222 | 1.6982 | Day | 202601 | 2026-01-07 | 1.6982
2026-01-07 11:00 | 74.0714 | FALSE | TRUE | -3.1505 | -4.4422 | -0.18498 | -0.24911 | 0.2826 |  | 2026-01-07 09:00 | none | FALSE | 3 | 70.9209 | FALSE | FALSE | 0.6043 | 2.2942 | 72.5887 | 10 | 0.2826 | 0.11295 | 0.16897 | 1.004 | 0.83387 | Confirmed/Materialized Shift | 74.2564 | 1.7782 | Day | 202601 | 2026-01-07 | 1.7782
2026-01-07 11:03 | 74.0714 | FALSE | TRUE | -3.1201 | -4.3975 | -0.38052 | -0.51109 | 0 |  | 2026-01-07 09:00 | none | FALSE | 2 | 70.9513 | FALSE | FALSE | 0.5615 | 2.2279 | 72.7016 | 11 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.87516 | Confirmed/Materialized Shift | 74.4519 | 1.5652 | Day | 202601 | 2026-01-07 | 1.5652
2026-01-07 11:18 | 74.0714 | FALSE | TRUE | -3.0564 | -4.3039 | -0.54272 | -0.72737 | 0 |  | 2026-01-07 09:00 | none | FALSE | 1 | 71.015 | FALSE | FALSE | 0.5217 | 2.1587 | 72.8145 | 12 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.89979 | Confirmed/Materialized Shift | 74.6141 | 1.3968 | Day | 202601 | 2026-01-07 | 1.3968
2026-01-07 11:29 | 73.7888 | TRUE | FALSE | -2.6603 | -3.7401 | -0.90943 | -1.2175 | -0.2826 |  |  | none | FALSE | 2 | 71.1285 | TRUE | FALSE | 0.1225 |  | 72.9134 | 0 | -0.2826 | 0.09882 | 0.18948 | -2.013 | 0.89243 | Persistence ends | 74.6982 | 0.98095 | Day | 202601 | 2026-01-07 | 0.98095
2026-01-07 11:44 | 73.7888 | FALSE | FALSE | -2.5233 | -3.5406 | -0.97004 | -1.2976 | 0 |  |  | none | FALSE | 2 | 71.2655 | FALSE | FALSE | 0.1164 |  | 73.0122 | 0 | 0 | 0.09882 | 0.18948 | -0.52153 | 0.87332 | Normal | 74.7588 | 0.88926 | Day | 202601 | 2026-01-07 | 0.88926
2026-01-07 11:59 | 73.7888 | FALSE | FALSE | -2.3611 | -3.3056 | -1.0055 | -1.3444 | 0 |  |  | none | FALSE | 2 | 71.4277 | FALSE | FALSE | 0.1108 |  | 73.111 | 0 | 0 | 0.09882 | 0.18948 | -0.52153 | 0.84166 | Normal | 74.7943 | 0.8053 | Day | 202601 | 2026-01-07 | 0.8053
2026-01-07 12:14 | 73.7888 | FALSE | FALSE | -2.1709 | -3.0312 | -1.0129 | -1.3542 | 0 |  |  | none | FALSE | 2 | 71.6179 | FALSE | FALSE | 0.1056 |  | 73.2098 | 0 | 0 | 0.09882 | 0.18948 | -0.52153 | 0.79595 | Normal | 74.8017 | 0.7274 | Day | 202601 | 2026-01-07 | 0.7274
2026-01-07 12:29 | 73.7888 | FALSE | FALSE | -1.9473 | -2.7105 | -0.98698 | -1.3199 | 0 |  |  | none | FALSE | 1 | 71.8415 | FALSE | FALSE | 0.0722 |  | 73.3087 | 0 | 0 | 0.09882 | 0.18948 | -0.52153 | 0.73357 | Normal | 74.7758 | 0.65454 | Day | 202601 | 2026-01-07 | 0.65454
2026-01-07 12:44 | 73.5062 | FALSE | FALSE | -1.401 | -1.9429 | -1.1752 | -1.5737 | -0.2826 |  |  | none | FALSE | 1 | 72.1052 | FALSE | FALSE | 0.0403 |  | 73.3933 | 0 | -0.2826 | 0.08469 | 0.20697 | -1.7746 | 0.64405 | Normal | 74.6814 | 0.17524 | Day | 202601 | 2026-01-07 | 0.17524
2026-01-07 13:14 | 73.5062 | FALSE | FALSE | -1.1763 | -1.6263 | -1.0917 | -1.4635 | 0 |  |  | none | FALSE | 1 | 72.3299 | FALSE | FALSE | 0.0335 |  | 73.4639 | 0 | 0 | 0.07056 | 0.20234 | -0.34872 | 0.56701 | Normal | 74.5979 | 0.074602 | Day | 202601 | 2026-01-07 | 0.074602
2026-01-07 13:28 | 73.5062 | FALSE | FALSE | -0.90497 | -1.2465 | -0.96149 | -1.2912 | 0 |  |  | none | FALSE | 1 | 72.6012 | FALSE | FALSE | 0.0326 |  | 73.5345 | 0 | 0 | 0.07056 | 0.20234 | -0.34872 | 0.46662 | Normal | 74.4677 | -0.060564 | Day | 202601 | 2026-01-07 | 0.060564
2026-01-07 13:43 | 73.5062 | FALSE | FALSE | -0.67352 | -0.92474 | -0.84308 | -1.1339 | 0 |  |  | none | FALSE | 1 | 72.8327 | FALSE | FALSE | 0.0435 |  | 73.591 | 0 | 0 | 0.05652 | 0.19665 | -0.28742 | 0.37915 | Normal | 74.3493 | -0.22361 | Day | 202601 | 2026-01-07 | 0.22361
2026-01-07 13:59 | 73.2236 | FALSE | FALSE | -0.25009 | -0.34271 | -1.0414 | -1.4022 | -0.2826 |  |  | none | FALSE | 1 | 72.9735 | FALSE | FALSE | 0.1103 |  | 73.6192 | 0 | -0.2826 | 0.02826 | 0.20296 | -1.5316 | 0.32287 | Normal | 74.265 | -1.2254 | Day | 202601 | 2026-01-07 | 1.2254
2026-01-07 14:14 | 73.5062 | FALSE | FALSE | -0.4239 | -0.58003 | -0.7065 | -0.95199 | 0.2826 |  |  | none | FALSE | 0 | 73.0823 | FALSE | FALSE | 0.0333 |  | 73.6475 | 0 | 0.2826 | 0.02826 | 0.20296 | 1.2532 | 0.2826 | Normal | 74.2127 | -0.5 | Day | 202601 | 2026-01-07 | 0.5
2026-01-07 14:28 | 73.5062 | FALSE | FALSE | -0.37841 | -0.51746 | -0.68927 | -0.92899 | 0 |  |  | none | FALSE | 0 | 73.1278 | FALSE | FALSE | 0.0388 |  | 73.6616 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.26692 | Normal | 74.1955 | -0.58231 | Day | 202601 | 2026-01-07 | 0.58231
2026-01-07 14:43 | 73.2236 | FALSE | FALSE | -0.095809 | -0.13102 | -0.97187 | -1.3099 | -0.2826 |  |  | none | FALSE | 0 | 73.1278 | FALSE | FALSE | 0.1094 |  | 73.6616 | 0 | -0.2826 | 0 | 0.20502 | -1.3784 | 0.26692 | Normal | 74.1955 | -1.6411 | Day | 202601 | 2026-01-07 | 1.6411
2026-01-07 14:58 | 72.941 | FALSE | FALSE | 0.1123 | 0.15372 | -1.3007 | -1.752 | -0.2826 | 2026-01-07 15:58 | 2026-01-07 14:58 | lower | TRUE | 0 | 73.0533 | FALSE | FALSE | 0.2157 | 2.378 | 73.6475 | 1 | -0.2826 | -0.01413 | 0.21454 | -1.2514 | 0.2971 | Extreme triggered | 74.2417 | -2.378 | Day | 202601 | 2026-01-07 | 2.378
2026-01-07 15:13 | 73.2236 | FALSE | FALSE | -0.22351 | -0.30617 | -1.0148 | -1.3669 | 0.2826 |  | 2026-01-07 14:58 | none | FALSE | 0 | 73.0001 | FALSE | FALSE | 0.1995 | 1.828 | 73.6192 | 2 | 0.2826 | -0.02826 | 0.18107 | 1.7168 | 0.30957 | Extreme/elevated | 74.2384 | -1.278 | Day | 202601 | 2026-01-07 | 1.278
2026-01-07 15:28 | 73.2236 | FALSE | FALSE | -0.27049 | -0.37077 | -1.0053 | -1.3543 | 0 |  | 2026-01-07 14:58 | none | FALSE | 0 | 72.9531 | FALSE | FALSE | 0.2482 | 1.6026 | 73.591 | 3 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.31894 | Persistent | 74.2289 | -1.1519 | Day | 202601 | 2026-01-07 | 1.1519
2026-01-07 15:43 | 73.2236 | FALSE | FALSE | -0.3118 | -0.42764 | -0.99004 | -1.334 | 0 |  | 2026-01-07 14:58 | none | FALSE | 0 | 72.9118 | FALSE | FALSE | 0.298 | 1.4625 | 73.5627 | 4 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.32546 | Persistent | 74.2136 | -1.042 | Day | 202601 | 2026-01-07 | 1.042
2026-01-07 15:58 | 73.2236 | FALSE | FALSE | -0.32445 | -0.44507 | -0.91791 | -1.238 | 0 |  |  | none | FALSE | 0 | 72.8992 | FALSE | FALSE | 0.0637 |  | 73.5203 | 0 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.31059 | Persistence ends | 74.1415 | -0.95538 | Day | 202601 | 2026-01-07 | 0.95538
2026-01-07 16:13 | 72.941 | FALSE | FALSE | -0.092932 | -0.12757 | -1.1386 | -1.5369 | -0.2826 |  |  | none | FALSE | 0 | 72.8481 | FALSE | FALSE | 0.1132 |  | 73.4638 | 0 | -0.2826 | -0.05652 | 0.17396 | -1.2996 | 0.30787 | Normal | 74.0796 | -1.6981 | Day | 202601 | 2026-01-07 | 1.6981
2026-01-07 16:28 | 72.941 | FALSE | FALSE | -0.12151 | -0.16687 | -1.0541 | -1.4245 | 0 |  |  | none | FALSE | 0 | 72.8195 | FALSE | FALSE | 0.1058 |  | 73.4073 | 0 | 0 | -0.05652 | 0.17396 | 0.32489 | 0.2939 | Normal | 73.9951 | -1.5866 | Day | 202601 | 2026-01-07 | 1.5866
2026-01-07 16:43 | 72.941 | FALSE | FALSE | -0.1703 | -0.23403 | -1.0181 | -1.3766 | 0 |  |  | none | FALSE | 0 | 72.7707 | FALSE | FALSE | 0.0951 |  | 73.3649 | 0 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.2971 | Normal | 73.9591 | -1.4268 | Day | 202601 | 2026-01-07 | 1.4268
2026-01-07 16:58 | 72.6584 | FALSE | FALSE | 0.012109 | 0.016663 | -1.2879 | -1.7416 | -0.2826 | 2026-01-07 18:27 | 2026-01-07 16:58 | lower | TRUE | 0 | 72.6705 | FALSE | FALSE | 0.193 | 2.038 | 73.3084 | 1 | -0.2826 | -0.05652 | 0.17396 | -1.2996 | 0.31894 | Extreme triggered | 73.9463 | -2.038 | Day | 202601 | 2026-01-07 | 2.038
2026-01-07 17:13 | 72.3758 | FALSE | FALSE | 0.14056 | 0.19384 | -1.5833 | -2.1408 | -0.2826 |  | 2026-01-07 16:58 | lower | TRUE | 0 | 72.5164 | FALSE | FALSE | 0.2736 | 2.2138 | 73.2377 | 2 | -0.2826 | -0.07065 | 0.18049 | -1.1743 | 0.36068 | Extreme/elevated | 73.9591 | -2.3897 | Day | 202601 | 2026-01-07 | 2.3897
2026-01-07 17:27 | 72.3758 | FALSE | FALSE | 0.021978 | 0.030358 | -1.5606 | -2.1107 | 0 |  | 2026-01-07 16:58 | lower | TRUE | 0 | 72.3978 | FALSE | TRUE | 0.3086 | 2.1616 | 73.1671 | 3 | 0 | -0.07065 | 0.18049 | 0.39144 | 0.38465 | Persistent | 73.9364 | -2.0571 | Day | 202601 | 2026-01-07 | 2.0571
2026-01-07 17:42 | 72.095 | FALSE | FALSE | 0.13756 | 0.19043 | -1.8372 | -2.485 | -0.2808 |  | 2026-01-07 16:58 | lower | TRUE | 0 | 72.2326 | FALSE | TRUE | 0.3835 | 2.2021 | 73.0824 | 4 | -0.2808 | -0.08469 | 0.18555 | -1.0569 | 0.42492 | Persistent | 73.9322 | -2.3237 | Day | 202601 | 2026-01-07 | 2.3237
2026-01-07 17:57 | 72.095 | FALSE | FALSE | -0.015207 | -0.021097 | -1.8489 | -2.5004 | 0 |  | 2026-01-07 16:58 | none | FALSE | 0 | 72.0798 | FALSE | FALSE | 0.4169 | 2.1552 | 73.0118 | 5 | 0 | -0.07056 | 0.18038 | 0.39118 | 0.46602 | Persistent | 73.9439 | -1.9674 | Night | 202601 | 2026-01-07 | 1.9674
2026-01-07 18:12 | 72.3758 | FALSE | FALSE | -0.36333 | -0.50454 | -1.5224 | -2.0601 | 0.2808 |  | 2026-01-07 16:58 | none | FALSE | 0 | 72.0125 | FALSE | FALSE | 0.4248 | 2.0009 | 72.9553 | 6 | 0.2808 | -0.05652 | 0.19638 | 1.7177 | 0.47142 | Persistent | 73.8982 | -1.2293 | Night | 202601 | 2026-01-07 | 1.2293
2026-01-07 18:27 | 72.6584 | FALSE | FALSE | -0.65984 | -0.91646 | -1.1689 | -1.5833 | 0.2826 |  |  | none | FALSE | 0 | 71.9986 | FALSE | FALSE | 0.0371 |  | 72.9129 | 0 | 0.2826 | -0.04239 | 0.21033 | 1.5452 | 0.45718 | Persistence ends | 73.8273 | -0.55672 | Night | 202601 | 2026-01-07 | 0.55672
2026-01-07 18:30 | 72.3758 | FALSE | FALSE | -0.41898 | -0.58226 | -1.3802 | -1.8713 | -0.2826 |  |  | none | FALSE | 0 | 71.9568 | FALSE | FALSE | 0.0712 |  | 72.8564 | 0 | -0.2826 | -0.05652 | 0.21673 | -1.0432 | 0.44979 | Normal | 73.756 | -1.0685 | Night | 202601 | 2026-01-07 | 1.0685
2026-01-07 18:31 | 72.3758 | FALSE | FALSE | -0.46839 | -0.65137 | -1.3448 | -1.8242 | 0 |  |  | none | FALSE | 0 | 71.9074 | FALSE | FALSE | 0.0644 |  | 72.814 | 0 | 0 | -0.04239 | 0.21033 | 0.20154 | 0.4533 | Normal | 73.7206 | -0.96672 | Night | 202601 | 2026-01-07 | 0.96672
2026-01-07 18:46 | 73.2236 | TRUE | FALSE | -1.2929 | -1.7975 | -0.44549 | -0.60472 | 0.8478 |  |  | none | FALSE | 1 | 71.9307 | FALSE | FALSE | 0.0936 |  | 72.7999 | 0 | 0.8478 | -0.01413 | 0.28204 | 3.0561 | 0.4346 | Normal | 73.6691 | 0.97495 | Night | 202601 | 2026-01-07 | 0.97495
2026-01-07 19:01 | 73.5062 | FALSE | FALSE | -1.5755 | -2.1903 | -0.16289 | -0.22111 | 0.2826 |  |  | none | FALSE | 1 | 71.9307 | FALSE | FALSE | 0.1369 |  | 72.7999 | 0 | 0.2826 | 0 | 0.28976 | 0.9753 | 0.4346 | Normal | 73.6691 | 1.6252 | Night | 202601 | 2026-01-07 | 1.6252
2026-01-07 19:16 | 73.5062 | FALSE | FALSE | -1.5988 | -2.2234 | -0.21441 | -0.29084 | 0 |  |  | none | FALSE | 1 | 71.9074 | FALSE | FALSE | 0.1304 |  | 72.814 | 0 | 0 | 0.01413 | 0.28204 | -0.0501 | 0.4533 | Normal | 73.7206 | 1.527 | Night | 202601 | 2026-01-07 | 1.527
2026-01-07 19:30 | 73.7888 | FALSE | FALSE | -1.9379 | -2.6971 | -0.073085 | -0.098948 | 0.2826 |  |  | none | FALSE | 1 | 71.8509 | FALSE | FALSE | 0.1522 |  | 72.8564 | 0 | 0.2826 | 0.04239 | 0.27904 | 0.86084 | 0.50274 | Normal | 73.8619 | 1.8546 | Night | 202601 | 2026-01-07 | 1.8546
2026-01-07 19:45 | 73.7888 | FALSE | FALSE | -1.9822 | -2.7605 | -0.17395 | -0.23518 | 0 |  |  | none | FALSE | 1 | 71.8066 | FALSE | FALSE | 0.1404 |  | 72.8847 | 0 | 0 | 0.02826 | 0.27334 | -0.10339 | 0.53904 | Normal | 73.9627 | 1.6773 | Night | 202601 | 2026-01-07 | 1.6773
2026-01-07 20:00 | 73.7888 | FALSE | FALSE | -2.019 | -2.8132 | -0.26729 | -0.36092 | 0 |  |  | none | FALSE | 1 | 71.7698 | FALSE | FALSE | 0.1307 |  | 72.9129 | 0 | 0 | 0.02826 | 0.27334 | -0.10339 | 0.57158 | Normal | 74.0561 | 1.5324 | Night | 202601 | 2026-01-07 | 1.5324
2026-01-07 20:15 | 73.7888 | FALSE | FALSE | -2.0496 | -2.857 | -0.35432 | -0.47788 | 0 |  |  | none | FALSE | 1 | 71.7392 | FALSE | FALSE | 0.1226 |  | 72.9412 | 0 | 0 | 0.02826 | 0.27334 | -0.10339 | 0.60097 | Normal | 74.1431 | 1.4104 | Night | 202601 | 2026-01-07 | 1.4104
2026-01-07 20:29 | 74.0714 | FALSE | FALSE | -2.3875 | -3.3306 | -0.21187 | -0.28522 | 0.2826 |  |  | none | FALSE | 1 | 71.6839 | FALSE | FALSE | 0.1402 |  | 72.9836 | 0 | 0.2826 | 0.04239 | 0.27904 | 0.86084 | 0.64985 | Normal | 74.2833 | 1.674 | Night | 202601 | 2026-01-07 | 1.674
2026-01-07 20:44 | 74.0714 | FALSE | FALSE | -2.4186 | -3.3754 | -0.35596 | -0.47827 | 0 |  |  | none | FALSE | 1 | 71.6528 | FALSE | FALSE | 0.1277 |  | 73.0401 | 0 | 0 | 0.05652 | 0.26868 | -0.21036 | 0.69364 | Normal | 74.4274 | 1.4868 | Night | 202601 | 2026-01-07 | 1.4868
2026-01-07 20:59 | 74.0714 | FALSE | FALSE | -2.4352 | -3.3995 | -0.48566 | -0.6514 | 0 |  |  | none | FALSE | 1 | 71.6362 | FALSE | FALSE | 0.1176 |  | 73.0966 | 0 | 0 | 0.05652 | 0.26868 | -0.21036 | 0.73023 | Normal | 74.5571 | 1.3349 | Night | 202601 | 2026-01-07 | 1.3349
2026-01-07 21:14 | 74.0714 | FALSE | FALSE | -2.4396 | -3.4057 | -0.60305 | -0.80757 | 0 |  |  | none | FALSE | 0 | 71.6318 | FALSE | FALSE | 0.0805 |  | 73.1531 | 0 | 0 | 0.05652 | 0.26868 | -0.21036 | 0.76066 | Normal | 74.6745 | 1.2072 | Night | 202601 | 2026-01-07 | 1.2072
2026-01-07 21:29 | 74.0714 | FALSE | FALSE | -2.4031 | -3.353 | -0.70782 | -0.94655 | 0 |  |  | none | FALSE | 0 | 71.6683 | FALSE | FALSE | 0.0727 |  | 73.2238 | 0 | 0 | 0.07065 | 0.25709 | -0.27481 | 0.77772 | Normal | 74.7792 | 1.0899 | Night | 202601 | 2026-01-07 | 1.0899
2026-01-07 21:44 | 73.7888 | FALSE | FALSE | -2.0156 | -2.8083 | -1.0269 | -1.3725 | -0.2826 |  |  | none | FALSE | 0 | 71.7732 | FALSE | FALSE | 0.0433 |  | 73.2944 | 0 | -0.2826 | 0.07065 | 0.25709 | -1.374 | 0.76062 | Normal | 74.8157 | 0.64995 | Night | 202601 | 2026-01-07 | 0.64995
2026-01-07 21:59 | 73.7888 | FALSE | FALSE | -1.8958 | -2.637 | -1.0483 | -1.4008 | 0 |  |  | none | FALSE | 0 | 71.893 | FALSE | FALSE | 0.0384 |  | 73.3651 | 0 | 0 | 0.07065 | 0.25709 | -0.27481 | 0.73603 | Normal | 74.8371 | 0.57568 | Night | 202601 | 2026-01-07 | 0.57568
2026-01-07 22:14 | 73.7888 | FALSE | FALSE | -1.6936 | -2.3492 | -1.0156 | -1.3577 | 0 |  |  | none | FALSE | 0 | 72.0952 | FALSE | FALSE | 0.0334 |  | 73.4498 | 0 | 0 | 0.08469 | 0.24423 | -0.34676 | 0.67731 | Normal | 74.8044 | 0.50056 | Night | 202601 | 2026-01-07 | 0.50056
2026-01-07 22:29 | 73.7888 | FALSE | FALSE | -1.4554 | -2.0121 | -0.94673 | -1.2668 | 0 |  |  | none | FALSE | 0 | 72.3334 | FALSE | FALSE | 0.0282 |  | 73.5345 | 0 | 0 | 0.08469 | 0.24423 | -0.34676 | 0.60054 | Normal | 74.7355 | 0.42352 | Night | 202601 | 2026-01-07 | 0.42352
2026-01-07 22:44 | 73.7888 | FALSE | FALSE | -1.2573 | -1.7334 | -0.88988 | -1.1916 | 0 |  |  | none | FALSE | 0 | 72.5315 | FALSE | FALSE | 0.0228 |  | 73.6051 | 0 | 0 | 0.07065 | 0.24041 | -0.29388 | 0.53678 | Normal | 74.6787 | 0.34221 | Night | 202601 | 2026-01-07 | 0.34221
2026-01-07 22:59 | 73.7888 | FALSE | FALSE | -1.1057 | -1.5213 | -0.85136 | -1.1406 | 0 |  |  | none | FALSE | 0 | 72.6831 | FALSE | FALSE | 0.0173 |  | 73.6616 | 0 | 0 | 0.05652 | 0.23555 | -0.23995 | 0.48926 | Normal | 74.6402 | 0.25992 | Night | 202601 | 2026-01-07 | 0.25992
2026-01-07 23:14 | 73.7888 | FALSE | FALSE | -0.82582 | -1.1318 | -0.71278 | -0.95673 | 0 |  |  | none | FALSE | 0 | 72.963 | FALSE | FALSE | 0.0098 |  | 73.7323 | 0 | 0 | 0.07065 | 0.22224 | -0.31791 | 0.38465 | Normal | 74.5016 | 0.14694 | Night | 202601 | 2026-01-07 | 0.14694
2026-01-07 23:28 | 73.7888 | FALSE | FALSE | -0.41494 | -0.56552 | -0.4432 | -0.59705 | 0 |  |  | none | FALSE | 0 | 73.3739 | FALSE | FALSE | 0.0044 |  | 73.8029 | 0 | 0 | 0.07065 | 0.22224 | -0.31791 | 0.21454 | Normal | 74.232 | -0.065863 | Night | 202601 | 2026-01-07 | 0.065863
2026-01-07 23:43 | 73.5062 | TRUE | FALSE | -0.051277 | -0.069807 | -0.673 | -0.90726 | -0.2826 |  |  | none | FALSE | 1 | 73.4549 | FALSE | FALSE | 0.143 |  | 73.8171 | 0 | -0.2826 | 0.01413 | 0.14424 | -2.0571 | 0.18107 | Normal | 74.1792 | -1.7168 | Night | 202601 | 2026-01-07 | 1.7168
2026-01-07 23:58 | 73.5062 | FALSE | FALSE | -0.051277 | -0.069807 | -0.673 | -0.90726 | 0 |  |  | none | FALSE | 1 | 73.4549 | FALSE | FALSE | 0.143 |  | 73.8171 | 0 | 0 | 0 | 0.12967 | 0 | 0.18107 | Normal | 74.1792 | -1.7168 | Night | 202601 | 2026-01-07 | 1.7168
2026-01-08 00:14 | 73.5062 | FALSE | FALSE | -0.051277 | -0.069807 | -0.673 | -0.90726 | 0 |  |  | none | FALSE | 1 | 73.4549 | FALSE | FALSE | 0.143 |  | 73.8171 | 0 | 0 | 0 | 0.12967 | 0 | 0.18107 | Normal | 74.1792 | -1.7168 | Night | 202601 | 2026-01-08 | 1.7168
2026-01-08 00:28 | 73.5062 | FALSE | FALSE | -0.091185 | -0.12421 | -0.68465 | -0.92282 | 0 |  |  | none | FALSE | 1 | 73.415 | FALSE | FALSE | 0.1306 |  | 73.8029 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.19396 | Normal | 74.1908 | -1.5299 | Night | 202601 | 2026-01-08 | 1.5299
2026-01-08 00:43 | 73.2236 | TRUE | FALSE | 0.084453 | 0.1152 | -1.0177 | -1.3708 | -0.2826 | 2026-01-08 07:11 | 2026-01-08 00:43 | lower | TRUE | 2 | 73.3081 | TRUE | FALSE | 0.2718 | 2.362 | 73.7747 | 1 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.23331 | Extreme triggered | 74.2413 | -2.362 | Night | 202601 | 2026-01-08 | 2.362
2026-01-08 00:58 | 73.2236 | FALSE | FALSE | -0.0046923 | -0.0064086 | -1.0503 | -1.4141 | 0 |  | 2026-01-08 00:43 | none | FALSE | 2 | 73.2189 | FALSE | FALSE | 0.3036 | 2.1721 | 73.7464 | 2 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.26375 | Extreme/elevated | 74.2739 | -1.9822 | Night | 202601 | 2026-01-08 | 1.9822
2026-01-08 01:13 | 73.2236 | FALSE | FALSE | -0.081697 | -0.1117 | -1.0708 | -1.4413 | 0 |  | 2026-01-08 00:43 | none | FALSE | 2 | 73.1419 | FALSE | FALSE | 0.343 | 2.0202 | 73.7181 | 3 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.28812 | Persistent | 74.2944 | -1.7165 | Night | 202601 | 2026-01-08 | 1.7165
2026-01-08 01:28 | 73.2236 | FALSE | FALSE | -0.13921 | -0.19047 | -1.0435 | -1.4051 | 0 |  | 2026-01-08 00:43 | none | FALSE | 2 | 73.0844 | FALSE | FALSE | 0.3877 | 1.8975 | 73.6758 | 4 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.29568 | Persistent | 74.2671 | -1.5292 | Night | 202601 | 2026-01-08 | 1.5292
2026-01-08 01:43 | 73.2236 | FALSE | FALSE | -0.18373 | -0.25154 | -1.0033 | -1.3516 | 0 |  | 2026-01-08 00:43 | none | FALSE | 2 | 73.0399 | FALSE | FALSE | 0.4349 | 1.7941 | 73.6334 | 5 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.29675 | Persistent | 74.2269 | -1.3809 | Night | 202601 | 2026-01-08 | 1.3809
2026-01-08 01:58 | 73.2236 | FALSE | FALSE | -0.2154 | -0.29503 | -0.95016 | -1.281 | 0 |  | 2026-01-08 00:43 | none | FALSE | 2 | 73.0082 | FALSE | FALSE | 0.4841 | 1.7053 | 73.591 | 6 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.29139 | Persistent | 74.1738 | -1.2608 | Night | 202601 | 2026-01-08 | 1.2608
2026-01-08 02:13 | 72.941 | FALSE | TRUE | -0.011956 | -0.016393 | -1.1989 | -1.617 | -0.2826 |  | 2026-01-08 00:43 | none | FALSE | 1 | 72.929 | FALSE | FALSE | 0.5593 | 1.7417 | 73.5345 | 7 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.30271 | Confirmed/Materialized Shift | 74.1399 | -1.9605 | Night | 202601 | 2026-01-08 | 1.9605
2026-01-08 02:27 | 72.941 | FALSE | TRUE | -0.068476 | -0.093966 | -1.1424 | -1.542 | 0 |  | 2026-01-08 00:43 | none | FALSE | 1 | 72.8725 | FALSE | FALSE | 0.5468 | 1.7457 | 73.4779 | 8 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.30271 | Confirmed/Materialized Shift | 74.0834 | -1.7738 | Night | 202601 | 2026-01-08 | 1.7738
2026-01-08 02:43 | 72.941 | FALSE | TRUE | -0.13736 | -0.18868 | -1.1265 | -1.5209 | 0 |  | 2026-01-08 00:43 | none | FALSE | 1 | 72.8036 | FALSE | FALSE | 0.5329 | 1.7257 | 73.4356 | 9 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.31596 | Confirmed/Materialized Shift | 74.0675 | -1.5652 | Night | 202601 | 2026-01-08 | 1.5652
2026-01-08 02:58 | 72.941 | FALSE | TRUE | -0.19357 | -0.26609 | -1.0979 | -1.4829 | 0 |  | 2026-01-08 00:43 | none | FALSE | 1 | 72.7474 | FALSE | FALSE | 0.5219 | 1.6932 | 73.3932 | 10 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.32287 | Confirmed/Materialized Shift | 74.0389 | -1.4005 | Night | 202601 | 2026-01-08 | 1.4005
2026-01-08 03:13 | 72.6584 | FALSE | TRUE | -0.01762 | -0.024256 | -1.3741 | -1.8561 | -0.2826 |  | 2026-01-08 00:43 | none | FALSE | 0 | 72.6408 | FALSE | FALSE | 0.53 | 1.7164 | 73.3366 | 11 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.34793 | Confirmed/Materialized Shift | 74.0325 | -1.9494 | Night | 202601 | 2026-01-08 | 1.9494
2026-01-08 03:27 | 72.6584 | FALSE | TRUE | -0.10255 | -0.14134 | -1.346 | -1.8188 | 0 |  | 2026-01-08 00:43 | none | FALSE | 0 | 72.5558 | FALSE | FALSE | 0.5145 | 1.7165 | 73.2801 | 12 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.36214 | Confirmed/Materialized Shift | 74.0044 | -1.7168 | Night | 202601 | 2026-01-08 | 1.7168
2026-01-08 03:42 | 72.6584 | FALSE | TRUE | -0.1683 | -0.23217 | -1.2987 | -1.756 | 0 |  | 2026-01-08 00:43 | none | FALSE | 0 | 72.4901 | FALSE | FALSE | 0.5027 | 1.703 | 73.2236 | 13 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.36675 | Confirmed/Materialized Shift | 73.9571 | -1.5411 | Night | 202601 | 2026-01-08 | 1.5411
2026-01-08 03:57 | 72.3758 | FALSE | TRUE | 0.0018614 | 0.0025718 | -1.5524 | -2.0999 | -0.2826 |  | 2026-01-08 00:43 | lower | TRUE | 0 | 72.3777 | FALSE | TRUE | 0.5337 | 1.7245 | 73.153 | 14 | -0.2826 | -0.07065 | 0.12555 | -1.6882 | 0.38764 | Confirmed/Materialized Shift | 73.9282 | -2.0048 | Night | 202601 | 2026-01-08 | 2.0048
2026-01-08 04:12 | 72.3758 | FALSE | TRUE | -0.082226 | -0.11374 | -1.4952 | -2.0241 | 0 |  | 2026-01-08 00:43 | none | FALSE | 0 | 72.2936 | FALSE | FALSE | 0.5194 | 1.729 | 73.0823 | 15 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.39436 | Confirmed/Materialized Shift | 73.871 | -1.7915 | Night | 202601 | 2026-01-08 | 1.7915
2026-01-08 04:27 | 72.3758 | FALSE | TRUE | -0.13944 | -0.19303 | -1.4111 | -1.9125 | 0 |  | 2026-01-08 00:43 | none | FALSE | 0 | 72.2364 | FALSE | FALSE | 0.5094 | 1.7235 | 73.0117 | 16 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.38764 | Confirmed/Materialized Shift | 73.7869 | -1.6403 | Night | 202601 | 2026-01-08 | 1.6403
2026-01-08 04:42 | 72.3758 | FALSE | TRUE | -0.20886 | -0.28942 | -1.3675 | -1.8544 | 0 |  | 2026-01-08 00:43 | none | FALSE | 0 | 72.1669 | FALSE | FALSE | 0.498 | 1.7086 | 72.9551 | 17 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.3941 | Confirmed/Materialized Shift | 73.7433 | -1.47 | Night | 202601 | 2026-01-08 | 1.47
2026-01-08 04:57 | 72.3758 | FALSE | TRUE | -0.26111 | -0.36207 | -1.3067 | -1.7735 | 0 |  | 2026-01-08 00:43 | none | FALSE | 0 | 72.1147 | FALSE | FALSE | 0.4889 | 1.6877 | 72.8986 | 18 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.39196 | Confirmed/Materialized Shift | 73.6825 | -1.3338 | Night | 202601 | 2026-01-08 | 1.3338
2026-01-08 05:12 | 72.3758 | FALSE | TRUE | -0.29588 | -0.41048 | -1.2285 | -1.669 | 0 |  | 2026-01-08 00:43 | none | FALSE | 0 | 72.0799 | FALSE | FALSE | 0.4816 | 1.6633 | 72.8421 | 19 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.38108 | Confirmed/Materialized Shift | 73.6043 | -1.2236 | Night | 202601 | 2026-01-08 | 1.2236
2026-01-08 05:27 | 72.095 | FALSE | TRUE | -0.088053 | -0.12228 | -1.4411 | -1.9597 | -0.2808 |  | 2026-01-08 00:43 | none | FALSE | 0 | 72.0069 | FALSE | FALSE | 0.518 | 1.6686 | 72.7715 | 20 | -0.2808 | -0.07056 | 0.12539 | -1.6767 | 0.38229 | Confirmed/Materialized Shift | 73.5361 | -1.7697 | Night | 202601 | 2026-01-08 | 1.7697
2026-01-08 05:42 | 72.095 | FALSE | TRUE | -0.17016 | -0.23658 | -1.4104 | -1.9187 | 0 |  | 2026-01-08 00:43 | none | FALSE | 0 | 71.9248 | FALSE | FALSE | 0.5046 | 1.6639 | 72.7151 | 21 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.39513 | Confirmed/Materialized Shift | 73.5054 | -1.5694 | Night | 202601 | 2026-01-08 | 1.5694
2026-01-08 05:57 | 72.095 | FALSE | TRUE | -0.23484 | -0.3268 | -1.3622 | -1.8544 | 0 |  | 2026-01-08 00:43 | none | FALSE | 0 | 71.8602 | FALSE | FALSE | 0.4941 | 1.6524 | 72.6587 | 22 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.39926 | Confirmed/Materialized Shift | 73.4572 | -1.4118 | Night | 202601 | 2026-01-08 | 1.4118
2026-01-08 06:12 | 72.095 | FALSE | TRUE | -0.28264 | -0.39358 | -1.2971 | -1.7674 | 0 |  | 2026-01-08 00:43 | none | FALSE | 0 | 71.8124 | FALSE | FALSE | 0.4856 | 1.6364 | 72.6022 | 23 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.39494 | Confirmed/Materialized Shift | 73.3921 | -1.2843 | Night | 202601 | 2026-01-08 | 1.2843
2026-01-08 06:26 | 72.095 | FALSE | TRUE | -0.31299 | -0.43603 | -1.2146 | -1.6568 | 0 |  | 2026-01-08 00:43 | none | FALSE | 0 | 71.782 | FALSE | FALSE | 0.4787 | 1.6174 | 72.5458 | 24 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.3819 | Confirmed/Materialized Shift | 73.3096 | -1.1804 | Night | 202601 | 2026-01-08 | 1.1804
2026-01-08 06:41 | 72.095 | FALSE | TRUE | -0.32399 | -0.45142 | -1.1127 | -1.52 | 0 |  | 2026-01-08 00:43 | none | FALSE | 0 | 71.771 | FALSE | FALSE | 0.4732 | 1.5967 | 72.4894 | 25 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.35918 | Confirmed/Materialized Shift | 73.2077 | -1.098 | Night | 202601 | 2026-01-08 | 1.098
2026-01-08 06:56 | 72.095 | FALSE | TRUE | -0.31159 | -0.43406 | -0.98749 | -1.3512 | 0 |  | 2026-01-08 00:43 | none | FALSE | 0 | 71.7834 | FALSE | FALSE | 0.4694 | 1.5753 | 72.433 | 26 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.32477 | Confirmed/Materialized Shift | 73.0825 | -1.0406 | Night | 202601 | 2026-01-08 | 1.0406
2026-01-08 07:11 | 72.095 | FALSE | FALSE | -0.32408 | -0.45155 | -0.91538 | -1.2538 | 0 |  |  | none | FALSE | 0 | 71.7709 | FALSE | FALSE | 0.0636 |  | 72.3906 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.30987 | Persistence ends | 73.0104 | -0.95412 | Night | 202601 | 2026-01-08 | 0.95412
2026-01-08 07:26 | 72.095 | FALSE | FALSE | -0.32212 | -0.44881 | -0.82882 | -1.1366 | 0 |  |  | none | FALSE | 0 | 71.7729 | FALSE | FALSE | 0.0587 |  | 72.3483 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.28774 | Normal | 72.9238 | -0.88049 | Day | 202601 | 2026-01-08 | 0.88049
2026-01-08 07:30 | 71.8124 | FALSE | FALSE | -0.072105 | -0.10051 | -1.0311 | -1.4156 | -0.2826 |  |  | none | FALSE | 0 | 71.7403 | FALSE | FALSE | 0.1159 |  | 72.2919 | 0 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.27581 | Normal | 72.8435 | -1.7386 | Day | 202601 | 2026-01-08 | 1.7386
2026-01-08 07:45 | 71.8124 | FALSE | FALSE | -0.077505 | -0.10804 | -0.92368 | -1.2699 | 0 |  |  | none | FALSE | 0 | 71.7349 | FALSE | FALSE | 0.1127 |  | 72.2355 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.2503 | Normal | 72.7361 | -1.6903 | Day | 202601 | 2026-01-08 | 1.6903
2026-01-08 08:00 | 72.095 | TRUE | FALSE | -0.35002 | -0.48786 | -0.57466 | -0.79078 | 0.2826 |  |  | none | FALSE | 1 | 71.745 | FALSE | FALSE | 0.061 |  | 72.2073 | 0 | 0.2826 | -0.02817 | 0.12619 | 2.4627 | 0.23117 | Normal | 72.6697 | -0.48588 | Day | 202601 | 2026-01-08 | 0.48588
2026-01-08 08:15 | 72.095 | FALSE | FALSE | -0.32844 | -0.45766 | -0.49674 | -0.6843 | 0 |  |  | none | FALSE | 1 | 71.7666 | FALSE | FALSE | 0.0558 |  | 72.1792 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.2063 | Normal | 72.5917 | -0.40791 | Day | 202601 | 2026-01-08 | 0.40791
2026-01-08 08:30 | 72.095 | FALSE | FALSE | -0.29047 | -0.40453 | -0.40243 | -0.5551 | 0 |  |  | none | FALSE | 1 | 71.8045 | FALSE | FALSE | 0.0501 |  | 72.151 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.17323 | Normal | 72.4974 | -0.32316 | Day | 202601 | 2026-01-08 | 0.32316
2026-01-08 08:30 | 72.095 | FALSE | FALSE | -0.28854 | -0.40183 | -0.37242 | -0.51392 | 0 |  |  | none | FALSE | 1 | 71.8065 | FALSE | FALSE | 0.0455 |  | 72.1369 | 0 | 0 | -0.01404 | 0.11113 | 0.12634 | 0.16524 | Normal | 72.4674 | -0.25381 | Day | 202601 | 2026-01-08 | 0.25381
2026-01-08 08:45 | 72.3758 | TRUE | FALSE | -0.56934 | -0.79289 | -0.091623 | -0.12643 | 0.2808 |  |  | none | FALSE | 2 | 71.8065 | TRUE | FALSE | 0.1535 |  | 72.1369 | 0 | 0.2808 | 0 | 0.12925 | 2.1725 | 0.16524 | Normal | 72.4674 | 1.4455 | Day | 202601 | 2026-01-08 | 1.4455
2026-01-08 09:00 | 72.6584 | FALSE | FALSE | -0.89927 | -1.2532 | 0.11539 | 0.15907 | 0.2826 | 2026-01-08 11:29 | 2026-01-08 09:00 | upper | TRUE | 2 | 71.7591 | FALSE | FALSE | 0.2869 | 2.5888 | 72.1511 | 1 | 0.2826 | 0.01413 | 0.14387 | 1.866 | 0.19597 | Extreme triggered | 72.543 | 2.5888 | Day | 202601 | 2026-01-08 | 2.5888
2026-01-08 09:15 | 72.941 | FALSE | FALSE | -1.2822 | -1.7894 | 0.24111 | 0.33165 | 0.2826 |  | 2026-01-08 09:00 | upper | TRUE | 2 | 71.6588 | FALSE | FALSE | 0.3665 | 2.7576 | 72.1793 | 2 | 0.2826 | 0.02826 | 0.1558 | 1.6325 | 0.26028 | Extreme/elevated | 72.6999 | 2.9263 | Day | 202601 | 2026-01-08 | 2.9263
2026-01-08 09:30 | 72.941 | FALSE | FALSE | -1.3512 | -1.8874 | 0.11565 | 0.1588 | 0 |  | 2026-01-08 09:00 | upper | TRUE | 2 | 71.5898 | FALSE | TRUE | 0.3869 | 2.6299 | 72.2076 | 3 | 0 | 0.02826 | 0.1558 | -0.18139 | 0.30888 | Persistent | 72.8254 | 2.3744 | Day | 202601 | 2026-01-08 | 2.3744
2026-01-08 09:45 | 73.2236 | FALSE | FALSE | -1.7388 | -2.4323 | 0.20849 | 0.28554 | 0.2826 |  | 2026-01-08 09:00 | upper | TRUE | 2 | 71.4848 | FALSE | TRUE | 0.4554 | 2.6086 | 72.25 | 4 | 0.2826 | 0.04239 | 0.1656 | 1.4505 | 0.38257 | Persistent | 73.0151 | 2.545 | Day | 202601 | 2026-01-08 | 2.545
2026-01-08 10:00 | 73.5062 | FALSE | FALSE | -2.1299 | -2.9841 | 0.24139 | 0.32948 | 0.2826 |  | 2026-01-08 09:00 | upper | TRUE | 2 | 71.3763 | FALSE | TRUE | 0.5103 | 2.5892 | 72.3205 | 5 | 0.2826 | 0.07056 | 0.15534 | 1.365 | 0.47213 | Persistent | 73.2648 | 2.5113 | Day | 202601 | 2026-01-08 | 2.5113
2026-01-08 10:15 | 73.5062 | FALSE | FALSE | -2.1902 | -3.0712 | 0.039962 | 0.054395 | 0 |  | 2026-01-08 09:00 | upper | TRUE | 1 | 71.316 | FALSE | TRUE | 0.5097 | 2.5034 | 72.3911 | 6 | 0 | 0.07056 | 0.15534 | -0.45424 | 0.53757 | Persistent | 73.4662 | 2.0743 | Day | 202601 | 2026-01-08 | 2.0743
2026-01-08 10:29 | 73.2236 | FALSE | TRUE | -1.903 | -2.6682 | -0.35086 | -0.47687 | -0.2826 |  | 2026-01-08 09:00 | none | FALSE | 1 | 71.3206 | FALSE | FALSE | 0.5204 | 2.3425 | 72.4475 | 7 | -0.2826 | 0.05643 | 0.17384 | -1.9502 | 0.56346 | Confirmed/Materialized Shift | 73.5745 | 1.3773 | Day | 202601 | 2026-01-08 | 1.3773
2026-01-08 10:44 | 73.2236 | FALSE | TRUE | -1.8846 | -2.6418 | -0.44534 | -0.60452 | 0 |  | 2026-01-08 09:00 | none | FALSE | 1 | 71.339 | FALSE | FALSE | 0.5109 | 2.2041 | 72.504 | 8 | 0 | 0.05643 | 0.17384 | -0.3246 | 0.58249 | Confirmed/Materialized Shift | 73.6689 | 1.2355 | Day | 202601 | 2026-01-08 | 1.2355
2026-01-08 10:59 | 73.2236 | FALSE | TRUE | -1.8538 | -2.5975 | -0.52742 | -0.71513 | 0 |  | 2026-01-08 09:00 | none | FALSE | 1 | 71.3698 | FALSE | FALSE | 0.5028 | 2.083 | 72.5604 | 9 | 0 | 0.05643 | 0.17384 | -0.3246 | 0.59531 | Confirmed/Materialized Shift | 73.751 | 1.114 | Day | 202601 | 2026-01-08 | 1.114
2026-01-08 11:15 | 73.2236 | FALSE | TRUE | -1.8114 | -2.5366 | -0.59787 | -0.80989 | 0 |  | 2026-01-08 09:00 | none | FALSE | 0 | 71.4122 | FALSE | FALSE | 0.4672 | 1.9754 | 72.6168 | 10 | 0 | 0.05643 | 0.17384 | -0.3246 | 0.60233 | Confirmed/Materialized Shift | 73.8215 | 1.0074 | Day | 202601 | 2026-01-08 | 1.0074
2026-01-08 11:29 | 73.2236 | FALSE | FALSE | -1.7578 | -2.4597 | -0.65711 | -0.88943 | 0 |  |  | none | FALSE | 0 | 71.4658 | FALSE | FALSE | 0.0608 |  | 72.6732 | 0 | 0 | 0.05643 | 0.17384 | -0.3246 | 0.60373 | Persistence ends | 73.8807 | 0.91158 | Day | 202601 | 2026-01-08 | 0.91158
2026-01-08 11:44 | 73.5062 | FALSE | FALSE | -1.9923 | -2.7859 | -0.46752 | -0.63201 | 0.2826 |  |  | none | FALSE | 0 | 71.5139 | FALSE | FALSE | 0.0826 |  | 72.7438 | 0 | 0.2826 | 0.07056 | 0.18038 | 1.1755 | 0.61495 | Normal | 73.9737 | 1.2397 | Day | 202601 | 2026-01-08 | 1.2397
2026-01-08 11:59 | 73.5062 | FALSE | FALSE | -1.9269 | -2.692 | -0.54326 | -0.73365 | 0 |  |  | none | FALSE | 0 | 71.5793 | FALSE | FALSE | 0.0747 |  | 72.8144 | 0 | 0 | 0.07056 | 0.18038 | -0.39118 | 0.61755 | Normal | 74.0495 | 1.1203 | Day | 202601 | 2026-01-08 | 1.1203
2026-01-08 12:14 | 73.7888 | FALSE | FALSE | -2.0892 | -2.9139 | -0.33801 | -0.45599 | 0.2826 |  |  | none | FALSE | 0 | 71.6996 | FALSE | FALSE | 0.0962 |  | 72.9132 | 0 | 0.2826 | 0.09882 | 0.16582 | 1.1083 | 0.60681 | Normal | 74.1268 | 1.443 | Day | 202601 | 2026-01-08 | 1.443
2026-01-08 12:20 | 74.0714 | FALSE | FALSE | -2.248 | -3.1298 | -0.15743 | -0.21209 | 0.2826 |  |  | none | FALSE | 0 | 71.8234 | FALSE | FALSE | 0.1159 |  | 73.0261 | 0 | 0.2826 | 0.11295 | 0.16897 | 1.004 | 0.60135 | Normal | 74.2288 | 1.7382 | Day | 202601 | 2026-01-08 | 1.7382
2026-01-08 12:23 | 74.0714 | FALSE | FALSE | -2.1518 | -2.9919 | -0.2589 | -0.34831 | 0 |  |  | none | FALSE | 0 | 71.9196 | FALSE | FALSE | 0.1047 |  | 73.125 | 0 | 0 | 0.09882 | 0.16582 | -0.59594 | 0.60267 | Normal | 74.3303 | 1.5704 | Day | 202601 | 2026-01-08 | 1.5704
2026-01-08 12:29 | 74.0714 | FALSE | FALSE | -2.0211 | -2.8051 | -0.32582 | -0.43795 | 0 |  |  | none | FALSE | 0 | 72.0503 | FALSE | FALSE | 0.0963 |  | 73.2238 | 0 | 0 | 0.09882 | 0.16582 | -0.59594 | 0.58672 | Normal | 74.3972 | 1.4447 | Day | 202601 | 2026-01-08 | 1.4447
2026-01-08 12:44 | 73.7888 | FALSE | FALSE | -1.5507 | -2.1467 | -0.59006 | -0.79332 | -0.2826 |  |  | none | FALSE | 0 | 72.2381 | FALSE | FALSE | 0.0598 |  | 73.3085 | 0 | -0.2826 | 0.08469 | 0.18555 | -1.9794 | 0.5352 | Normal | 74.3789 | 0.89748 | Day | 202601 | 2026-01-08 | 0.89748
2026-01-08 12:59 | 73.5062 | FALSE | FALSE | -1.0344 | -1.4273 | -0.78003 | -1.05 | -0.2826 |  |  | none | FALSE | 0 | 72.4718 | FALSE | FALSE | 0.0187 |  | 73.379 | 0 | -0.2826 | 0.07056 | 0.20234 | -1.7454 | 0.4536 | Normal | 74.2862 | 0.28036 | Day | 202601 | 2026-01-08 | 0.28036
2026-01-08 13:14 | 73.2236 | FALSE | FALSE | -0.58233 | -0.80166 | -0.97797 | -1.318 | -0.2826 |  |  | none | FALSE | 0 | 72.6413 | FALSE | FALSE | 0.0338 |  | 73.4214 | 0 | -0.2826 | 0.04239 | 0.21058 | -1.5433 | 0.39008 | Normal | 74.2016 | -0.50713 | Day | 202601 | 2026-01-08 | 0.50713
2026-01-08 13:28 | 73.2236 | FALSE | FALSE | -0.4746 | -0.65237 | -0.92676 | -1.2498 | 0 |  |  | none | FALSE | 0 | 72.749 | FALSE | FALSE | 0.043 |  | 73.4497 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.35034 | Normal | 74.1504 | -0.64532 | Day | 202601 | 2026-01-08 | 0.64532
2026-01-08 13:43 | 72.941 | FALSE | FALSE | -0.192 | -0.26391 | -1.2094 | -1.631 | -0.2826 |  |  | none | FALSE | 0 | 72.749 | FALSE | FALSE | 0.0968 |  | 73.4497 | 0 | -0.2826 | 0 | 0.20502 | -1.3784 | 0.35034 | Normal | 74.1504 | -1.452 | Day | 202601 | 2026-01-08 | 1.452
2026-01-08 13:59 | 72.6584 | FALSE | FALSE | 0.02386 | 0.032828 | -1.5304 | -2.0629 | -0.2826 | 2026-01-08 15:13 | 2026-01-08 13:59 | lower | TRUE | 0 | 72.6823 | FALSE | FALSE | 0.1947 | 2.0633 | 73.4356 | 1 | -0.2826 | -0.01413 | 0.21454 | -1.2514 | 0.37665 | Extreme triggered | 74.1888 | -2.0633 | Day | 202601 | 2026-01-08 | 2.0633
2026-01-08 14:14 | 72.941 | FALSE | FALSE | -0.29973 | -0.41262 | -1.2606 | -1.6988 | 0.2826 |  | 2026-01-08 13:59 | none | FALSE | 0 | 72.6413 | FALSE | FALSE | 0.1964 | 1.6475 | 73.4214 | 2 | 0.2826 | -0.01413 | 0.21454 | 1.3831 | 0.39008 | Extreme/elevated | 74.2016 | -1.2316 | Day | 202601 | 2026-01-08 | 1.2316
2026-01-08 14:28 | 72.6584 | FALSE | FALSE | -0.12915 | -0.17807 | -1.5704 | -2.1156 | -0.2826 |  | 2026-01-08 13:59 | none | FALSE | 0 | 72.5292 | FALSE | FALSE | 0.2845 | 1.6637 | 73.379 | 3 | -0.2826 | -0.04239 | 0.21058 | -1.1407 | 0.42489 | Persistent | 74.2288 | -1.696 | Day | 202601 | 2026-01-08 | 1.696
2026-01-08 14:43 | 72.6584 | FALSE | FALSE | -0.22757 | -0.31418 | -1.584 | -2.1336 | 0 |  | 2026-01-08 13:59 | none | FALSE | 0 | 72.4308 | FALSE | FALSE | 0.3284 | 1.6221 | 73.3366 | 4 | 0 | -0.04239 | 0.21058 | 0.2013 | 0.4529 | Persistent | 74.2424 | -1.4975 | Day | 202601 | 2026-01-08 | 1.4975
2026-01-08 14:58 | 72.6584 | FALSE | FALSE | -0.30463 | -0.42103 | -1.6046 | -2.1607 | 0 |  | 2026-01-08 13:59 | none | FALSE | 0 | 72.3538 | FALSE | FALSE | 0.3765 | 1.5701 | 73.3084 | 5 | 0 | -0.02826 | 0.20296 | 0.13924 | 0.4773 | Persistent | 74.263 | -1.3618 | Day | 202601 | 2026-01-08 | 1.3618
2026-01-08 15:13 | 72.941 | FALSE | FALSE | -0.61491 | -0.85019 | -1.3214 | -1.7794 | 0.2826 |  |  | none | FALSE | 0 | 72.3261 | FALSE | FALSE | 0.0486 |  | 73.2943 | 0 | 0.2826 | -0.01413 | 0.21454 | 1.3831 | 0.48408 | Persistence ends | 74.2624 | -0.72973 | Day | 202601 | 2026-01-08 | 0.72973
2026-01-08 15:28 | 72.6584 | FALSE | FALSE | -0.40139 | -0.5555 | -1.6166 | -2.1765 | -0.2826 |  |  | none | FALSE | 0 | 72.257 | FALSE | FALSE | 0.0803 |  | 73.266 | 0 | -0.2826 | -0.02826 | 0.22271 | -1.142 | 0.50449 | Normal | 74.275 | -1.2044 | Day | 202601 | 2026-01-08 | 1.2044
2026-01-08 15:43 | 72.6584 | FALSE | FALSE | -0.46567 | -0.64503 | -1.6243 | -2.1867 | 0 |  |  | none | FALSE | 0 | 72.1927 | FALSE | FALSE | 0.0739 |  | 73.2377 | 0 | 0 | -0.02826 | 0.22271 | 0.12689 | 0.5225 | Normal | 74.2827 | -1.1088 | Day | 202601 | 2026-01-08 | 1.1088
2026-01-08 15:58 | 72.6584 | FALSE | FALSE | -0.52562 | -0.72869 | -1.6278 | -2.1912 | 0 |  |  | none | FALSE | 0 | 72.1328 | FALSE | FALSE | 0.0682 |  | 73.2095 | 0 | 0 | -0.02826 | 0.22271 | 0.12689 | 0.53835 | Normal | 74.2862 | -1.0236 | Day | 202601 | 2026-01-08 | 1.0236
2026-01-08 16:13 | 72.6584 | FALSE | FALSE | -0.58544 | -0.81229 | -1.6028 | -2.1583 | 0 |  |  | none | FALSE | 0 | 72.073 | FALSE | FALSE | 0.062 |  | 73.1671 | 0 | 0 | -0.04239 | 0.21058 | 0.2013 | 0.54706 | Normal | 74.2612 | -0.92984 | Day | 202601 | 2026-01-08 | 0.92984
2026-01-08 16:28 | 72.3758 | FALSE | FALSE | -0.40157 | -0.55794 | -1.8711 | -2.5201 | -0.2826 |  |  | none | FALSE | 0 | 71.9742 | FALSE | FALSE | 0.0862 |  | 73.1106 | 0 | -0.2826 | -0.05652 | 0.21697 | -1.042 | 0.56817 | Normal | 74.2469 | -1.2932 | Day | 202601 | 2026-01-08 | 1.2932
2026-01-08 16:43 | 72.3758 | FALSE | FALSE | -0.47037 | -0.65415 | -1.7986 | -2.4248 | 0 |  |  | none | FALSE | 0 | 71.9054 | FALSE | FALSE | 0.0781 |  | 73.0399 | 0 | 0 | -0.07065 | 0.20244 | 0.34899 | 0.56724 | Normal | 74.1744 | -1.1708 | Day | 202601 | 2026-01-08 | 1.1708
2026-01-08 16:58 | 72.3758 | FALSE | FALSE | -0.48163 | -0.66992 | -1.6403 | -2.2161 | 0 |  |  | none | FALSE | 0 | 71.8942 | FALSE | FALSE | 0.0728 |  | 72.9551 | 0 | 0 | -0.08478 | 0.18565 | 0.45666 | 0.53048 | Normal | 74.0161 | -1.0921 | Day | 202601 | 2026-01-08 | 1.0921
2026-01-08 17:13 | 72.3758 | FALSE | FALSE | -0.45609 | -0.63416 | -1.4452 | -1.9577 | 0 |  |  | none | FALSE | 0 | 71.9197 | FALSE | FALSE | 0.0694 |  | 72.8704 | 0 | 0 | -0.08478 | 0.18565 | 0.45666 | 0.47532 | Normal | 73.821 | -1.0405 | Day | 202601 | 2026-01-08 | 1.0405
2026-01-08 17:27 | 72.6584 | FALSE | FALSE | -0.62581 | -0.86879 | -0.90841 | -1.2348 | 0.2826 |  |  | none | FALSE | 0 | 72.0326 | FALSE | FALSE | 0.0246 |  | 72.7997 | 0 | 0.2826 | -0.07065 | 0.20244 | 1.745 | 0.38356 | Normal | 73.5668 | -0.36839 | Day | 202601 | 2026-01-08 | 0.36839
2026-01-08 17:42 | 72.941 | FALSE | FALSE | -0.79943 | -1.1081 | -0.43205 | -0.58884 | 0.2826 |  |  | none | FALSE | 0 | 72.1416 | FALSE | FALSE | 0.0398 |  | 72.7573 | 0 | 0.2826 | -0.04239 | 0.21058 | 1.5433 | 0.30787 | Normal | 73.3731 | 0.59665 | Day | 202601 | 2026-01-08 | 0.59665
2026-01-08 17:57 | 72.941 | FALSE | FALSE | -0.72655 | -1.0061 | -0.30265 | -0.4132 | 0 |  |  | none | FALSE | 0 | 72.2145 | FALSE | FALSE | 0.0549 |  | 72.7291 | 0 | 0 | -0.02826 | 0.20296 | 0.13924 | 0.2573 | Normal | 73.2436 | 0.82375 | Night | 202601 | 2026-01-08 | 0.82375
2026-01-08 18:12 | 72.941 | FALSE | FALSE | -0.69718 | -0.96504 | -0.24502 | -0.33479 | 0 |  |  | none | FALSE | 0 | 72.2438 | FALSE | FALSE | 0.064 |  | 72.7149 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.23555 | Normal | 73.186 | 0.9598 | Night | 202601 | 2026-01-08 | 0.9598
2026-01-08 18:27 | 72.941 | FALSE | FALSE | -0.66137 | -0.91502 | -0.18095 | -0.24747 | 0 |  |  | none | FALSE | 0 | 72.2796 | FALSE | FALSE | 0.076 |  | 72.7008 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.21058 | Normal | 73.122 | 1.1407 | Night | 202601 | 2026-01-08 | 1.1407
2026-01-08 18:30 | 72.941 | FALSE | FALSE | -0.66137 | -0.91502 | -0.18095 | -0.24747 | 0 |  |  | none | FALSE | 0 | 72.2796 | FALSE | FALSE | 0.076 |  | 72.7008 | 0 | 0 | 0 | 0.18338 | 0 | 0.21058 | Normal | 73.122 | 1.1407 | Night | 202601 | 2026-01-08 | 1.1407
2026-01-08 18:31 | 72.941 | FALSE | FALSE | -0.66002 | -0.91314 | -0.20786 | -0.28417 | 0 |  |  | none | FALSE | 0 | 72.281 | FALSE | FALSE | 0.0695 |  | 72.7149 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.21697 | Normal | 73.1489 | 1.042 | Night | 202601 | 2026-01-08 | 1.042
2026-01-08 18:46 | 73.2236 | FALSE | FALSE | -0.97536 | -1.35 | 0.013736 | 0.018763 | 0.2826 | 2026-01-08 22:29 | 2026-01-08 18:46 | upper | TRUE | 0 | 72.2482 | FALSE | FALSE | 0.1943 | 2.0571 | 72.7291 | 1 | 0.2826 | 0.01413 | 0.17092 | 1.5708 | 0.24041 | Extreme triggered | 73.2099 | 2.0571 | Night | 202601 | 2026-01-08 | 2.0571
2026-01-08 19:01 | 73.5062 | FALSE | FALSE | -1.3261 | -1.8372 | 0.14339 | 0.19546 | 0.2826 |  | 2026-01-08 18:46 | upper | TRUE | 0 | 72.1801 | FALSE | FALSE | 0.2799 | 2.271 | 72.7714 | 2 | 0.2826 | 0.04239 | 0.16593 | 1.4477 | 0.29568 | Extreme/elevated | 73.3628 | 2.485 | Night | 202601 | 2026-01-08 | 2.485
2026-01-08 19:16 | 73.5062 | FALSE | FALSE | -1.3655 | -1.8928 | 0.019231 | 0.026169 | 0 |  | 2026-01-08 18:46 | upper | TRUE | 0 | 72.1407 | FALSE | TRUE | 0.3086 | 2.1997 | 72.8138 | 3 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.33657 | Persistent | 73.487 | 2.0571 | Night | 202601 | 2026-01-08 | 2.0571
2026-01-08 19:30 | 73.5062 | FALSE | FALSE | -1.3858 | -1.9215 | -0.085809 | -0.1166 | 0 |  | 2026-01-08 18:46 | none | FALSE | 0 | 72.1204 | FALSE | FALSE | 0.3464 | 2.0915 | 72.8562 | 4 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.36789 | Persistent | 73.592 | 1.7668 | Night | 202601 | 2026-01-08 | 1.7668
2026-01-08 19:45 | 73.5062 | FALSE | FALSE | -1.4126 | -1.9594 | -0.16913 | -0.22957 | 0 |  | 2026-01-08 18:46 | none | FALSE | 0 | 72.0936 | FALSE | FALSE | 0.3905 | 1.9877 | 72.8845 | 5 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.39543 | Persistent | 73.6753 | 1.5723 | Night | 202601 | 2026-01-08 | 1.5723
2026-01-08 20:00 | 73.5062 | FALSE | FALSE | -1.4091 | -1.9544 | -0.25043 | -0.33954 | 0 |  | 2026-01-08 18:46 | none | FALSE | 0 | 72.0971 | FALSE | FALSE | 0.4359 | 1.8891 | 72.9269 | 6 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.41488 | Persistent | 73.7566 | 1.3964 | Night | 202601 | 2026-01-08 | 1.3964
2026-01-08 20:15 | 73.5062 | FALSE | TRUE | -1.3951 | -1.9346 | -0.32121 | -0.43508 | 0 |  | 2026-01-08 18:46 | none | FALSE | 0 | 72.1111 | FALSE | FALSE | 0.4834 | 1.798 | 72.9693 | 7 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.42907 | Confirmed/Materialized Shift | 73.8274 | 1.2514 | Night | 202601 | 2026-01-08 | 1.2514
2026-01-08 20:29 | 73.5062 | FALSE | TRUE | -1.3716 | -1.9014 | -0.38249 | -0.51766 | 0 |  | 2026-01-08 18:46 | none | FALSE | 0 | 72.1346 | FALSE | FALSE | 0.4752 | 1.7142 | 73.0117 | 8 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.43852 | Confirmed/Materialized Shift | 73.8887 | 1.1278 | Night | 202601 | 2026-01-08 | 1.1278
2026-01-08 20:44 | 73.7888 | FALSE | TRUE | -1.6462 | -2.2818 | -0.20491 | -0.27694 | 0.2826 |  | 2026-01-08 18:46 | none | FALSE | 0 | 72.1426 | FALSE | FALSE | 0.5038 | 1.6968 | 73.0682 | 9 | 0.2826 | 0.05652 | 0.14784 | 1.5292 | 0.46277 | Confirmed/Materialized Shift | 73.9937 | 1.5572 | Night | 202601 | 2026-01-08 | 1.5572
2026-01-08 20:59 | 73.7888 | FALSE | TRUE | -1.5687 | -2.1721 | -0.26873 | -0.36286 | 0 |  | 2026-01-08 18:46 | none | FALSE | 0 | 72.2201 | FALSE | FALSE | 0.4943 | 1.6686 | 73.1388 | 10 | 0 | 0.07065 | 0.12555 | -0.56273 | 0.45935 | Confirmed/Materialized Shift | 74.0575 | 1.415 | Night | 202601 | 2026-01-08 | 1.415
2026-01-08 21:14 | 73.7888 | FALSE | TRUE | -1.4678 | -2.0296 | -0.30914 | -0.41721 | 0 |  | 2026-01-08 18:46 | none | FALSE | 0 | 72.321 | FALSE | FALSE | 0.4869 | 1.6355 | 73.2095 | 11 | 0 | 0.07065 | 0.12555 | -0.56273 | 0.44424 | Confirmed/Materialized Shift | 74.0979 | 1.3041 | Night | 202601 | 2026-01-08 | 1.3041
2026-01-08 21:29 | 73.7888 | FALSE | TRUE | -1.341 | -1.8509 | -0.32361 | -0.43665 | 0 |  | 2026-01-08 18:46 | none | FALSE | 0 | 72.4478 | FALSE | FALSE | 0.4815 | 1.601 | 73.2801 | 12 | 0 | 0.07065 | 0.12555 | -0.56273 | 0.41614 | Confirmed/Materialized Shift | 74.1124 | 1.2224 | Night | 202601 | 2026-01-08 | 1.2224
2026-01-08 21:44 | 73.7888 | FALSE | TRUE | -1.1823 | -1.6284 | -0.30628 | -0.41336 | 0 |  | 2026-01-08 18:46 | none | FALSE | 0 | 72.6065 | FALSE | FALSE | 0.4785 | 1.5684 | 73.3508 | 13 | 0 | 0.07065 | 0.12555 | -0.56273 | 0.37215 | Confirmed/Materialized Shift | 74.0951 | 1.177 | Night | 202601 | 2026-01-08 | 1.177
2026-01-08 21:59 | 73.7888 | FALSE | TRUE | -1.0743 | -1.4775 | -0.31132 | -0.42014 | 0 |  | 2026-01-08 18:46 | none | FALSE | 0 | 72.7145 | FALSE | FALSE | 0.4734 | 1.5351 | 73.4073 | 14 | 0 | 0.05652 | 0.11598 | -0.48734 | 0.34642 | Confirmed/Materialized Shift | 74.1001 | 1.1013 | Night | 202601 | 2026-01-08 | 1.1013
2026-01-08 22:14 | 73.7888 | FALSE | TRUE | -1.0154 | -1.3953 | -0.33713 | -0.45481 | 0 |  | 2026-01-08 18:46 | none | FALSE | 0 | 72.7734 | FALSE | FALSE | 0.4669 | 1.4996 | 73.4497 | 15 | 0 | 0.04239 | 0.10353 | -0.40945 | 0.33813 | Confirmed/Materialized Shift | 74.1259 | 1.0029 | Night | 202601 | 2026-01-08 | 1.0029
2026-01-08 22:29 | 73.7888 | FALSE | FALSE | -0.94441 | -1.2965 | -0.35095 | -0.47336 | 0 |  |  | none | FALSE | 0 | 72.8444 | FALSE | FALSE | 0.0611 |  | 73.4921 | 0 | 0 | 0.04239 | 0.10353 | -0.40945 | 0.32384 | Persistence ends | 74.1398 | 0.91629 | Night | 202601 | 2026-01-08 | 0.91629
2026-01-08 22:44 | 73.7888 | FALSE | FALSE | -0.85976 | -1.1789 | -0.35108 | -0.47353 | 0 |  |  | none | FALSE | 0 | 72.929 | FALSE | FALSE | 0.056 |  | 73.5345 | 0 | 0 | 0.04239 | 0.10353 | -0.40945 | 0.30271 | Normal | 74.1399 | 0.84022 | Night | 202601 | 2026-01-08 | 0.84022
2026-01-08 22:59 | 73.7888 | FALSE | FALSE | -0.75824 | -1.0383 | -0.33434 | -0.45106 | 0 |  |  | none | FALSE | 0 | 73.0306 | FALSE | FALSE | 0.0517 |  | 73.5768 | 0 | 0 | 0.04239 | 0.10353 | -0.40945 | 0.27315 | Normal | 74.1231 | 0.77596 | Night | 202601 | 2026-01-08 | 0.77596
2026-01-08 23:14 | 73.5062 | TRUE | FALSE | -0.36044 | -0.49277 | -0.55826 | -0.75375 | -0.2826 |  |  | none | FALSE | 1 | 73.1458 | FALSE | FALSE | 0.0573 |  | 73.6051 | 0 | -0.2826 | 0.02826 | 0.12638 | -2.4597 | 0.22968 | Normal | 74.0645 | -0.43065 | Night | 202601 | 2026-01-08 | 0.43065
2026-01-08 23:28 | 73.5062 | FALSE | FALSE | -0.21467 | -0.29289 | -0.46901 | -0.634 | 0 |  |  | none | FALSE | 1 | 73.2915 | FALSE | FALSE | 0.0782 |  | 73.6334 | 0 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.17092 | Normal | 73.9752 | -0.74404 | Night | 202601 | 2026-01-08 | 0.74404
2026-01-08 23:43 | 73.5062 | FALSE | FALSE | -0.14864 | -0.20263 | -0.43124 | -0.58325 | 0 |  |  | none | FALSE | 1 | 73.3576 | FALSE | FALSE | 0.0936 |  | 73.6475 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.14497 | Normal | 73.9374 | -0.97468 | Night | 202601 | 2026-01-08 | 0.97468
2026-01-08 23:59 | 73.5062 | FALSE | FALSE | -0.14864 | -0.20263 | -0.43124 | -0.58325 | 0 |  |  | none | FALSE | 1 | 73.3576 | FALSE | FALSE | 0.0936 |  | 73.6475 | 0 | 0 | 0 | 0.091688 | 0 | 0.14497 | Normal | 73.9374 | -0.97468 | Night | 202601 | 2026-01-08 | 0.97468
2026-01-09 00:14 | 73.5062 | FALSE | FALSE | -0.14864 | -0.20263 | -0.43124 | -0.58325 | 0 |  |  | none | FALSE | 1 | 73.3576 | FALSE | FALSE | 0.0936 |  | 73.6475 | 0 | 0 | 0 | 0.091688 | 0 | 0.14497 | Normal | 73.9374 | -0.97468 | Night | 202601 | 2026-01-09 | 0.97468
2026-01-09 00:28 | 73.5062 | FALSE | FALSE | -0.14864 | -0.20263 | -0.43124 | -0.58325 | 0 |  |  | none | FALSE | 1 | 73.3576 | FALSE | FALSE | 0.0936 |  | 73.6475 | 0 | 0 | 0 | 0.091688 | 0 | 0.14497 | Normal | 73.9374 | -0.97468 | Night | 202601 | 2026-01-09 | 0.97468
2026-01-09 00:43 | 73.2236 | TRUE | FALSE | 0.067934 | 0.09269 | -0.75161 | -1.016 | -0.2826 | 2026-01-09 02:43 | 2026-01-09 00:43 | lower | TRUE | 2 | 73.2915 | TRUE | FALSE | 0.2741 | 2.3975 | 73.6334 | 1 | -0.2826 | -0.01413 | 0.11135 | -2.411 | 0.17092 | Extreme triggered | 73.9752 | -2.3975 | Night | 202601 | 2026-01-09 | 2.3975
2026-01-09 00:58 | 73.2236 | FALSE | FALSE | 0.010989 | 0.015005 | -0.78029 | -1.0544 | 0 |  | 2026-01-09 00:43 | lower | TRUE | 2 | 73.2346 | FALSE | FALSE | 0.3086 | 2.2273 | 73.6192 | 2 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.19233 | Extreme/elevated | 74.0039 | -2.0571 | Night | 202601 | 2026-01-09 | 2.0571
2026-01-09 01:13 | 73.2236 | FALSE | FALSE | -0.039654 | -0.054184 | -0.80267 | -1.0843 | 0 |  | 2026-01-09 00:43 | none | FALSE | 2 | 73.1839 | FALSE | FALSE | 0.3494 | 2.0888 | 73.6051 | 3 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.21058 | Persistent | 74.0263 | -1.8117 | Night | 202601 | 2026-01-09 | 1.8117
2026-01-09 01:28 | 73.2236 | FALSE | FALSE | -0.085523 | -0.11693 | -0.82028 | -1.1078 | 0 |  | 2026-01-09 00:43 | none | FALSE | 2 | 73.1381 | FALSE | FALSE | 0.3939 | 1.9722 | 73.591 | 4 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.22645 | Persistent | 74.0439 | -1.6223 | Night | 202601 | 2026-01-09 | 1.6223
2026-01-09 01:43 | 73.2236 | FALSE | FALSE | -0.13198 | -0.18057 | -0.81022 | -1.0944 | 0 |  | 2026-01-09 00:43 | none | FALSE | 1 | 73.0916 | FALSE | FALSE | 0.4103 | 1.8657 | 73.5627 | 5 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.23555 | Persistent | 74.0338 | -1.4397 | Night | 202601 | 2026-01-09 | 1.4397
2026-01-09 01:58 | 73.2236 | FALSE | FALSE | -0.17083 | -0.23384 | -0.79255 | -1.0708 | 0 |  | 2026-01-09 00:43 | none | FALSE | 1 | 73.0528 | FALSE | FALSE | 0.4575 | 1.7698 | 73.5345 | 6 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.24084 | Persistent | 74.0161 | -1.2907 | Night | 202601 | 2026-01-09 | 1.2907
2026-01-09 02:13 | 73.2236 | FALSE | TRUE | -0.20256 | -0.27741 | -0.76776 | -1.0376 | 0 |  | 2026-01-09 00:43 | none | FALSE | 1 | 73.021 | FALSE | FALSE | 0.5062 | 1.6834 | 73.5062 | 7 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.24258 | Confirmed/Materialized Shift | 73.9914 | -1.165 | Night | 202601 | 2026-01-09 | 1.165
2026-01-09 02:28 | 72.941 | TRUE | TRUE | -0.0046923 | -0.0064334 | -1.0503 | -1.4195 | -0.2826 |  | 2026-01-09 00:43 | none | FALSE | 2 | 72.9363 | TRUE | FALSE | 0.5893 | 1.7208 | 73.4638 | 8 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.26375 | Confirmed/Materialized Shift | 73.9913 | -1.9822 | Night | 202601 | 2026-01-09 | 1.9822
2026-01-09 02:43 | 73.2236 | TRUE | FALSE | -0.30265 | -0.41503 | -0.72655 | -0.98248 | 0.2826 |  |  | none | FALSE | 3 | 72.921 | TRUE | FALSE | 0.1406 |  | 73.4356 | 0 | 0.2826 | -0.02826 | 0.12638 | 2.4597 | 0.2573 | Persistence ends | 73.9501 | -0.82375 | Night | 202601 | 2026-01-09 | 0.82375
2026-01-09 02:58 | 72.941 | FALSE | FALSE | -0.079312 | -0.10885 | -0.98363 | -1.3306 | -0.2826 |  |  | none | FALSE | 3 | 72.8617 | FALSE | FALSE | 0.1992 |  | 73.3932 | 0 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.26574 | Normal | 73.9246 | -1.7015 | Night | 202601 | 2026-01-09 | 1.7015
2026-01-09 03:13 | 72.941 | FALSE | FALSE | -0.12407 | -0.17038 | -0.94361 | -1.2771 | 0 |  |  | none | FALSE | 2 | 72.8169 | FALSE | FALSE | 0.1595 |  | 73.3508 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.26692 | Normal | 73.8846 | -1.5352 | Night | 202601 | 2026-01-09 | 1.5352
2026-01-09 03:27 | 72.941 | FALSE | FALSE | -0.15451 | -0.21228 | -0.88927 | -1.2045 | 0 |  |  | none | FALSE | 2 | 72.7865 | FALSE | FALSE | 0.151 |  | 73.3084 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.26095 | Normal | 73.8303 | -1.4079 | Night | 202601 | 2026-01-09 | 1.4079
2026-01-09 03:42 | 72.941 | FALSE | FALSE | -0.16961 | -0.23308 | -0.81959 | -1.1112 | 0 |  |  | none | FALSE | 2 | 72.7714 | FALSE | FALSE | 0.1448 |  | 73.266 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.2473 | Normal | 73.7606 | -1.3141 | Night | 202601 | 2026-01-09 | 1.3141
2026-01-09 03:57 | 72.941 | FALSE | FALSE | -0.16658 | -0.22889 | -0.73178 | -0.99328 | 0 |  |  | none | FALSE | 2 | 72.7744 | FALSE | FALSE | 0.141 |  | 73.2236 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.22459 | Normal | 73.6728 | -1.2583 | Night | 202601 | 2026-01-09 | 1.2583
2026-01-09 04:12 | 72.941 | FALSE | FALSE | -0.19108 | -0.26265 | -0.69976 | -0.95023 | 0 |  |  | none | FALSE | 2 | 72.7499 | FALSE | FALSE | 0.1333 |  | 73.1953 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.22271 | Normal | 73.6408 | -1.142 | Night | 202601 | 2026-01-09 | 1.142
2026-01-09 04:27 | 72.941 | FALSE | FALSE | -0.20786 | -0.28579 | -0.66002 | -0.89676 | 0 |  |  | none | FALSE | 2 | 72.7331 | FALSE | FALSE | 0.1266 |  | 73.1671 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21697 | Normal | 73.601 | -1.042 | Night | 202601 | 2026-01-09 | 1.042
2026-01-09 04:42 | 72.941 | FALSE | FALSE | -0.2163 | -0.29742 | -0.61194 | -0.83197 | 0 |  |  | none | FALSE | 2 | 72.7247 | FALSE | FALSE | 0.1208 |  | 73.1388 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.20706 | Normal | 73.5529 | -0.95538 | Night | 202601 | 2026-01-09 | 0.95538
2026-01-09 04:57 | 72.941 | FALSE | FALSE | -0.21509 | -0.29576 | -0.55421 | -0.75408 | 0 |  |  | none | FALSE | 1 | 72.7259 | FALSE | FALSE | 0.0873 |  | 73.1106 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.19233 | Normal | 73.4952 | -0.88163 | Night | 202601 | 2026-01-09 | 0.88163
2026-01-09 05:12 | 72.941 | FALSE | FALSE | -0.20176 | -0.27738 | -0.48436 | -0.65967 | 0 |  |  | none | FALSE | 0 | 72.7392 | FALSE | FALSE | 0.0549 |  | 73.0823 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.17153 | Normal | 73.4254 | -0.82375 | Night | 202601 | 2026-01-09 | 0.82375
2026-01-09 05:27 | 72.6584 | FALSE | FALSE | 0.049657 | 0.068296 | -0.71336 | -0.97226 | -0.2826 | 2026-01-09 08:16 | 2026-01-09 05:27 | lower | TRUE | 0 | 72.7081 | FALSE | FALSE | 0.2104 | 2.2993 | 73.0399 | 1 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.16593 | Extreme triggered | 73.3718 | -2.2993 | Night | 202601 | 2026-01-09 | 2.2993
2026-01-09 05:42 | 72.6584 | FALSE | FALSE | -0.0077242 | -0.010632 | -0.71422 | -0.97342 | 0 |  | 2026-01-09 05:27 | none | FALSE | 0 | 72.6507 | FALSE | FALSE | 0.2448 | 2.1282 | 73.0117 | 2 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.18049 | Extreme/elevated | 73.3726 | -1.9572 | Night | 202601 | 2026-01-09 | 1.9572
2026-01-09 05:57 | 72.6584 | FALSE | FALSE | -0.054158 | -0.074593 | -0.70414 | -0.95981 | 0 |  | 2026-01-09 05:27 | none | FALSE | 0 | 72.6042 | FALSE | FALSE | 0.2857 | 1.9903 | 72.9834 | 3 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.18957 | Persistent | 73.3625 | -1.7143 | Night | 202601 | 2026-01-09 | 1.7143
2026-01-09 06:12 | 72.6584 | FALSE | FALSE | -0.091185 | -0.12566 | -0.68465 | -0.93348 | 0 |  | 2026-01-09 05:27 | none | FALSE | 0 | 72.5672 | FALSE | FALSE | 0.3306 | 1.8752 | 72.9551 | 4 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.19396 | Persistent | 73.343 | -1.5299 | Night | 202601 | 2026-01-09 | 1.5299
2026-01-09 06:26 | 72.6584 | FALSE | FALSE | -0.11945 | -0.16466 | -0.65639 | -0.8953 | 0 |  | 2026-01-09 05:27 | none | FALSE | 0 | 72.539 | FALSE | FALSE | 0.378 | 1.777 | 72.9269 | 5 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.19396 | Persistent | 73.3148 | -1.3842 | Night | 202601 | 2026-01-09 | 1.3842
2026-01-09 06:41 | 72.3758 | FALSE | FALSE | 0.074735 | 0.10315 | -0.94262 | -1.2857 | -0.2826 |  | 2026-01-09 05:27 | lower | TRUE | 0 | 72.4505 | FALSE | TRUE | 0.4992 | 1.8715 | 72.8845 | 6 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.21697 | Persistent | 73.3184 | -2.3444 | Night | 202601 | 2026-01-09 | 2.3444
2026-01-09 06:56 | 72.3758 | FALSE | TRUE | 0.0069363 | 0.0095828 | -0.92564 | -1.2628 | 0 |  | 2026-01-09 05:27 | lower | TRUE | 0 | 72.3827 | FALSE | TRUE | 0.5353 | 1.8942 | 72.8421 | 7 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.22968 | Confirmed/Materialized Shift | 73.3014 | -2.0302 | Night | 202601 | 2026-01-09 | 2.0302
2026-01-09 07:11 | 72.3758 | FALSE | TRUE | -0.043617 | -0.0603 | -0.89142 | -1.2167 | 0 |  | 2026-01-09 05:27 | none | FALSE | 0 | 72.3322 | FALSE | FALSE | 0.5209 | 1.8841 | 72.7997 | 8 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.23376 | Confirmed/Materialized Shift | 73.2672 | -1.8134 | Night | 202601 | 2026-01-09 | 1.8134
2026-01-09 07:26 | 72.3758 | FALSE | TRUE | -0.10319 | -0.14278 | -0.89447 | -1.2208 | 0 |  | 2026-01-09 05:27 | none | FALSE | 0 | 72.2726 | FALSE | FALSE | 0.5058 | 1.851 | 72.7714 | 9 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.24942 | Confirmed/Materialized Shift | 73.2703 | -1.5863 | Day | 202601 | 2026-01-09 | 1.5863
2026-01-09 07:30 | 72.3758 | FALSE | TRUE | -0.12756 | -0.17656 | -0.83406 | -1.1393 | 0 |  | 2026-01-09 05:27 | none | FALSE | 0 | 72.2482 | FALSE | FALSE | 0.498 | 1.8129 | 72.7291 | 10 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.24041 | Confirmed/Materialized Shift | 73.2099 | -1.4694 | Day | 202601 | 2026-01-09 | 1.4694
2026-01-09 07:45 | 72.3758 | FALSE | TRUE | -0.16961 | -0.2349 | -0.81959 | -1.1197 | 0 |  | 2026-01-09 05:27 | none | FALSE | 0 | 72.2062 | FALSE | FALSE | 0.4876 | 1.7675 | 72.7008 | 11 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.2473 | Confirmed/Materialized Shift | 73.1954 | -1.3141 | Day | 202601 | 2026-01-09 | 1.3141
2026-01-09 08:00 | 72.3758 | FALSE | TRUE | -0.20463 | -0.28353 | -0.79809 | -1.0907 | 0 |  | 2026-01-09 05:27 | none | FALSE | 0 | 72.1712 | FALSE | FALSE | 0.4789 | 1.7189 | 72.6725 | 12 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.25068 | Confirmed/Materialized Shift | 73.1739 | -1.1837 | Day | 202601 | 2026-01-09 | 1.1837
2026-01-09 08:16 | 72.6584 | TRUE | FALSE | -0.48516 | -0.67222 | -0.48516 | -0.6633 | 0.2826 |  |  | none | FALSE | 1 | 72.1732 | FALSE | FALSE | 0.0286 |  | 72.6584 | 0 | 0.2826 | -0.01413 | 0.11135 | 2.6647 | 0.24258 | Persistence ends | 73.1436 | 0 | Day | 202601 | 2026-01-09 | 0
2026-01-09 08:30 | 72.6584 | FALSE | FALSE | -0.48075 | -0.66606 | -0.45249 | -0.6189 | 0 |  |  | none | FALSE | 1 | 72.1777 | FALSE | FALSE | 0.0326 |  | 72.6443 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.23331 | Normal | 73.1109 | 0.060564 | Day | 202601 | 2026-01-09 | 0.060564
2026-01-09 08:30 | 72.6584 | FALSE | FALSE | -0.47368 | -0.6562 | -0.41716 | -0.57086 | 0 |  |  | none | FALSE | 1 | 72.1847 | FALSE | FALSE | 0.037 |  | 72.6301 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.22271 | Normal | 73.0756 | 0.12689 | Day | 202601 | 2026-01-09 | 0.12689
2026-01-09 08:45 | 72.6584 | FALSE | FALSE | -0.46355 | -0.64209 | -0.37877 | -0.5186 | 0 |  |  | none | FALSE | 1 | 72.1948 | FALSE | FALSE | 0.042 |  | 72.616 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.21058 | Normal | 73.0372 | 0.2013 | Day | 202601 | 2026-01-09 | 0.2013
2026-01-09 09:00 | 72.941 | TRUE | FALSE | -0.74615 | -1.0335 | -0.096174 | -0.13168 | 0.2826 |  |  | none | FALSE | 2 | 72.1948 | TRUE | FALSE | 0.16 |  | 72.616 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.21058 | Normal | 73.0372 | 1.5433 | Day | 202601 | 2026-01-09 | 1.5433
2026-01-09 09:15 | 72.941 | FALSE | FALSE | -0.74615 | -1.0335 | -0.096174 | -0.13168 | 0 |  |  | none | FALSE | 2 | 72.1948 | FALSE | FALSE | 0.16 |  | 72.616 | 0 | 0 | 0 | 0.12967 | 0 | 0.21058 | Normal | 73.0372 | 1.5433 | Day | 202601 | 2026-01-09 | 1.5433
2026-01-09 09:30 | 73.2236 | FALSE | FALSE | -1.0751 | -1.4902 | 0.11177 | 0.15288 | 0.2826 | 2026-01-09 11:29 | 2026-01-09 09:30 | upper | TRUE | 2 | 72.1485 | FALSE | FALSE | 0.2786 | 2.4641 | 72.6301 | 1 | 0.2826 | 0.01413 | 0.14424 | 1.8612 | 0.24084 | Extreme triggered | 73.1118 | 2.4641 | Day | 202601 | 2026-01-09 | 2.4641
2026-01-09 09:45 | 73.2236 | FALSE | FALSE | -1.1132 | -1.5437 | 0.045491 | 0.062165 | 0 |  | 2026-01-09 09:30 | upper | TRUE | 2 | 72.1104 | FALSE | FALSE | 0.3161 | 2.3173 | 72.6443 | 2 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.26692 | Extreme/elevated | 73.1781 | 2.1704 | Day | 202601 | 2026-01-09 | 2.1704
2026-01-09 10:00 | 73.5062 | FALSE | FALSE | -1.4782 | -2.0522 | 0.16092 | 0.2194 | 0.2826 |  | 2026-01-09 09:30 | upper | TRUE | 2 | 72.028 | FALSE | TRUE | 0.3945 | 2.3744 | 72.6867 | 3 | 0.2826 | 0.04239 | 0.13829 | 1.737 | 0.32931 | Persistent | 73.3453 | 2.4887 | Day | 202601 | 2026-01-09 | 2.4887
2026-01-09 10:15 | 73.5062 | FALSE | FALSE | -1.5304 | -2.1263 | 0.02386 | 0.03247 | 0 |  | 2026-01-09 09:30 | upper | TRUE | 2 | 71.9758 | FALSE | TRUE | 0.4233 | 2.2966 | 72.7291 | 4 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.37665 | Persistent | 73.4823 | 2.0633 | Day | 202601 | 2026-01-09 | 2.0633
2026-01-09 10:29 | 73.5062 | FALSE | FALSE | -1.563 | -2.1725 | -0.093479 | -0.12701 | 0 |  | 2026-01-09 09:30 | none | FALSE | 1 | 71.9432 | FALSE | FALSE | 0.4326 | 2.1922 | 72.7714 | 5 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.41412 | Persistent | 73.5997 | 1.7743 | Day | 202601 | 2026-01-09 | 1.7743
2026-01-09 10:44 | 73.7888 | FALSE | FALSE | -1.903 | -2.6473 | 0.018642 | 0.02527 | 0.2826 |  | 2026-01-09 09:30 | upper | TRUE | 1 | 71.8858 | FALSE | TRUE | 0.5074 | 2.1667 | 72.828 | 6 | 0.2826 | 0.05652 | 0.14784 | 1.5292 | 0.4711 | Persistent | 73.7702 | 2.0396 | Day | 202601 | 2026-01-09 | 2.0396
2026-01-09 10:59 | 73.7888 | FALSE | TRUE | -1.9351 | -2.6932 | -0.1265 | -0.17115 | 0 |  | 2026-01-09 09:30 | none | FALSE | 1 | 71.8537 | FALSE | FALSE | 0.5455 | 2.1078 | 72.8845 | 7 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.51541 | Confirmed/Materialized Shift | 73.9153 | 1.7546 | Day | 202601 | 2026-01-09 | 1.7546
2026-01-09 11:03 | 74.0714 | FALSE | TRUE | -2.2311 | -3.1056 | -0.026772 | -0.03613 | 0.2826 |  | 2026-01-09 09:30 | none | FALSE | 1 | 71.8403 | FALSE | FALSE | 0.5587 | 2.0884 | 72.9693 | 8 | 0.2826 | 0.08478 | 0.13287 | 1.4888 | 0.56446 | Confirmed/Materialized Shift | 74.0982 | 1.9526 | Day | 202601 | 2026-01-09 | 1.9526
2026-01-09 11:06 | 74.0714 | FALSE | TRUE | -2.2114 | -3.0774 | -0.17669 | -0.23798 | 0 |  | 2026-01-09 09:30 | none | FALSE | 0 | 71.86 | FALSE | FALSE | 0.5136 | 2.0457 | 73.054 | 9 | 0 | 0.08478 | 0.13287 | -0.63808 | 0.59703 | Confirmed/Materialized Shift | 74.2481 | 1.704 | Day | 202601 | 2026-01-09 | 1.704
2026-01-09 11:21 | 73.7888 | TRUE | TRUE | -1.8564 | -2.5808 | -0.52818 | -0.71071 | -0.2826 |  | 2026-01-09 09:30 | none | FALSE | 1 | 71.9324 | FALSE | FALSE | 0.5028 | 1.9526 | 73.1247 | 10 | -0.2826 | 0.07065 | 0.15546 | -2.2722 | 0.59615 | Confirmed/Materialized Shift | 74.317 | 1.114 | Day | 202601 | 2026-01-09 | 1.114
2026-01-09 11:29 | 73.5062 | FALSE | FALSE | -1.4742 | -2.0466 | -0.82422 | -1.1089 | -0.2826 |  |  | none | FALSE | 1 | 72.032 | FALSE | FALSE | 0.0663 |  | 73.1812 | 0 | -0.2826 | 0.05652 | 0.17396 | -1.9494 | 0.5746 | Persistence ends | 74.3304 | 0.56559 | Day | 202601 | 2026-01-09 | 0.56559
2026-01-09 11:44 | 73.5062 | FALSE | FALSE | -1.3607 | -1.886 | -0.82373 | -1.1082 | 0 |  |  | none | FALSE | 1 | 72.1455 | FALSE | FALSE | 0.0613 |  | 73.2377 | 0 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.5461 | Normal | 74.3299 | 0.49161 | Day | 202601 | 2026-01-09 | 0.49161
2026-01-09 11:59 | 73.5062 | FALSE | FALSE | -1.2309 | -1.703 | -0.80698 | -1.0859 | 0 |  |  | none | FALSE | 1 | 72.2753 | FALSE | FALSE | 0.0563 |  | 73.2943 | 0 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.50946 | Normal | 74.3132 | 0.41603 | Day | 202601 | 2026-01-09 | 0.41603
2026-01-09 12:14 | 73.2236 | FALSE | FALSE | -0.81114 | -1.1202 | -1.0372 | -1.3967 | -0.2826 |  |  | none | FALSE | 1 | 72.4125 | FALSE | FALSE | 0.0449 |  | 73.3366 | 0 | -0.2826 | 0.04239 | 0.18957 | -1.7143 | 0.46209 | Normal | 74.2608 | -0.24463 | Day | 202601 | 2026-01-09 | 0.24463
2026-01-09 12:29 | 73.2236 | FALSE | FALSE | -0.72852 | -1.0049 | -1.0111 | -1.3621 | 0 |  |  | none | FALSE | 1 | 72.4951 | FALSE | FALSE | 0.0502 |  | 73.3649 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.43491 | Normal | 74.2347 | -0.32489 | Day | 202601 | 2026-01-09 | 0.32489
2026-01-09 12:44 | 73.2236 | FALSE | FALSE | -0.63812 | -0.87913 | -0.97724 | -1.317 | 0 |  |  | none | FALSE | 1 | 72.5855 | FALSE | FALSE | 0.0566 |  | 73.3932 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.40384 | Normal | 74.2008 | -0.41987 | Day | 202601 | 2026-01-09 | 0.41987
2026-01-09 12:59 | 73.2236 | FALSE | FALSE | -0.53797 | -0.74013 | -0.93361 | -1.259 | 0 |  |  | none | FALSE | 1 | 72.6856 | FALSE | FALSE | 0.0644 |  | 73.4214 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.36789 | Normal | 74.1572 | -0.53771 | Day | 202601 | 2026-01-09 | 0.53771
2026-01-09 13:14 | 73.2236 | FALSE | FALSE | -0.42484 | -0.58358 | -0.877 | -1.1835 | 0 |  |  | none | FALSE | 1 | 72.7988 | FALSE | FALSE | 0.0749 |  | 73.4497 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.32546 | Normal | 74.1006 | -0.69465 | Day | 202601 | 2026-01-09 | 0.69465
2026-01-09 13:29 | 73.2236 | FALSE | FALSE | -0.37553 | -0.5155 | -0.85595 | -1.1554 | 0 |  |  | none | FALSE | 1 | 72.8481 | FALSE | FALSE | 0.0806 |  | 73.4638 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.30787 | Normal | 74.0796 | -0.78023 | Day | 202601 | 2026-01-09 | 0.78023
2026-01-09 13:44 | 73.5062 | FALSE | FALSE | -0.57859 | -0.79337 | -0.55033 | -0.74312 | 0.2826 |  |  | none | FALSE | 0 | 72.9276 | FALSE | FALSE | 0.0033 |  | 73.4921 | 0 | 0.2826 | 0.02826 | 0.18107 | 1.4047 | 0.28223 | Normal | 74.0565 | 0.050066 | Day | 202601 | 2026-01-09 | 0.050066
2026-01-09 13:59 | 73.5062 | FALSE | FALSE | -0.55013 | -0.75405 | -0.55013 | -0.74285 | 0 |  |  | none | FALSE | 0 | 72.9561 | FALSE | FALSE | 0 |  | 73.5062 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.27506 | Normal | 74.0563 | 0 | Day | 202601 | 2026-01-09 | 0
2026-01-09 14:14 | 73.2236 | FALSE | FALSE | -0.26753 | -0.36669 | -0.83273 | -1.1244 | -0.2826 |  |  | none | FALSE | 0 | 72.9561 | FALSE | FALSE | 0.0685 |  | 73.5062 | 0 | -0.2826 | 0 | 0.18338 | -1.5411 | 0.27506 | Normal | 74.0563 | -1.0274 | Day | 202601 | 2026-01-09 | 1.0274
2026-01-09 14:28 | 73.2236 | FALSE | FALSE | -0.29599 | -0.40586 | -0.83293 | -1.1247 | 0 |  |  | none | FALSE | 0 | 72.9276 | FALSE | FALSE | 0.0634 |  | 73.4921 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.28223 | Normal | 74.0565 | -0.95125 | Day | 202601 | 2026-01-09 | 0.95125
2026-01-09 14:43 | 73.2236 | FALSE | FALSE | -0.32264 | -0.44257 | -0.83132 | -1.1226 | 0 |  |  | none | FALSE | 0 | 72.901 | FALSE | FALSE | 0.0588 |  | 73.4779 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.28849 | Normal | 74.0549 | -0.88163 | Day | 202601 | 2026-01-09 | 0.88163
2026-01-09 14:58 | 73.2236 | FALSE | FALSE | -0.34759 | -0.47696 | -0.82801 | -1.1182 | 0 |  |  | none | FALSE | 0 | 72.876 | FALSE | FALSE | 0.0545 |  | 73.4638 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.2939 | Normal | 74.0516 | -0.81732 | Day | 202601 | 2026-01-09 | 0.81732
2026-01-09 15:13 | 73.2236 | FALSE | FALSE | -0.3643 | -0.5 | -0.7882 | -1.065 | 0 |  |  | none | FALSE | 0 | 72.8593 | FALSE | FALSE | 0.049 |  | 73.4356 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.28812 | Normal | 74.0118 | -0.73562 | Day | 202601 | 2026-01-09 | 0.73562
2026-01-09 15:28 | 73.2236 | FALSE | FALSE | -0.37478 | -0.51446 | -0.74216 | -1.0034 | 0 |  |  | none | FALSE | 0 | 72.8488 | FALSE | FALSE | 0.0439 |  | 73.4073 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.27923 | Normal | 73.9658 | -0.65784 | Day | 202601 | 2026-01-09 | 0.65784
2026-01-09 15:43 | 73.2236 | FALSE | FALSE | -0.32622 | -0.4475 | -0.60882 | -0.82459 | 0 |  |  | none | FALSE | 0 | 72.8974 | FALSE | FALSE | 0.0403 |  | 73.3649 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.23376 | Normal | 73.8324 | -0.60447 | Day | 202601 | 2026-01-09 | 0.60447
2026-01-09 15:58 | 73.2236 | FALSE | FALSE | -0.23294 | -0.31914 | -0.43076 | -0.58484 | 0 |  |  | none | FALSE | 0 | 72.9907 | FALSE | FALSE | 0.0397 |  | 73.3225 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.16593 | Normal | 73.6544 | -0.59611 | Day | 202601 | 2026-01-09 | 0.59611
2026-01-09 16:13 | 73.2236 | FALSE | FALSE | -0.18045 | -0.24704 | -0.32175 | -0.43748 | 0 |  |  | none | FALSE | 0 | 73.0432 | FALSE | FALSE | 0.0375 |  | 73.2943 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.12555 | Normal | 73.5453 | -0.56273 | Day | 202601 | 2026-01-09 | 0.56273
2026-01-09 16:28 | 73.2236 | FALSE | FALSE | -0.17543 | -0.24016 | -0.28847 | -0.39242 | 0 |  |  | none | FALSE | 0 | 73.0482 | FALSE | FALSE | 0.0325 |  | 73.2801 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.11598 | Normal | 73.5121 | -0.48734 | Day | 202601 | 2026-01-09 | 0.48734
2026-01-09 16:43 | 73.2236 | FALSE | FALSE | -0.16467 | -0.22539 | -0.24945 | -0.33951 | 0 |  |  | none | FALSE | 0 | 73.0589 | FALSE | FALSE | 0.0273 |  | 73.266 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.10353 | Normal | 73.473 | -0.40945 | Day | 202601 | 2026-01-09 | 0.40945
2026-01-09 16:58 | 72.941 | TRUE | FALSE | 0.074022 | 0.10138 | -0.51944 | -0.7071 | -0.2826 | 2026-01-09 18:42 | 2026-01-09 16:58 | lower | TRUE | 1 | 73.015 | FALSE | FALSE | 0.2634 | 2.6647 | 73.2377 | 1 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.11135 | Extreme triggered | 73.4604 | -2.6647 | Day | 202601 | 2026-01-09 | 2.6647
2026-01-09 17:13 | 72.941 | FALSE | FALSE | 0.023268 | 0.03189 | -0.54193 | -0.73749 | 0 |  | 2026-01-09 16:58 | lower | TRUE | 1 | 72.9643 | FALSE | FALSE | 0.2882 | 2.4221 | 73.2236 | 2 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.12967 | Extreme/elevated | 73.4829 | -2.1794 | Day | 202601 | 2026-01-09 | 2.1794
2026-01-09 17:27 | 72.6584 | TRUE | FALSE | 0.1748 | 0.24 | -0.89908 | -1.2223 | -0.2826 |  | 2026-01-09 16:58 | lower | TRUE | 2 | 72.8332 | TRUE | TRUE | 0.4263 | 2.6032 | 73.1953 | 3 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.18107 | Persistent | 73.5575 | -2.9654 | Day | 202601 | 2026-01-09 | 2.9654
2026-01-09 17:42 | 72.6584 | FALSE | FALSE | 0.074735 | 0.10275 | -0.94262 | -1.2807 | 0 |  | 2026-01-09 16:58 | lower | TRUE | 2 | 72.7331 | FALSE | TRUE | 0.442 | 2.5385 | 73.1671 | 4 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21697 | Persistent | 73.601 | -2.3444 | Day | 202601 | 2026-01-09 | 2.3444
2026-01-09 17:57 | 72.3758 | FALSE | FALSE | 0.19042 | 0.26241 | -1.3074 | -1.7743 | -0.2826 |  | 2026-01-09 16:58 | lower | TRUE | 2 | 72.5662 | FALSE | TRUE | 0.5217 | 2.5672 | 73.1247 | 5 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.27923 | Persistent | 73.6832 | -2.682 | Night | 202601 | 2026-01-09 | 2.682
2026-01-09 18:12 | 72.3758 | FALSE | FALSE | 0.058171 | 0.080309 | -1.3548 | -1.8375 | 0 |  | 2026-01-09 16:58 | lower | TRUE | 2 | 72.434 | FALSE | TRUE | 0.5453 | 2.5026 | 73.0823 | 6 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.32416 | Persistent | 73.7306 | -2.1794 | Night | 202601 | 2026-01-09 | 2.1794
2026-01-09 18:27 | 72.3758 | FALSE | TRUE | -0.052579 | -0.072701 | -1.3808 | -1.8721 | 0 |  | 2026-01-09 16:58 | none | FALSE | 2 | 72.3232 | FALSE | FALSE | 0.5807 | 2.4098 | 73.0399 | 7 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.35834 | Confirmed/Materialized Shift | 73.7566 | -1.8533 | Night | 202601 | 2026-01-09 | 1.8533
2026-01-09 18:42 | 72.941 | TRUE | FALSE | -0.61241 | -0.8467 | -0.75371 | -1.0227 | 0.5652 |  |  | none | FALSE | 3 | 72.3286 | TRUE | FALSE | 0.0995 |  | 73.0117 | 0 | 0.5652 | -0.02826 | 0.18107 | 3.2775 | 0.34153 | Persistence ends | 73.6947 | -0.20686 | Night | 202601 | 2026-01-09 | 0.20686
2026-01-09 18:42 | 72.941 | FALSE | FALSE | -0.60008 | -0.82951 | -0.68486 | -0.93019 | 0 |  |  | none | FALSE | 3 | 72.3409 | FALSE | FALSE | 0.0945 |  | 72.9834 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.32123 | Normal | 73.6259 | -0.13196 | Night | 202601 | 2026-01-09 | 0.13196
2026-01-09 18:43 | 72.941 | FALSE | FALSE | -0.60432 | -0.83542 | -0.66084 | -0.89785 | 0 |  |  | none | FALSE | 3 | 72.3367 | FALSE | FALSE | 0.0917 |  | 72.9693 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.31629 | Normal | 73.6018 | -0.089349 | Night | 202601 | 2026-01-09 | 0.089349
2026-01-09 18:58 | 73.5062 | TRUE | FALSE | -1.1909 | -1.6469 | -0.14531 | -0.1973 | 0.5652 |  |  | none | FALSE | 3 | 72.3153 | TRUE | FALSE | 0.19 |  | 72.9834 | 0 | 0.5652 | 0.01413 | 0.21454 | 2.5686 | 0.33406 | Normal | 73.6515 | 1.565 | Night | 202601 | 2026-01-09 | 1.565
2026-01-09 19:13 | 73.5062 | FALSE | FALSE | -1.2094 | -1.6728 | -0.192 | -0.26052 | 0 |  |  | none | FALSE | 3 | 72.2968 | FALSE | FALSE | 0.1825 |  | 72.9975 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.35034 | Normal | 73.6982 | 1.452 | Night | 202601 | 2026-01-09 | 1.452
2026-01-09 19:28 | 73.5062 | FALSE | FALSE | -1.2252 | -1.695 | -0.23608 | -0.32014 | 0 |  |  | none | FALSE | 2 | 72.281 | FALSE | FALSE | 0.1474 |  | 73.0117 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.36531 | Normal | 73.7423 | 1.3538 | Night | 202601 | 2026-01-09 | 1.3538
2026-01-09 19:42 | 73.5062 | FALSE | FALSE | -1.2387 | -1.7141 | -0.27788 | -0.37661 | 0 |  |  | none | FALSE | 2 | 72.2675 | FALSE | FALSE | 0.1416 |  | 73.0258 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.37915 | Normal | 73.7841 | 1.2671 | Night | 202601 | 2026-01-09 | 1.2671
2026-01-09 19:57 | 73.5062 | FALSE | FALSE | -1.2502 | -1.7302 | -0.31763 | -0.43025 | 0 |  |  | none | FALSE | 2 | 72.256 | FALSE | FALSE | 0.1365 |  | 73.0399 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.39196 | Normal | 73.8238 | 1.1896 | Night | 202601 | 2026-01-09 | 1.1896
2026-01-09 20:12 | 73.5062 | FALSE | FALSE | -1.2598 | -1.7438 | -0.35552 | -0.48134 | 0 |  |  | none | FALSE | 2 | 72.2464 | FALSE | FALSE | 0.1318 |  | 73.054 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.40384 | Normal | 73.8617 | 1.1196 | Night | 202601 | 2026-01-09 | 1.1196
2026-01-09 20:27 | 73.7888 | FALSE | FALSE | -1.5763 | -2.1829 | -0.16332 | -0.22085 | 0.2826 |  |  | none | FALSE | 2 | 72.2125 | FALSE | FALSE | 0.1654 |  | 73.0823 | 0 | 0.2826 | 0.02826 | 0.22271 | 1.142 | 0.43491 | Normal | 73.9521 | 1.6245 | Night | 202601 | 2026-01-09 | 1.6245
2026-01-09 20:41 | 73.7888 | FALSE | FALSE | -1.6024 | -2.2198 | -0.24594 | -0.3322 | 0 |  |  | none | FALSE | 1 | 72.1864 | FALSE | FALSE | 0.1264 |  | 73.1106 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.46209 | Normal | 74.0347 | 1.4678 | Night | 202601 | 2026-01-09 | 1.4678
2026-01-09 20:56 | 73.7888 | FALSE | FALSE | -1.622 | -2.2476 | -0.32208 | -0.43459 | 0 |  |  | none | FALSE | 1 | 72.1668 | FALSE | FALSE | 0.1177 |  | 73.1388 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.48603 | Normal | 74.1109 | 1.3373 | Night | 202601 | 2026-01-09 | 1.3373
2026-01-09 21:12 | 73.7888 | FALSE | FALSE | -1.6361 | -2.2676 | -0.39266 | -0.52932 | 0 |  |  | none | FALSE | 1 | 72.1527 | FALSE | FALSE | 0.1103 |  | 73.1671 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.50719 | Normal | 74.1815 | 1.2258 | Night | 202601 | 2026-01-09 | 1.2258
2026-01-09 21:27 | 73.7888 | FALSE | FALSE | -1.6243 | -2.2509 | -0.46567 | -0.62712 | 0 |  |  | none | FALSE | 0 | 72.1645 | FALSE | FALSE | 0.0739 |  | 73.2095 | 0 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.5225 | Normal | 74.2545 | 1.1088 | Night | 202601 | 2026-01-09 | 1.1088
2026-01-09 21:41 | 74.0714 | FALSE | FALSE | -1.9099 | -2.6466 | -0.29903 | -0.40209 | 0.2826 |  |  | none | FALSE | 0 | 72.1615 | FALSE | FALSE | 0.0972 |  | 73.266 | 0 | 0.2826 | 0.05652 | 0.21697 | 1.042 | 0.55222 | Normal | 74.3704 | 1.4585 | Night | 202601 | 2026-01-09 | 1.4585
2026-01-09 21:56 | 74.0714 | FALSE | FALSE | -1.8562 | -2.5704 | -0.38668 | -0.51933 | 0 |  |  | none | FALSE | 0 | 72.2152 | FALSE | FALSE | 0.0874 |  | 73.3366 | 0 | 0 | 0.07065 | 0.20244 | -0.34899 | 0.56072 | Normal | 74.4581 | 1.3104 | Night | 202601 | 2026-01-09 | 1.3104
2026-01-09 22:11 | 74.0714 | FALSE | FALSE | -1.7837 | -2.4675 | -0.45545 | -0.61113 | 0 |  |  | none | FALSE | 0 | 72.2877 | FALSE | FALSE | 0.0791 |  | 73.4073 | 0 | 0 | 0.07065 | 0.20244 | -0.34899 | 0.55978 | Normal | 74.5269 | 1.1864 | Night | 202601 | 2026-01-09 | 1.1864
2026-01-09 22:26 | 74.0714 | FALSE | FALSE | -1.6243 | -2.2421 | -0.46567 | -0.62475 | 0 |  |  | none | FALSE | 0 | 72.4471 | FALSE | FALSE | 0.0739 |  | 73.4921 | 0 | 0 | 0.08478 | 0.18565 | -0.45666 | 0.5225 | Normal | 74.5371 | 1.1088 | Night | 202601 | 2026-01-09 | 1.1088
2026-01-09 22:41 | 74.0714 | FALSE | FALSE | -1.4273 | -1.9648 | -0.43823 | -0.58816 | 0 |  |  | none | FALSE | 0 | 72.6441 | FALSE | FALSE | 0.0707 |  | 73.5768 | 0 | 0 | 0.08478 | 0.18565 | -0.45666 | 0.46639 | Normal | 74.5096 | 1.0604 | Night | 202601 | 2026-01-09 | 1.0604
2026-01-09 22:56 | 74.0714 | FALSE | FALSE | -1.1763 | -1.6137 | -0.35679 | -0.47938 | 0 |  |  | none | FALSE | 0 | 72.8951 | FALSE | FALSE | 0.0713 |  | 73.6616 | 0 | 0 | 0.08478 | 0.18565 | -0.45666 | 0.38328 | Normal | 74.4282 | 1.0691 | Night | 202601 | 2026-01-09 | 1.0691
2026-01-09 23:11 | 74.0714 | FALSE | FALSE | -1.0605 | -1.4525 | -0.35399 | -0.47564 | 0 |  |  | none | FALSE | 0 | 73.0109 | FALSE | FALSE | 0.0666 |  | 73.7181 | 0 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.35362 | Normal | 74.4254 | 0.99895 | Night | 202601 | 2026-01-09 | 0.99895
2026-01-09 23:26 | 74.0714 | FALSE | FALSE | -0.91791 | -1.2548 | -0.32445 | -0.43611 | 0 |  |  | none | FALSE | 0 | 73.1535 | FALSE | FALSE | 0.0637 |  | 73.7747 | 0 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.31059 | Normal | 74.3958 | 0.95538 | Night | 202601 | 2026-01-09 | 0.95538
2026-01-09 23:41 | 74.0714 | FALSE | FALSE | -0.73481 | -1.002 | -0.25439 | -0.34227 | 0 |  |  | none | FALSE | 0 | 73.3366 | FALSE | FALSE | 0.0648 |  | 73.8312 | 0 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.2473 | Normal | 74.3258 | 0.97132 | Night | 202601 | 2026-01-09 | 0.97132
2026-01-09 23:56 | 74.0714 | FALSE | FALSE | -0.69276 | -0.94409 | -0.26886 | -0.36167 | 0 |  |  | none | FALSE | 0 | 73.3786 | FALSE | FALSE | 0.0588 |  | 73.8594 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.24041 | Normal | 74.3403 | 0.88163 | Night | 202601 | 2026-01-09 | 0.88163
2026-01-10 00:11 | 74.0714 | FALSE | FALSE | -0.64304 | -0.87574 | -0.27566 | -0.37078 | 0 |  |  | none | FALSE | 0 | 73.4284 | FALSE | FALSE | 0.0533 |  | 73.8877 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.22968 | Normal | 74.3471 | 0.79978 | Night | 202601 | 2026-01-10 | 0.79978
2026-01-10 00:26 | 74.0714 | FALSE | FALSE | -0.5845 | -0.79539 | -0.27364 | -0.36807 | 0 |  |  | none | FALSE | 0 | 73.4869 | FALSE | FALSE | 0.0483 |  | 73.916 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.21454 | Normal | 74.345 | 0.72449 | Night | 202601 | 2026-01-10 | 0.72449
2026-01-10 00:40 | 74.0714 | FALSE | FALSE | -0.51509 | -0.70026 | -0.26075 | -0.35078 | 0 |  |  | none | FALSE | 0 | 73.5563 | FALSE | FALSE | 0.0437 |  | 73.9442 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.19396 | Normal | 74.3321 | 0.65566 | Night | 202601 | 2026-01-10 | 0.65566
2026-01-10 00:55 | 74.0714 | FALSE | FALSE | -0.43076 | -0.58495 | -0.23294 | -0.3135 | 0 |  |  | none | FALSE | 0 | 73.6406 | FALSE | FALSE | 0.0397 |  | 73.9725 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.16593 | Normal | 74.3043 | 0.59611 | Night | 202601 | 2026-01-10 | 0.59611
2026-01-10 01:10 | 74.0714 | FALSE | FALSE | -0.32175 | -0.43627 | -0.18045 | -0.24302 | 0 |  |  | none | FALSE | 0 | 73.7497 | FALSE | FALSE | 0.0375 |  | 74.0007 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.12555 | Normal | 74.2518 | 0.56273 | Night | 202601 | 2026-01-10 | 0.56273
2026-01-10 01:25 | 73.7888 | TRUE | FALSE | -0.039147 | -0.053081 | -0.46305 | -0.62362 | -0.2826 |  |  | none | FALSE | 1 | 73.7497 | FALSE | FALSE | 0.1411 |  | 74.0007 | 0 | -0.2826 | 0 | 0.091688 | -3.0822 | 0.12555 | Normal | 74.2518 | -1.6882 | Night | 202601 | 2026-01-10 | 1.6882
2026-01-10 01:40 | 73.7888 | FALSE | FALSE | -0.039147 | -0.053081 | -0.46305 | -0.62362 | 0 |  |  | none | FALSE | 1 | 73.7497 | FALSE | FALSE | 0.1411 |  | 74.0007 | 0 | 0 | 0 | 0.091688 | 0 | 0.12555 | Normal | 74.2518 | -1.6882 | Night | 202601 | 2026-01-10 | 1.6882
2026-01-10 01:55 | 74.0714 | TRUE | FALSE | -0.28847 | -0.39098 | -0.17543 | -0.23628 | 0.2826 |  |  | none | FALSE | 2 | 73.7829 | TRUE | FALSE | 0.0896 |  | 74.0149 | 0 | 0.2826 | 0.01413 | 0.11135 | 2.411 | 0.11598 | Normal | 74.2468 | 0.48734 | Night | 202601 | 2026-01-10 | 0.48734
2026-01-10 02:10 | 73.7888 | TRUE | FALSE | -0.0058732 | -0.0079601 | -0.45803 | -0.61691 | -0.2826 |  |  | none | FALSE | 3 | 73.7829 | TRUE | FALSE | 0.2157 |  | 74.0149 | 0 | -0.2826 | 0 | 0.12967 | -2.1794 | 0.11598 | Normal | 74.2468 | -1.9494 | Night | 202601 | 2026-01-10 | 1.9494
2026-01-10 02:25 | 73.7888 | FALSE | FALSE | -0.0058732 | -0.0079601 | -0.45803 | -0.61691 | 0 |  |  | none | FALSE | 3 | 73.7829 | FALSE | FALSE | 0.2157 |  | 74.0149 | 0 | 0 | 0 | 0.12967 | 0 | 0.11598 | Normal | 74.2468 | -1.9494 | Night | 202601 | 2026-01-10 | 1.9494
2026-01-10 02:40 | 73.7888 | FALSE | FALSE | -0.039147 | -0.053081 | -0.46305 | -0.62362 | 0 |  |  | none | FALSE | 3 | 73.7497 | FALSE | FALSE | 0.1983 |  | 74.0007 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.12555 | Normal | 74.2518 | -1.6882 | Night | 202601 | 2026-01-10 | 1.6882
2026-01-10 02:55 | 73.7888 | FALSE | FALSE | -0.067916 | -0.092126 | -0.46356 | -0.6243 | 0 |  |  | none | FALSE | 3 | 73.7209 | FALSE | FALSE | 0.185 |  | 73.9866 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13287 | Normal | 74.2524 | -1.4888 | Night | 202601 | 2026-01-10 | 1.4888
2026-01-10 03:10 | 73.7888 | FALSE | FALSE | -0.092897 | -0.12605 | -0.46028 | -0.61991 | 0 |  |  | none | FALSE | 3 | 73.6959 | FALSE | FALSE | 0.1743 |  | 73.9725 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13829 | Normal | 74.2491 | -1.3283 | Night | 202601 | 2026-01-10 | 1.3283
2026-01-10 03:25 | 73.7888 | FALSE | FALSE | -0.11452 | -0.15545 | -0.45364 | -0.61103 | 0 |  |  | none | FALSE | 3 | 73.6743 | FALSE | FALSE | 0.1653 |  | 73.9584 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14204 | Normal | 74.2424 | -1.1937 | Night | 202601 | 2026-01-10 | 1.1937
2026-01-10 03:39 | 73.7888 | FALSE | FALSE | -0.13306 | -0.18065 | -0.44392 | -0.59801 | 0 |  |  | none | FALSE | 3 | 73.6557 | FALSE | FALSE | 0.1576 |  | 73.9442 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14424 | Normal | 74.2327 | -1.0775 | Night | 202601 | 2026-01-10 | 1.0775
2026-01-10 03:54 | 73.5062 | TRUE | FALSE | 0.067934 | 0.092334 | -0.75161 | -1.0122 | -0.2826 | 2026-01-10 05:24 | 2026-01-10 03:54 | lower | TRUE | 3 | 73.5741 | TRUE | FALSE | 0.3027 | 2.3975 | 73.916 | 1 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.17092 | Extreme triggered | 74.2578 | -2.3975 | Night | 202601 | 2026-01-10 | 2.3975
2026-01-10 04:09 | 73.5062 | FALSE | FALSE | 0.0023623 | 0.0032137 | -0.76066 | -1.0242 | 0 |  | 2026-01-10 03:54 | lower | TRUE | 3 | 73.5086 | FALSE | FALSE | 0.3342 | 2.205 | 73.8877 | 2 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.18957 | Extreme/elevated | 74.2669 | -2.0125 | Night | 202601 | 2026-01-10 | 2.0125
2026-01-10 04:24 | 73.5062 | FALSE | FALSE | -0.051631 | -0.07029 | -0.75813 | -1.0209 | 0 |  | 2026-01-10 03:54 | none | FALSE | 2 | 73.4546 | FALSE | FALSE | 0.3449 | 2.0516 | 73.8594 | 3 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.20244 | Persistent | 74.2643 | -1.745 | Night | 202601 | 2026-01-10 | 1.745
2026-01-10 04:39 | 73.5062 | FALSE | FALSE | -0.096174 | -0.13101 | -0.74615 | -1.0049 | 0 |  | 2026-01-10 03:54 | none | FALSE | 1 | 73.41 | FALSE | FALSE | 0.36 | 1.9245 | 73.8312 | 4 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21058 | Persistent | 74.2524 | -1.5433 | Night | 202601 | 2026-01-10 | 1.5433
2026-01-10 04:54 | 73.5062 | FALSE | FALSE | -0.13234 | -0.18037 | -0.7258 | -0.97775 | 0 |  | 2026-01-10 03:54 | none | FALSE | 1 | 73.3739 | FALSE | FALSE | 0.4065 | 1.8163 | 73.8029 | 5 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21454 | Persistent | 74.232 | -1.3831 | Night | 202601 | 2026-01-10 | 1.3831
2026-01-10 05:09 | 73.2236 | FALSE | FALSE | 0.055253 | 0.075401 | -1.0186 | -1.372 | -0.2826 |  | 2026-01-10 03:54 | lower | TRUE | 1 | 73.2789 | FALSE | TRUE | 0.5201 | 1.8851 | 73.7605 | 6 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.24084 | Persistent | 74.2422 | -2.2294 | Night | 202601 | 2026-01-10 | 2.2294
2026-01-10 05:24 | 73.5062 | FALSE | FALSE | -0.24502 | -0.33445 | -0.69718 | -0.93955 | 0.2826 |  |  | none | FALSE | 1 | 73.2612 | FALSE | FALSE | 0.0926 |  | 73.7323 | 0 | 0.2826 | -0.02826 | 0.15614 | 1.9909 | 0.23555 | Persistence ends | 74.2034 | -0.9598 | Night | 202601 | 2026-01-10 | 0.9598
2026-01-10 05:39 | 73.2236 | FALSE | FALSE | -0.028313 | -0.038682 | -0.96089 | -1.2953 | -0.2826 |  |  | none | FALSE | 1 | 73.1953 | FALSE | FALSE | 0.1543 |  | 73.6899 | 0 | -0.2826 | -0.04239 | 0.16593 | -1.4477 | 0.2473 | Normal | 74.1845 | -1.8855 | Night | 202601 | 2026-01-10 | 1.8855
2026-01-10 05:54 | 73.2236 | FALSE | FALSE | -0.078293 | -0.10704 | -0.92609 | -1.249 | 0 |  |  | none | FALSE | 1 | 73.1453 | FALSE | FALSE | 0.1411 |  | 73.6475 | 0 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.2511 | Normal | 74.1497 | -1.6882 | Night | 202601 | 2026-01-10 | 1.6882
2026-01-10 06:09 | 73.2236 | FALSE | FALSE | -0.11309 | -0.15469 | -0.87611 | -1.1823 | 0 |  |  | none | FALSE | 1 | 73.1105 | FALSE | FALSE | 0.1314 |  | 73.6051 | 0 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.2473 | Normal | 74.0997 | -1.5427 | Night | 202601 | 2026-01-10 | 1.5427
2026-01-10 06:24 | 73.2236 | FALSE | FALSE | -0.16135 | -0.22083 | -0.86785 | -1.1713 | 0 |  |  | none | FALSE | 0 | 73.0623 | FALSE | FALSE | 0.0915 |  | 73.5768 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.2573 | Normal | 74.0914 | -1.3729 | Night | 202601 | 2026-01-10 | 1.3729
2026-01-10 06:38 | 73.2236 | FALSE | FALSE | -0.20251 | -0.27733 | -0.85249 | -1.1508 | 0 |  |  | none | FALSE | 0 | 73.0211 | FALSE | FALSE | 0.0821 |  | 73.5486 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.26375 | Normal | 74.0761 | -1.2322 | Night | 202601 | 2026-01-10 | 1.2322
2026-01-10 06:53 | 72.941 | FALSE | FALSE | 0.017231 | 0.023618 | -1.0849 | -1.4656 | -0.2826 | 2026-01-10 07:08 | 2026-01-10 06:53 | lower | TRUE | 0 | 72.9582 | FALSE | FALSE | 0.1948 | 2.0646 | 73.4921 | 1 | -0.2826 | -0.05652 | 0.14784 | -1.5292 | 0.26692 | Extreme triggered | 74.0259 | -2.0646 | Night | 202601 | 2026-01-10 | 2.0646
2026-01-10 07:08 | 73.2236 | FALSE | FALSE | -0.28729 | -0.39389 | -0.76771 | -1.0376 | 0.2826 |  |  | none | FALSE | 0 | 72.9363 | FALSE | FALSE | 0.0607 |  | 73.4638 | 0 | 0.2826 | -0.02826 | 0.15614 | 1.9909 | 0.26375 | Persistence ends | 73.9913 | -0.91074 | Night | 202601 | 2026-01-10 | 0.91074
2026-01-10 07:23 | 72.941 | FALSE | FALSE | -0.072753 | -0.099842 | -1.0336 | -1.3972 | -0.2826 |  |  | none | FALSE | 0 | 72.8682 | FALSE | FALSE | 0.1158 |  | 73.4214 | 0 | -0.2826 | -0.04239 | 0.16593 | -1.4477 | 0.27659 | Normal | 73.9746 | -1.737 | Day | 202601 | 2026-01-10 | 1.737
2026-01-10 07:30 | 72.941 | FALSE | FALSE | -0.12643 | -0.17363 | -1.0025 | -1.3557 | 0 |  |  | none | FALSE | 0 | 72.8146 | FALSE | FALSE | 0.1035 |  | 73.379 | 0 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.28223 | Normal | 73.9435 | -1.552 | Day | 202601 | 2026-01-10 | 1.552
2026-01-10 07:45 | 72.941 | FALSE | FALSE | -0.16658 | -0.2289 | -0.95786 | -1.2962 | 0 |  |  | none | FALSE | 0 | 72.7744 | FALSE | FALSE | 0.0938 |  | 73.3366 | 0 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.28111 | Normal | 73.8989 | -1.4074 | Day | 202601 | 2026-01-10 | 1.4074
2026-01-10 08:00 | 73.2236 | FALSE | FALSE | -0.43711 | -0.60054 | -0.60667 | -0.82172 | 0.2826 |  |  | none | FALSE | 0 | 72.7865 | FALSE | FALSE | 0.0217 |  | 73.3084 | 0 | 0.2826 | -0.02826 | 0.18107 | 1.7168 | 0.26095 | Normal | 73.8303 | -0.32489 | Day | 202601 | 2026-01-10 | 0.32489
2026-01-10 08:15 | 73.2236 | FALSE | FALSE | -0.41458 | -0.56941 | -0.52762 | -0.7154 | 0 |  |  | none | FALSE | 0 | 72.809 | FALSE | FALSE | 0.016 |  | 73.2801 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.23555 | Normal | 73.7512 | -0.23995 | Day | 202601 | 2026-01-10 | 0.23995
2026-01-10 08:30 | 73.2236 | FALSE | FALSE | -0.37766 | -0.51843 | -0.43418 | -0.58945 | 0 |  |  | none | FALSE | 0 | 72.8459 | FALSE | FALSE | 0.0093 |  | 73.2519 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.20296 | Normal | 73.6578 | -0.13924 | Day | 202601 | 2026-01-10 | 0.13924
2026-01-10 08:30 | 73.2236 | FALSE | FALSE | -0.37379 | -0.51309 | -0.40205 | -0.54607 | 0 |  |  | none | FALSE | 0 | 72.8498 | FALSE | FALSE | 0.0049 |  | 73.2377 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.19396 | Normal | 73.6256 | -0.072851 | Day | 202601 | 2026-01-10 | 0.072851
2026-01-10 08:45 | 73.2236 | FALSE | FALSE | -0.36675 | -0.50338 | -0.36675 | -0.49837 | 0 |  |  | none | FALSE | 0 | 72.8568 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.18338 | Normal | 73.5904 | 0 | Day | 202601 | 2026-01-10 | 0
2026-01-10 09:00 | 73.5062 | FALSE | FALSE | -0.64935 | -0.89127 | -0.08415 | -0.11435 | 0.2826 |  |  | none | FALSE | 0 | 72.8568 | FALSE | FALSE | 0.1027 |  | 73.2236 | 0 | 0.2826 | 0 | 0.18338 | 1.5411 | 0.18338 | Normal | 73.5904 | 1.5411 | Day | 202601 | 2026-01-10 | 1.5411
2026-01-10 09:15 | 73.5062 | FALSE | FALSE | -0.64935 | -0.89127 | -0.08415 | -0.11435 | 0 |  |  | none | FALSE | 0 | 72.8568 | FALSE | FALSE | 0.1027 |  | 73.2236 | 0 | 0 | 0 | 0.18338 | 0 | 0.18338 | Normal | 73.5904 | 1.5411 | Day | 202601 | 2026-01-10 | 1.5411
2026-01-10 09:30 | 73.5062 | FALSE | FALSE | -0.64935 | -0.89127 | -0.08415 | -0.11435 | 0 |  |  | none | FALSE | 0 | 72.8568 | FALSE | FALSE | 0.1027 |  | 73.2236 | 0 | 0 | 0 | 0.18338 | 0 | 0.18338 | Normal | 73.5904 | 1.5411 | Day | 202601 | 2026-01-10 | 1.5411
2026-01-10 09:45 | 73.2236 | FALSE | FALSE | -0.36675 | -0.50338 | -0.36675 | -0.49837 | -0.2826 |  |  | none | FALSE | 0 | 72.8568 | FALSE | FALSE | 0 |  | 73.2236 | 0 | -0.2826 | 0 | 0.18338 | -1.5411 | 0.18338 | Normal | 73.5904 | 0 | Day | 202601 | 2026-01-10 | 0
2026-01-10 10:00 | 73.2236 | FALSE | FALSE | -0.35597 | -0.48851 | -0.32771 | -0.44555 | 0 |  |  | none | FALSE | 0 | 72.8676 | FALSE | FALSE | 0.0055 |  | 73.2095 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.17092 | Normal | 73.5513 | 0.082671 | Day | 202601 | 2026-01-10 | 0.082671
2026-01-10 10:15 | 73.2236 | FALSE | FALSE | -0.35597 | -0.48851 | -0.32771 | -0.44555 | 0 |  |  | none | FALSE | 0 | 72.8676 | FALSE | FALSE | 0.0055 |  | 73.2095 | 0 | 0 | 0 | 0.15881 | 0 | 0.17092 | Normal | 73.5513 | 0.082671 | Day | 202601 | 2026-01-10 | 0.082671
2026-01-10 10:29 | 73.2236 | FALSE | FALSE | -0.35597 | -0.48851 | -0.32771 | -0.44555 | 0 |  |  | none | FALSE | 0 | 72.8676 | FALSE | FALSE | 0.0055 |  | 73.2095 | 0 | 0 | 0 | 0.15881 | 0 | 0.17092 | Normal | 73.5513 | 0.082671 | Day | 202601 | 2026-01-10 | 0.082671
2026-01-10 10:44 | 73.2236 | FALSE | FALSE | -0.35597 | -0.48851 | -0.32771 | -0.44555 | 0 |  |  | none | FALSE | 0 | 72.8676 | FALSE | FALSE | 0.0055 |  | 73.2095 | 0 | 0 | 0 | 0.15881 | 0 | 0.17092 | Normal | 73.5513 | 0.082671 | Day | 202601 | 2026-01-10 | 0.082671
2026-01-10 10:59 | 73.2236 | FALSE | FALSE | -0.35597 | -0.48851 | -0.32771 | -0.44555 | 0 |  |  | none | FALSE | 0 | 72.8676 | FALSE | FALSE | 0.0055 |  | 73.2095 | 0 | 0 | 0 | 0.15881 | 0 | 0.17092 | Normal | 73.5513 | 0.082671 | Day | 202601 | 2026-01-10 | 0.082671
2026-01-10 11:14 | 73.2236 | FALSE | FALSE | -0.35597 | -0.48851 | -0.32771 | -0.44555 | 0 |  |  | none | FALSE | 0 | 72.8676 | FALSE | FALSE | 0.0055 |  | 73.2095 | 0 | 0 | 0 | 0.15881 | 0 | 0.17092 | Normal | 73.5513 | 0.082671 | Day | 202601 | 2026-01-10 | 0.082671
2026-01-10 11:29 | 73.5062 | FALSE | FALSE | -0.61031 | -0.83723 | -0.073366 | -0.09971 | 0.2826 |  |  | none | FALSE | 0 | 72.8959 | FALSE | FALSE | 0.1047 |  | 73.2377 | 0 | 0.2826 | 0.02826 | 0.15614 | 1.6289 | 0.17092 | Normal | 73.5796 | 1.5708 | Day | 202601 | 2026-01-10 | 1.5708
2026-01-10 11:44 | 73.5062 | FALSE | FALSE | -0.61648 | -0.84577 | -0.1078 | -0.14644 | 0 |  |  | none | FALSE | 0 | 72.8897 | FALSE | FALSE | 0.0936 |  | 73.2519 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.18107 | Normal | 73.614 | 1.4047 | Day | 202601 | 2026-01-10 | 1.4047
2026-01-10 11:59 | 73.7888 | FALSE | FALSE | -0.89943 | -1.234 | 0.089669 | 0.12167 | 0.2826 | 2026-01-10 12:21 | 2026-01-10 11:59 | upper | TRUE | 0 | 72.8894 | FALSE | FALSE | 0.22 | 2.4429 | 73.2943 | 1 | 0.2826 | 0.04239 | 0.13829 | 1.737 | 0.20244 | Extreme triggered | 73.6991 | 2.4429 | Day | 202601 | 2026-01-10 | 2.4429
2026-01-10 12:03 | 74.0714 | FALSE | FALSE | -1.222 | -1.6774 | 0.21927 | 0.29691 | 0.2826 |  | 2026-01-10 11:59 | upper | TRUE | 0 | 72.8494 | FALSE | FALSE | 0.3059 | 2.6588 | 73.3508 | 2 | 0.2826 | 0.05652 | 0.14784 | 1.5292 | 0.25068 | Extreme/elevated | 73.8521 | 2.8747 | Day | 202601 | 2026-01-10 | 2.8747
2026-01-10 12:06 | 73.7888 | FALSE | FALSE | -0.89447 | -1.2271 | -0.10319 | -0.13966 | -0.2826 |  | 2026-01-10 11:59 | none | FALSE | 0 | 72.8943 | FALSE | FALSE | 0.2772 | 2.3013 | 73.3932 | 3 | -0.2826 | 0.04239 | 0.16593 | -1.9586 | 0.24942 | Persistent | 73.892 | 1.5863 | Day | 202601 | 2026-01-10 | 1.5863
2026-01-10 12:21 | 73.2236 | TRUE | FALSE | -0.32927 | -0.45171 | -0.66839 | -0.90456 | -0.5652 |  |  | none | FALSE | 1 | 72.8943 | FALSE | FALSE | 0.0739 |  | 73.3932 | 0 | -0.5652 | 0 | 0.20502 | -2.7568 | 0.24942 | Persistence ends | 73.892 | -0.67983 | Day | 202601 | 2026-01-10 | 0.67983
2026-01-10 12:29 | 73.2236 | FALSE | FALSE | -0.32927 | -0.45171 | -0.66839 | -0.90456 | 0 |  |  | none | FALSE | 1 | 72.8943 | FALSE | FALSE | 0.0739 |  | 73.3932 | 0 | 0 | 0 | 0.20502 | 0 | 0.24942 | Normal | 73.892 | -0.67983 | Day | 202601 | 2026-01-10 | 0.67983
2026-01-10 12:44 | 73.2236 | FALSE | FALSE | -0.32927 | -0.45171 | -0.66839 | -0.90456 | 0 |  |  | none | FALSE | 1 | 72.8943 | FALSE | FALSE | 0.0739 |  | 73.3932 | 0 | 0 | 0 | 0.20502 | 0 | 0.24942 | Normal | 73.892 | -0.67983 | Day | 202601 | 2026-01-10 | 0.67983
2026-01-10 12:59 | 72.941 | FALSE | FALSE | -0.095809 | -0.13152 | -0.97187 | -1.3149 | -0.2826 |  |  | none | FALSE | 1 | 72.8452 | FALSE | FALSE | 0.138 |  | 73.379 | 0 | -0.2826 | -0.01413 | 0.21454 | -1.2514 | 0.26692 | Normal | 73.9129 | -1.6411 | Day | 202601 | 2026-01-10 | 1.6411
2026-01-10 13:14 | 72.941 | FALSE | FALSE | -0.1413 | -0.19409 | -0.9891 | -1.3379 | 0 |  |  | none | FALSE | 1 | 72.7997 | FALSE | FALSE | 0.1286 |  | 73.3649 | 0 | 0 | -0.01413 | 0.21454 | 0.065863 | 0.2826 | Normal | 73.9301 | -1.5 | Day | 202601 | 2026-01-10 | 1.5
2026-01-10 13:28 | 72.6584 | FALSE | FALSE | 0.021643 | 0.029778 | -1.3066 | -1.7665 | -0.2826 | 2026-01-10 13:59 | 2026-01-10 13:28 | lower | TRUE | 1 | 72.68 | FALSE | FALSE | 0.2235 | 2.0674 | 73.3225 | 1 | -0.2826 | -0.04239 | 0.21058 | -1.1407 | 0.32123 | Extreme triggered | 73.965 | -2.0674 | Day | 202601 | 2026-01-10 | 2.0674
2026-01-10 13:43 | 72.6584 | FALSE | FALSE | -0.078955 | -0.10878 | -1.3224 | -1.7875 | 0 |  | 2026-01-10 13:28 | none | FALSE | 1 | 72.5794 | FALSE | FALSE | 0.2612 | 1.921 | 73.2801 | 2 | 0 | -0.04239 | 0.21058 | 0.2013 | 0.35034 | Extreme/elevated | 73.9808 | -1.7746 | Day | 202601 | 2026-01-10 | 1.7746
2026-01-10 13:59 | 72.941 | FALSE | FALSE | -0.39698 | -0.54722 | -1.0187 | -1.3774 | 0.2826 |  |  | none | FALSE | 1 | 72.544 | FALSE | FALSE | 0.0871 |  | 73.2519 | 0 | 0.2826 | -0.02826 | 0.22271 | 1.3958 | 0.35392 | Persistence ends | 73.9597 | -0.87834 | Day | 202601 | 2026-01-10 | 0.87834
2026-01-10 14:14 | 72.941 | FALSE | FALSE | -0.42464 | -0.58557 | -1.0181 | -1.3766 | 0 |  |  | none | FALSE | 1 | 72.5164 | FALSE | FALSE | 0.0834 |  | 73.2377 | 0 | 0 | -0.01413 | 0.21454 | 0.065863 | 0.36068 | Normal | 73.9591 | -0.82269 | Day | 202601 | 2026-01-10 | 0.82269
2026-01-10 14:28 | 73.2236 | FALSE | FALSE | -0.70724 | -0.97528 | -0.7355 | -0.99446 | 0.2826 |  |  | none | FALSE | 1 | 72.5164 | FALSE | FALSE | 0.0312 |  | 73.2377 | 0 | 0.2826 | 0 | 0.22459 | 1.2583 | 0.36068 | Normal | 73.9591 | -0.039176 | Day | 202601 | 2026-01-10 | 0.039176
2026-01-10 14:43 | 73.2236 | FALSE | FALSE | -0.70724 | -0.97528 | -0.7355 | -0.99446 | 0 |  |  | none | FALSE | 0 | 72.5164 | FALSE | FALSE | 0.0026 |  | 73.2377 | 0 | 0 | 0 | 0.22459 | 0 | 0.36068 | Normal | 73.9591 | -0.039176 | Day | 202601 | 2026-01-10 | 0.039176
2026-01-10 14:58 | 73.2236 | FALSE | FALSE | -0.70724 | -0.97528 | -0.7355 | -0.99446 | 0 |  |  | none | FALSE | 0 | 72.5164 | FALSE | FALSE | 0.0026 |  | 73.2377 | 0 | 0 | 0 | 0.22459 | 0 | 0.36068 | Normal | 73.9591 | -0.039176 | Day | 202601 | 2026-01-10 | 0.039176
2026-01-10 15:13 | 73.5062 | FALSE | FALSE | -0.98554 | -1.359 | -0.47686 | -0.64456 | 0.2826 |  |  | none | FALSE | 0 | 72.5207 | FALSE | FALSE | 0.0464 |  | 73.2519 | 0 | 0.2826 | 0.01413 | 0.23331 | 1.1507 | 0.3656 | Normal | 73.9831 | 0.69567 | Day | 202601 | 2026-01-10 | 0.69567
2026-01-10 15:28 | 73.5062 | FALSE | FALSE | -0.97999 | -1.3512 | -0.49957 | -0.67504 | 0 |  |  | none | FALSE | 0 | 72.5262 | FALSE | FALSE | 0.0433 |  | 73.266 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.36989 | Normal | 74.0058 | 0.64941 | Day | 202601 | 2026-01-10 | 0.64941
2026-01-10 15:38 | 73.5062 | FALSE | FALSE | -0.97321 | -1.3417 | -0.52105 | -0.70386 | 0 |  |  | none | FALSE | 0 | 72.533 | FALSE | FALSE | 0.0403 |  | 73.2801 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.37356 | Normal | 74.0272 | 0.6052 | Day | 202601 | 2026-01-10 | 0.6052
2026-01-10 15:38 | 73.5062 | FALSE | FALSE | -0.97321 | -1.3417 | -0.52105 | -0.70386 | 0 |  |  | none | FALSE | 0 | 72.533 | FALSE | FALSE | 0.0403 |  | 73.2801 | 0 | 0 | 0 | 0.22459 | 0 | 0.37356 | Normal | 74.0272 | 0.6052 | Day | 202601 | 2026-01-10 | 0.6052
2026-01-10 15:53 | 73.5062 | FALSE | FALSE | -0.97321 | -1.3417 | -0.52105 | -0.70386 | 0 |  |  | none | FALSE | 0 | 72.533 | FALSE | FALSE | 0.0403 |  | 73.2801 | 0 | 0 | 0 | 0.22459 | 0 | 0.37356 | Normal | 74.0272 | 0.6052 | Day | 202601 | 2026-01-10 | 0.6052
2026-01-10 16:08 | 73.5062 | FALSE | FALSE | -0.9569 | -1.319 | -0.47648 | -0.64404 | 0 |  |  | none | FALSE | 0 | 72.5493 | FALSE | FALSE | 0.0447 |  | 73.266 | 0 | 0 | -0.01413 | 0.21454 | 0.065863 | 0.35834 | Normal | 73.9827 | 0.67033 | Day | 202601 | 2026-01-10 | 0.67033
2026-01-10 16:23 | 73.5062 | FALSE | FALSE | -0.88965 | -1.2251 | -0.35271 | -0.47754 | 0 |  |  | none | FALSE | 0 | 72.6166 | FALSE | FALSE | 0.0576 |  | 73.2377 | 0 | 0 | -0.02826 | 0.20296 | 0.13924 | 0.31059 | Normal | 73.8589 | 0.86439 | Day | 202601 | 2026-01-10 | 0.86439
2026-01-10 16:37 | 73.2236 | FALSE | FALSE | -0.57859 | -0.79646 | -0.55033 | -0.74596 | -0.2826 |  |  | none | FALSE | 0 | 72.645 | FALSE | FALSE | 0.0033 |  | 73.2095 | 0 | -0.2826 | -0.02826 | 0.20296 | -1.2532 | 0.28223 | Normal | 73.7739 | 0.050066 | Day | 202601 | 2026-01-10 | 0.050066
2026-01-10 16:52 | 73.2236 | FALSE | FALSE | -0.57859 | -0.79646 | -0.55033 | -0.74596 | 0 |  |  | none | FALSE | 0 | 72.645 | FALSE | FALSE | 0.0033 |  | 73.2095 | 0 | 0 | 0 | 0.15881 | 0 | 0.28223 | Normal | 73.7739 | 0.050066 | Day | 202601 | 2026-01-10 | 0.050066
2026-01-10 17:07 | 72.941 | FALSE | FALSE | -0.32264 | -0.44429 | -0.83132 | -1.1269 | -0.2826 |  |  | none | FALSE | 0 | 72.6184 | FALSE | FALSE | 0.0588 |  | 73.1953 | 0 | -0.2826 | -0.01413 | 0.17092 | -1.5708 | 0.28849 | Normal | 73.7723 | -0.88163 | Day | 202601 | 2026-01-10 | 0.88163
2026-01-10 17:22 | 72.941 | FALSE | FALSE | -0.34759 | -0.47882 | -0.82801 | -1.1224 | 0 |  |  | none | FALSE | 0 | 72.5934 | FALSE | FALSE | 0.0545 |  | 73.1812 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.2939 | Normal | 73.769 | -0.81732 | Day | 202601 | 2026-01-10 | 0.81732
2026-01-10 17:30 | 72.941 | FALSE | FALSE | -0.34759 | -0.47882 | -0.82801 | -1.1224 | 0 |  |  | none | FALSE | 0 | 72.5934 | FALSE | FALSE | 0.0545 |  | 73.1812 | 0 | 0 | 0 | 0.15881 | 0 | 0.2939 | Normal | 73.769 | -0.81732 | Day | 202601 | 2026-01-10 | 0.81732
2026-01-10 17:31 | 72.941 | FALSE | FALSE | -0.34759 | -0.47882 | -0.82801 | -1.1224 | 0 |  |  | none | FALSE | 0 | 72.5934 | FALSE | FALSE | 0.0545 |  | 73.1812 | 0 | 0 | 0 | 0.15881 | 0 | 0.2939 | Normal | 73.769 | -0.81732 | Day | 202601 | 2026-01-10 | 0.81732
2026-01-10 17:46 | 73.2236 | FALSE | FALSE | -0.54797 | -0.75399 | -0.51971 | -0.70475 | 0.2826 |  |  | none | FALSE | 0 | 72.6756 | FALSE | FALSE | 0.0035 |  | 73.2095 | 0 | 0.2826 | 0.02826 | 0.15614 | 1.6289 | 0.26692 | Normal | 73.7433 | 0.052937 | Day | 202601 | 2026-01-10 | 0.052937
2026-01-10 18:01 | 73.7888 | TRUE | FALSE | -1.0503 | -1.444 | -0.0046923 | -0.0063587 | 0.5652 |  |  | none | FALSE | 1 | 72.7385 | FALSE | FALSE | 0.1607 |  | 73.266 | 0 | 0.5652 | 0.05652 | 0.19665 | 2.5868 | 0.26375 | Normal | 73.7935 | 1.9822 | Night | 202601 | 2026-01-10 | 1.9822
2026-01-10 18:16 | 74.0714 | FALSE | FALSE | -1.3646 | -1.8769 | 0.13315 | 0.18008 | 0.2826 | 2026-01-10 21:14 | 2026-01-10 18:16 | upper | TRUE | 1 | 72.7068 | FALSE | FALSE | 0.2479 | 2.4325 | 73.3225 | 1 | 0.2826 | 0.05652 | 0.19665 | 1.1497 | 0.30787 | Extreme triggered | 73.9383 | 2.4325 | Night | 202601 | 2026-01-10 | 2.4325
2026-01-10 18:30 | 74.0714 | FALSE | FALSE | -1.3655 | -1.8781 | 0.019231 | 0.02597 | 0 |  | 2026-01-10 18:16 | upper | TRUE | 1 | 72.7059 | FALSE | FALSE | 0.28 | 2.2448 | 73.379 | 2 | 0 | 0.05652 | 0.19665 | -0.28742 | 0.33657 | Extreme/elevated | 74.0522 | 2.0571 | Night | 202601 | 2026-01-10 | 2.0571
2026-01-10 18:45 | 74.0714 | FALSE | FALSE | -1.3858 | -1.9065 | -0.085809 | -0.11571 | 0 |  | 2026-01-10 18:16 | none | FALSE | 1 | 72.6856 | FALSE | FALSE | 0.3178 | 2.0855 | 73.4214 | 3 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.36789 | Persistent | 74.1572 | 1.7668 | Night | 202601 | 2026-01-10 | 1.7668
2026-01-10 19:00 | 74.3522 | FALSE | FALSE | -1.7123 | -2.3572 | 0.036419 | 0.049005 | 0.2808 |  | 2026-01-10 18:16 | upper | TRUE | 1 | 72.6399 | FALSE | TRUE | 0.3963 | 2.0858 | 73.4779 | 4 | 0.2808 | 0.05643 | 0.19654 | 1.1416 | 0.41897 | Persistent | 74.3158 | 2.0869 | Night | 202601 | 2026-01-10 | 2.0869
2026-01-10 19:15 | 74.3522 | FALSE | FALSE | -1.7323 | -2.3854 | -0.096442 | -0.12954 | 0 |  | 2026-01-10 18:16 | none | FALSE | 1 | 72.6199 | FALSE | FALSE | 0.4336 | 2.0265 | 73.5343 | 5 | 0 | 0.05643 | 0.19654 | -0.28712 | 0.45718 | Persistent | 74.4486 | 1.7891 | Night | 202601 | 2026-01-10 | 1.7891
2026-01-10 19:29 | 74.3522 | FALSE | FALSE | -1.7601 | -2.4246 | -0.20886 | -0.28012 | 0 |  | 2026-01-10 18:16 | none | FALSE | 1 | 72.5921 | FALSE | FALSE | 0.4765 | 1.9513 | 73.5766 | 6 | 0 | 0.0423 | 0.18945 | -0.22327 | 0.49224 | Persistent | 74.5611 | 1.5757 | Night | 202601 | 2026-01-10 | 1.5757
2026-01-10 19:44 | 74.3522 | FALSE | TRUE | -1.776 | -2.4471 | -0.3094 | -0.41441 | 0 |  | 2026-01-10 18:16 | none | FALSE | 1 | 72.5762 | FALSE | FALSE | 0.5223 | 1.8735 | 73.6189 | 7 | 0 | 0.0423 | 0.18945 | -0.22327 | 0.52136 | Confirmed/Materialized Shift | 74.6616 | 1.4065 | Night | 202601 | 2026-01-10 | 1.4065
2026-01-10 19:59 | 74.6348 | FALSE | TRUE | -2.0946 | -2.8875 | -0.17562 | -0.23475 | 0.2826 |  | 2026-01-10 18:16 | none | FALSE | 1 | 72.5402 | FALSE | FALSE | 0.5413 | 1.8506 | 73.6753 | 8 | 0.2826 | 0.05643 | 0.19654 | 1.1508 | 0.56755 | Confirmed/Materialized Shift | 74.8104 | 1.6906 | Night | 202601 | 2026-01-10 | 1.6906
2026-01-10 20:15 | 74.6348 | FALSE | TRUE | -2.1125 | -2.913 | -0.30643 | -0.40889 | 0 |  | 2026-01-10 18:16 | none | FALSE | 1 | 72.5223 | FALSE | FALSE | 0.5281 | 1.8109 | 73.7317 | 9 | 0 | 0.05643 | 0.19654 | -0.28712 | 0.60474 | Confirmed/Materialized Shift | 74.9412 | 1.4933 | Night | 202601 | 2026-01-10 | 1.4933
2026-01-10 20:29 | 74.6348 | FALSE | TRUE | -2.1157 | -2.9174 | -0.4224 | -0.56277 | 0 |  | 2026-01-10 18:16 | none | FALSE | 0 | 72.5191 | FALSE | FALSE | 0.489 | 1.7633 | 73.7882 | 10 | 0 | 0.05643 | 0.19654 | -0.28712 | 0.63451 | Confirmed/Materialized Shift | 75.0572 | 1.3343 | Night | 202601 | 2026-01-10 | 1.3343
2026-01-10 20:44 | 74.6348 | FALSE | TRUE | -2.1059 | -2.9036 | -0.52555 | -0.69923 | 0 |  | 2026-01-10 18:16 | none | FALSE | 0 | 72.5289 | FALSE | FALSE | 0.4801 | 1.7122 | 73.8446 | 11 | 0 | 0.05643 | 0.19654 | -0.28712 | 0.65787 | Confirmed/Materialized Shift | 75.1603 | 1.2011 | Night | 202601 | 2026-01-10 | 1.2011
2026-01-10 20:59 | 74.6348 | FALSE | TRUE | -2.0847 | -2.8735 | -0.6172 | -0.82018 | 0 |  | 2026-01-10 18:16 | none | FALSE | 0 | 72.5501 | FALSE | FALSE | 0.4724 | 1.66 | 73.901 | 12 | 0 | 0.05643 | 0.19654 | -0.28712 | 0.67549 | Confirmed/Materialized Shift | 75.252 | 1.0863 | Night | 202601 | 2026-01-10 | 1.0863
2026-01-10 21:14 | 74.6348 | FALSE | FALSE | -2.0126 | -2.7714 | -0.6862 | -0.91103 | 0 |  |  | none | FALSE | 0 | 72.6222 | FALSE | FALSE | 0.0655 |  | 73.9716 | 0 | 0 | 0.07056 | 0.18038 | -0.39118 | 0.6747 | Persistence ends | 75.321 | 0.98296 | Night | 202601 | 2026-01-10 | 0.98296
2026-01-10 21:29 | 74.6348 | FALSE | FALSE | -1.9248 | -2.6473 | -0.73955 | -0.98117 | 0 |  |  | none | FALSE | 0 | 72.71 | FALSE | FALSE | 0.0593 |  | 74.0422 | 0 | 0 | 0.07056 | 0.18038 | -0.39118 | 0.6661 | Normal | 75.3743 | 0.88973 | Night | 202601 | 2026-01-10 | 0.88973
2026-01-10 21:44 | 74.6348 | FALSE | FALSE | -1.7583 | -2.4126 | -0.74233 | -0.98482 | 0 |  |  | none | FALSE | 0 | 72.8765 | FALSE | FALSE | 0.0542 |  | 74.1268 | 0 | 0 | 0.08469 | 0.16132 | -0.52499 | 0.62515 | Normal | 75.3771 | 0.81255 | Night | 202601 | 2026-01-10 | 0.81255
2026-01-10 21:59 | 74.6348 | FALSE | FALSE | -1.5596 | -2.1343 | -0.71308 | -0.94639 | 0 |  |  | none | FALSE | 0 | 73.0752 | FALSE | FALSE | 0.0497 |  | 74.2115 | 0 | 0 | 0.08469 | 0.16132 | -0.52499 | 0.56818 | Normal | 75.3479 | 0.74496 | Night | 202601 | 2026-01-10 | 0.74496
2026-01-10 22:14 | 74.6348 | FALSE | FALSE | -1.3179 | -1.7975 | -0.64069 | -0.85113 | 0 |  |  | none | FALSE | 0 | 73.3169 | FALSE | FALSE | 0.0461 |  | 74.2962 | 0 | 0 | 0.08469 | 0.16132 | -0.52499 | 0.48964 | Normal | 75.2755 | 0.69149 | Night | 202601 | 2026-01-10 | 0.69149
2026-01-10 22:28 | 74.3522 | FALSE | FALSE | -0.7284 | -0.98935 | -0.75756 | -1.0086 | -0.2826 |  |  | none | FALSE | 0 | 73.6238 | FALSE | FALSE | 0.0026 |  | 74.3668 | 0 | -0.2826 | 0.07056 | 0.18038 | -1.9579 | 0.37149 | Normal | 75.1098 | -0.039247 | Night | 202601 | 2026-01-10 | 0.039247
2026-01-10 22:44 | 74.3522 | FALSE | FALSE | -0.44234 | -0.59848 | -0.58436 | -0.7798 | 0 |  |  | none | FALSE | 0 | 73.9099 | FALSE | FALSE | 0.0184 |  | 74.4232 | 0 | 0 | 0.05643 | 0.17384 | -0.3246 | 0.25667 | Normal | 74.9366 | -0.27665 | Night | 202601 | 2026-01-10 | 0.27665
2026-01-10 22:59 | 74.3522 | FALSE | FALSE | -0.32096 | -0.43354 | -0.51932 | -0.69361 | 0 |  |  | none | FALSE | 0 | 74.0312 | FALSE | FALSE | 0.0315 |  | 74.4514 | 0 | 0 | 0.02817 | 0.12619 | -0.22323 | 0.21007 | Normal | 74.8715 | -0.47213 | Night | 202601 | 2026-01-10 | 0.47213
2026-01-10 23:14 | 74.3522 | FALSE | FALSE | -0.27065 | -0.36534 | -0.49709 | -0.66412 | 0 |  |  | none | FALSE | 0 | 74.0815 | FALSE | FALSE | 0.0393 |  | 74.4654 | 0 | 0 | 0.01404 | 0.11113 | -0.12634 | 0.19194 | Normal | 74.8493 | -0.58988 | Night | 202601 | 2026-01-10 | 0.58988
2026-01-10 23:28 | 74.0714 | TRUE | FALSE | 0.010148 | 0.013698 | -0.77789 | -1.0393 | -0.2808 | 2026-01-11 07:26 | 2026-01-10 23:28 | lower | TRUE | 1 | 74.0815 | FALSE | FALSE | 0.2226 | 2.0529 | 74.4654 | 1 | -0.2808 | 0 | 0.12925 | -2.1725 | 0.19194 | Extreme triggered | 74.8493 | -2.0529 | Night | 202601 | 2026-01-10 | 2.0529
2026-01-10 23:43 | 74.0714 | FALSE | FALSE | 0.010148 | 0.013698 | -0.77789 | -1.0393 | 0 |  | 2026-01-10 23:28 | lower | TRUE | 1 | 74.0815 | FALSE | FALSE | 0.2797 | 2.0529 | 74.4654 | 2 | 0 | 0 | 0.12925 | 0 | 0.19194 | Extreme/elevated | 74.8493 | -2.0529 | Night | 202601 | 2026-01-10 | 2.0529
2026-01-10 23:58 | 74.0714 | FALSE | FALSE | -0.040155 | -0.054241 | -0.80012 | -1.0687 | 0 |  | 2026-01-10 23:28 | none | FALSE | 1 | 74.0312 | FALSE | FALSE | 0.3206 | 1.9715 | 74.4514 | 3 | 0 | -0.01404 | 0.11113 | 0.12634 | 0.21007 | Persistent | 74.8715 | -1.8088 | Night | 202601 | 2026-01-10 | 1.8088
2026-01-11 00:13 | 74.0714 | FALSE | FALSE | -0.085734 | -0.11588 | -0.81761 | -1.0918 | 0 |  | 2026-01-10 23:28 | none | FALSE | 1 | 73.9857 | FALSE | FALSE | 0.3652 | 1.8837 | 74.4373 | 4 | 0 | -0.01404 | 0.11113 | 0.12634 | 0.22584 | Persistent | 74.889 | -1.6204 | Night | 202601 | 2026-01-11 | 1.6204
2026-01-11 00:28 | 74.0714 | FALSE | FALSE | -0.12752 | -0.17246 | -0.83132 | -1.1099 | 0 |  | 2026-01-10 23:28 | none | FALSE | 1 | 73.9439 | FALSE | FALSE | 0.4122 | 1.8006 | 74.4233 | 5 | 0 | -0.01404 | 0.11113 | 0.12634 | 0.23971 | Persistent | 74.9027 | -1.468 | Night | 202601 | 2026-01-11 | 1.468
2026-01-11 00:43 | 74.0714 | FALSE | FALSE | -0.16615 | -0.22481 | -0.84187 | -1.1238 | 0 |  | 2026-01-10 23:28 | none | FALSE | 1 | 73.9053 | FALSE | FALSE | 0.4608 | 1.7239 | 74.4093 | 6 | 0 | -0.01404 | 0.11113 | 0.12634 | 0.252 | Persistent | 74.9133 | -1.3407 | Night | 202601 | 2026-01-11 | 1.3407
2026-01-11 00:58 | 73.7888 | TRUE | TRUE | 0.015288 | 0.020714 | -1.141 | -1.5228 | -0.2826 |  | 2026-01-10 23:28 | lower | TRUE | 2 | 73.8041 | TRUE | TRUE | 0.5941 | 1.7711 | 74.367 | 7 | -0.2826 | -0.0423 | 0.10331 | -2.326 | 0.28144 | Confirmed/Materialized Shift | 74.9298 | -2.0543 | Night | 202601 | 2026-01-11 | 2.0543
2026-01-11 01:13 | 73.7888 | FALSE | TRUE | -0.067929 | -0.092143 | -1.1396 | -1.521 | 0 |  | 2026-01-10 23:28 | none | FALSE | 2 | 73.7209 | FALSE | FALSE | 0.5755 | 1.7716 | 74.3247 | 8 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.30189 | Confirmed/Materialized Shift | 74.9284 | -1.775 | Night | 202601 | 2026-01-11 | 1.775
2026-01-11 01:28 | 73.7888 | FALSE | TRUE | -0.1367 | -0.1856 | -1.1238 | -1.5002 | 0 |  | 2026-01-10 23:28 | none | FALSE | 2 | 73.6521 | FALSE | FALSE | 0.5616 | 1.7488 | 74.2824 | 9 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.31513 | Confirmed/Materialized Shift | 74.9126 | -1.5662 | Night | 202601 | 2026-01-11 | 1.5662
2026-01-11 01:43 | 73.7888 | FALSE | TRUE | -0.19281 | -0.26199 | -1.0953 | -1.4627 | 0 |  | 2026-01-10 23:28 | none | FALSE | 2 | 73.596 | FALSE | FALSE | 0.5506 | 1.714 | 74.2401 | 10 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.32204 | Confirmed/Materialized Shift | 74.8841 | -1.4013 | Night | 202601 | 2026-01-11 | 1.4013
2026-01-11 01:58 | 73.7888 | FALSE | TRUE | -0.23708 | -0.32232 | -1.055 | -1.4096 | 0 |  | 2026-01-10 23:28 | none | FALSE | 1 | 73.5517 | FALSE | FALSE | 0.513 | 1.6733 | 74.1978 | 11 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.32302 | Confirmed/Materialized Shift | 74.8438 | -1.2661 | Night | 202601 | 2026-01-11 | 1.2661
2026-01-11 02:13 | 73.7888 | FALSE | TRUE | -0.2696 | -0.36671 | -1.0029 | -1.341 | 0 |  | 2026-01-10 23:28 | none | FALSE | 1 | 73.5192 | FALSE | FALSE | 0.5054 | 1.6299 | 74.1555 | 12 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.31813 | Confirmed/Materialized Shift | 74.7917 | -1.1525 | Night | 202601 | 2026-01-11 | 1.1525
2026-01-11 02:27 | 73.7888 | FALSE | TRUE | -0.28983 | -0.39433 | -0.93855 | -1.256 | 0 |  | 2026-01-10 23:28 | none | FALSE | 1 | 73.499 | FALSE | FALSE | 0.499 | 1.5858 | 74.1132 | 13 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.30709 | Confirmed/Materialized Shift | 74.7273 | -1.0562 | Night | 202601 | 2026-01-11 | 1.0562
2026-01-11 02:42 | 73.5062 | FALSE | TRUE | -0.069219 | -0.094256 | -1.1703 | -1.5671 | -0.2826 |  | 2026-01-10 23:28 | none | FALSE | 1 | 73.437 | FALSE | FALSE | 0.547 | 1.5994 | 74.0567 | 14 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.30987 | Confirmed/Materialized Shift | 74.6765 | -1.7766 | Night | 202601 | 2026-01-11 | 1.7766
2026-01-11 02:57 | 73.5062 | FALSE | TRUE | -0.10934 | -0.14897 | -1.0975 | -1.4712 | 0 |  | 2026-01-10 23:28 | none | FALSE | 1 | 73.3969 | FALSE | FALSE | 0.5377 | 1.602 | 74.0003 | 15 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.30172 | Confirmed/Materialized Shift | 74.6037 | -1.6376 | Night | 202601 | 2026-01-11 | 1.6376
2026-01-11 03:12 | 73.5062 | FALSE | TRUE | -0.12569 | -0.17128 | -1.001 | -1.3435 | 0 |  | 2026-01-10 23:28 | none | FALSE | 1 | 73.3805 | FALSE | FALSE | 0.5322 | 1.599 | 73.9439 | 16 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.28168 | Confirmed/Materialized Shift | 74.5072 | -1.5538 | Night | 202601 | 2026-01-11 | 1.5538
2026-01-11 03:27 | 73.5062 | FALSE | TRUE | -0.16593 | -0.22625 | -0.95667 | -1.2848 | 0 |  | 2026-01-10 23:28 | none | FALSE | 0 | 73.3403 | FALSE | FALSE | 0.4939 | 1.5878 | 73.9016 | 17 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.28065 | Confirmed/Materialized Shift | 74.4629 | -1.4088 | Night | 202601 | 2026-01-11 | 1.4088
2026-01-11 03:42 | 73.5062 | FALSE | TRUE | -0.19254 | -0.26262 | -0.89868 | -1.2078 | 0 |  | 2026-01-10 23:28 | none | FALSE | 0 | 73.3137 | FALSE | FALSE | 0.4863 | 1.5715 | 73.8593 | 18 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.2728 | Confirmed/Materialized Shift | 74.4049 | -1.2942 | Night | 202601 | 2026-01-11 | 1.2942
2026-01-11 03:57 | 73.2236 | FALSE | TRUE | 0.015154 | 0.020691 | -1.1433 | -1.5374 | -0.2826 |  | 2026-01-10 23:28 | lower | TRUE | 0 | 73.2388 | FALSE | TRUE | 0.5369 | 1.5968 | 73.8028 | 19 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.28204 | Confirmed/Materialized Shift | 74.3669 | -2.0537 | Night | 202601 | 2026-01-11 | 2.0537
2026-01-11 04:12 | 73.2236 | FALSE | TRUE | -0.035657 | -0.048719 | -1.0813 | -1.4552 | 0 |  | 2026-01-10 23:28 | none | FALSE | 0 | 73.1879 | FALSE | FALSE | 0.5248 | 1.6106 | 73.7464 | 20 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.27923 | Confirmed/Materialized Shift | 74.3049 | -1.8723 | Night | 202601 | 2026-01-11 | 1.8723
2026-01-11 04:27 | 73.2236 | FALSE | TRUE | -0.10236 | -0.13998 | -1.0632 | -1.4312 | 0 |  | 2026-01-10 23:28 | none | FALSE | 0 | 73.1212 | FALSE | FALSE | 0.5099 | 1.6124 | 73.704 | 21 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.29139 | Confirmed/Materialized Shift | 74.2868 | -1.6487 | Night | 202601 | 2026-01-11 | 1.6487
2026-01-11 04:42 | 73.2236 | FALSE | TRUE | -0.15547 | -0.21277 | -1.0315 | -1.3892 | 0 |  | 2026-01-10 23:28 | none | FALSE | 0 | 73.0681 | FALSE | FALSE | 0.4984 | 1.6062 | 73.6616 | 22 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.29675 | Confirmed/Materialized Shift | 74.2551 | -1.4761 | Night | 202601 | 2026-01-11 | 1.4761
2026-01-11 04:57 | 73.2236 | FALSE | TRUE | -0.19573 | -0.26802 | -0.98701 | -1.33 | 0 |  | 2026-01-10 23:28 | none | FALSE | 0 | 73.0279 | FALSE | FALSE | 0.4892 | 1.5946 | 73.6192 | 23 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.29568 | Confirmed/Materialized Shift | 74.2106 | -1.3381 | Night | 202601 | 2026-01-11 | 1.3381
2026-01-11 05:12 | 73.2236 | FALSE | TRUE | -0.223 | -0.30547 | -0.9295 | -1.2535 | 0 |  | 2026-01-10 23:28 | none | FALSE | 0 | 73.0006 | FALSE | FALSE | 0.4817 | 1.5792 | 73.5768 | 24 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.28812 | Confirmed/Materialized Shift | 74.1531 | -1.226 | Night | 202601 | 2026-01-11 | 1.226
2026-01-11 05:26 | 73.2236 | FALSE | TRUE | -0.2362 | -0.32362 | -0.85792 | -1.1581 | 0 |  | 2026-01-10 23:28 | none | FALSE | 0 | 72.9874 | FALSE | FALSE | 0.4758 | 1.5615 | 73.5345 | 25 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27353 | Confirmed/Materialized Shift | 74.0815 | -1.1365 | Night | 202601 | 2026-01-11 | 1.1365
2026-01-11 05:41 | 72.941 | FALSE | TRUE | -0.01012 | -0.013877 | -1.084 | -1.4644 | -0.2826 |  | 2026-01-10 23:28 | none | FALSE | 0 | 72.9309 | FALSE | FALSE | 0.5309 | 1.577 | 73.4779 | 26 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.27353 | Confirmed/Materialized Shift | 74.025 | -1.963 | Night | 202601 | 2026-01-11 | 1.963
2026-01-11 05:56 | 72.941 | FALSE | TRUE | -0.081697 | -0.11213 | -1.0708 | -1.4468 | 0 |  | 2026-01-10 23:28 | none | FALSE | 0 | 72.8593 | FALSE | FALSE | 0.5144 | 1.5821 | 73.4356 | 27 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.28812 | Confirmed/Materialized Shift | 74.0118 | -1.7165 | Night | 202601 | 2026-01-11 | 1.7165
2026-01-11 06:11 | 72.941 | FALSE | TRUE | -0.13921 | -0.19121 | -1.0435 | -1.4105 | 0 |  | 2026-01-10 23:28 | none | FALSE | 0 | 72.8018 | FALSE | FALSE | 0.5019 | 1.5802 | 73.3932 | 28 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.29568 | Confirmed/Materialized Shift | 73.9845 | -1.5292 | Night | 202601 | 2026-01-11 | 1.5292
2026-01-11 06:26 | 72.941 | FALSE | TRUE | -0.18373 | -0.25252 | -1.0033 | -1.3568 | 0 |  | 2026-01-10 23:28 | none | FALSE | 0 | 72.7573 | FALSE | FALSE | 0.4921 | 1.5734 | 73.3508 | 29 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.29675 | Confirmed/Materialized Shift | 73.9443 | -1.3809 | Night | 202601 | 2026-01-11 | 1.3809
2026-01-11 06:41 | 72.941 | FALSE | TRUE | -0.2154 | -0.29618 | -0.95016 | -1.2859 | 0 |  | 2026-01-10 23:28 | none | FALSE | 0 | 72.7256 | FALSE | FALSE | 0.4841 | 1.5629 | 73.3084 | 30 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.29139 | Confirmed/Materialized Shift | 73.8912 | -1.2608 | Night | 202601 | 2026-01-11 | 1.2608
2026-01-11 06:56 | 72.941 | FALSE | TRUE | -0.23348 | -0.32112 | -0.88346 | -1.1967 | 0 |  | 2026-01-10 23:28 | none | FALSE | 0 | 72.7075 | FALSE | FALSE | 0.4776 | 1.5501 | 73.266 | 31 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27923 | Confirmed/Materialized Shift | 73.8245 | -1.1639 | Night | 202601 | 2026-01-11 | 1.1639
2026-01-11 07:11 | 72.6584 | FALSE | TRUE | -0.013386 | -0.018426 | -1.1155 | -1.5121 | -0.2826 |  | 2026-01-10 23:28 | none | FALSE | 0 | 72.645 | FALSE | FALSE | 0.5302 | 1.5626 | 73.2095 | 32 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.28223 | Confirmed/Materialized Shift | 73.7739 | -1.9526 | Night | 202601 | 2026-01-11 | 1.9526
2026-01-11 07:26 | 72.941 | TRUE | FALSE | -0.27945 | -0.38459 | -0.73161 | -0.99306 | 0.2826 |  |  | none | FALSE | 1 | 72.6615 | FALSE | FALSE | 0.0882 |  | 73.1671 | 0 | 0.2826 | -0.04239 | 0.13829 | 2.35 | 0.25277 | Persistence ends | 73.6726 | -0.89443 | Day | 202601 | 2026-01-11 | 0.89443
2026-01-11 07:41 | 72.6584 | FALSE | FALSE | -0.061212 | -0.084318 | -0.99379 | -1.3493 | -0.2826 |  |  | none | FALSE | 1 | 72.5972 | FALSE | FALSE | 0.1464 |  | 73.1247 | 0 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.26375 | Normal | 73.6522 | -1.7679 | Day | 202601 | 2026-01-11 | 1.7679
2026-01-11 07:56 | 72.6584 | FALSE | FALSE | -0.11073 | -0.15262 | -0.95853 | -1.302 | 0 |  |  | none | FALSE | 1 | 72.5477 | FALSE | FALSE | 0.1343 |  | 73.0823 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.26731 | Normal | 73.6169 | -1.5858 | Day | 202601 | 2026-01-11 | 1.5858
2026-01-11 08:11 | 72.941 | FALSE | FALSE | -0.38579 | -0.53173 | -0.61187 | -0.83188 | 0.2826 |  |  | none | FALSE | 1 | 72.5552 | FALSE | FALSE | 0.0588 |  | 73.054 | 0 | 0.2826 | -0.02826 | 0.15614 | 1.9909 | 0.24942 | Normal | 73.5529 | -0.45322 | Day | 202601 | 2026-01-11 | 0.45322
2026-01-11 08:25 | 72.941 | FALSE | FALSE | -0.36812 | -0.50725 | -0.53768 | -0.73175 | 0 |  |  | none | FALSE | 1 | 72.5729 | FALSE | FALSE | 0.0535 |  | 73.0258 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.22645 | Normal | 73.4787 | -0.37438 | Day | 202601 | 2026-01-11 | 0.37438
2026-01-11 08:40 | 72.941 | FALSE | FALSE | -0.33678 | -0.46385 | -0.44982 | -0.6129 | 0 |  |  | none | FALSE | 1 | 72.6042 | FALSE | FALSE | 0.0477 |  | 72.9975 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.19665 | Normal | 73.3908 | -0.28742 | Day | 202601 | 2026-01-11 | 0.28742
2026-01-11 08:41 | 72.941 | FALSE | FALSE | -0.33676 | -0.46383 | -0.42154 | -0.5746 | 0 |  |  | none | FALSE | 1 | 72.6042 | FALSE | FALSE | 0.0435 |  | 72.9834 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.18957 | Normal | 73.3625 | -0.22361 | Day | 202601 | 2026-01-11 | 0.22361
2026-01-11 08:56 | 73.2236 | FALSE | FALSE | -0.61936 | -0.85306 | -0.13894 | -0.18939 | 0.2826 |  |  | none | FALSE | 1 | 72.6042 | FALSE | FALSE | 0.113 |  | 72.9834 | 0 | 0.2826 | 0 | 0.15881 | 1.7795 | 0.18957 | Normal | 73.3625 | 1.2671 | Day | 202601 | 2026-01-11 | 1.2671
2026-01-11 09:11 | 73.2236 | FALSE | FALSE | -0.61936 | -0.85306 | -0.13894 | -0.18939 | 0 |  |  | none | FALSE | 1 | 72.6042 | FALSE | FALSE | 0.113 |  | 72.9834 | 0 | 0 | 0 | 0.15881 | 0 | 0.18957 | Normal | 73.3625 | 1.2671 | Day | 202601 | 2026-01-11 | 1.2671
2026-01-11 09:26 | 73.5062 | FALSE | FALSE | -0.94262 | -1.299 | 0.074735 | 0.10178 | 0.2826 | 2026-01-11 09:59 | 2026-01-11 09:26 | upper | TRUE | 1 | 72.5636 | FALSE | FALSE | 0.242 | 2.3444 | 72.9975 | 1 | 0.2826 | 0.01413 | 0.17092 | 1.5708 | 0.21697 | Extreme triggered | 73.4315 | 2.3444 | Day | 202601 | 2026-01-11 | 2.3444
2026-01-11 09:40 | 73.7888 | FALSE | FALSE | -1.3162 | -1.8161 | 0.20985 | 0.2852 | 0.2826 |  | 2026-01-11 09:26 | upper | TRUE | 0 | 72.4726 | FALSE | FALSE | 0.2982 | 2.5516 | 73.0258 | 2 | 0.2826 | 0.02826 | 0.18107 | 1.4047 | 0.27659 | Extreme/elevated | 73.579 | 2.7587 | Day | 202601 | 2026-01-11 | 2.7587
2026-01-11 09:40 | 73.7888 | FALSE | FALSE | -1.3805 | -1.9065 | 0.08903 | 0.1208 | 0 |  | 2026-01-11 09:26 | upper | TRUE | 0 | 72.4083 | FALSE | TRUE | 0.3231 | 2.4596 | 73.054 | 3 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.32287 | Persistent | 73.6998 | 2.2757 | Day | 202601 | 2026-01-11 | 2.2757
2026-01-11 09:41 | 74.0714 | FALSE | FALSE | -1.7632 | -2.4384 | 0.18678 | 0.2528 | 0.2826 |  | 2026-01-11 09:26 | upper | TRUE | 0 | 72.3082 | FALSE | TRUE | 0.3935 | 2.4632 | 73.0964 | 4 | 0.2826 | 0.04239 | 0.18957 | 1.2671 | 0.3941 | Persistent | 73.8846 | 2.4739 | Day | 202601 | 2026-01-11 | 2.4739
2026-01-11 09:44 | 74.0714 | FALSE | FALSE | -1.8145 | -2.5111 | 0.022442 | 0.030307 | 0 |  | 2026-01-11 09:26 | upper | TRUE | 0 | 72.2569 | FALSE | TRUE | 0.4224 | 2.3806 | 73.153 | 5 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.448 | Persistent | 74.049 | 2.0501 | Day | 202601 | 2026-01-11 | 2.0501
2026-01-11 09:59 | 73.2236 | TRUE | FALSE | -0.94735 | -1.3107 | -0.83431 | -1.1266 | -0.8478 |  |  | none | FALSE | 1 | 72.2762 | FALSE | FALSE | 0.037 |  | 73.1671 | 0 | -0.8478 | 0.01413 | 0.26692 | -3.2292 | 0.44542 | Persistence ends | 74.0579 | 0.12689 | Day | 202601 | 2026-01-11 | 0.12689
2026-01-11 10:14 | 72.941 | FALSE | FALSE | -0.66475 | -0.91974 | -1.1169 | -1.5082 | -0.2826 |  |  | none | FALSE | 1 | 72.2762 | FALSE | FALSE | 0.0624 |  | 73.1671 | 0 | -0.2826 | 0 | 0.27506 | -1.0274 | 0.44542 | Normal | 74.0579 | -0.50757 | Day | 202601 | 2026-01-11 | 0.50757
2026-01-11 10:29 | 72.3758 | FALSE | FALSE | -0.19159 | -0.26542 | -1.7176 | -2.3182 | -0.5652 |  |  | none | FALSE | 1 | 72.1842 | FALSE | FALSE | 0.1351 |  | 73.1388 | 0 | -0.5652 | -0.02826 | 0.30271 | -1.7738 | 0.4773 | Normal | 74.0934 | -1.5986 | Day | 202601 | 2026-01-11 | 1.5986
2026-01-11 10:40 | 72.6584 | FALSE | FALSE | -0.50879 | -0.70519 | -1.4414 | -1.9452 | 0.2826 |  |  | none | FALSE | 1 | 72.1496 | FALSE | FALSE | 0.0923 |  | 73.1247 | 0 | 0.2826 | -0.01413 | 0.31059 | 0.95538 | 0.48754 | Normal | 74.0998 | -0.95641 | Day | 202601 | 2026-01-11 | 0.95641
2026-01-11 10:55 | 72.6584 | FALSE | FALSE | -0.54213 | -0.75175 | -1.4465 | -1.9519 | 0 |  |  | none | FALSE | 1 | 72.1163 | FALSE | FALSE | 0.0892 |  | 73.1106 | 0 | 0 | -0.01413 | 0.31059 | 0.045494 | 0.49715 | Normal | 74.1049 | -0.90951 | Day | 202601 | 2026-01-11 | 0.90951
2026-01-11 11:10 | 72.6584 | FALSE | FALSE | -0.54213 | -0.75175 | -1.4465 | -1.9519 | 0 |  |  | none | FALSE | 1 | 72.1163 | FALSE | FALSE | 0.0892 |  | 73.1106 | 0 | 0 | 0 | 0.30409 | 0 | 0.49715 | Normal | 74.1049 | -0.90951 | Day | 202601 | 2026-01-11 | 0.90951
2026-01-11 11:25 | 72.6584 | FALSE | FALSE | -0.57428 | -0.79668 | -1.4503 | -1.957 | 0 |  |  | none | FALSE | 1 | 72.0841 | FALSE | FALSE | 0.0863 |  | 73.0964 | 0 | 0 | -0.01413 | 0.29675 | 0.047616 | 0.50615 | Normal | 74.1087 | -0.86541 | Day | 202601 | 2026-01-11 | 0.86541
2026-01-11 11:39 | 72.941 | FALSE | FALSE | -0.82473 | -1.1436 | -1.1639 | -1.5705 | 0.2826 |  |  | none | FALSE | 1 | 72.1163 | FALSE | FALSE | 0.0513 |  | 73.1106 | 0 | 0.2826 | 0.01413 | 0.29675 | 0.90471 | 0.49715 | Normal | 74.1049 | -0.34107 | Day | 202601 | 2026-01-11 | 0.34107
2026-01-11 11:55 | 72.6584 | FALSE | FALSE | -0.54213 | -0.75175 | -1.4465 | -1.9519 | -0.2826 |  |  | none | FALSE | 1 | 72.1163 | FALSE | FALSE | 0.0892 |  | 73.1106 | 0 | -0.2826 | 0 | 0.30409 | -0.92932 | 0.49715 | Normal | 74.1049 | -0.90951 | Day | 202601 | 2026-01-11 | 0.90951
2026-01-11 12:10 | 72.6584 | FALSE | FALSE | -0.57428 | -0.79668 | -1.4503 | -1.957 | 0 |  |  | none | FALSE | 1 | 72.0841 | FALSE | FALSE | 0.0863 |  | 73.0964 | 0 | 0 | -0.01413 | 0.29675 | 0.047616 | 0.50615 | Normal | 74.1087 | -0.86541 | Day | 202601 | 2026-01-11 | 0.86541
2026-01-11 12:25 | 72.941 | FALSE | FALSE | -0.85688 | -1.1887 | -1.1677 | -1.5757 | 0.2826 |  |  | none | FALSE | 0 | 72.0841 | FALSE | FALSE | 0.0205 |  | 73.0964 | 0 | 0.2826 | 0 | 0.30409 | 0.92932 | 0.50615 | Normal | 74.1087 | -0.30708 | Day | 202601 | 2026-01-11 | 0.30708
2026-01-11 12:39 | 72.941 | FALSE | FALSE | -0.85688 | -1.1887 | -1.1677 | -1.5757 | 0 |  |  | none | FALSE | 0 | 72.0841 | FALSE | FALSE | 0.0205 |  | 73.0964 | 0 | 0 | 0 | 0.30409 | 0 | 0.50615 | Normal | 74.1087 | -0.30708 | Day | 202601 | 2026-01-11 | 0.30708
2026-01-11 12:54 | 72.941 | FALSE | FALSE | -0.85688 | -1.1887 | -1.1677 | -1.5757 | 0 |  |  | none | FALSE | 0 | 72.0841 | FALSE | FALSE | 0.0205 |  | 73.0964 | 0 | 0 | 0 | 0.30409 | 0 | 0.50615 | Normal | 74.1087 | -0.30708 | Day | 202601 | 2026-01-11 | 0.30708
2026-01-11 13:09 | 73.2236 | FALSE | FALSE | -1.1395 | -1.5808 | -0.88514 | -1.1944 | 0.2826 |  |  | none | FALSE | 0 | 72.0841 | FALSE | FALSE | 0.0167 |  | 73.0964 | 0 | 0.2826 | 0 | 0.30409 | 0.92932 | 0.50615 | Normal | 74.1087 | 0.25125 | Day | 202601 | 2026-01-11 | 0.25125
2026-01-11 13:24 | 73.2236 | FALSE | FALSE | -1.1395 | -1.5808 | -0.88514 | -1.1944 | 0 |  |  | none | FALSE | 0 | 72.0841 | FALSE | FALSE | 0.0167 |  | 73.0964 | 0 | 0 | 0 | 0.30409 | 0 | 0.50615 | Normal | 74.1087 | 0.25125 | Day | 202601 | 2026-01-11 | 0.25125
2026-01-11 13:39 | 73.5062 | FALSE | FALSE | -1.4221 | -1.9728 | -0.60254 | -0.81304 | 0.2826 |  |  | none | FALSE | 0 | 72.0841 | FALSE | FALSE | 0.054 |  | 73.0964 | 0 | 0.2826 | 0 | 0.30409 | 0.92932 | 0.50615 | Normal | 74.1087 | 0.80958 | Day | 202601 | 2026-01-11 | 0.80958
2026-01-11 13:54 | 73.5062 | FALSE | FALSE | -1.4029 | -1.9456 | -0.55506 | -0.74945 | 0 |  |  | none | FALSE | 0 | 72.1033 | FALSE | FALSE | 0.0577 |  | 73.0823 | 0 | 0 | -0.01413 | 0.29675 | 0.047616 | 0.48948 | Normal | 74.0613 | 0.86603 | Day | 202601 | 2026-01-11 | 0.86603
2026-01-11 14:09 | 73.5062 | FALSE | FALSE | -1.3816 | -1.9155 | -0.50551 | -0.68301 | 0 |  |  | none | FALSE | 0 | 72.1246 | FALSE | FALSE | 0.0619 |  | 73.0682 | 0 | 0 | -0.01413 | 0.29675 | 0.047616 | 0.47177 | Normal | 74.0117 | 0.92849 | Day | 202601 | 2026-01-11 | 0.92849
2026-01-11 14:24 | 73.5062 | FALSE | FALSE | -1.3121 | -1.8175 | -0.37952 | -0.51366 | 0 |  |  | none | FALSE | 0 | 72.1941 | FALSE | FALSE | 0.0735 |  | 73.0399 | 0 | 0 | -0.02826 | 0.28849 | 0.097959 | 0.42291 | Normal | 73.8857 | 1.1026 | Day | 202601 | 2026-01-11 | 1.1026
2026-01-11 14:39 | 73.5062 | FALSE | FALSE | -1.2252 | -1.695 | -0.23608 | -0.32014 | 0 |  |  | none | FALSE | 0 | 72.281 | FALSE | FALSE | 0.0903 |  | 73.0117 | 0 | 0 | -0.02826 | 0.28849 | 0.097959 | 0.36531 | Normal | 73.7423 | 1.3538 | Day | 202601 | 2026-01-11 | 1.3538
2026-01-11 14:54 | 73.5062 | FALSE | FALSE | -1.2387 | -1.7141 | -0.27788 | -0.37661 | 0 |  |  | none | FALSE | 0 | 72.2675 | FALSE | FALSE | 0.0845 |  | 73.0258 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.37915 | Normal | 73.7841 | 1.2671 | Day | 202601 | 2026-01-11 | 1.2671
2026-01-11 15:09 | 73.5062 | FALSE | FALSE | -1.2388 | -1.7141 | -0.33443 | -0.45291 | 0 |  |  | none | FALSE | 0 | 72.2674 | FALSE | FALSE | 0.0766 |  | 73.054 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.3933 | Normal | 73.8406 | 1.1497 | Day | 202601 | 2026-01-11 | 1.1497
2026-01-11 15:24 | 73.7888 | FALSE | FALSE | -1.448 | -2.0017 | -0.11981 | -0.1621 | 0.2826 |  |  | none | FALSE | 0 | 72.3408 | FALSE | FALSE | 0.113 |  | 73.1247 | 0 | 0.2826 | 0.07065 | 0.15546 | 1.3633 | 0.39196 | Normal | 73.9086 | 1.6943 | Day | 202601 | 2026-01-11 | 1.6943
2026-01-11 15:38 | 73.5062 | FALSE | FALSE | -1.1084 | -1.531 | -0.43018 | -0.58183 | -0.2826 |  |  | none | FALSE | 0 | 72.3978 | FALSE | FALSE | 0.0588 |  | 73.1671 | 0 | -0.2826 | 0.04239 | 0.16593 | -1.9586 | 0.38465 | Normal | 73.9364 | 0.88163 | Day | 202601 | 2026-01-11 | 0.88163
2026-01-11 15:53 | 73.5062 | FALSE | FALSE | -1.041 | -1.4366 | -0.44758 | -0.60521 | 0 |  |  | none | FALSE | 0 | 72.4652 | FALSE | FALSE | 0.0532 |  | 73.2095 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.37215 | Normal | 73.9538 | 0.79733 | Day | 202601 | 2026-01-11 | 0.79733
2026-01-11 16:08 | 73.5062 | FALSE | FALSE | -0.96218 | -1.3263 | -0.4535 | -0.61317 | 0 |  |  | none | FALSE | 0 | 72.544 | FALSE | FALSE | 0.0479 |  | 73.2519 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.35392 | Normal | 73.9597 | 0.71864 | Day | 202601 | 2026-01-11 | 0.71864
2026-01-11 16:23 | 73.2236 | FALSE | FALSE | -0.5944 | -0.8184 | -0.70744 | -0.95689 | -0.2826 |  |  | none | FALSE | 0 | 72.6292 | FALSE | FALSE | 0.0116 |  | 73.2801 | 0 | -0.2826 | 0.02826 | 0.18107 | -1.7168 | 0.32546 | Normal | 73.931 | -0.17366 | Day | 202601 | 2026-01-11 | 0.17366
2026-01-11 16:38 | 73.2236 | FALSE | FALSE | -0.56126 | -0.77243 | -0.70256 | -0.95036 | 0 |  |  | none | FALSE | 0 | 72.6623 | FALSE | FALSE | 0.0149 |  | 73.2943 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.31596 | Normal | 73.9262 | -0.22361 | Day | 202601 | 2026-01-11 | 0.22361
2026-01-11 16:53 | 73.2236 | FALSE | FALSE | -0.45956 | -0.63157 | -0.65738 | -0.88978 | 0 |  |  | none | FALSE | 0 | 72.764 | FALSE | FALSE | 0.0236 |  | 73.3225 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.27923 | Normal | 73.881 | -0.35422 | Day | 202601 | 2026-01-11 | 0.35422
2026-01-11 17:08 | 73.2236 | FALSE | FALSE | -0.33945 | -0.46573 | -0.59379 | -0.8044 | 0 |  |  | none | FALSE | 0 | 72.8842 | FALSE | FALSE | 0.0363 |  | 73.3508 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.23331 | Normal | 73.8174 | -0.54507 | Day | 202601 | 2026-01-11 | 0.54507
2026-01-11 17:23 | 72.941 | FALSE | FALSE | -0.056847 | -0.077996 | -0.87639 | -1.1872 | -0.2826 |  |  | none | FALSE | 0 | 72.8842 | FALSE | FALSE | 0.1171 |  | 73.3508 | 0 | -0.2826 | 0 | 0.15881 | -1.7795 | 0.23331 | Normal | 73.8174 | -1.7563 | Day | 202601 | 2026-01-11 | 1.7563
2026-01-11 17:30 | 72.941 | FALSE | FALSE | -0.056847 | -0.077996 | -0.87639 | -1.1872 | 0 |  |  | none | FALSE | 0 | 72.8842 | FALSE | FALSE | 0.1171 |  | 73.3508 | 0 | 0 | 0 | 0.15881 | 0 | 0.23331 | Normal | 73.8174 | -1.7563 | Day | 202601 | 2026-01-11 | 1.7563
2026-01-11 17:31 | 72.941 | FALSE | FALSE | -0.056847 | -0.077996 | -0.87639 | -1.1872 | 0 |  |  | none | FALSE | 0 | 72.8842 | FALSE | FALSE | 0.1171 |  | 73.3508 | 0 | 0 | 0 | 0.15881 | 0 | 0.23331 | Normal | 73.8174 | -1.7563 | Day | 202601 | 2026-01-11 | 1.7563
2026-01-11 17:46 | 73.2236 | FALSE | FALSE | -0.33945 | -0.46573 | -0.59379 | -0.8044 | 0.2826 |  |  | none | FALSE | 0 | 72.8842 | FALSE | FALSE | 0.0363 |  | 73.3508 | 0 | 0.2826 | 0 | 0.15881 | 1.7795 | 0.23331 | Normal | 73.8174 | -0.54507 | Day | 202601 | 2026-01-11 | 0.54507
2026-01-11 18:01 | 73.7888 | TRUE | FALSE | -0.91113 | -1.2502 | -0.091586 | -0.12396 | 0.5652 |  |  | none | FALSE | 1 | 72.8777 | FALSE | FALSE | 0.1375 |  | 73.379 | 0 | 0.5652 | 0.02826 | 0.20296 | 2.6456 | 0.25068 | Normal | 73.8804 | 1.6346 | Night | 202601 | 2026-01-11 | 1.6346
2026-01-11 18:16 | 74.0714 | FALSE | FALSE | -1.2519 | -1.7192 | 0.076308 | 0.10313 | 0.2826 | 2026-01-11 21:44 | 2026-01-11 18:16 | upper | TRUE | 1 | 72.8195 | FALSE | FALSE | 0.2364 | 2.2596 | 73.4073 | 1 | 0.2826 | 0.02826 | 0.20296 | 1.2532 | 0.2939 | Extreme triggered | 73.9951 | 2.2596 | Night | 202601 | 2026-01-11 | 2.2596
2026-01-11 18:30 | 74.3522 | FALSE | FALSE | -1.6264 | -2.2364 | 0.17881 | 0.24107 | 0.2808 |  | 2026-01-11 18:16 | upper | TRUE | 1 | 72.7258 | FALSE | FALSE | 0.3091 | 2.3769 | 73.4496 | 2 | 0.2808 | 0.0423 | 0.21047 | 1.1332 | 0.3619 | Extreme/elevated | 74.1734 | 2.4941 | Night | 202601 | 2026-01-11 | 2.4941
2026-01-11 18:45 | 74.6348 | FALSE | FALSE | -2.0263 | -2.7907 | 0.23126 | 0.31082 | 0.2826 |  | 2026-01-11 18:16 | upper | TRUE | 1 | 72.6085 | FALSE | TRUE | 0.3677 | 2.423 | 73.506 | 3 | 0.2826 | 0.05643 | 0.21687 | 1.0429 | 0.44876 | Persistent | 74.4035 | 2.5153 | Night | 202601 | 2026-01-11 | 2.5153
2026-01-11 19:00 | 74.6348 | FALSE | FALSE | -2.1021 | -2.8981 | 0.042608 | 0.057121 | 0 |  | 2026-01-11 18:16 | upper | TRUE | 1 | 72.5327 | FALSE | TRUE | 0.396 | 2.338 | 73.5624 | 4 | 0 | 0.05643 | 0.21687 | -0.2602 | 0.51487 | Persistent | 74.5922 | 2.0828 | Night | 202601 | 2026-01-11 | 2.0828
2026-01-11 19:15 | 74.6348 | FALSE | FALSE | -2.151 | -2.9675 | -0.11915 | -0.15939 | 0 |  | 2026-01-11 18:16 | none | FALSE | 1 | 72.4838 | FALSE | FALSE | 0.4336 | 2.2284 | 73.6189 | 5 | 0 | 0.05643 | 0.21687 | -0.2602 | 0.56754 | Persistent | 74.754 | 1.7901 | Night | 202601 | 2026-01-11 | 1.7901
2026-01-11 19:29 | 74.6348 | FALSE | FALSE | -2.18 | -3.0087 | -0.261 | -0.34848 | 0 |  | 2026-01-11 18:16 | none | FALSE | 1 | 72.4548 | FALSE | FALSE | 0.4762 | 2.119 | 73.6753 | 6 | 0 | 0.05643 | 0.21687 | -0.2602 | 0.61024 | Persistent | 74.8958 | 1.5723 | Night | 202601 | 2026-01-11 | 1.5723
2026-01-11 19:44 | 74.9174 | FALSE | TRUE | -2.5085 | -3.4643 | -0.16541 | -0.2203 | 0.2826 |  | 2026-01-11 18:16 | none | FALSE | 1 | 72.4089 | FALSE | FALSE | 0.5454 | 2.0667 | 73.7459 | 7 | 0.2826 | 0.07056 | 0.22215 | 0.95451 | 0.66847 | Confirmed/Materialized Shift | 75.0828 | 1.7526 | Night | 202601 | 2026-01-11 | 1.7526
2026-01-11 19:59 | 74.9174 | FALSE | TRUE | -2.5513 | -3.5255 | -0.32106 | -0.42672 | 0 |  | 2026-01-11 18:16 | none | FALSE | 1 | 72.3661 | FALSE | FALSE | 0.5321 | 2.0025 | 73.8023 | 8 | 0 | 0.05643 | 0.21687 | -0.2602 | 0.71808 | Confirmed/Materialized Shift | 75.2385 | 1.5529 | Night | 202601 | 2026-01-11 | 1.5529
2026-01-11 20:15 | 74.9174 | FALSE | TRUE | -2.5561 | -3.5325 | -0.46705 | -0.61956 | 0 |  | 2026-01-11 18:16 | none | FALSE | 1 | 72.3613 | FALSE | FALSE | 0.5207 | 1.9335 | 73.8729 | 9 | 0 | 0.07056 | 0.20234 | -0.34872 | 0.7558 | Confirmed/Materialized Shift | 75.3845 | 1.382 | Night | 202601 | 2026-01-11 | 1.382
2026-01-11 20:29 | 74.9174 | FALSE | TRUE | -2.5441 | -3.5153 | -0.59616 | -0.78947 | 0 |  | 2026-01-11 18:16 | none | FALSE | 0 | 72.3733 | FALSE | FALSE | 0.4827 | 1.8642 | 73.9434 | 10 | 0 | 0.07056 | 0.20234 | -0.34872 | 0.78507 | Confirmed/Materialized Shift | 75.5136 | 1.2406 | Night | 202601 | 2026-01-11 | 1.2406
2026-01-11 20:44 | 74.9174 | FALSE | TRUE | -2.5171 | -3.4766 | -0.71022 | -0.93911 | 0 |  | 2026-01-11 18:16 | none | FALSE | 0 | 72.4003 | FALSE | FALSE | 0.4746 | 1.7965 | 74.014 | 11 | 0 | 0.07056 | 0.20234 | -0.34872 | 0.80682 | Confirmed/Materialized Shift | 75.6276 | 1.1197 | Night | 202601 | 2026-01-11 | 1.1197
2026-01-11 20:59 | 75.2 | FALSE | TRUE | -2.7387 | -3.7795 | -0.56427 | -0.74477 | 0.2826 |  | 2026-01-11 18:16 | none | FALSE | 0 | 72.4613 | FALSE | FALSE | 0.4878 | 1.7566 | 74.1128 | 12 | 0.2826 | 0.09882 | 0.18948 | 0.96991 | 0.82573 | Confirmed/Materialized Shift | 75.7643 | 1.3166 | Night | 202601 | 2026-01-11 | 1.3166
2026-01-11 21:14 | 75.2 | FALSE | TRUE | -2.6523 | -3.6559 | -0.67554 | -0.89032 | 0 |  | 2026-01-11 18:16 | none | FALSE | 0 | 72.5477 | FALSE | FALSE | 0.4792 | 1.7128 | 74.2116 | 13 | 0 | 0.09882 | 0.18948 | -0.52153 | 0.83196 | Confirmed/Materialized Shift | 75.8755 | 1.188 | Night | 202601 | 2026-01-11 | 1.188
2026-01-11 21:29 | 75.2 | FALSE | TRUE | -2.5411 | -3.4973 | -0.762 | -1.0031 | 0 |  | 2026-01-11 18:16 | none | FALSE | 0 | 72.6589 | FALSE | FALSE | 0.4718 | 1.6674 | 74.3104 | 14 | 0 | 0.09882 | 0.18948 | -0.52153 | 0.82578 | Confirmed/Materialized Shift | 75.962 | 1.0772 | Night | 202601 | 2026-01-11 | 1.0772
2026-01-11 21:44 | 75.2 | FALSE | FALSE | -2.4046 | -3.3032 | -0.82309 | -1.0827 | 0 |  |  | none | FALSE | 0 | 72.7954 | FALSE | FALSE | 0.0653 |  | 74.4093 | 0 | 0 | 0.09882 | 0.18948 | -0.52153 | 0.80691 | Persistence ends | 76.0231 | 0.97996 | Night | 202601 | 2026-01-11 | 0.97996
2026-01-11 21:59 | 75.2 | FALSE | FALSE | -2.1706 | -2.9722 | -0.81503 | -1.0722 | 0 |  |  | none | FALSE | 0 | 73.0294 | FALSE | FALSE | 0.0605 |  | 74.5222 | 0 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.74641 | Normal | 76.015 | 0.90807 | Night | 202601 | 2026-01-11 | 0.90807
2026-01-11 22:14 | 75.2 | FALSE | FALSE | -1.8859 | -2.5723 | -0.7562 | -0.99558 | 0 |  |  | none | FALSE | 0 | 73.3141 | FALSE | FALSE | 0.057 |  | 74.6352 | 0 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.66052 | Normal | 75.9562 | 0.85514 | Night | 202601 | 2026-01-11 | 0.85514
2026-01-11 22:28 | 75.2 | FALSE | FALSE | -1.5263 | -2.0717 | -0.62252 | -0.82102 | 0 |  |  | none | FALSE | 0 | 73.6737 | FALSE | FALSE | 0.0561 |  | 74.7481 | 0 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.5372 | Normal | 75.8225 | 0.84119 | Night | 202601 | 2026-01-11 | 0.84119
2026-01-11 22:43 | 75.2 | FALSE | FALSE | -1.1697 | -1.5801 | -0.46359 | -0.6127 | 0 |  |  | none | FALSE | 0 | 74.0303 | FALSE | FALSE | 0.0576 |  | 74.8469 | 0 | 0 | 0.09882 | 0.16582 | -0.59594 | 0.40833 | Normal | 75.6636 | 0.86467 | Night | 202601 | 2026-01-11 | 0.86467
2026-01-11 22:59 | 75.2 | FALSE | FALSE | -0.94319 | -1.2702 | -0.37817 | -0.50037 | 0 |  |  | none | FALSE | 0 | 74.2568 | FALSE | FALSE | 0.057 |  | 74.9175 | 0 | 0 | 0.07056 | 0.12539 | -0.56273 | 0.33034 | Normal | 75.5782 | 0.85521 | Night | 202601 | 2026-01-11 | 0.85521
2026-01-11 23:14 | 75.2 | FALSE | FALSE | -0.76384 | -1.0262 | -0.31168 | -0.41276 | 0 |  |  | none | FALSE | 0 | 74.4362 | FALSE | FALSE | 0.0561 |  | 74.9739 | 0 | 0 | 0.05643 | 0.11579 | -0.48734 | 0.26888 | Normal | 75.5117 | 0.84082 | Night | 202601 | 2026-01-11 | 0.84082
2026-01-11 23:28 | 74.9174 | TRUE | FALSE | -0.36812 | -0.4938 | -0.53768 | -0.71259 | -0.2826 |  |  | none | FALSE | 1 | 74.5493 | FALSE | FALSE | 0.0535 |  | 75.0022 | 0 | -0.2826 | 0.02826 | 0.12638 | -2.4597 | 0.22645 | Normal | 75.4551 | -0.37438 | Night | 202601 | 2026-01-11 | 0.37438
2026-01-11 23:43 | 74.9174 | FALSE | FALSE | -0.32225 | -0.432 | -0.52007 | -0.68941 | 0 |  |  | none | FALSE | 1 | 74.5951 | FALSE | FALSE | 0.0599 |  | 75.0163 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.21058 | Normal | 75.4375 | -0.4697 | Night | 202601 | 2026-01-11 | 0.4697
2026-01-11 23:58 | 74.9174 | FALSE | FALSE | -0.27161 | -0.36387 | -0.49769 | -0.65994 | 0 |  |  | none | FALSE | 1 | 74.6458 | FALSE | FALSE | 0.0678 |  | 75.0304 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.19233 | Normal | 75.4151 | -0.58775 | Night | 202601 | 2026-01-11 | 0.58775
2026-01-12 00:13 | 74.9174 | FALSE | FALSE | -0.21467 | -0.28736 | -0.46901 | -0.62214 | 0 |  |  | none | FALSE | 1 | 74.7027 | FALSE | FALSE | 0.0782 |  | 75.0446 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.17092 | Normal | 75.3864 | -0.74404 | Night | 202601 | 2026-01-12 | 0.74404
2026-01-12 00:28 | 74.9174 | FALSE | FALSE | -0.14864 | -0.1988 | -0.43124 | -0.57233 | 0 |  |  | none | FALSE | 1 | 74.7688 | FALSE | FALSE | 0.0936 |  | 75.0587 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.14497 | Normal | 75.3486 | -0.97468 | Night | 202601 | 2026-01-12 | 0.97468
2026-01-12 00:43 | 74.9174 | FALSE | FALSE | -0.14864 | -0.1988 | -0.43124 | -0.57233 | 0 |  |  | none | FALSE | 1 | 74.7688 | FALSE | FALSE | 0.0936 |  | 75.0587 | 0 | 0 | 0 | 0.091688 | 0 | 0.14497 | Normal | 75.3486 | -0.97468 | Night | 202601 | 2026-01-12 | 0.97468
2026-01-12 00:58 | 74.9174 | FALSE | FALSE | -0.14864 | -0.1988 | -0.43124 | -0.57233 | 0 |  |  | none | FALSE | 1 | 74.7688 | FALSE | FALSE | 0.0936 |  | 75.0587 | 0 | 0 | 0 | 0.091688 | 0 | 0.14497 | Normal | 75.3486 | -0.97468 | Night | 202601 | 2026-01-12 | 0.97468
2026-01-12 01:13 | 74.9174 | FALSE | FALSE | -0.14864 | -0.1988 | -0.43124 | -0.57233 | 0 |  |  | none | FALSE | 1 | 74.7688 | FALSE | FALSE | 0.0936 |  | 75.0587 | 0 | 0 | 0 | 0.091688 | 0 | 0.14497 | Normal | 75.3486 | -0.97468 | Night | 202601 | 2026-01-12 | 0.97468
2026-01-12 01:27 | 74.9174 | FALSE | FALSE | -0.14864 | -0.1988 | -0.43124 | -0.57233 | 0 |  |  | none | FALSE | 1 | 74.7688 | FALSE | FALSE | 0.0936 |  | 75.0587 | 0 | 0 | 0 | 0.091688 | 0 | 0.14497 | Normal | 75.3486 | -0.97468 | Night | 202601 | 2026-01-12 | 0.97468
2026-01-12 01:43 | 74.9174 | FALSE | FALSE | -0.14864 | -0.1988 | -0.43124 | -0.57233 | 0 |  |  | none | FALSE | 1 | 74.7688 | FALSE | FALSE | 0.0936 |  | 75.0587 | 0 | 0 | 0 | 0.091688 | 0 | 0.14497 | Normal | 75.3486 | -0.97468 | Night | 202601 | 2026-01-12 | 0.97468
2026-01-12 01:58 | 74.9174 | FALSE | FALSE | -0.16132 | -0.21579 | -0.41566 | -0.55176 | 0 |  |  | none | FALSE | 0 | 74.7561 | FALSE | FALSE | 0.0588 |  | 75.0446 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14424 | Normal | 75.3331 | -0.88163 | Night | 202601 | 2026-01-12 | 0.88163
2026-01-12 02:13 | 74.6348 | TRUE | FALSE | 0.049657 | 0.066489 | -0.71336 | -0.94676 | -0.2826 | 2026-01-12 06:11 | 2026-01-12 02:13 | lower | TRUE | 1 | 74.6845 | FALSE | FALSE | 0.239 | 2.2993 | 75.0163 | 1 | -0.2826 | -0.02826 | 0.086982 | -2.924 | 0.16593 | Extreme triggered | 75.3482 | -2.2993 | Night | 202601 | 2026-01-12 | 2.2993
2026-01-12 02:27 | 74.6348 | FALSE | FALSE | -0.0077242 | -0.01035 | -0.71422 | -0.94789 | 0 |  | 2026-01-12 02:13 | none | FALSE | 1 | 74.6271 | FALSE | FALSE | 0.2733 | 2.1282 | 74.9881 | 2 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18049 | Extreme/elevated | 75.349 | -1.9572 | Night | 202601 | 2026-01-12 | 1.9572
2026-01-12 02:42 | 74.3522 | TRUE | FALSE | 0.14804 | 0.19872 | -1.0389 | -1.378 | -0.2826 |  | 2026-01-12 02:13 | lower | TRUE | 2 | 74.5002 | TRUE | TRUE | 0.4062 | 2.3071 | 74.9457 | 3 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.22271 | Persistent | 75.3911 | -2.6647 | Night | 202601 | 2026-01-12 | 2.6647
2026-01-12 02:57 | 74.3522 | FALSE | FALSE | 0.049714 | 0.066819 | -1.0524 | -1.3957 | 0 |  | 2026-01-12 02:13 | lower | TRUE | 2 | 74.4019 | FALSE | TRUE | 0.4323 | 2.2799 | 74.9033 | 4 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.25068 | Persistent | 75.4046 | -2.1983 | Night | 202601 | 2026-01-12 | 2.1983
2026-01-12 03:12 | 74.3522 | FALSE | FALSE | -0.029081 | -0.039128 | -1.0464 | -1.3879 | 0 |  | 2026-01-12 02:13 | none | FALSE | 2 | 74.3231 | FALSE | FALSE | 0.469 | 2.2023 | 74.8609 | 5 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.26888 | Persistent | 75.3986 | -1.8918 | Night | 202601 | 2026-01-12 | 1.8918
2026-01-12 03:27 | 74.0714 | FALSE | FALSE | 0.11435 | 0.15415 | -1.3517 | -1.7922 | -0.2808 |  | 2026-01-12 02:13 | lower | TRUE | 2 | 74.1858 | FALSE | TRUE | 0.558 | 2.2302 | 74.8045 | 6 | -0.2808 | -0.05643 | 0.11579 | -1.9377 | 0.30935 | Persistent | 75.4231 | -2.3697 | Night | 202601 | 2026-01-12 | 2.3697
2026-01-12 03:42 | 74.0714 | FALSE | TRUE | 0.0061222 | 0.0082646 | -1.3471 | -1.7862 | 0 |  | 2026-01-12 02:13 | lower | TRUE | 2 | 74.0775 | FALSE | TRUE | 0.5917 | 2.1999 | 74.748 | 7 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.33525 | Confirmed/Materialized Shift | 75.4185 | -2.0183 | Night | 202601 | 2026-01-12 | 2.0183
2026-01-12 03:57 | 74.0714 | FALSE | TRUE | -0.079477 | -0.10741 | -1.3199 | -1.7507 | 0 |  | 2026-01-12 02:13 | none | FALSE | 2 | 73.9919 | FALSE | FALSE | 0.5753 | 2.1465 | 74.6916 | 8 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.34983 | Confirmed/Materialized Shift | 75.3913 | -1.7728 | Night | 202601 | 2026-01-12 | 1.7728
2026-01-12 04:12 | 74.0714 | FALSE | TRUE | -0.14524 | -0.19647 | -1.2728 | -1.6893 | 0 |  | 2026-01-12 02:13 | none | FALSE | 2 | 73.9262 | FALSE | FALSE | 0.5632 | 2.0847 | 74.6352 | 9 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.3545 | Confirmed/Materialized Shift | 75.3442 | -1.5903 | Night | 202601 | 2026-01-12 | 1.5903
2026-01-12 04:27 | 74.0714 | FALSE | TRUE | -0.21698 | -0.29379 | -1.2599 | -1.6725 | 0 |  | 2026-01-12 02:13 | none | FALSE | 2 | 73.8544 | FALSE | FALSE | 0.5513 | 2.0175 | 74.5929 | 10 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.36922 | Confirmed/Materialized Shift | 75.3313 | -1.4123 | Night | 202601 | 2026-01-12 | 1.4123
2026-01-12 04:42 | 74.0714 | FALSE | TRUE | -0.2777 | -0.37631 | -1.236 | -1.6413 | 0 |  | 2026-01-12 02:13 | none | FALSE | 1 | 73.7937 | FALSE | FALSE | 0.513 | 1.9492 | 74.5506 | 11 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.37843 | Confirmed/Materialized Shift | 75.3074 | -1.2662 | Night | 202601 | 2026-01-12 | 1.2662
2026-01-12 04:57 | 74.0714 | FALSE | TRUE | -0.32819 | -0.44504 | -1.2019 | -1.5967 | 0 |  | 2026-01-12 02:13 | none | FALSE | 1 | 73.7432 | FALSE | FALSE | 0.5047 | 1.8819 | 74.5083 | 12 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.38252 | Confirmed/Materialized Shift | 75.2733 | -1.142 | Night | 202601 | 2026-01-12 | 1.142
2026-01-12 05:12 | 74.0714 | FALSE | TRUE | -0.36879 | -0.50038 | -1.1579 | -1.5392 | 0 |  | 2026-01-12 02:13 | none | FALSE | 0 | 73.7026 | FALSE | FALSE | 0.4689 | 1.8167 | 74.466 | 13 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.38168 | Confirmed/Materialized Shift | 75.2293 | -1.0338 | Night | 202601 | 2026-01-12 | 1.0338
2026-01-12 05:26 | 73.7888 | FALSE | TRUE | -0.16853 | -0.22891 | -1.41 | -1.875 | -0.2826 |  | 2026-01-12 02:13 | none | FALSE | 0 | 73.6203 | FALSE | FALSE | 0.5049 | 1.7993 | 74.4095 | 14 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.39463 | Confirmed/Materialized Shift | 75.1988 | -1.5729 | Night | 202601 | 2026-01-12 | 1.5729
2026-01-12 05:41 | 73.7888 | FALSE | TRUE | -0.23341 | -0.31732 | -1.362 | -1.8124 | 0 |  | 2026-01-12 02:13 | none | FALSE | 0 | 73.5554 | FALSE | FALSE | 0.4943 | 1.7736 | 74.3531 | 15 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.39885 | Confirmed/Materialized Shift | 75.1508 | -1.4148 | Night | 202601 | 2026-01-12 | 1.4148
2026-01-12 05:56 | 73.7888 | FALSE | TRUE | -0.28139 | -0.3828 | -1.2971 | -1.7275 | 0 |  | 2026-01-12 02:13 | none | FALSE | 0 | 73.5074 | FALSE | FALSE | 0.4858 | 1.7432 | 74.2967 | 16 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.39463 | Confirmed/Materialized Shift | 75.0859 | -1.287 | Night | 202601 | 2026-01-12 | 1.287
2026-01-12 06:11 | 74.0714 | TRUE | FALSE | -0.55524 | -0.75527 | -0.92118 | -1.2284 | 0.2826 |  |  | none | FALSE | 1 | 73.5162 | FALSE | FALSE | 0.0616 |  | 74.2544 | 0 | 0.2826 | -0.0423 | 0.13813 | 2.3521 | 0.36911 | Persistence ends | 74.9926 | -0.49571 | Night | 202601 | 2026-01-12 | 0.49571
2026-01-12 06:26 | 73.7888 | FALSE | FALSE | -0.28702 | -0.39049 | -1.1053 | -1.4758 | -0.2826 |  |  | none | FALSE | 1 | 73.5018 | FALSE | FALSE | 0.1069 |  | 74.1979 | 0 | -0.2826 | -0.05643 | 0.1477 | -1.5313 | 0.34808 | Normal | 74.8941 | -1.1754 | Night | 202601 | 2026-01-12 | 1.1754
2026-01-12 06:41 | 73.7888 | FALSE | FALSE | -0.27776 | -0.37785 | -0.98318 | -1.3149 | 0 |  |  | none | FALSE | 1 | 73.511 | FALSE | FALSE | 0.1032 |  | 74.1415 | 0 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.31524 | Normal | 74.772 | -1.1189 | Night | 202601 | 2026-01-12 | 1.1189
2026-01-12 06:56 | 73.7888 | FALSE | FALSE | -0.23621 | -0.32114 | -0.82877 | -1.1107 | 0 |  |  | none | FALSE | 1 | 73.5526 | FALSE | FALSE | 0.1028 |  | 74.0851 | 0 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.26624 | Normal | 74.6176 | -1.1128 | Night | 202601 | 2026-01-12 | 1.1128
2026-01-12 07:11 | 73.7888 | FALSE | FALSE | -0.22651 | -0.30791 | -0.73447 | -0.98555 | 0 |  |  | none | FALSE | 1 | 73.5623 | FALSE | FALSE | 0.099 |  | 74.0428 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.24024 | Normal | 74.5233 | -1.0572 | Night | 202601 | 2026-01-12 | 1.0572
2026-01-12 07:26 | 73.7888 | FALSE | FALSE | -0.19221 | -0.26117 | -0.61557 | -0.82733 | 0 |  |  | none | FALSE | 1 | 73.5966 | FALSE | FALSE | 0.0985 |  | 74.0005 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.20195 | Normal | 74.4044 | -1.0482 | Day | 202601 | 2026-01-12 | 1.0482
2026-01-12 07:30 | 73.7888 | FALSE | FALSE | -0.19488 | -0.2648 | -0.5619 | -0.75574 | 0 |  |  | none | FALSE | 1 | 73.5939 | FALSE | FALSE | 0.0932 |  | 73.9723 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.18919 | Normal | 74.3507 | -0.96996 | Day | 202601 | 2026-01-12 | 0.96996
2026-01-12 07:45 | 73.7888 | FALSE | FALSE | -0.18604 | -0.25277 | -0.49672 | -0.66867 | 0 |  |  | none | FALSE | 1 | 73.6028 | FALSE | FALSE | 0.0892 |  | 73.9441 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.17069 | Normal | 74.2855 | -0.91006 | Day | 202601 | 2026-01-12 | 0.91006
2026-01-12 08:00 | 73.7888 | FALSE | FALSE | -0.16132 | -0.2191 | -0.41566 | -0.56015 | 0 |  |  | none | FALSE | 1 | 73.6275 | FALSE | FALSE | 0.0873 |  | 73.916 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.14424 | Normal | 74.2045 | -0.88163 | Day | 202601 | 2026-01-12 | 0.88163
2026-01-12 08:15 | 73.7888 | FALSE | FALSE | -0.17104 | -0.23234 | -0.39712 | -0.53531 | 0 |  |  | none | FALSE | 1 | 73.6178 | FALSE | FALSE | 0.0816 |  | 73.9018 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14204 | Normal | 74.1859 | -0.79582 | Day | 202601 | 2026-01-12 | 0.79582
2026-01-12 08:30 | 73.7888 | FALSE | FALSE | -0.17768 | -0.24137 | -0.3755 | -0.5063 | 0 |  |  | none | FALSE | 0 | 73.6111 | FALSE | FALSE | 0.0477 |  | 73.8877 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13829 | Normal | 74.1643 | -0.71522 | Day | 202601 | 2026-01-12 | 0.71522
2026-01-12 08:45 | 73.7888 | FALSE | FALSE | -0.18096 | -0.24584 | -0.35052 | -0.47278 | 0 |  |  | none | FALSE | 0 | 73.6078 | FALSE | FALSE | 0.0425 |  | 73.8736 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13287 | Normal | 74.1393 | -0.63808 | Day | 202601 | 2026-01-12 | 0.63808
2026-01-12 08:45 | 73.7888 | FALSE | FALSE | -0.18045 | -0.24514 | -0.32175 | -0.43414 | 0 |  |  | none | FALSE | 0 | 73.6084 | FALSE | FALSE | 0.0375 |  | 73.8594 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.12555 | Normal | 74.1105 | -0.56273 | Day | 202601 | 2026-01-12 | 0.56273
2026-01-12 09:00 | 73.7888 | FALSE | FALSE | -0.17543 | -0.23832 | -0.28847 | -0.38942 | 0 |  |  | none | FALSE | 0 | 73.6134 | FALSE | FALSE | 0.0325 |  | 73.8453 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.11598 | Normal | 74.0773 | -0.48734 | Day | 202601 | 2026-01-12 | 0.48734
2026-01-12 09:15 | 73.5062 | TRUE | FALSE | 0.058095 | 0.078972 | -0.56363 | -0.76094 | -0.2826 | 2026-01-12 10:14 | 2026-01-12 09:15 | lower | TRUE | 1 | 73.5643 | FALSE | FALSE | 0.2497 | 2.4597 | 73.8171 | 1 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.12638 | Extreme triggered | 74.0698 | -2.4597 | Day | 202601 | 2026-01-12 | 2.4597
2026-01-12 09:30 | 73.2236 | FALSE | FALSE | 0.20923 | 0.28493 | -0.89291 | -1.2047 | -0.2826 |  | 2026-01-12 09:15 | lower | TRUE | 1 | 73.4328 | FALSE | FALSE | 0.3578 | 2.8419 | 73.7747 | 2 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.17092 | Extreme/elevated | 74.1165 | -3.2242 | Day | 202601 | 2026-01-12 | 3.2242
2026-01-12 09:44 | 73.2236 | FALSE | FALSE | 0.11538 | 0.15733 | -0.90198 | -1.2168 | 0 |  | 2026-01-12 09:15 | lower | TRUE | 1 | 73.339 | FALSE | TRUE | 0.3725 | 2.7569 | 73.7323 | 3 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.19665 | Persistent | 74.1256 | -2.5868 | Day | 202601 | 2026-01-12 | 2.5868
2026-01-12 09:59 | 73.2236 | FALSE | FALSE | 0.027517 | 0.037565 | -0.93332 | -1.2586 | 0 |  | 2026-01-12 09:15 | lower | TRUE | 1 | 73.2511 | FALSE | TRUE | 0.3986 | 2.598 | 73.704 | 4 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.22645 | Persistent | 74.1569 | -2.1215 | Day | 202601 | 2026-01-12 | 2.1215
2026-01-12 10:14 | 73.5062 | TRUE | FALSE | -0.27566 | -0.37643 | -0.64304 | -0.86723 | 0.2826 |  |  | none | FALSE | 2 | 73.2305 | TRUE | FALSE | 0.1105 |  | 73.6899 | 0 | 0.2826 | -0.01413 | 0.14424 | 2.0571 | 0.22968 | Persistence ends | 74.1492 | -0.79978 | Day | 202601 | 2026-01-12 | 0.79978
2026-01-12 10:30 | 73.5062 | FALSE | FALSE | -0.29435 | -0.40205 | -0.63347 | -0.85442 | 0 |  |  | none | FALSE | 2 | 73.2119 | FALSE | FALSE | 0.1059 |  | 73.6758 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.23195 | Normal | 74.1397 | -0.73101 | Day | 202601 | 2026-01-12 | 0.73101
2026-01-12 10:44 | 73.5062 | FALSE | FALSE | -0.28875 | -0.39438 | -0.57135 | -0.77129 | 0 |  |  | none | FALSE | 2 | 73.2174 | FALSE | FALSE | 0.101 |  | 73.6475 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21503 | Normal | 74.0776 | -0.65713 | Day | 202601 | 2026-01-12 | 0.65713
2026-01-12 10:59 | 73.5062 | FALSE | FALSE | -0.3019 | -0.41241 | -0.55624 | -0.75105 | 0 |  |  | none | FALSE | 2 | 73.2043 | FALSE | FALSE | 0.0967 |  | 73.6334 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.21454 | Normal | 74.0624 | -0.59276 | Day | 202601 | 2026-01-12 | 0.59276
2026-01-12 11:14 | 73.5062 | FALSE | FALSE | -0.31309 | -0.42775 | -0.53917 | -0.72816 | 0 |  |  | none | FALSE | 2 | 73.1931 | FALSE | FALSE | 0.0925 |  | 73.6192 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.21306 | Normal | 74.0454 | -0.53055 | Day | 202601 | 2026-01-12 | 0.53055
2026-01-12 11:29 | 73.5062 | FALSE | FALSE | -0.32225 | -0.44033 | -0.52007 | -0.70255 | 0 |  |  | none | FALSE | 2 | 73.1839 | FALSE | FALSE | 0.0885 |  | 73.6051 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.21058 | Normal | 74.0263 | -0.4697 | Day | 202601 | 2026-01-12 | 0.4697
2026-01-12 11:44 | 73.5062 | FALSE | FALSE | -0.32934 | -0.45006 | -0.4989 | -0.67414 | 0 |  |  | none | FALSE | 1 | 73.1769 | FALSE | FALSE | 0.0559 |  | 73.591 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.20706 | Normal | 74.0051 | -0.40945 | Day | 202601 | 2026-01-12 | 0.40945
2026-01-12 11:59 | 73.7888 | TRUE | FALSE | -0.61194 | -0.83625 | -0.2163 | -0.29228 | 0.2826 |  |  | none | FALSE | 2 | 73.1769 | TRUE | FALSE | 0.1208 |  | 73.591 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.20706 | Normal | 74.0051 | 0.95538 | Day | 202601 | 2026-01-12 | 0.95538
2026-01-12 12:14 | 73.7888 | FALSE | FALSE | -0.61194 | -0.83625 | -0.2163 | -0.29228 | 0 |  |  | none | FALSE | 2 | 73.1769 | FALSE | FALSE | 0.1208 |  | 73.591 | 0 | 0 | 0 | 0.12967 | 0 | 0.20706 | Normal | 74.0051 | 0.95538 | Day | 202601 | 2026-01-12 | 0.95538
2026-01-12 12:29 | 73.7888 | FALSE | FALSE | -0.61194 | -0.83625 | -0.2163 | -0.29228 | 0 |  |  | none | FALSE | 2 | 73.1769 | FALSE | FALSE | 0.1208 |  | 73.591 | 0 | 0 | 0 | 0.12967 | 0 | 0.20706 | Normal | 74.0051 | 0.95538 | Day | 202601 | 2026-01-12 | 0.95538
2026-01-12 12:43 | 73.2236 | TRUE | FALSE | -0.094825 | -0.12967 | -0.77306 | -1.0447 | -0.5652 |  |  | none | FALSE | 2 | 73.1288 | TRUE | FALSE | 0.1613 |  | 73.5627 | 0 | -0.5652 | -0.02826 | 0.18107 | -2.9654 | 0.21697 | Normal | 73.9967 | -1.563 | Day | 202601 | 2026-01-12 | 1.563
2026-01-12 12:59 | 72.6584 | TRUE | FALSE | 0.26792 | 0.36738 | -1.4277 | -1.9271 | -0.5652 | 2026-01-12 13:43 | 2026-01-12 12:59 | lower | TRUE | 3 | 72.9263 | TRUE | FALSE | 0.3378 | 2.924 | 73.5062 | 1 | -0.5652 | -0.05652 | 0.21697 | -2.3444 | 0.28994 | Extreme triggered | 74.0861 | -2.924 | Day | 202601 | 2026-01-12 | 2.924
2026-01-12 13:14 | 71.8124 | TRUE | FALSE | 0.65566 | 0.90476 | -2.5343 | -3.4088 | -0.846 |  | 2026-01-12 12:59 | lower | TRUE | 4 | 72.4681 | TRUE | FALSE | 0.455 | 3.16 | 73.4074 | 2 | -0.846 | -0.09882 | 0.27898 | -2.6783 | 0.46966 | Extreme/elevated | 74.3467 | -3.396 | Day | 202601 | 2026-01-12 | 3.396
2026-01-12 13:29 | 72.095 | FALSE | FALSE | 0.13953 | 0.19316 | -2.3159 | -3.1122 | 0.2826 |  | 2026-01-12 12:59 | lower | TRUE | 4 | 72.2345 | FALSE | TRUE | 0.4361 | 2.8588 | 73.3227 | 3 | 0.2826 | -0.08469 | 0.29114 | 1.2616 | 0.54408 | Persistent | 74.4109 | -2.2564 | Day | 202601 | 2026-01-12 | 2.2564
2026-01-12 13:43 | 72.941 | TRUE | FALSE | -0.73841 | -1.0227 | -1.417 | -1.9057 | 0.846 |  |  | none | FALSE | 5 | 72.2026 | TRUE | FALSE | 0.1848 |  | 73.2803 | 0 | 0.846 | -0.04239 | 0.3579 | 2.4823 | 0.53886 | Persistence ends | 74.358 | -0.62967 | Day | 202601 | 2026-01-12 | 0.62967
2026-01-12 13:58 | 73.5062 | FALSE | FALSE | -1.2969 | -1.796 | -0.81682 | -1.099 | 0.5652 |  |  | none | FALSE | 5 | 72.2093 | FALSE | FALSE | 0.1731 |  | 73.2662 | 0 | 0.5652 | -0.01413 | 0.38286 | 1.5131 | 0.52842 | Normal | 74.323 | 0.45424 | Day | 202601 | 2026-01-12 | 0.45424
2026-01-12 14:13 | 73.7888 | FALSE | FALSE | -1.5862 | -2.1969 | -0.56921 | -0.7655 | 0.2826 |  |  | none | FALSE | 5 | 72.2026 | FALSE | FALSE | 0.2058 |  | 73.2803 | 0 | 0.2826 | 0.01413 | 0.38286 | 0.70122 | 0.53886 | Normal | 74.358 | 0.94367 | Day | 202601 | 2026-01-12 | 0.94367
2026-01-12 14:14 | 74.0714 | FALSE | FALSE | -1.8823 | -2.6074 | -0.38486 | -0.51689 | 0.2826 |  |  | none | FALSE | 4 | 72.1891 | FALSE | FALSE | 0.2024 |  | 73.3227 | 0 | 0.2826 | 0.04239 | 0.38066 | 0.63103 | 0.56678 | Normal | 74.4563 | 1.321 | Day | 202601 | 2026-01-12 | 1.321
2026-01-12 14:17 | 74.0714 | FALSE | FALSE | -1.8867 | -2.6137 | -0.47409 | -0.63597 | 0 |  |  | none | FALSE | 4 | 72.1847 | FALSE | FALSE | 0.1941 |  | 73.3651 | 0 | 0 | 0.04239 | 0.38066 | -0.11136 | 0.5902 | Normal | 74.5455 | 1.1967 | Day | 202601 | 2026-01-12 | 1.1967
2026-01-12 14:29 | 72.6584 | TRUE | FALSE | -0.54261 | -0.75242 | -1.8995 | -2.5476 | -1.413 |  |  | none | FALSE | 5 | 72.1158 | TRUE | FALSE | 0.2169 |  | 73.3368 | 0 | -1.413 | -0.02826 | 0.50104 | -2.7638 | 0.61052 | Normal | 74.5579 | -1.1112 | Day | 202601 | 2026-01-12 | 1.1112
2026-01-12 14:43 | 72.095 | FALSE | FALSE | -0.16611 | -0.23094 | -2.5086 | -3.3626 | -0.5634 |  |  | none | FALSE | 4 | 71.9289 | FALSE | FALSE | 0.2311 |  | 73.2663 | 0 | -0.5634 | -0.07056 | 0.50906 | -0.96814 | 0.66869 | Normal | 74.6036 | -1.7516 | Day | 202601 | 2026-01-12 | 1.7516
2026-01-12 14:58 | 71.8124 | FALSE | FALSE | -0.11111 | -0.15497 | -2.8495 | -3.8165 | -0.2826 |  |  | none | FALSE | 3 | 71.7013 | FALSE | FALSE | 0.209 |  | 73.1816 | 0 | -0.2826 | -0.08469 | 0.51091 | -0.38736 | 0.74014 | Normal | 74.6619 | -1.8499 | Day | 202601 | 2026-01-12 | 1.8499
2026-01-12 15:02 | 71.8124 | FALSE | FALSE | -0.30722 | -0.42965 | -2.8762 | -3.8509 | 0 |  |  | none | FALSE | 2 | 71.5052 | FALSE | FALSE | 0.1647 |  | 73.0969 | 0 | 0 | -0.08469 | 0.51091 | 0.16576 | 0.79585 | Normal | 74.6886 | -1.614 | Day | 202601 | 2026-01-12 | 1.614
2026-01-12 15:17 | 72.3758 | FALSE | FALSE | -0.94611 | -1.3245 | -2.2752 | -3.0478 | 0.5634 |  |  | none | FALSE | 2 | 71.4297 | FALSE | FALSE | 0.1122 |  | 73.0404 | 0 | 0.5634 | -0.05652 | 0.53097 | 1.1675 | 0.80533 | Normal | 74.651 | -0.8252 | Day | 202601 | 2026-01-12 | 0.8252
2026-01-12 15:32 | 72.6584 | FALSE | FALSE | -1.2641 | -1.7706 | -1.9432 | -2.6048 | 0.2826 |  |  | none | FALSE | 1 | 71.3943 | FALSE | FALSE | 0.0568 |  | 72.998 | 0 | 0.2826 | -0.04239 | 0.53629 | 0.606 | 0.80183 | Normal | 74.6016 | -0.42349 | Day | 202601 | 2026-01-12 | 0.42349
2026-01-12 15:43 | 72.6584 | FALSE | FALSE | -1.2947 | -1.8142 | -1.889 | -2.534 | 0 |  |  | none | FALSE | 1 | 71.3637 | FALSE | FALSE | 0.0535 |  | 72.9556 | 0 | 0 | -0.04239 | 0.53629 | 0.079044 | 0.79593 | Normal | 74.5474 | -0.37337 | Day | 202601 | 2026-01-12 | 0.37337
2026-01-12 15:58 | 72.941 | FALSE | FALSE | -1.5843 | -2.2203 | -1.557 | -2.0899 | 0.2826 |  |  | none | FALSE | 1 | 71.3567 | FALSE | FALSE | 0.0297 |  | 72.9273 | 0 | 0.2826 | -0.02826 | 0.54116 | 0.57443 | 0.78532 | Normal | 74.498 | 0.01742 | Day | 202601 | 2026-01-12 | 0.01742
2026-01-12 16:13 | 72.941 | FALSE | FALSE | -1.5737 | -2.205 | -1.4615 | -1.9644 | 0 |  |  | none | FALSE | 1 | 71.3673 | FALSE | FALSE | 0.0335 |  | 72.8849 | 0 | 0 | -0.04239 | 0.53629 | 0.079044 | 0.7588 | Normal | 74.4025 | 0.073893 | Day | 202601 | 2026-01-12 | 0.073893
2026-01-12 16:28 | 72.941 | FALSE | FALSE | -1.5559 | -2.1796 | -1.359 | -1.8291 | 0 |  |  | none | FALSE | 1 | 71.3851 | FALSE | FALSE | 0.0376 |  | 72.8425 | 0 | 0 | -0.04239 | 0.53629 | 0.079044 | 0.72874 | Normal | 74.3 | 0.13511 | Day | 202601 | 2026-01-12 | 0.13511
2026-01-12 16:42 | 72.941 | FALSE | FALSE | -1.5302 | -2.1428 | -1.2485 | -1.6828 | 0 |  |  | none | FALSE | 0 | 71.4108 | FALSE | FALSE | 0.0135 |  | 72.8002 | 0 | 0 | -0.04239 | 0.53629 | 0.079044 | 0.69466 | Normal | 74.1895 | 0.20276 | Day | 202601 | 2026-01-12 | 0.20276
2026-01-12 16:57 | 72.941 | FALSE | FALSE | -1.5319 | -2.1452 | -1.2219 | -1.6476 | 0 |  |  | none | FALSE | 0 | 71.4091 | FALSE | FALSE | 0.015 |  | 72.786 | 0 | 0 | -0.01413 | 0.52199 | 0.02707 | 0.68844 | Normal | 74.1629 | 0.22512 | Day | 202601 | 2026-01-12 | 0.22512
2026-01-12 17:12 | 72.941 | FALSE | FALSE | -1.518 | -2.1254 | -1.2363 | -1.6667 | 0 |  |  | none | FALSE | 0 | 71.423 | FALSE | FALSE | 0.0136 |  | 72.8002 | 0 | 0 | 0.01413 | 0.50562 | -0.027946 | 0.68858 | Normal | 74.1773 | 0.20455 | Day | 202601 | 2026-01-12 | 0.20455
2026-01-12 17:27 | 73.2236 | FALSE | FALSE | -1.6598 | -2.3193 | -0.954 | -1.2861 | 0.2826 |  |  | none | FALSE | 0 | 71.5638 | FALSE | FALSE | 0.036 |  | 72.8707 | 0 | 0.2826 | 0.07056 | 0.466 | 0.45502 | 0.65345 | Normal | 74.1776 | 0.54005 | Day | 202601 | 2026-01-12 | 0.54005
2026-01-12 17:42 | 72.941 | FALSE | FALSE | -1.2829 | -1.7903 | -1.2269 | -1.6542 | -0.2826 |  |  | none | FALSE | 0 | 71.6581 | FALSE | FALSE | 0.003 |  | 72.913 | 0 | -0.2826 | 0.0423 | 0.46959 | -0.69188 | 0.62745 | Normal | 74.1679 | 0.044609 | Day | 202601 | 2026-01-12 | 0.044609
2026-01-12 17:57 | 72.941 | FALSE | FALSE | -1.2829 | -1.7903 | -1.2269 | -1.6542 | 0 |  |  | none | FALSE | 0 | 71.6581 | FALSE | FALSE | 0.003 |  | 72.913 | 0 | 0 | 0 | 0.4298 | 0 | 0.62745 | Normal | 74.1679 | 0.044609 | Night | 202601 | 2026-01-12 | 0.044609
2026-01-12 18:12 | 72.941 | FALSE | FALSE | -1.28 | -1.7862 | -1.1675 | -1.5754 | 0 |  |  | none | FALSE | 0 | 71.661 | FALSE | FALSE | 0.0061 |  | 72.8847 | 0 | 0 | -0.02826 | 0.40875 | 0.069137 | 0.61186 | Normal | 74.1085 | 0.091932 | Night | 202601 | 2026-01-12 | 0.091932
2026-01-12 18:27 | 72.941 | FALSE | FALSE | -1.2469 | -1.7392 | -1.0496 | -1.4186 | 0 |  |  | none | FALSE | 0 | 71.6941 | FALSE | FALSE | 0.0115 |  | 72.8424 | 0 | 0 | -0.04239 | 0.40227 | 0.10538 | 0.57414 | Normal | 73.9906 | 0.1718 | Night | 202601 | 2026-01-12 | 0.1718
2026-01-12 18:42 | 72.941 | FALSE | FALSE | -1.1497 | -1.6015 | -0.83939 | -1.1377 | 0 |  |  | none | FALSE | 0 | 71.7913 | FALSE | FALSE | 0.0208 |  | 72.7858 | 0 | 0 | -0.05652 | 0.39516 | 0.14303 | 0.49728 | Normal | 73.7804 | 0.31202 | Night | 202601 | 2026-01-12 | 0.31202
2026-01-12 18:42 | 72.941 | FALSE | FALSE | -1.0072 | -1.4002 | -0.58382 | -0.79405 | 0 |  |  | none | FALSE | 0 | 71.9338 | FALSE | FALSE | 0.0355 |  | 72.7293 | 0 | 0 | -0.05652 | 0.39516 | 0.14303 | 0.39775 | Normal | 73.5248 | 0.53219 | Night | 202601 | 2026-01-12 | 0.53219
2026-01-12 18:57 | 73.2236 | FALSE | FALSE | -1.2905 | -1.7941 | -0.3585 | -0.48722 | 0.2826 |  |  | none | FALSE | 0 | 71.9331 | FALSE | FALSE | 0.0754 |  | 72.7576 | 0 | 0.2826 | 0.02826 | 0.2404 | 1.058 | 0.41226 | Normal | 73.5821 | 1.1304 | Night | 202601 | 2026-01-12 | 1.1304
2026-01-12 19:12 | 73.7888 | TRUE | FALSE | -1.8303 | -2.5436 | 0.062735 | 0.085093 | 0.5652 | 2026-01-12 20:11 | 2026-01-12 19:12 | upper | TRUE | 1 | 71.9585 | FALSE | FALSE | 0.2285 | 2.142 | 72.8423 | 1 | 0.5652 | 0.08469 | 0.22625 | 2.1238 | 0.4419 | Extreme triggered | 73.7261 | 2.142 | Night | 202601 | 2026-01-12 | 2.142
2026-01-12 19:27 | 73.7888 | FALSE | FALSE | -1.6875 | -2.3405 | 0.0078893 | 0.010693 | 0 |  | 2026-01-12 19:12 | upper | TRUE | 1 | 72.1013 | FALSE | FALSE | 0.2774 | 2.0804 | 72.9411 | 2 | 0 | 0.09882 | 0.21037 | -0.46974 | 0.41991 | Extreme/elevated | 73.7809 | 2.0188 | Night | 202601 | 2026-01-12 | 2.0188
2026-01-12 19:41 | 73.7888 | FALSE | FALSE | -1.4887 | -2.059 | 0.009113 | 0.012352 | 0 |  | 2026-01-12 19:12 | upper | TRUE | 1 | 72.3001 | FALSE | TRUE | 0.335 | 2.0618 | 73.0399 | 3 | 0 | 0.09882 | 0.21037 | -0.46974 | 0.36989 | Persistent | 73.7797 | 2.0246 | Night | 202601 | 2026-01-12 | 2.0246
2026-01-12 19:56 | 73.7888 | FALSE | FALSE | -1.4209 | -1.9634 | -0.064373 | -0.087163 | 0 |  | 2026-01-12 19:12 | none | FALSE | 1 | 72.3679 | FALSE | FALSE | 0.3789 | 2.003 | 73.1106 | 4 | 0 | 0.07065 | 0.18049 | -0.39144 | 0.37131 | Persistent | 73.8532 | 1.8266 | Night | 202601 | 2026-01-12 | 1.8266
2026-01-12 20:11 | 73.5062 | FALSE | FALSE | -1.0839 | -1.4966 | -0.37738 | -0.51078 | -0.2826 |  |  | none | FALSE | 1 | 72.4223 | FALSE | FALSE | 0.093 |  | 73.153 | 0 | -0.2826 | 0.04239 | 0.18957 | -1.7143 | 0.36531 | Persistence ends | 73.8836 | 0.96697 | Night | 202601 | 2026-01-12 | 0.96697
2026-01-12 20:26 | 73.5062 | FALSE | FALSE | -1.0187 | -1.4053 | -0.39698 | -0.53716 | 0 |  |  | none | FALSE | 1 | 72.4875 | FALSE | FALSE | 0.0871 |  | 73.1953 | 0 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.35392 | Normal | 73.9032 | 0.87834 | Night | 202601 | 2026-01-12 | 0.87834
2026-01-12 20:41 | 73.5062 | FALSE | FALSE | -0.99281 | -1.3691 | -0.42761 | -0.57837 | 0 |  |  | none | FALSE | 1 | 72.5134 | FALSE | FALSE | 0.0816 |  | 73.2236 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.3551 | Normal | 73.9338 | 0.79582 | Night | 202601 | 2026-01-12 | 0.79582
2026-01-12 20:56 | 73.5062 | FALSE | FALSE | -0.96218 | -1.3263 | -0.4535 | -0.61317 | 0 |  |  | none | FALSE | 1 | 72.544 | FALSE | FALSE | 0.0765 |  | 73.2519 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.35392 | Normal | 73.9597 | 0.71864 | Night | 202601 | 2026-01-12 | 0.71864
2026-01-12 21:11 | 73.2236 | FALSE | FALSE | -0.65044 | -0.89626 | -0.73522 | -0.9941 | -0.2826 |  |  | none | FALSE | 1 | 72.5732 | FALSE | FALSE | 0.0367 |  | 73.266 | 0 | -0.2826 | 0.01413 | 0.19396 | -1.5299 | 0.34642 | Normal | 73.9588 | -0.12237 | Night | 202601 | 2026-01-12 | 0.12237
2026-01-12 21:26 | 73.5062 | FALSE | FALSE | -0.89501 | -1.2326 | -0.47111 | -0.63683 | 0.2826 |  |  | none | FALSE | 1 | 72.6112 | FALSE | FALSE | 0.0699 |  | 73.2943 | 0 | 0.2826 | 0.02826 | 0.20296 | 1.2532 | 0.34153 | Normal | 73.9773 | 0.62059 | Night | 202601 | 2026-01-12 | 0.62059
2026-01-12 21:41 | 73.5062 | FALSE | FALSE | -0.85181 | -1.1724 | -0.48443 | -0.65472 | 0 |  |  | none | FALSE | 0 | 72.6544 | FALSE | FALSE | 0.0367 |  | 73.3225 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.33406 | Normal | 73.9906 | 0.54987 | Night | 202601 | 2026-01-12 | 0.54987
2026-01-12 21:56 | 73.5062 | FALSE | FALSE | -0.80311 | -1.1046 | -0.49225 | -0.66522 | 0 |  |  | none | FALSE | 0 | 72.7031 | FALSE | FALSE | 0.032 |  | 73.3508 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.32384 | Normal | 73.9985 | 0.47996 | Night | 202601 | 2026-01-12 | 0.47996
2026-01-12 22:11 | 73.5062 | FALSE | FALSE | -0.78963 | -1.0859 | -0.50703 | -0.68505 | 0 |  |  | none | FALSE | 0 | 72.7166 | FALSE | FALSE | 0.0291 |  | 73.3649 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.32416 | Normal | 74.0132 | 0.43589 | Night | 202601 | 2026-01-12 | 0.43589
2026-01-12 22:26 | 73.5062 | FALSE | FALSE | -0.73219 | -1.0061 | -0.50611 | -0.68381 | 0 |  |  | none | FALSE | 0 | 72.774 | FALSE | FALSE | 0.0243 |  | 73.3932 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.30957 | Normal | 74.0123 | 0.36515 | Night | 202601 | 2026-01-12 | 0.36515
2026-01-12 22:40 | 73.5062 | FALSE | FALSE | -0.66756 | -0.91648 | -0.498 | -0.67293 | 0 |  |  | none | FALSE | 0 | 72.8386 | FALSE | FALSE | 0.0194 |  | 73.4214 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.29139 | Normal | 74.0042 | 0.29095 | Night | 202601 | 2026-01-12 | 0.29095
2026-01-12 22:55 | 73.2236 | FALSE | FALSE | -0.33434 | -0.4587 | -0.75824 | -1.0249 | -0.2826 |  |  | none | FALSE | 0 | 72.8893 | FALSE | FALSE | 0.0517 |  | 73.4356 | 0 | -0.2826 | 0.01413 | 0.19396 | -1.5299 | 0.27315 | Normal | 73.9818 | -0.77596 | Night | 202601 | 2026-01-12 | 0.77596
2026-01-12 23:11 | 73.2236 | FALSE | FALSE | -0.27945 | -0.3831 | -0.73161 | -0.98926 | 0 |  |  | none | FALSE | 0 | 72.9441 | FALSE | FALSE | 0.0596 |  | 73.4497 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.25277 | Normal | 73.9552 | -0.89443 | Night | 202601 | 2026-01-12 | 0.89443
2026-01-12 23:26 | 73.2236 | FALSE | FALSE | -0.21914 | -0.30018 | -0.69956 | -0.94634 | 0 |  |  | none | FALSE | 0 | 73.0045 | FALSE | FALSE | 0.0697 |  | 73.4638 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.22968 | Normal | 73.9232 | -1.0459 | Night | 202601 | 2026-01-12 | 1.0459
2026-01-12 23:40 | 73.2236 | FALSE | FALSE | -0.15158 | -0.20744 | -0.66026 | -0.89364 | 0 |  |  | none | FALSE | 0 | 73.072 | FALSE | FALSE | 0.0835 |  | 73.4779 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.20296 | Normal | 73.8839 | -1.2532 | Night | 202601 | 2026-01-12 | 1.2532
2026-01-12 23:55 | 73.2236 | FALSE | FALSE | -0.15158 | -0.20744 | -0.66026 | -0.89364 | 0 |  |  | none | FALSE | 0 | 73.072 | FALSE | FALSE | 0.0835 |  | 73.4779 | 0 | 0 | 0 | 0.18338 | 0 | 0.20296 | Normal | 73.8839 | -1.2532 | Night | 202601 | 2026-01-12 | 1.2532
2026-01-13 00:10 | 73.2236 | FALSE | FALSE | -0.16722 | -0.22889 | -0.61938 | -0.83877 | 0 |  |  | none | FALSE | 0 | 73.0564 | FALSE | FALSE | 0.0766 |  | 73.4497 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.19665 | Normal | 73.843 | -1.1497 | Night | 202601 | 2026-01-13 | 1.1497
2026-01-13 00:25 | 73.2236 | FALSE | FALSE | -0.17349 | -0.23749 | -0.56913 | -0.77125 | 0 |  |  | none | FALSE | 0 | 73.0501 | FALSE | FALSE | 0.071 |  | 73.4214 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.18565 | Normal | 73.7927 | -1.0655 | Night | 202601 | 2026-01-13 | 1.0655
2026-01-13 00:40 | 73.2236 | FALSE | FALSE | -0.16857 | -0.23074 | -0.50769 | -0.68856 | 0 |  |  | none | FALSE | 0 | 73.055 | FALSE | FALSE | 0.0669 |  | 73.3932 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.16906 | Normal | 73.7313 | -1.0029 | Night | 202601 | 2026-01-13 | 1.0029
2026-01-13 00:55 | 73.2236 | FALSE | FALSE | -0.14864 | -0.20341 | -0.43124 | -0.58549 | 0 |  |  | none | FALSE | 0 | 73.075 | FALSE | FALSE | 0.065 |  | 73.3649 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.14497 | Normal | 73.6548 | -0.97468 | Night | 202601 | 2026-01-13 | 0.97468
2026-01-13 01:10 | 73.2236 | FALSE | FALSE | -0.16132 | -0.2208 | -0.41566 | -0.56445 | 0 |  |  | none | FALSE | 0 | 73.0623 | FALSE | FALSE | 0.0588 |  | 73.3508 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14424 | Normal | 73.6393 | -0.88163 | Night | 202601 | 2026-01-13 | 0.88163
2026-01-13 01:25 | 73.2236 | FALSE | FALSE | -0.17104 | -0.23414 | -0.39712 | -0.53942 | 0 |  |  | none | FALSE | 0 | 73.0526 | FALSE | FALSE | 0.0531 |  | 73.3366 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14204 | Normal | 73.6207 | -0.79582 | Night | 202601 | 2026-01-13 | 0.79582
2026-01-13 01:39 | 73.2236 | FALSE | FALSE | -0.17768 | -0.24324 | -0.3755 | -0.51019 | 0 |  |  | none | FALSE | 0 | 73.0459 | FALSE | FALSE | 0.0477 |  | 73.3225 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13829 | Normal | 73.5991 | -0.71522 | Night | 202601 | 2026-01-13 | 0.71522
2026-01-13 01:55 | 73.2236 | FALSE | FALSE | -0.18096 | -0.24774 | -0.35052 | -0.47641 | 0 |  |  | none | FALSE | 0 | 73.0426 | FALSE | FALSE | 0.0425 |  | 73.3084 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13287 | Normal | 73.5741 | -0.63808 | Night | 202601 | 2026-01-13 | 0.63808
2026-01-13 02:10 | 73.2236 | FALSE | FALSE | -0.18096 | -0.24774 | -0.35052 | -0.47641 | 0 |  |  | none | FALSE | 0 | 73.0426 | FALSE | FALSE | 0.0425 |  | 73.3084 | 0 | 0 | 0 | 0.091688 | 0 | 0.13287 | Normal | 73.5741 | -0.63808 | Night | 202601 | 2026-01-13 | 0.63808
2026-01-13 02:25 | 73.2236 | FALSE | FALSE | -0.18045 | -0.24704 | -0.32175 | -0.43748 | 0 |  |  | none | FALSE | 0 | 73.0432 | FALSE | FALSE | 0.0375 |  | 73.2943 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.12555 | Normal | 73.5453 | -0.56273 | Night | 202601 | 2026-01-13 | 0.56273
2026-01-13 02:39 | 73.2236 | FALSE | FALSE | -0.17543 | -0.24016 | -0.28847 | -0.39242 | 0 |  |  | none | FALSE | 0 | 73.0482 | FALSE | FALSE | 0.0325 |  | 73.2801 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.11598 | Normal | 73.5121 | -0.48734 | Night | 202601 | 2026-01-13 | 0.48734
2026-01-13 02:54 | 73.2236 | FALSE | FALSE | -0.16467 | -0.22539 | -0.24945 | -0.33951 | 0 |  |  | none | FALSE | 0 | 73.0589 | FALSE | FALSE | 0.0273 |  | 73.266 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.10353 | Normal | 73.473 | -0.40945 | Night | 202601 | 2026-01-13 | 0.40945
2026-01-13 03:09 | 73.2236 | FALSE | FALSE | -0.1457 | -0.19938 | -0.20222 | -0.27541 | 0 |  |  | none | FALSE | 0 | 73.0779 | FALSE | FALSE | 0.0217 |  | 73.2519 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.086982 | Normal | 73.4258 | -0.32489 | Night | 202601 | 2026-01-13 | 0.32489
2026-01-13 03:24 | 73.2236 | FALSE | FALSE | -0.11225 | -0.15354 | -0.14051 | -0.19153 | 0 |  |  | none | FALSE | 0 | 73.1113 | FALSE | FALSE | 0.0149 |  | 73.2377 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.063191 | Normal | 73.3641 | -0.22361 | Night | 202601 | 2026-01-13 | 0.22361
2026-01-13 03:39 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-13
2026-01-13 03:54 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-13
2026-01-13 04:09 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-13
2026-01-13 04:24 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-13
2026-01-13 04:39 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-13
2026-01-13 04:54 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-13
2026-01-13 05:09 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-13
2026-01-13 05:24 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-13
2026-01-13 05:38 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-13
2026-01-13 05:53 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-13
2026-01-13 06:08 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-13
2026-01-13 06:23 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-13
2026-01-13 06:38 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-13
2026-01-13 06:53 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-13
2026-01-13 07:08 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-13
2026-01-13 07:23 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Day | 202601 | 2026-01-13
2026-01-13 07:30 | 72.941 | TRUE | FALSE | 0.14209 | 0.19442 | -0.39485 | -0.53842 | -0.2826 | 2026-01-13 07:45 | 2026-01-13 07:30 | lower | TRUE | 1 | 73.0831 | FALSE | FALSE | 0.3689 | 4.2485 | 73.2095 | 1 | -0.2826 | -0.01413 | 0.063191 | -4.2485 | 0.063191 | Extreme triggered | 73.3359 | -4.2485 | Day | 202601 | 2026-01-13 | 4.2485
2026-01-13 07:45 | 73.2236 | TRUE | FALSE | -0.14051 | -0.19226 | -0.11225 | -0.15307 | 0.2826 |  |  | none | FALSE | 2 | 73.0831 | TRUE | FALSE | 0.072 |  | 73.2095 | 0 | 0.2826 | 0 | 0.091688 | 3.0822 | 0.063191 | Persistence ends | 73.3359 | 0.22361 | Day | 202601 | 2026-01-13 | 0.22361
2026-01-13 08:00 | 73.2236 | FALSE | FALSE | -0.14051 | -0.19226 | -0.11225 | -0.15307 | 0 |  |  | none | FALSE | 2 | 73.0831 | FALSE | FALSE | 0.072 |  | 73.2095 | 0 | 0 | 0 | 0.091688 | 0 | 0.063191 | Normal | 73.3359 | 0.22361 | Day | 202601 | 2026-01-13 | 0.22361
2026-01-13 08:15 | 72.941 | TRUE | FALSE | 0.080375 | 0.11007 | -0.4283 | -0.58377 | -0.2826 | 2026-01-13 08:30 | 2026-01-13 08:15 | lower | TRUE | 3 | 73.0214 | TRUE | FALSE | 0.3378 | 2.924 | 73.1953 | 1 | -0.2826 | -0.01413 | 0.11135 | -2.411 | 0.086982 | Extreme triggered | 73.3693 | -2.924 | Day | 202601 | 2026-01-13 | 2.924
2026-01-13 08:30 | 73.2236 | TRUE | FALSE | -0.20222 | -0.27694 | -0.1457 | -0.19859 | 0.2826 |  |  | none | FALSE | 4 | 73.0214 | TRUE | FALSE | 0.1359 |  | 73.1953 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.086982 | Persistence ends | 73.3693 | 0.32489 | Day | 202601 | 2026-01-13 | 0.32489
2026-01-13 08:45 | 73.2236 | FALSE | FALSE | -0.20222 | -0.27694 | -0.1457 | -0.19859 | 0 |  |  | none | FALSE | 4 | 73.0214 | FALSE | FALSE | 0.1359 |  | 73.1953 | 0 | 0 | 0 | 0.12967 | 0 | 0.086982 | Normal | 73.3693 | 0.32489 | Day | 202601 | 2026-01-13 | 0.32489
2026-01-13 08:45 | 73.2236 | FALSE | FALSE | -0.20222 | -0.27694 | -0.1457 | -0.19859 | 0 |  |  | none | FALSE | 4 | 73.0214 | FALSE | FALSE | 0.1359 |  | 73.1953 | 0 | 0 | 0 | 0.12967 | 0 | 0.086982 | Normal | 73.3693 | 0.32489 | Day | 202601 | 2026-01-13 | 0.32489
2026-01-13 09:00 | 73.2236 | FALSE | FALSE | -0.20222 | -0.27694 | -0.1457 | -0.19859 | 0 |  |  | none | FALSE | 4 | 73.0214 | FALSE | FALSE | 0.1359 |  | 73.1953 | 0 | 0 | 0 | 0.12967 | 0 | 0.086982 | Normal | 73.3693 | 0.32489 | Day | 202601 | 2026-01-13 | 0.32489
2026-01-13 09:15 | 73.5062 | FALSE | FALSE | -0.51944 | -0.71169 | 0.074022 | 0.1008 | 0.2826 | 2026-01-13 09:59 | 2026-01-13 09:15 | upper | TRUE | 4 | 72.9868 | FALSE | FALSE | 0.3491 | 2.6647 | 73.2095 | 1 | 0.2826 | 0.01413 | 0.14424 | 1.8612 | 0.11135 | Extreme triggered | 73.4322 | 2.6647 | Day | 202601 | 2026-01-13 | 2.6647
2026-01-13 09:30 | 73.7888 | FALSE | FALSE | -0.89291 | -1.2249 | 0.20923 | 0.28436 | 0.2826 |  | 2026-01-13 09:15 | upper | TRUE | 4 | 72.8959 | FALSE | FALSE | 0.4435 | 2.9445 | 73.2377 | 2 | 0.2826 | 0.02826 | 0.15614 | 1.6289 | 0.17092 | Extreme/elevated | 73.5796 | 3.2242 | Day | 202601 | 2026-01-13 | 3.2242
2026-01-13 09:44 | 73.5062 | FALSE | FALSE | -0.61648 | -0.84577 | -0.1078 | -0.14644 | -0.2826 |  | 2026-01-13 09:15 | none | FALSE | 3 | 72.8897 | FALSE | FALSE | 0.3508 | 2.4312 | 73.2519 | 3 | -0.2826 | 0.01413 | 0.17092 | -1.7361 | 0.18107 | Persistent | 73.614 | 1.4047 | Day | 202601 | 2026-01-13 | 1.4047
2026-01-13 09:59 | 73.2236 | FALSE | FALSE | -0.33388 | -0.45806 | -0.3904 | -0.53033 | -0.2826 |  |  | none | FALSE | 2 | 72.8897 | FALSE | FALSE | 0.0675 |  | 73.2519 | 0 | -0.2826 | 0 | 0.18338 | -1.5411 | 0.18107 | Persistence ends | 73.614 | -0.15607 | Day | 202601 | 2026-01-13 | 0.15607
2026-01-13 10:14 | 73.2236 | FALSE | FALSE | -0.33388 | -0.45806 | -0.3904 | -0.53033 | 0 |  |  | none | FALSE | 2 | 72.8897 | FALSE | FALSE | 0.0675 |  | 73.2519 | 0 | 0 | 0 | 0.18338 | 0 | 0.18107 | Normal | 73.614 | -0.15607 | Day | 202601 | 2026-01-13 | 0.15607
2026-01-13 10:30 | 73.2236 | FALSE | FALSE | -0.33388 | -0.45806 | -0.3904 | -0.53033 | 0 |  |  | none | FALSE | 1 | 72.8897 | FALSE | FALSE | 0.039 |  | 73.2519 | 0 | 0 | 0 | 0.18338 | 0 | 0.18107 | Normal | 73.614 | -0.15607 | Day | 202601 | 2026-01-13 | 0.15607
2026-01-13 10:44 | 73.2236 | FALSE | FALSE | -0.33388 | -0.45806 | -0.3904 | -0.53033 | 0 |  |  | none | FALSE | 0 | 72.8897 | FALSE | FALSE | 0.0104 |  | 73.2519 | 0 | 0 | 0 | 0.18338 | 0 | 0.18107 | Normal | 73.614 | -0.15607 | Day | 202601 | 2026-01-13 | 0.15607
2026-01-13 10:59 | 73.2236 | FALSE | FALSE | -0.33388 | -0.45806 | -0.3904 | -0.53033 | 0 |  |  | none | FALSE | 0 | 72.8897 | FALSE | FALSE | 0.0104 |  | 73.2519 | 0 | 0 | 0 | 0.18338 | 0 | 0.18107 | Normal | 73.614 | -0.15607 | Day | 202601 | 2026-01-13 | 0.15607
2026-01-13 11:14 | 73.2236 | FALSE | FALSE | -0.33388 | -0.45806 | -0.3904 | -0.53033 | 0 |  |  | none | FALSE | 0 | 72.8897 | FALSE | FALSE | 0.0104 |  | 73.2519 | 0 | 0 | 0 | 0.18338 | 0 | 0.18107 | Normal | 73.614 | -0.15607 | Day | 202601 | 2026-01-13 | 0.15607
2026-01-13 11:29 | 73.2236 | FALSE | FALSE | -0.33388 | -0.45806 | -0.3904 | -0.53033 | 0 |  |  | none | FALSE | 0 | 72.8897 | FALSE | FALSE | 0.0104 |  | 73.2519 | 0 | 0 | 0 | 0.18338 | 0 | 0.18107 | Normal | 73.614 | -0.15607 | Day | 202601 | 2026-01-13 | 0.15607
2026-01-13 11:44 | 73.5062 | FALSE | FALSE | -0.61936 | -0.84975 | -0.13894 | -0.18866 | 0.2826 |  |  | none | FALSE | 0 | 72.8868 | FALSE | FALSE | 0.0845 |  | 73.266 | 0 | 0.2826 | 0.01413 | 0.19396 | 1.3842 | 0.18957 | Normal | 73.6451 | 1.2671 | Day | 202601 | 2026-01-13 | 1.2671
2026-01-13 11:59 | 73.5062 | FALSE | FALSE | -0.61938 | -0.84978 | -0.16722 | -0.22697 | 0 |  |  | none | FALSE | 0 | 72.8868 | FALSE | FALSE | 0.0766 |  | 73.2801 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.19665 | Normal | 73.6734 | 1.1497 | Day | 202601 | 2026-01-13 | 1.1497
2026-01-13 12:14 | 73.5062 | FALSE | FALSE | -0.56913 | -0.7803 | -0.17349 | -0.23546 | 0 |  |  | none | FALSE | 0 | 72.9371 | FALSE | FALSE | 0.071 |  | 73.3084 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.18565 | Normal | 73.6797 | 1.0655 | Day | 202601 | 2026-01-13 | 1.0655
2026-01-13 12:29 | 73.5062 | FALSE | FALSE | -0.56284 | -0.77161 | -0.19546 | -0.2652 | 0 |  |  | none | FALSE | 0 | 72.9434 | FALSE | FALSE | 0.0646 |  | 73.3225 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.18957 | Normal | 73.7017 | 0.96896 | Day | 202601 | 2026-01-13 | 0.96896
2026-01-13 12:43 | 73.7888 | FALSE | FALSE | -0.8671 | -1.1891 | 0.0089558 | 0.012139 | 0.2826 | 2026-01-13 14:40 | 2026-01-13 12:43 | upper | TRUE | 0 | 72.9217 | FALSE | FALSE | 0.1933 | 2.0417 | 73.3508 | 1 | 0.2826 | 0.02826 | 0.18107 | 1.4047 | 0.21454 | Extreme triggered | 73.7798 | 2.0417 | Day | 202601 | 2026-01-13 | 2.0417
2026-01-13 12:59 | 73.7888 | FALSE | FALSE | -0.82177 | -1.1262 | -0.030485 | -0.041297 | 0 |  | 2026-01-13 12:43 | none | FALSE | 0 | 72.967 | FALSE | FALSE | 0.2381 | 1.9493 | 73.3932 | 2 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.21306 | Extreme/elevated | 73.8193 | 1.8569 | Day | 202601 | 2026-01-13 | 1.8569
2026-01-13 13:14 | 73.7888 | FALSE | FALSE | -0.82028 | -1.1242 | -0.085523 | -0.11577 | 0 |  | 2026-01-13 12:43 | none | FALSE | 0 | 72.9685 | FALSE | FALSE | 0.2796 | 1.8403 | 73.4214 | 3 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.22645 | Persistent | 73.8743 | 1.6223 | Day | 202601 | 2026-01-13 | 1.6223
2026-01-13 13:29 | 73.7888 | FALSE | FALSE | -0.81022 | -1.1102 | -0.13198 | -0.17854 | 0 |  | 2026-01-13 12:43 | none | FALSE | 0 | 72.9786 | FALSE | FALSE | 0.3246 | 1.7402 | 73.4497 | 4 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.23555 | Persistent | 73.9208 | 1.4397 | Day | 202601 | 2026-01-13 | 1.4397
2026-01-13 13:32 | 74.0714 | FALSE | FALSE | -1.1132 | -1.5258 | 0.045491 | 0.061453 | 0.2826 |  | 2026-01-13 12:43 | upper | TRUE | 0 | 72.9582 | FALSE | TRUE | 0.4304 | 1.8262 | 73.4921 | 5 | 0.2826 | 0.04239 | 0.16593 | 1.4477 | 0.26692 | Persistent | 74.0259 | 2.1704 | Day | 202601 | 2026-01-13 | 2.1704
2026-01-13 13:35 | 73.7888 | FALSE | FALSE | -0.80231 | -1.0993 | -0.26537 | -0.35834 | -0.2826 |  | 2026-01-13 12:43 | none | FALSE | 0 | 72.9865 | FALSE | FALSE | 0.4099 | 1.6895 | 73.5203 | 6 | -0.2826 | 0.02826 | 0.18107 | -1.7168 | 0.26692 | Persistent | 74.0542 | 1.0058 | Day | 202601 | 2026-01-13 | 1.0058
2026-01-13 13:43 | 73.2236 | TRUE | TRUE | -0.26753 | -0.36669 | -0.83273 | -1.1244 | -0.5652 |  | 2026-01-13 12:43 | none | FALSE | 1 | 72.9561 | FALSE | FALSE | 0.4971 | 1.5949 | 73.5062 | 7 | -0.5652 | -0.01413 | 0.21454 | -2.5686 | 0.27506 | Confirmed/Materialized Shift | 74.0563 | -1.0274 | Day | 202601 | 2026-01-13 | 1.0274
2026-01-13 13:55 | 71.8124 | TRUE | TRUE | 0.67373 | 0.92946 | -2.5162 | -3.3853 | -1.4112 |  | 2026-01-13 12:43 | lower | TRUE | 2 | 72.4861 | TRUE | TRUE | 0.688 | 1.8284 | 73.4074 | 8 | -1.4112 | -0.09882 | 0.36955 | -3.5513 | 0.46062 | Confirmed/Materialized Shift | 74.3286 | -3.4626 | Day | 202601 | 2026-01-13 | 3.4626
2026-01-13 14:10 | 72.3758 | FALSE | TRUE | -0.053155 | -0.073496 | -2.0033 | -2.6933 | 0.5634 |  | 2026-01-13 12:43 | none | FALSE | 2 | 72.3226 | FALSE | FALSE | 0.5836 | 1.836 | 73.3509 | 9 | 0.5634 | -0.05652 | 0.39495 | 1.5696 | 0.51411 | Confirmed/Materialized Shift | 74.3791 | -1.8966 | Day | 202601 | 2026-01-13 | 1.8966
2026-01-13 14:25 | 72.6584 | FALSE | TRUE | -0.40883 | -0.56586 | -1.7372 | -2.3351 | 0.2826 |  | 2026-01-13 12:43 | none | FALSE | 2 | 72.2496 | FALSE | FALSE | 0.5397 | 1.7762 | 73.3226 | 10 | 0.2826 | -0.02826 | 0.39813 | 0.78079 | 0.53652 | Confirmed/Materialized Shift | 74.3956 | -1.238 | Day | 202601 | 2026-01-13 | 1.238
2026-01-13 14:40 | 73.2236 | FALSE | FALSE | -0.97403 | -1.3482 | -1.172 | -1.5754 | 0.5652 |  |  | none | FALSE | 2 | 72.2496 | FALSE | FALSE | 0.0694 |  | 73.3226 | 0 | 0.5652 | 0 | 0.41972 | 1.3466 | 0.53652 | Persistence ends | 74.3956 | -0.18452 | Day | 202601 | 2026-01-13 | 0.18452
2026-01-13 14:43 | 73.2236 | FALSE | FALSE | -0.97403 | -1.3482 | -1.172 | -1.5754 | 0 |  |  | none | FALSE | 2 | 72.2496 | FALSE | FALSE | 0.0694 |  | 73.3226 | 0 | 0 | 0 | 0.41972 | 0 | 0.53652 | Normal | 74.3956 | -0.18452 | Day | 202601 | 2026-01-13 | 0.18452
2026-01-13 14:58 | 73.2236 | FALSE | FALSE | -0.97403 | -1.3482 | -1.172 | -1.5754 | 0 |  |  | none | FALSE | 2 | 72.2496 | FALSE | FALSE | 0.0694 |  | 73.3226 | 0 | 0 | 0 | 0.41972 | 0 | 0.53652 | Normal | 74.3956 | -0.18452 | Day | 202601 | 2026-01-13 | 0.18452
2026-01-13 15:13 | 73.2236 | FALSE | FALSE | -0.97403 | -1.3482 | -1.172 | -1.5754 | 0 |  |  | none | FALSE | 2 | 72.2496 | FALSE | FALSE | 0.0694 |  | 73.3226 | 0 | 0 | 0 | 0.41972 | 0 | 0.53652 | Normal | 74.3956 | -0.18452 | Day | 202601 | 2026-01-13 | 0.18452
2026-01-13 15:28 | 73.5062 | FALSE | FALSE | -1.2445 | -1.7221 | -0.90552 | -1.2169 | 0.2826 |  |  | none | FALSE | 2 | 72.2617 | FALSE | FALSE | 0.0782 |  | 73.3367 | 0 | 0.2826 | 0.01413 | 0.42445 | 0.63251 | 0.53749 | Normal | 74.4117 | 0.3153 | Day | 202601 | 2026-01-13 | 0.3153
2026-01-13 15:43 | 73.5062 | FALSE | FALSE | -1.2315 | -1.7039 | -0.92081 | -1.2372 | 0 |  |  | none | FALSE | 2 | 72.2747 | FALSE | FALSE | 0.0764 |  | 73.3509 | 0 | 0 | 0.01413 | 0.42445 | -0.03329 | 0.53808 | Normal | 74.427 | 0.2887 | Day | 202601 | 2026-01-13 | 0.2887
2026-01-13 15:58 | 73.2236 | FALSE | FALSE | -0.96186 | -1.3311 | -1.1881 | -1.5967 | -0.2826 |  |  | none | FALSE | 1 | 72.2617 | FALSE | FALSE | 0.0426 |  | 73.3367 | 0 | -0.2826 | -0.01413 | 0.42445 | -0.63251 | 0.53749 | Normal | 74.4117 | -0.21048 | Day | 202601 | 2026-01-13 | 0.21048
2026-01-13 16:13 | 73.2236 | FALSE | FALSE | -0.97403 | -1.3482 | -1.172 | -1.5754 | 0 |  |  | none | FALSE | 0 | 72.2496 | FALSE | FALSE | 0.0123 |  | 73.3226 | 0 | 0 | -0.01413 | 0.42445 | 0.03329 | 0.53652 | Normal | 74.3956 | -0.18452 | Day | 202601 | 2026-01-13 | 0.18452
2026-01-13 16:22 | 73.2236 | FALSE | FALSE | -0.98542 | -1.3641 | -1.1552 | -1.5531 | 0 |  |  | none | FALSE | 0 | 72.2382 | FALSE | FALSE | 0.0106 |  | 73.3085 | 0 | 0 | -0.01413 | 0.42445 | 0.03329 | 0.53515 | Normal | 74.3788 | -0.15859 | Day | 202601 | 2026-01-13 | 0.15859
2026-01-13 16:23 | 73.2236 | FALSE | FALSE | -0.99602 | -1.379 | -1.1375 | -1.5297 | 0 |  |  | none | FALSE | 0 | 72.2276 | FALSE | FALSE | 0.0088 |  | 73.2943 | 0 | 0 | -0.01413 | 0.42445 | 0.03329 | 0.53338 | Normal | 74.3611 | -0.13263 | Day | 202601 | 2026-01-13 | 0.13263
2026-01-13 16:38 | 73.5062 | FALSE | FALSE | -1.2725 | -1.7616 | -0.82048 | -1.1039 | 0.2826 |  |  | none | FALSE | 0 | 72.2337 | FALSE | FALSE | 0.0288 |  | 73.2802 | 0 | 0.2826 | -0.01413 | 0.42445 | 0.69909 | 0.52324 | Normal | 74.3267 | 0.43191 | Day | 202601 | 2026-01-13 | 0.43191
2026-01-13 16:53 | 73.7888 | FALSE | FALSE | -1.5551 | -2.1528 | -0.53788 | -0.72368 | 0.2826 |  |  | none | FALSE | 0 | 72.2337 | FALSE | FALSE | 0.0648 |  | 73.2802 | 0 | 0.2826 | 0 | 0.42962 | 0.6578 | 0.52324 | Normal | 74.3267 | 0.97201 | Day | 202601 | 2026-01-13 | 0.97201
2026-01-13 17:08 | 73.7888 | FALSE | FALSE | -1.5551 | -2.1528 | -0.53788 | -0.72368 | 0 |  |  | none | FALSE | 0 | 72.2337 | FALSE | FALSE | 0.0648 |  | 73.2802 | 0 | 0 | 0 | 0.42962 | 0 | 0.52324 | Normal | 74.3267 | 0.97201 | Day | 202601 | 2026-01-13 | 0.97201
2026-01-13 17:22 | 73.7888 | FALSE | FALSE | -1.5551 | -2.1528 | -0.53788 | -0.72368 | 0 |  |  | none | FALSE | 0 | 72.2337 | FALSE | FALSE | 0.0648 |  | 73.2802 | 0 | 0 | 0 | 0.42962 | 0 | 0.52324 | Normal | 74.3267 | 0.97201 | Day | 202601 | 2026-01-13 | 0.97201
2026-01-13 17:37 | 73.7888 | FALSE | FALSE | -1.5312 | -2.119 | -0.48571 | -0.65394 | 0 |  |  | none | FALSE | 0 | 72.2576 | FALSE | FALSE | 0.0691 |  | 73.2661 | 0 | 0 | -0.01413 | 0.42445 | 0.03329 | 0.50422 | Normal | 74.2745 | 1.0367 | Day | 202601 | 2026-01-13 | 1.0367
2026-01-13 17:52 | 73.5062 | FALSE | FALSE | -1.2395 | -1.7152 | -0.731 | -0.98468 | -0.2826 |  |  | none | FALSE | 0 | 72.2667 | FALSE | FALSE | 0.0344 |  | 73.2519 | 0 | -0.2826 | -0.01413 | 0.42445 | -0.63251 | 0.49262 | Normal | 74.2372 | 0.51611 | Night | 202601 | 2026-01-13 | 0.51611
2026-01-13 18:07 | 73.5062 | FALSE | FALSE | -1.2317 | -1.7043 | -0.7515 | -1.012 | 0 |  |  | none | FALSE | 0 | 72.2745 | FALSE | FALSE | 0.0323 |  | 73.2661 | 0 | 0 | 0.01413 | 0.40416 | -0.034962 | 0.49581 | Normal | 74.2577 | 0.4843 | Night | 202601 | 2026-01-13 | 0.4843
2026-01-13 18:22 | 73.2236 | FALSE | FALSE | -0.60658 | -0.83531 | -0.83266 | -1.1244 | -0.2826 |  |  | none | FALSE | 0 | 72.617 | FALSE | FALSE | 0.0209 |  | 73.3366 | 0 | -0.2826 | 0.07056 | 0.24021 | -1.4702 | 0.35981 | Normal | 74.0563 | -0.31417 | Night | 202601 | 2026-01-13 | 0.31417
2026-01-13 18:37 | 73.2236 | FALSE | FALSE | -0.40903 | -0.56174 | -0.71989 | -0.97356 | 0 |  |  | none | FALSE | 0 | 72.8146 | FALSE | FALSE | 0.0367 |  | 73.379 | 0 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.28223 | Normal | 73.9435 | -0.55073 | Night | 202601 | 2026-01-13 | 0.55073
2026-01-13 18:37 | 73.2236 | FALSE | FALSE | -0.27566 | -0.37789 | -0.64304 | -0.87055 | 0 |  |  | none | FALSE | 0 | 72.9479 | FALSE | FALSE | 0.0533 |  | 73.4073 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.22968 | Normal | 73.8666 | -0.79978 | Night | 202601 | 2026-01-13 | 0.79978
2026-01-13 18:38 | 73.2236 | FALSE | FALSE | -0.27566 | -0.37789 | -0.64304 | -0.87055 | 0 |  |  | none | FALSE | 0 | 72.9479 | FALSE | FALSE | 0.0533 |  | 73.4073 | 0 | 0 | 0 | 0.15881 | 0 | 0.22968 | Normal | 73.8666 | -0.79978 | Night | 202601 | 2026-01-13 | 0.79978
2026-01-13 18:53 | 73.7888 | TRUE | FALSE | -0.83406 | -1.1433 | -0.12756 | -0.17258 | 0.5652 |  |  | none | FALSE | 1 | 72.9547 | FALSE | FALSE | 0.1265 |  | 73.4356 | 0 | 0.5652 | 0.02826 | 0.20296 | 2.6456 | 0.24041 | Normal | 73.9164 | 1.4694 | Night | 202601 | 2026-01-13 | 1.4694
2026-01-13 19:08 | 73.7888 | FALSE | FALSE | -0.81959 | -1.1232 | -0.16961 | -0.22934 | 0 |  |  | none | FALSE | 1 | 72.9692 | FALSE | FALSE | 0.1162 |  | 73.4638 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.2473 | Normal | 73.9584 | 1.3141 | Night | 202601 | 2026-01-13 | 1.3141
2026-01-13 19:23 | 73.7888 | FALSE | FALSE | -0.79809 | -1.0934 | -0.20463 | -0.27655 | 0 |  |  | none | FALSE | 1 | 72.9907 | FALSE | FALSE | 0.1075 |  | 73.4921 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.25068 | Normal | 73.9934 | 1.1837 | Night | 202601 | 2026-01-13 | 1.1837
2026-01-13 19:37 | 73.7888 | FALSE | FALSE | -0.80126 | -1.0978 | -0.23606 | -0.3189 | 0 |  |  | none | FALSE | 1 | 72.9875 | FALSE | FALSE | 0.1012 |  | 73.5062 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.25933 | Normal | 74.0249 | 1.0897 | Night | 202601 | 2026-01-13 | 1.0897
2026-01-13 19:52 | 73.7888 | FALSE | FALSE | -0.80231 | -1.0993 | -0.26537 | -0.35834 | 0 |  |  | none | FALSE | 1 | 72.9865 | FALSE | FALSE | 0.0956 |  | 73.5203 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.26692 | Normal | 74.0542 | 1.0058 | Night | 202601 | 2026-01-13 | 1.0058
2026-01-13 20:07 | 73.7888 | FALSE | FALSE | -0.76771 | -1.0514 | -0.28729 | -0.38783 | 0 |  |  | none | FALSE | 1 | 73.0211 | FALSE | FALSE | 0.0893 |  | 73.5486 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.26375 | Normal | 74.0761 | 0.91074 | Night | 202601 | 2026-01-13 | 0.91074
2026-01-13 20:22 | 73.7888 | FALSE | FALSE | -0.72655 | -0.99442 | -0.30265 | -0.40848 | 0 |  |  | none | FALSE | 1 | 73.0623 | FALSE | FALSE | 0.0835 |  | 73.5768 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.2573 | Normal | 74.0914 | 0.82375 | Night | 202601 | 2026-01-13 | 0.82375
2026-01-13 20:36 | 73.7888 | FALSE | FALSE | -0.67829 | -0.92776 | -0.31091 | -0.41959 | 0 |  |  | none | FALSE | 1 | 73.1105 | FALSE | FALSE | 0.0781 |  | 73.6051 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.2473 | Normal | 74.0997 | 0.74278 | Night | 202601 | 2026-01-13 | 0.74278
2026-01-13 20:51 | 73.7888 | FALSE | FALSE | -0.62205 | -0.85018 | -0.31119 | -0.41996 | 0 |  |  | none | FALSE | 1 | 73.1668 | FALSE | FALSE | 0.073 |  | 73.6334 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.23331 | Normal | 74.1 | 0.6662 | Night | 202601 | 2026-01-13 | 0.6662
2026-01-13 21:06 | 73.7888 | FALSE | FALSE | -0.60882 | -0.83194 | -0.32622 | -0.44015 | 0 |  |  | none | FALSE | 1 | 73.18 | FALSE | FALSE | 0.0689 |  | 73.6475 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.23376 | Normal | 74.115 | 0.60447 | Night | 202601 | 2026-01-13 | 0.60447
2026-01-13 21:21 | 73.7888 | FALSE | FALSE | -0.60882 | -0.83194 | -0.32622 | -0.44015 | 0 |  |  | none | FALSE | 0 | 73.18 | FALSE | FALSE | 0.0403 |  | 73.6475 | 0 | 0 | 0 | 0.15881 | 0 | 0.23376 | Normal | 74.115 | 0.60447 | Night | 202601 | 2026-01-13 | 0.60447
2026-01-13 21:36 | 73.7888 | FALSE | FALSE | -0.60882 | -0.83194 | -0.32622 | -0.44015 | 0 |  |  | none | FALSE | 0 | 73.18 | FALSE | FALSE | 0.0403 |  | 73.6475 | 0 | 0 | 0 | 0.15881 | 0 | 0.23376 | Normal | 74.115 | 0.60447 | Night | 202601 | 2026-01-13 | 0.60447
2026-01-13 21:51 | 73.7888 | FALSE | FALSE | -0.60882 | -0.83194 | -0.32622 | -0.44015 | 0 |  |  | none | FALSE | 0 | 73.18 | FALSE | FALSE | 0.0403 |  | 73.6475 | 0 | 0 | 0 | 0.15881 | 0 | 0.23376 | Normal | 74.115 | 0.60447 | Night | 202601 | 2026-01-13 | 0.60447
2026-01-13 22:06 | 73.7888 | FALSE | FALSE | -0.60882 | -0.83194 | -0.32622 | -0.44015 | 0 |  |  | none | FALSE | 0 | 73.18 | FALSE | FALSE | 0.0403 |  | 73.6475 | 0 | 0 | 0 | 0.15881 | 0 | 0.23376 | Normal | 74.115 | 0.60447 | Night | 202601 | 2026-01-13 | 0.60447
2026-01-13 22:21 | 73.7888 | FALSE | FALSE | -0.59379 | -0.81124 | -0.33945 | -0.45792 | 0 |  |  | none | FALSE | 0 | 73.195 | FALSE | FALSE | 0.0363 |  | 73.6616 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.23331 | Normal | 74.1282 | 0.54507 | Night | 202601 | 2026-01-13 | 0.54507
2026-01-13 22:36 | 73.7888 | FALSE | FALSE | -0.57695 | -0.78805 | -0.35087 | -0.47325 | 0 |  |  | none | FALSE | 0 | 73.2119 | FALSE | FALSE | 0.0325 |  | 73.6758 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.23195 | Normal | 74.1397 | 0.48734 | Night | 202601 | 2026-01-13 | 0.48734
2026-01-13 22:51 | 73.7888 | FALSE | FALSE | -0.4989 | -0.68072 | -0.32934 | -0.44434 | 0 |  |  | none | FALSE | 0 | 73.2899 | FALSE | FALSE | 0.0273 |  | 73.704 | 0 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.20706 | Normal | 74.1181 | 0.40945 | Night | 202601 | 2026-01-13 | 0.40945
2026-01-13 23:06 | 73.7888 | FALSE | FALSE | -0.40445 | -0.55114 | -0.29141 | -0.39337 | 0 |  |  | none | FALSE | 0 | 73.3844 | FALSE | FALSE | 0.0217 |  | 73.7323 | 0 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.17396 | Normal | 74.0802 | 0.32489 | Night | 202601 | 2026-01-13 | 0.32489
2026-01-13 23:21 | 73.7888 | FALSE | FALSE | -0.28103 | -0.38231 | -0.22451 | -0.30333 | 0 |  |  | none | FALSE | 0 | 73.5078 | FALSE | FALSE | 0.0149 |  | 73.7605 | 0 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.12638 | Normal | 74.0133 | 0.22361 | Night | 202601 | 2026-01-13 | 0.22361
2026-01-13 23:35 | 73.7888 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.7888 | FALSE | FALSE | 0 |  | 73.7888 | 0 | 0 | 0.02826 | 0.12638 | -0.22361 | 0 | Normal | 73.7888 |  | Night | 202601 | 2026-01-13
2026-01-13 23:50 | 73.7888 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.7888 | FALSE | FALSE | 0 |  | 73.7888 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.7888 |  | Night | 202601 | 2026-01-13
2026-01-14 00:05 | 73.7888 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.7888 | FALSE | FALSE | 0 |  | 73.7888 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.7888 |  | Night | 202601 | 2026-01-14
2026-01-14 00:20 | 73.7888 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.7888 | FALSE | FALSE | 0 |  | 73.7888 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.7888 |  | Night | 202601 | 2026-01-14
2026-01-14 00:35 | 73.7888 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.7888 | FALSE | FALSE | 0 |  | 73.7888 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.7888 |  | Night | 202601 | 2026-01-14
2026-01-14 00:50 | 73.5062 | TRUE | FALSE | 0.14209 | 0.19293 | -0.39485 | -0.5343 | -0.2826 | 2026-01-14 01:05 | 2026-01-14 00:50 | lower | TRUE | 1 | 73.6483 | FALSE | FALSE | 0.3689 | 4.2485 | 73.7747 | 1 | -0.2826 | -0.01413 | 0.063191 | -4.2485 | 0.063191 | Extreme triggered | 73.9011 | -4.2485 | Night | 202601 | 2026-01-14 | 4.2485
2026-01-14 01:05 | 73.7888 | TRUE | FALSE | -0.14051 | -0.19079 | -0.11225 | -0.1519 | 0.2826 |  |  | none | FALSE | 2 | 73.6483 | TRUE | FALSE | 0.072 |  | 73.7747 | 0 | 0.2826 | 0 | 0.091688 | 3.0822 | 0.063191 | Persistence ends | 73.9011 | 0.22361 | Night | 202601 | 2026-01-14 | 0.22361
2026-01-14 01:20 | 73.7888 | FALSE | FALSE | -0.14051 | -0.19079 | -0.11225 | -0.1519 | 0 |  |  | none | FALSE | 2 | 73.6483 | FALSE | FALSE | 0.072 |  | 73.7747 | 0 | 0 | 0 | 0.091688 | 0 | 0.063191 | Normal | 73.9011 | 0.22361 | Night | 202601 | 2026-01-14 | 0.22361
2026-01-14 01:35 | 73.7888 | FALSE | FALSE | -0.14051 | -0.19079 | -0.11225 | -0.1519 | 0 |  |  | none | FALSE | 2 | 73.6483 | FALSE | FALSE | 0.072 |  | 73.7747 | 0 | 0 | 0 | 0.091688 | 0 | 0.063191 | Normal | 73.9011 | 0.22361 | Night | 202601 | 2026-01-14 | 0.22361
2026-01-14 01:50 | 73.5062 | TRUE | FALSE | 0.080375 | 0.10923 | -0.4283 | -0.5793 | -0.2826 | 2026-01-14 03:49 | 2026-01-14 01:50 | lower | TRUE | 3 | 73.5866 | TRUE | FALSE | 0.3378 | 2.924 | 73.7605 | 1 | -0.2826 | -0.01413 | 0.11135 | -2.411 | 0.086982 | Extreme triggered | 73.9345 | -2.924 | Night | 202601 | 2026-01-14 | 2.924
2026-01-14 02:05 | 73.5062 | FALSE | FALSE | 0.03315 | 0.045078 | -0.44727 | -0.6048 | 0 |  | 2026-01-14 01:50 | lower | TRUE | 3 | 73.5394 | FALSE | FALSE | 0.3547 | 2.6221 | 73.7464 | 2 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.10353 | Extreme/elevated | 73.9535 | -2.3202 | Night | 202601 | 2026-01-14 | 2.3202
2026-01-14 02:20 | 73.5062 | FALSE | FALSE | -0.0058732 | -0.0079907 | -0.45803 | -0.61926 | 0 |  | 2026-01-14 01:50 | none | FALSE | 3 | 73.5003 | FALSE | FALSE | 0.3871 | 2.3979 | 73.7323 | 3 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.11598 | Persistent | 73.9642 | -1.9494 | Night | 202601 | 2026-01-14 | 1.9494
2026-01-14 02:34 | 73.5062 | FALSE | FALSE | -0.039147 | -0.053285 | -0.46305 | -0.626 | 0 |  | 2026-01-14 01:50 | none | FALSE | 3 | 73.4671 | FALSE | FALSE | 0.4268 | 2.2204 | 73.7181 | 4 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.12555 | Persistent | 73.9692 | -1.6882 | Night | 202601 | 2026-01-14 | 1.6882
2026-01-14 02:49 | 73.5062 | FALSE | FALSE | -0.067916 | -0.09248 | -0.46356 | -0.62668 | 0 |  | 2026-01-14 01:50 | none | FALSE | 3 | 73.4383 | FALSE | FALSE | 0.4707 | 2.0741 | 73.704 | 5 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13287 | Persistent | 73.9698 | -1.4888 | Night | 202601 | 2026-01-14 | 1.4888
2026-01-14 03:05 | 73.5062 | FALSE | FALSE | -0.092897 | -0.12654 | -0.46028 | -0.62228 | 0 |  | 2026-01-14 01:50 | none | FALSE | 3 | 73.4133 | FALSE | FALSE | 0.5171 | 1.9498 | 73.6899 | 6 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13829 | Persistent | 73.9665 | -1.3283 | Night | 202601 | 2026-01-14 | 1.3283
2026-01-14 03:20 | 73.5062 | FALSE | TRUE | -0.11452 | -0.15604 | -0.45364 | -0.61336 | 0 |  | 2026-01-14 01:50 | none | FALSE | 2 | 73.3917 | FALSE | FALSE | 0.5367 | 1.8418 | 73.6758 | 7 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14204 | Confirmed/Materialized Shift | 73.9598 | -1.1937 | Night | 202601 | 2026-01-14 | 1.1937
2026-01-14 03:34 | 73.5062 | FALSE | TRUE | -0.13306 | -0.18134 | -0.44392 | -0.60029 | 0 |  | 2026-01-14 01:50 | none | FALSE | 1 | 73.3731 | FALSE | FALSE | 0.5004 | 1.7463 | 73.6616 | 8 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14424 | Confirmed/Materialized Shift | 73.9501 | -1.0775 | Night | 202601 | 2026-01-14 | 1.0775
2026-01-14 03:49 | 73.5062 | FALSE | FALSE | -0.14864 | -0.20263 | -0.43124 | -0.58325 | 0 |  |  | none | FALSE | 1 | 73.3576 | FALSE | FALSE | 0.0936 |  | 73.6475 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14497 | Persistence ends | 73.9374 | -0.97468 | Night | 202601 | 2026-01-14 | 0.97468
2026-01-14 04:04 | 73.5062 | FALSE | FALSE | -0.16132 | -0.21994 | -0.41566 | -0.56229 | 0 |  |  | none | FALSE | 1 | 73.3449 | FALSE | FALSE | 0.0873 |  | 73.6334 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14424 | Normal | 73.9219 | -0.88163 | Night | 202601 | 2026-01-14 | 0.88163
2026-01-14 04:19 | 73.2236 | TRUE | FALSE | 0.049657 | 0.067769 | -0.71336 | -0.96483 | -0.2826 | 2026-01-14 05:49 | 2026-01-14 04:19 | lower | TRUE | 1 | 73.2733 | FALSE | FALSE | 0.239 | 2.2993 | 73.6051 | 1 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.16593 | Extreme triggered | 73.937 | -2.2993 | Night | 202601 | 2026-01-14 | 2.2993
2026-01-14 04:34 | 73.2236 | FALSE | FALSE | -0.0077242 | -0.01055 | -0.71422 | -0.96598 | 0 |  | 2026-01-14 04:19 | none | FALSE | 1 | 73.2159 | FALSE | FALSE | 0.2733 | 2.1282 | 73.5768 | 2 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.18049 | Extreme/elevated | 73.9378 | -1.9572 | Night | 202601 | 2026-01-14 | 1.9572
2026-01-14 04:49 | 73.2236 | FALSE | FALSE | -0.054158 | -0.074017 | -0.70414 | -0.95247 | 0 |  | 2026-01-14 04:19 | none | FALSE | 1 | 73.1694 | FALSE | FALSE | 0.3143 | 1.9903 | 73.5486 | 3 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.18957 | Persistent | 73.9277 | -1.7143 | Night | 202601 | 2026-01-14 | 1.7143
2026-01-14 05:04 | 73.2236 | FALSE | FALSE | -0.091185 | -0.12469 | -0.68465 | -0.92634 | 0 |  | 2026-01-14 04:19 | none | FALSE | 1 | 73.1324 | FALSE | FALSE | 0.3591 | 1.8752 | 73.5203 | 4 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.19396 | Persistent | 73.9082 | -1.5299 | Night | 202601 | 2026-01-14 | 1.5299
2026-01-14 05:19 | 73.2236 | FALSE | FALSE | -0.11945 | -0.16339 | -0.65639 | -0.88845 | 0 |  | 2026-01-14 04:19 | none | FALSE | 1 | 73.1042 | FALSE | FALSE | 0.4066 | 1.777 | 73.4921 | 5 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.19396 | Persistent | 73.88 | -1.3842 | Night | 202601 | 2026-01-14 | 1.3842
2026-01-14 05:33 | 73.2236 | FALSE | FALSE | -0.13894 | -0.19011 | -0.61936 | -0.83875 | 0 |  | 2026-01-14 04:19 | none | FALSE | 1 | 73.0847 | FALSE | FALSE | 0.4559 | 1.692 | 73.4638 | 6 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.18957 | Persistent | 73.843 | -1.2671 | Night | 202601 | 2026-01-14 | 1.2671
2026-01-14 05:49 | 73.5062 | TRUE | FALSE | -0.42154 | -0.57678 | -0.33676 | -0.45605 | 0.2826 |  |  | none | FALSE | 2 | 73.0847 | TRUE | FALSE | 0.072 |  | 73.4638 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.18957 | Persistence ends | 73.843 | 0.22361 | Night | 202601 | 2026-01-14 | 0.22361
2026-01-14 06:04 | 73.2236 | TRUE | FALSE | -0.14902 | -0.20393 | -0.57292 | -0.77636 | -0.2826 |  |  | none | FALSE | 3 | 73.0746 | TRUE | FALSE | 0.164 |  | 73.4356 | 0 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.18049 | Normal | 73.7965 | -1.1743 | Night | 202601 | 2026-01-14 | 1.1743
2026-01-14 06:19 | 73.2236 | FALSE | FALSE | -0.14816 | -0.20275 | -0.51554 | -0.69914 | 0 |  |  | none | FALSE | 3 | 73.0754 | FALSE | FALSE | 0.1595 |  | 73.4073 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.16593 | Normal | 73.7391 | -1.1071 | Night | 202601 | 2026-01-14 | 1.1071
2026-01-14 06:33 | 73.2236 | FALSE | FALSE | -0.13306 | -0.18205 | -0.44392 | -0.6026 | 0 |  |  | none | FALSE | 3 | 73.0905 | FALSE | FALSE | 0.1576 |  | 73.379 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.14424 | Normal | 73.6675 | -1.0775 | Night | 202601 | 2026-01-14 | 1.0775
2026-01-14 06:48 | 73.2236 | FALSE | FALSE | -0.14864 | -0.20341 | -0.43124 | -0.58549 | 0 |  |  | none | FALSE | 2 | 73.075 | FALSE | FALSE | 0.1221 |  | 73.3649 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14497 | Normal | 73.6548 | -0.97468 | Night | 202601 | 2026-01-14 | 0.97468
2026-01-14 07:03 | 73.2236 | FALSE | FALSE | -0.16132 | -0.2208 | -0.41566 | -0.56445 | 0 |  |  | none | FALSE | 2 | 73.0623 | FALSE | FALSE | 0.1159 |  | 73.3508 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14424 | Normal | 73.6393 | -0.88163 | Night | 202601 | 2026-01-14 | 0.88163
2026-01-14 07:18 | 73.2236 | FALSE | FALSE | -0.17104 | -0.23414 | -0.39712 | -0.53942 | 0 |  |  | none | FALSE | 2 | 73.0526 | FALSE | FALSE | 0.1102 |  | 73.3366 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14204 | Normal | 73.6207 | -0.79582 | Day | 202601 | 2026-01-14 | 0.79582
2026-01-14 07:30 | 73.2236 | FALSE | FALSE | -0.17768 | -0.24324 | -0.3755 | -0.51019 | 0 |  |  | none | FALSE | 2 | 73.0459 | FALSE | FALSE | 0.1048 |  | 73.3225 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13829 | Normal | 73.5991 | -0.71522 | Day | 202601 | 2026-01-14 | 0.71522
2026-01-14 07:45 | 73.2236 | FALSE | FALSE | -0.18096 | -0.24774 | -0.35052 | -0.47641 | 0 |  |  | none | FALSE | 2 | 73.0426 | FALSE | FALSE | 0.0997 |  | 73.3084 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13287 | Normal | 73.5741 | -0.63808 | Day | 202601 | 2026-01-14 | 0.63808
2026-01-14 08:00 | 73.2236 | FALSE | FALSE | -0.18045 | -0.24704 | -0.32175 | -0.43748 | 0 |  |  | none | FALSE | 2 | 73.0432 | FALSE | FALSE | 0.0947 |  | 73.2943 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.12555 | Normal | 73.5453 | -0.56273 | Day | 202601 | 2026-01-14 | 0.56273
2026-01-14 08:15 | 73.2236 | FALSE | FALSE | -0.17543 | -0.24016 | -0.28847 | -0.39242 | 0 |  |  | none | FALSE | 1 | 73.0482 | FALSE | FALSE | 0.0611 |  | 73.2801 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.11598 | Normal | 73.5121 | -0.48734 | Day | 202601 | 2026-01-14 | 0.48734
2026-01-14 08:30 | 73.2236 | FALSE | FALSE | -0.16467 | -0.22539 | -0.24945 | -0.33951 | 0 |  |  | none | FALSE | 0 | 73.0589 | FALSE | FALSE | 0.0273 |  | 73.266 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.10353 | Normal | 73.473 | -0.40945 | Day | 202601 | 2026-01-14 | 0.40945
2026-01-14 08:45 | 73.2236 | FALSE | FALSE | -0.1457 | -0.19938 | -0.20222 | -0.27541 | 0 |  |  | none | FALSE | 0 | 73.0779 | FALSE | FALSE | 0.0217 |  | 73.2519 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.086982 | Normal | 73.4258 | -0.32489 | Day | 202601 | 2026-01-14 | 0.32489
2026-01-14 08:45 | 73.2236 | FALSE | FALSE | -0.11225 | -0.15354 | -0.14051 | -0.19153 | 0 |  |  | none | FALSE | 0 | 73.1113 | FALSE | FALSE | 0.0149 |  | 73.2377 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.063191 | Normal | 73.3641 | -0.22361 | Day | 202601 | 2026-01-14 | 0.22361
2026-01-14 09:00 | 73.5062 | TRUE | FALSE | -0.4283 | -0.58609 | 0.080375 | 0.10946 | 0.2826 | 2026-01-14 10:30 | 2026-01-14 09:00 | upper | TRUE | 1 | 73.0779 | FALSE | FALSE | 0.2807 | 2.924 | 73.2519 | 1 | 0.2826 | 0.01413 | 0.11135 | 2.411 | 0.086982 | Extreme triggered | 73.4258 | 2.924 | Day | 202601 | 2026-01-14 | 2.924
2026-01-14 09:15 | 73.5062 | FALSE | FALSE | -0.44727 | -0.6122 | 0.03315 | 0.045119 | 0 |  | 2026-01-14 09:00 | upper | TRUE | 1 | 73.0589 | FALSE | FALSE | 0.2975 | 2.6221 | 73.266 | 2 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.10353 | Extreme/elevated | 73.473 | 2.3202 | Day | 202601 | 2026-01-14 | 2.3202
2026-01-14 09:30 | 73.5062 | FALSE | FALSE | -0.45803 | -0.62703 | -0.0058732 | -0.0079894 | 0 |  | 2026-01-14 09:00 | none | FALSE | 1 | 73.0482 | FALSE | FALSE | 0.33 | 2.3979 | 73.2801 | 3 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.11598 | Persistent | 73.5121 | 1.9494 | Day | 202601 | 2026-01-14 | 1.9494
2026-01-14 09:44 | 73.5062 | FALSE | FALSE | -0.46305 | -0.63394 | -0.039147 | -0.053228 | 0 |  | 2026-01-14 09:00 | none | FALSE | 1 | 73.0432 | FALSE | FALSE | 0.3697 | 2.2204 | 73.2943 | 4 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.12555 | Persistent | 73.5453 | 1.6882 | Day | 202601 | 2026-01-14 | 1.6882
2026-01-14 09:59 | 73.5062 | FALSE | FALSE | -0.46356 | -0.63464 | -0.067916 | -0.092309 | 0 |  | 2026-01-14 09:00 | none | FALSE | 1 | 73.0426 | FALSE | FALSE | 0.4135 | 2.0741 | 73.3084 | 5 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.13287 | Persistent | 73.5741 | 1.4888 | Day | 202601 | 2026-01-14 | 1.4888
2026-01-14 10:14 | 73.5062 | FALSE | FALSE | -0.46028 | -0.63012 | -0.092897 | -0.12622 | 0 |  | 2026-01-14 09:00 | none | FALSE | 1 | 73.0459 | FALSE | FALSE | 0.46 | 1.9498 | 73.3225 | 6 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.13829 | Persistent | 73.5991 | 1.3283 | Day | 202601 | 2026-01-14 | 1.3283
2026-01-14 10:30 | 73.2236 | TRUE | FALSE | -0.18096 | -0.24774 | -0.35052 | -0.47641 | -0.2826 |  |  | none | FALSE | 2 | 73.0426 | TRUE | FALSE | 0.0997 |  | 73.3084 | 0 | -0.2826 | -0.01413 | 0.11135 | -2.411 | 0.13287 | Persistence ends | 73.5741 | -0.63808 | Day | 202601 | 2026-01-14 | 0.63808
2026-01-14 10:44 | 72.6584 | TRUE | FALSE | 0.22842 | 0.3134 | -1.015 | -1.3777 | -0.5652 | 2026-01-14 11:14 | 2026-01-14 10:44 | lower | TRUE | 3 | 72.8868 | TRUE | FALSE | 0.3536 | 3.1616 | 73.2801 | 1 | -0.5652 | -0.02826 | 0.15614 | -3.4389 | 0.19665 | Extreme triggered | 73.6734 | -3.1616 | Day | 202601 | 2026-01-14 | 3.1616
2026-01-14 10:59 | 72.3758 | FALSE | FALSE | 0.29747 | 0.40933 | -1.4264 | -1.9327 | -0.2826 |  | 2026-01-14 10:44 | lower | TRUE | 3 | 72.6733 | FALSE | FALSE | 0.4036 | 3.1078 | 73.2377 | 2 | -0.2826 | -0.04239 | 0.16593 | -1.4477 | 0.28223 | Extreme/elevated | 73.8022 | -3.054 | Day | 202601 | 2026-01-14 | 3.054
2026-01-14 11:14 | 72.941 | TRUE | FALSE | -0.29728 | -0.40923 | -0.86248 | -1.1686 | 0.5652 |  |  | none | FALSE | 4 | 72.6437 | TRUE | FALSE | 0.1793 |  | 73.2236 | 0 | 0.5652 | -0.01413 | 0.21454 | 2.7004 | 0.28994 | Persistence ends | 73.8035 | -0.97468 | Day | 202601 | 2026-01-14 | 0.97468
2026-01-14 11:29 | 72.941 | FALSE | FALSE | -0.32503 | -0.44759 | -0.86197 | -1.1679 | 0 |  |  | none | FALSE | 3 | 72.616 | FALSE | FALSE | 0.146 |  | 73.2095 | 0 | 0 | -0.01413 | 0.21454 | 0.065863 | 0.29675 | Normal | 73.803 | -0.90471 | Day | 202601 | 2026-01-14 | 0.90471
2026-01-14 11:44 | 73.2236 | FALSE | FALSE | -0.60763 | -0.83677 | -0.57937 | -0.78502 | 0.2826 |  |  | none | FALSE | 3 | 72.616 | FALSE | FALSE | 0.0889 |  | 73.2095 | 0 | 0.2826 | 0 | 0.22459 | 1.2583 | 0.29675 | Normal | 73.803 | 0.047616 | Day | 202601 | 2026-01-14 | 0.047616
2026-01-14 11:59 | 73.2236 | FALSE | FALSE | -0.60763 | -0.83677 | -0.57937 | -0.78502 | 0 |  |  | none | FALSE | 3 | 72.616 | FALSE | FALSE | 0.0889 |  | 73.2095 | 0 | 0 | 0 | 0.22459 | 0 | 0.29675 | Normal | 73.803 | 0.047616 | Day | 202601 | 2026-01-14 | 0.047616
2026-01-14 12:14 | 73.2236 | FALSE | FALSE | -0.60763 | -0.83677 | -0.57937 | -0.78502 | 0 |  |  | none | FALSE | 3 | 72.616 | FALSE | FALSE | 0.0889 |  | 73.2095 | 0 | 0 | 0 | 0.22459 | 0 | 0.29675 | Normal | 73.803 | 0.047616 | Day | 202601 | 2026-01-14 | 0.047616
2026-01-14 12:29 | 73.2236 | FALSE | FALSE | -0.60763 | -0.83677 | -0.57937 | -0.78502 | 0 |  |  | none | FALSE | 3 | 72.616 | FALSE | FALSE | 0.0889 |  | 73.2095 | 0 | 0 | 0 | 0.22459 | 0 | 0.29675 | Normal | 73.803 | 0.047616 | Day | 202601 | 2026-01-14 | 0.047616
2026-01-14 12:43 | 73.2236 | FALSE | FALSE | -0.60763 | -0.83677 | -0.57937 | -0.78502 | 0 |  |  | none | FALSE | 3 | 72.616 | FALSE | FALSE | 0.0889 |  | 73.2095 | 0 | 0 | 0 | 0.22459 | 0 | 0.29675 | Normal | 73.803 | 0.047616 | Day | 202601 | 2026-01-14 | 0.047616
2026-01-14 12:58 | 72.941 | FALSE | FALSE | -0.35108 | -0.48364 | -0.85976 | -1.165 | -0.2826 |  |  | none | FALSE | 2 | 72.5899 | FALSE | FALSE | 0.1132 |  | 73.1953 | 0 | -0.2826 | -0.01413 | 0.23331 | -1.1507 | 0.30271 | Normal | 73.8008 | -0.84022 | Day | 202601 | 2026-01-14 | 0.84022
2026-01-14 13:14 | 72.941 | FALSE | FALSE | -0.37553 | -0.51751 | -0.85595 | -1.1599 | 0 |  |  | none | FALSE | 1 | 72.5655 | FALSE | FALSE | 0.0806 |  | 73.1812 | 0 | 0 | -0.01413 | 0.23331 | 0.060564 | 0.30787 | Normal | 73.797 | -0.78023 | Day | 202601 | 2026-01-14 | 0.78023
2026-01-14 13:29 | 73.2236 | FALSE | FALSE | -0.65813 | -0.90695 | -0.57335 | -0.77693 | 0.2826 |  |  | none | FALSE | 1 | 72.5655 | FALSE | FALSE | 0.0378 |  | 73.1812 | 0 | 0.2826 | 0 | 0.24258 | 1.165 | 0.30787 | Normal | 73.797 | 0.13769 | Day | 202601 | 2026-01-14 | 0.13769
2026-01-14 13:43 | 73.5062 | FALSE | FALSE | -0.94344 | -1.3002 | -0.32172 | -0.43577 | 0.2826 |  |  | none | FALSE | 0 | 72.5628 | FALSE | FALSE | 0.0655 |  | 73.1953 | 0 | 0.2826 | 0.01413 | 0.25068 | 1.071 | 0.31629 | Normal | 73.8279 | 0.98284 | Day | 202601 | 2026-01-14 | 0.98284
2026-01-14 13:43 | 73.5062 | FALSE | FALSE | -0.94344 | -1.3002 | -0.32172 | -0.43577 | 0 |  |  | none | FALSE | 0 | 72.5628 | FALSE | FALSE | 0.0655 |  | 73.1953 | 0 | 0 | 0 | 0.24258 | 0 | 0.31629 | Normal | 73.8279 | 0.98284 | Day | 202601 | 2026-01-14 | 0.98284
2026-01-14 13:46 | 73.5062 | FALSE | FALSE | -0.94344 | -1.3002 | -0.32172 | -0.43577 | 0 |  |  | none | FALSE | 0 | 72.5628 | FALSE | FALSE | 0.0655 |  | 73.1953 | 0 | 0 | 0 | 0.24258 | 0 | 0.31629 | Normal | 73.8279 | 0.98284 | Day | 202601 | 2026-01-14 | 0.98284
2026-01-14 14:01 | 72.941 | FALSE | FALSE | -0.39847 | -0.5493 | -0.85063 | -1.1528 | -0.5652 |  |  | none | FALSE | 0 | 72.5425 | FALSE | FALSE | 0.0483 |  | 73.1671 | 0 | -0.5652 | -0.02826 | 0.27353 | -1.963 | 0.31228 | Normal | 73.7916 | -0.72397 | Day | 202601 | 2026-01-14 | 0.72397
2026-01-14 14:11 | 72.941 | FALSE | FALSE | -0.41312 | -0.56961 | -0.80876 | -1.0966 | 0 |  |  | none | FALSE | 0 | 72.5279 | FALSE | FALSE | 0.0432 |  | 73.1388 | 0 | 0 | -0.02826 | 0.27353 | 0.10332 | 0.30547 | Normal | 73.7498 | -0.64759 | Day | 202601 | 2026-01-14 | 0.64759
2026-01-14 14:12 | 72.941 | FALSE | FALSE | -0.42181 | -0.58165 | -0.76093 | -1.0324 | 0 |  |  | none | FALSE | 0 | 72.5192 | FALSE | FALSE | 0.0382 |  | 73.1106 | 0 | 0 | -0.02826 | 0.27353 | 0.10332 | 0.29568 | Normal | 73.7019 | -0.57345 | Day | 202601 | 2026-01-14 | 0.57345
2026-01-14 14:27 | 72.941 | FALSE | FALSE | -0.4239 | -0.58455 | -0.7065 | -0.9593 | 0 |  |  | none | FALSE | 0 | 72.5171 | FALSE | FALSE | 0.0333 |  | 73.0823 | 0 | 0 | -0.02826 | 0.27353 | 0.10332 | 0.2826 | Normal | 73.6475 | -0.5 | Day | 202601 | 2026-01-14 | 0.5
2026-01-14 14:42 | 72.941 | FALSE | FALSE | -0.43729 | -0.60312 | -0.69163 | -0.93929 | 0 |  |  | none | FALSE | 0 | 72.5037 | FALSE | FALSE | 0.03 |  | 73.0682 | 0 | 0 | -0.01413 | 0.26692 | 0.052937 | 0.28223 | Normal | 73.6326 | -0.45059 | Day | 202601 | 2026-01-14 | 0.45059
2026-01-14 14:57 | 72.941 | FALSE | FALSE | -0.39333 | -0.54216 | -0.67593 | -0.91817 | 0 |  |  | none | FALSE | 0 | 72.5477 | FALSE | FALSE | 0.0352 |  | 73.0823 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.26731 | Normal | 73.6169 | -0.52859 | Day | 202601 | 2026-01-14 | 0.52859
2026-01-14 15:11 | 72.6584 | FALSE | FALSE | -0.028587 | -0.039359 | -0.90465 | -1.2298 | -0.2826 |  |  | none | FALSE | 0 | 72.6298 | FALSE | FALSE | 0.1252 |  | 73.0964 | 0 | -0.2826 | 0.01413 | 0.23331 | -1.2718 | 0.23331 | Normal | 73.563 | -1.8775 | Day | 202601 | 2026-01-14 | 1.8775
2026-01-14 15:26 | 72.6584 | FALSE | FALSE | -0.078293 | -0.10787 | -0.92609 | -1.2585 | 0 |  |  | none | FALSE | 0 | 72.5801 | FALSE | FALSE | 0.1125 |  | 73.0823 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.2511 | Normal | 73.5845 | -1.6882 | Day | 202601 | 2026-01-14 | 1.6882
2026-01-14 15:41 | 72.3758 | FALSE | FALSE | 0.086873 | 0.11989 | -1.2696 | -1.7239 | -0.2826 | 2026-01-14 16:26 | 2026-01-14 15:41 | lower | TRUE | 0 | 72.4627 | FALSE | FALSE | 0.2101 | 2.2938 | 73.054 | 1 | -0.2826 | -0.02826 | 0.20296 | -1.2532 | 0.29568 | Extreme triggered | 73.6454 | -2.2938 | Day | 202601 | 2026-01-14 | 2.2938
2026-01-14 15:56 | 72.3758 | FALSE | FALSE | -0.022132 | -0.030589 | -1.2938 | -1.7563 | 0 |  | 2026-01-14 15:41 | none | FALSE | 0 | 72.3537 | FALSE | FALSE | 0.2431 | 2.1133 | 73.0117 | 2 | 0 | -0.04239 | 0.18957 | 0.22361 | 0.32899 | Extreme/elevated | 73.6696 | -1.9327 | Day | 202601 | 2026-01-14 | 1.9327
2026-01-14 16:11 | 72.3758 | FALSE | FALSE | -0.11438 | -0.15828 | -1.3013 | -1.7662 | 0 |  | 2026-01-14 15:41 | none | FALSE | 0 | 72.2614 | FALSE | FALSE | 0.2832 | 1.9678 | 72.9693 | 3 | 0 | -0.04239 | 0.18957 | 0.22361 | 0.35392 | Persistent | 73.6771 | -1.6768 | Day | 202601 | 2026-01-14 | 1.6768
2026-01-14 16:26 | 72.941 | TRUE | FALSE | -0.68354 | -0.94598 | -0.7118 | -0.96643 | 0.5652 |  |  | none | FALSE | 1 | 72.2575 | FALSE | FALSE | 0.0313 |  | 72.9551 | 0 | 0.5652 | -0.01413 | 0.23331 | 2.4831 | 0.34883 | Persistence ends | 73.6528 | -0.040506 | Day | 202601 | 2026-01-14 | 0.040506
2026-01-14 16:41 | 73.2236 | FALSE | FALSE | -0.96614 | -1.3371 | -0.4292 | -0.58273 | 0.2826 |  |  | none | FALSE | 1 | 72.2575 | FALSE | FALSE | 0.0799 |  | 72.9551 | 0 | 0.2826 | 0 | 0.24258 | 1.165 | 0.34883 | Normal | 73.6528 | 0.76962 | Day | 202601 | 2026-01-14 | 0.76962
2026-01-14 16:56 | 73.2236 | FALSE | FALSE | -0.96614 | -1.3371 | -0.4292 | -0.58273 | 0 |  |  | none | FALSE | 1 | 72.2575 | FALSE | FALSE | 0.0799 |  | 72.9551 | 0 | 0 | 0 | 0.24258 | 0 | 0.34883 | Normal | 73.6528 | 0.76962 | Day | 202601 | 2026-01-14 | 0.76962
2026-01-14 17:11 | 73.2236 | FALSE | FALSE | -0.96218 | -1.3315 | -0.4535 | -0.61552 | 0 |  |  | none | FALSE | 1 | 72.2614 | FALSE | FALSE | 0.0765 |  | 72.9693 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.35392 | Normal | 73.6771 | 0.71864 | Day | 202601 | 2026-01-14 | 0.71864
2026-01-14 17:26 | 73.2236 | FALSE | FALSE | -0.9569 | -1.3241 | -0.47648 | -0.64651 | 0 |  |  | none | FALSE | 1 | 72.2667 | FALSE | FALSE | 0.0733 |  | 72.9834 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.35834 | Normal | 73.7001 | 0.67033 | Day | 202601 | 2026-01-14 | 0.67033
2026-01-14 17:41 | 73.2236 | FALSE | FALSE | -0.9569 | -1.3241 | -0.47648 | -0.64651 | 0 |  |  | none | FALSE | 1 | 72.2667 | FALSE | FALSE | 0.0733 |  | 72.9834 | 0 | 0 | 0 | 0.22459 | 0 | 0.35834 | Normal | 73.7001 | 0.67033 | Day | 202601 | 2026-01-14 | 0.67033
2026-01-14 17:56 | 72.941 | FALSE | FALSE | -0.65901 | -0.91172 | -0.68727 | -0.93343 | -0.2826 |  |  | none | FALSE | 1 | 72.282 | FALSE | FALSE | 0.0314 |  | 72.9551 | 0 | -0.2826 | -0.02826 | 0.22271 | -1.142 | 0.33657 | Normal | 73.6283 | -0.041982 | Night | 202601 | 2026-01-14 | 0.041982
2026-01-14 18:10 | 72.941 | FALSE | FALSE | -0.63531 | -0.87864 | -0.60705 | -0.82538 | 0 |  |  | none | FALSE | 1 | 72.3057 | FALSE | FALSE | 0.0316 |  | 72.9269 | 0 | 0 | -0.02826 | 0.22271 | 0.12689 | 0.31059 | Normal | 73.548 | 0.045494 | Night | 202601 | 2026-01-14 | 0.045494
2026-01-14 18:25 | 72.941 | FALSE | FALSE | -0.60086 | -0.8306 | -0.51608 | -0.70256 | 0 |  |  | none | FALSE | 1 | 72.3401 | FALSE | FALSE | 0.0387 |  | 72.8986 | 0 | 0 | -0.02826 | 0.22271 | 0.12689 | 0.27923 | Normal | 73.4571 | 0.15181 | Night | 202601 | 2026-01-14 | 0.15181
2026-01-14 18:40 | 72.941 | FALSE | FALSE | -0.60086 | -0.8306 | -0.51608 | -0.70256 | 0 |  |  | none | FALSE | 1 | 72.3401 | FALSE | FALSE | 0.0387 |  | 72.8986 | 0 | 0 | 0 | 0.18338 | 0 | 0.27923 | Normal | 73.4571 | 0.15181 | Night | 202601 | 2026-01-14 | 0.15181
2026-01-14 18:41 | 72.941 | FALSE | FALSE | -0.60086 | -0.8306 | -0.51608 | -0.70256 | 0 |  |  | none | FALSE | 0 | 72.3401 | FALSE | FALSE | 0.0101 |  | 72.8986 | 0 | 0 | 0 | 0.18338 | 0 | 0.27923 | Normal | 73.4571 | 0.15181 | Night | 202601 | 2026-01-14 | 0.15181
2026-01-14 18:41 | 72.941 | FALSE | FALSE | -0.60086 | -0.8306 | -0.51608 | -0.70256 | 0 |  |  | none | FALSE | 0 | 72.3401 | FALSE | FALSE | 0.0101 |  | 72.8986 | 0 | 0 | 0 | 0.18338 | 0 | 0.27923 | Normal | 73.4571 | 0.15181 | Night | 202601 | 2026-01-14 | 0.15181
2026-01-14 18:56 | 73.2236 | FALSE | FALSE | -0.88784 | -1.2274 | -0.26612 | -0.36211 | 0.2826 |  |  | none | FALSE | 0 | 72.3358 | FALSE | FALSE | 0.0718 |  | 72.9127 | 0 | 0.2826 | 0.01413 | 0.19396 | 1.3842 | 0.28849 | Normal | 73.4897 | 1.0775 | Night | 202601 | 2026-01-14 | 1.0775
2026-01-14 19:11 | 73.2236 | FALSE | FALSE | -0.89023 | -1.2307 | -0.29677 | -0.40365 | 0 |  |  | none | FALSE | 0 | 72.3334 | FALSE | FALSE | 0.0667 |  | 72.9269 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.29675 | Normal | 73.5204 | 0.99994 | Night | 202601 | 2026-01-14 | 0.99994
2026-01-14 19:26 | 73.2236 | FALSE | FALSE | -0.89079 | -1.2315 | -0.32559 | -0.44268 | 0 |  |  | none | FALSE | 0 | 72.3328 | FALSE | FALSE | 0.062 |  | 72.941 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.30409 | Normal | 73.5492 | 0.92932 | Night | 202601 | 2026-01-14 | 0.92932
2026-01-14 19:40 | 73.2236 | FALSE | FALSE | -0.85976 | -1.1881 | -0.35108 | -0.47717 | 0 |  |  | none | FALSE | 0 | 72.3638 | FALSE | FALSE | 0.056 |  | 72.9693 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.30271 | Normal | 73.5747 | 0.84022 | Night | 202601 | 2026-01-14 | 0.84022
2026-01-14 19:55 | 73.2236 | FALSE | FALSE | -0.82311 | -1.1369 | -0.37095 | -0.50404 | 0 |  |  | none | FALSE | 0 | 72.4005 | FALSE | FALSE | 0.0505 |  | 72.9975 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.29851 | Normal | 73.5945 | 0.75735 | Night | 202601 | 2026-01-14 | 0.75735
2026-01-14 20:10 | 73.2236 | FALSE | FALSE | -0.71119 | -0.98079 | -0.34381 | -0.46734 | 0 |  |  | none | FALSE | 0 | 72.5124 | FALSE | FALSE | 0.0464 |  | 73.0399 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.26375 | Normal | 73.5674 | 0.69645 | Night | 202601 | 2026-01-14 | 0.69645
2026-01-14 20:25 | 73.2236 | FALSE | FALSE | -0.57135 | -0.78642 | -0.28875 | -0.39279 | 0 |  |  | none | FALSE | 0 | 72.6522 | FALSE | FALSE | 0.0438 |  | 73.0823 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.21503 | Normal | 73.5124 | 0.65713 | Night | 202601 | 2026-01-14 | 0.65713
2026-01-14 20:40 | 73.2236 | FALSE | FALSE | -0.3755 | -0.51545 | -0.17768 | -0.24206 | 0 |  |  | none | FALSE | 0 | 72.8481 | FALSE | FALSE | 0.0477 |  | 73.1247 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.13829 | Normal | 73.4013 | 0.71522 | Night | 202601 | 2026-01-14 | 0.71522
2026-01-14 20:55 | 72.941 | TRUE | FALSE | -0.092897 | -0.12752 | -0.46028 | -0.62707 | -0.2826 |  |  | none | FALSE | 1 | 72.8481 | FALSE | FALSE | 0.1171 |  | 73.1247 | 0 | -0.2826 | 0 | 0.12967 | -2.1794 | 0.13829 | Normal | 73.4013 | -1.3283 | Night | 202601 | 2026-01-14 | 1.3283
2026-01-14 21:10 | 72.941 | FALSE | FALSE | -0.11452 | -0.15726 | -0.45364 | -0.61809 | 0 |  |  | none | FALSE | 1 | 72.8265 | FALSE | FALSE | 0.1082 |  | 73.1106 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14204 | Normal | 73.3946 | -1.1937 | Night | 202601 | 2026-01-14 | 1.1937
2026-01-14 21:25 | 72.941 | FALSE | FALSE | -0.13306 | -0.18275 | -0.44392 | -0.60492 | 0 |  |  | none | FALSE | 1 | 72.8079 | FALSE | FALSE | 0.1004 |  | 73.0964 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14424 | Normal | 73.3849 | -1.0775 | Night | 202601 | 2026-01-14 | 1.0775
2026-01-14 21:39 | 72.941 | FALSE | FALSE | -0.14864 | -0.2042 | -0.43124 | -0.58774 | 0 |  |  | none | FALSE | 1 | 72.7924 | FALSE | FALSE | 0.0936 |  | 73.0823 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14497 | Normal | 73.3722 | -0.97468 | Night | 202601 | 2026-01-14 | 0.97468
2026-01-14 21:55 | 72.941 | FALSE | FALSE | -0.16132 | -0.22165 | -0.41566 | -0.56663 | 0 |  |  | none | FALSE | 1 | 72.7797 | FALSE | FALSE | 0.0873 |  | 73.0682 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14424 | Normal | 73.3567 | -0.88163 | Night | 202601 | 2026-01-14 | 0.88163
2026-01-14 22:10 | 72.941 | FALSE | FALSE | -0.17104 | -0.23505 | -0.39712 | -0.5415 | 0 |  |  | none | FALSE | 1 | 72.77 | FALSE | FALSE | 0.0816 |  | 73.054 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14204 | Normal | 73.3381 | -0.79582 | Night | 202601 | 2026-01-14 | 0.79582
2026-01-14 22:25 | 72.941 | FALSE | FALSE | -0.17104 | -0.23505 | -0.39712 | -0.5415 | 0 |  |  | none | FALSE | 1 | 72.77 | FALSE | FALSE | 0.0816 |  | 73.054 | 0 | 0 | 0 | 0.091688 | 0 | 0.14204 | Normal | 73.3381 | -0.79582 | Night | 202601 | 2026-01-14 | 0.79582
2026-01-14 22:39 | 72.941 | FALSE | FALSE | -0.17104 | -0.23505 | -0.39712 | -0.5415 | 0 |  |  | none | FALSE | 1 | 72.77 | FALSE | FALSE | 0.0816 |  | 73.054 | 0 | 0 | 0 | 0.091688 | 0 | 0.14204 | Normal | 73.3381 | -0.79582 | Night | 202601 | 2026-01-14 | 0.79582
2026-01-14 22:54 | 72.941 | FALSE | FALSE | -0.17104 | -0.23505 | -0.39712 | -0.5415 | 0 |  |  | none | FALSE | 1 | 72.77 | FALSE | FALSE | 0.0816 |  | 73.054 | 0 | 0 | 0 | 0.091688 | 0 | 0.14204 | Normal | 73.3381 | -0.79582 | Night | 202601 | 2026-01-14 | 0.79582
2026-01-14 23:09 | 72.6584 | TRUE | FALSE | 0.049657 | 0.068296 | -0.71336 | -0.97226 | -0.2826 | 2026-01-15 04:23 | 2026-01-14 23:09 | lower | TRUE | 2 | 72.7081 | TRUE | FALSE | 0.2676 | 2.2993 | 73.0399 | 1 | -0.2826 | -0.01413 | 0.11135 | -2.411 | 0.16593 | Extreme triggered | 73.3718 | -2.2993 | Night | 202601 | 2026-01-14 | 2.2993
2026-01-14 23:24 | 72.6584 | FALSE | FALSE | -0.0039263 | -0.005404 | -0.73869 | -1.0064 | 0 |  | 2026-01-14 23:09 | none | FALSE | 1 | 72.6545 | FALSE | FALSE | 0.2748 | 2.1391 | 73.0258 | 2 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.18565 | Extreme/elevated | 73.3971 | -1.9789 | Night | 202601 | 2026-01-14 | 1.9789
2026-01-14 23:39 | 72.6584 | FALSE | FALSE | -0.051631 | -0.071111 | -0.75813 | -1.0326 | 0 |  | 2026-01-14 23:09 | none | FALSE | 1 | 72.6068 | FALSE | FALSE | 0.3163 | 2.0077 | 73.0117 | 3 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.20244 | Persistent | 73.4165 | -1.745 | Night | 202601 | 2026-01-14 | 1.745
2026-01-14 23:54 | 72.6584 | FALSE | FALSE | -0.096174 | -0.13254 | -0.74615 | -1.0165 | 0 |  | 2026-01-14 23:09 | none | FALSE | 1 | 72.5622 | FALSE | FALSE | 0.36 | 1.8916 | 72.9834 | 4 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21058 | Persistent | 73.4046 | -1.5433 | Night | 202601 | 2026-01-14 | 1.5433
2026-01-15 00:09 | 72.6584 | FALSE | FALSE | -0.13234 | -0.18248 | -0.7258 | -0.98905 | 0 |  | 2026-01-14 23:09 | none | FALSE | 1 | 72.5261 | FALSE | FALSE | 0.4065 | 1.7899 | 72.9551 | 5 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21454 | Persistent | 73.3842 | -1.3831 | Night | 202601 | 2026-01-15 | 1.3831
2026-01-15 00:24 | 72.3758 | TRUE | FALSE | 0.055253 | 0.076284 | -1.0186 | -1.3879 | -0.2826 |  | 2026-01-14 23:09 | lower | TRUE | 2 | 72.4311 | TRUE | TRUE | 0.5486 | 1.8632 | 72.9127 | 6 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.24084 | Persistent | 73.3944 | -2.2294 | Night | 202601 | 2026-01-15 | 2.2294
2026-01-15 00:39 | 72.3758 | FALSE | TRUE | -0.020045 | -0.027704 | -1.0091 | -1.3751 | 0 |  | 2026-01-14 23:09 | none | FALSE | 2 | 72.3558 | FALSE | FALSE | 0.5853 | 1.8716 | 72.8704 | 7 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.2573 | Confirmed/Materialized Shift | 73.3849 | -1.9221 | Night | 202601 | 2026-01-15 | 1.9221
2026-01-15 00:54 | 72.3758 | FALSE | TRUE | -0.079312 | -0.1097 | -0.98363 | -1.3408 | 0 |  | 2026-01-14 23:09 | none | FALSE | 2 | 72.2965 | FALSE | FALSE | 0.5706 | 1.8503 | 72.828 | 8 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.26574 | Confirmed/Materialized Shift | 73.3594 | -1.7015 | Night | 202601 | 2026-01-15 | 1.7015
2026-01-15 01:09 | 72.3758 | FALSE | TRUE | -0.12407 | -0.17172 | -0.94361 | -1.287 | 0 |  | 2026-01-14 23:09 | none | FALSE | 2 | 72.2517 | FALSE | FALSE | 0.5595 | 1.8153 | 72.7856 | 9 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.26692 | Confirmed/Materialized Shift | 73.3194 | -1.5352 | Night | 202601 | 2026-01-15 | 1.5352
2026-01-15 01:24 | 72.3758 | FALSE | TRUE | -0.15451 | -0.21395 | -0.88927 | -1.2138 | 0 |  | 2026-01-14 23:09 | none | FALSE | 2 | 72.2213 | FALSE | FALSE | 0.551 | 1.7746 | 72.7432 | 10 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.26095 | Confirmed/Materialized Shift | 73.2651 | -1.4079 | Night | 202601 | 2026-01-15 | 1.4079
2026-01-15 01:38 | 72.3758 | FALSE | TRUE | -0.16961 | -0.2349 | -0.81959 | -1.1197 | 0 |  | 2026-01-14 23:09 | none | FALSE | 1 | 72.2062 | FALSE | FALSE | 0.5162 | 1.7327 | 72.7008 | 11 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.2473 | Confirmed/Materialized Shift | 73.1954 | -1.3141 | Night | 202601 | 2026-01-15 | 1.3141
2026-01-15 01:53 | 72.3758 | FALSE | TRUE | -0.20463 | -0.28353 | -0.79809 | -1.0907 | 0 |  | 2026-01-14 23:09 | none | FALSE | 1 | 72.1712 | FALSE | FALSE | 0.5075 | 1.687 | 72.6725 | 12 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.25068 | Confirmed/Materialized Shift | 73.1739 | -1.1837 | Night | 202601 | 2026-01-15 | 1.1837
2026-01-15 02:08 | 72.3758 | FALSE | TRUE | -0.23289 | -0.32281 | -0.76983 | -1.0525 | 0 |  | 2026-01-14 23:09 | none | FALSE | 1 | 72.1429 | FALSE | FALSE | 0.5 | 1.6396 | 72.6443 | 13 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.25068 | Confirmed/Materialized Shift | 73.1456 | -1.071 | Night | 202601 | 2026-01-15 | 1.071
2026-01-15 02:23 | 72.095 | TRUE | TRUE | -0.030433 | -0.042231 | -1.0444 | -1.4279 | -0.2808 |  | 2026-01-14 23:09 | none | FALSE | 2 | 72.0646 | TRUE | FALSE | 0.5829 | 1.6572 | 72.602 | 14 | -0.2808 | -0.0423 | 0.10331 | -2.3086 | 0.2687 | Confirmed/Materialized Shift | 73.1394 | -1.8867 | Night | 202601 | 2026-01-15 | 1.8867
2026-01-15 02:38 | 72.095 | FALSE | TRUE | -0.093165 | -0.12939 | -1.0225 | -1.3984 | 0 |  | 2026-01-14 23:09 | none | FALSE | 2 | 72.0018 | FALSE | FALSE | 0.5682 | 1.6578 | 72.5597 | 15 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.27892 | Confirmed/Materialized Shift | 73.1175 | -1.666 | Night | 202601 | 2026-01-15 | 1.666
2026-01-15 02:53 | 72.095 | FALSE | TRUE | -0.14198 | -0.19732 | -0.98672 | -1.3502 | 0 |  | 2026-01-14 23:09 | none | FALSE | 1 | 71.953 | FALSE | FALSE | 0.5284 | 1.6477 | 72.5174 | 16 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.28217 | Confirmed/Materialized Shift | 73.0817 | -1.4968 | Night | 202601 | 2026-01-15 | 1.4968
2026-01-15 03:08 | 72.095 | FALSE | TRUE | -0.17736 | -0.24662 | -0.9375 | -1.2837 | 0 |  | 2026-01-14 23:09 | none | FALSE | 1 | 71.9176 | FALSE | FALSE | 0.5195 | 1.631 | 72.4751 | 17 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.27872 | Confirmed/Materialized Shift | 73.0325 | -1.3636 | Night | 202601 | 2026-01-15 | 1.3636
2026-01-15 03:23 | 72.095 | FALSE | TRUE | -0.1988 | -0.27651 | -0.87434 | -1.1982 | 0 |  | 2026-01-14 23:09 | none | FALSE | 1 | 71.8962 | FALSE | FALSE | 0.5125 | 1.6104 | 72.4328 | 18 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.26828 | Confirmed/Materialized Shift | 72.9693 | -1.259 | Night | 202601 | 2026-01-15 | 1.259
2026-01-15 03:38 | 72.095 | FALSE | TRUE | -0.20454 | -0.28452 | -0.79548 | -1.0913 | 0 |  | 2026-01-14 23:09 | none | FALSE | 1 | 71.8905 | FALSE | FALSE | 0.5074 | 1.5878 | 72.3905 | 19 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.25001 | Confirmed/Materialized Shift | 72.8905 | -1.1819 | Night | 202601 | 2026-01-15 | 1.1819
2026-01-15 03:53 | 72.095 | FALSE | TRUE | -0.19073 | -0.26526 | -0.69707 | -0.95762 | 0 |  | 2026-01-14 23:09 | none | FALSE | 1 | 71.9043 | FALSE | FALSE | 0.5046 | 1.5655 | 72.3482 | 20 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.22195 | Confirmed/Materialized Shift | 72.7921 | -1.1407 | Night | 202601 | 2026-01-15 | 1.1407
2026-01-15 04:08 | 72.095 | FALSE | TRUE | -0.20737 | -0.28846 | -0.65737 | -0.90357 | 0 |  | 2026-01-14 23:09 | none | FALSE | 1 | 71.8876 | FALSE | FALSE | 0.498 | 1.5405 | 72.32 | 21 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.21618 | Confirmed/Materialized Shift | 72.7524 | -1.0408 | Night | 202601 | 2026-01-15 | 1.0408
2026-01-15 04:23 | 72.095 | FALSE | FALSE | -0.21566 | -0.30003 | -0.60932 | -0.83808 | 0 |  |  | none | FALSE | 1 | 71.8793 | FALSE | FALSE | 0.0922 |  | 72.2918 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.20625 | Persistence ends | 72.7043 | -0.95435 | Night | 202601 | 2026-01-15 | 0.95435
2026-01-15 04:37 | 72.095 | FALSE | FALSE | -0.21432 | -0.29816 | -0.55164 | -0.75935 | 0 |  |  | none | FALSE | 1 | 71.8807 | FALSE | FALSE | 0.0873 |  | 72.2637 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.19149 | Normal | 72.6466 | -0.88077 | Night | 202601 | 2026-01-15 | 0.88077
2026-01-15 04:52 | 71.8124 | TRUE | FALSE | 0.022686 | 0.031581 | -0.79523 | -1.0952 | -0.2826 | 2026-01-15 05:07 | 2026-01-15 04:52 | lower | TRUE | 1 | 71.8351 | FALSE | FALSE | 0.2269 | 2.1175 | 72.2214 | 1 | -0.2826 | -0.0423 | 0.10331 | -2.326 | 0.19314 | Extreme triggered | 72.6076 | -2.1175 | Night | 202601 | 2026-01-15 | 2.1175
2026-01-15 05:07 | 72.095 | TRUE | FALSE | -0.23199 | -0.32282 | -0.42837 | -0.59066 | 0.2826 |  |  | none | FALSE | 2 | 71.863 | TRUE | FALSE | 0.0968 |  | 72.1932 | 0 | 0.2826 | -0.02817 | 0.12619 | 2.4627 | 0.16509 | Persistence ends | 72.5234 | -0.59477 | Night | 202601 | 2026-01-15 | 0.59477
2026-01-15 05:22 | 72.095 | FALSE | FALSE | -0.23709 | -0.32994 | -0.40539 | -0.55916 | 0 |  |  | none | FALSE | 2 | 71.8579 | FALSE | FALSE | 0.0921 |  | 72.1792 | 0 | 0 | -0.01404 | 0.11113 | 0.12634 | 0.16062 | Normal | 72.5004 | -0.52391 | Night | 202601 | 2026-01-15 | 0.52391
2026-01-15 05:37 | 72.095 | FALSE | FALSE | -0.23927 | -0.33298 | -0.37949 | -0.52362 | 0 |  |  | none | FALSE | 2 | 71.8557 | FALSE | FALSE | 0.0874 |  | 72.1651 | 0 | 0 | -0.01404 | 0.11113 | 0.12634 | 0.15469 | Normal | 72.4745 | -0.45323 | Night | 202601 | 2026-01-15 | 0.45323
2026-01-15 05:52 | 71.8124 | TRUE | FALSE | -0.0059427 | -0.008276 | -0.65502 | -0.90389 | -0.2826 |  |  | none | FALSE | 3 | 71.8065 | TRUE | FALSE | 0.2167 |  | 72.1369 | 0 | -0.2826 | -0.02817 | 0.12619 | -2.0162 | 0.16524 | Normal | 72.4674 | -1.964 | Night | 202601 | 2026-01-15 | 1.964
2026-01-15 06:07 | 71.8124 | FALSE | FALSE | -0.044277 | -0.061694 | -0.63702 | -0.87926 | 0 |  |  | none | FALSE | 3 | 71.7681 | FALSE | FALSE | 0.2017 |  | 72.1088 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.17032 | Normal | 72.4494 | -1.74 | Night | 202601 | 2026-01-15 | 1.74
2026-01-15 06:22 | 71.8124 | FALSE | FALSE | -0.07265 | -0.10127 | -0.60905 | -0.84098 | 0 |  |  | none | FALSE | 3 | 71.7397 | FALSE | FALSE | 0.1906 |  | 72.0806 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.17043 | Normal | 72.4215 | -1.5737 | Night | 202601 | 2026-01-15 | 1.5737
2026-01-15 06:37 | 71.8124 | FALSE | FALSE | -0.091082 | -0.12699 | -0.57114 | -0.78905 | 0 |  |  | none | FALSE | 3 | 71.7213 | FALSE | FALSE | 0.1824 |  | 72.0524 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.16556 | Normal | 72.3835 | -1.4498 | Night | 202601 | 2026-01-15 | 1.4498
2026-01-15 06:52 | 71.8124 | FALSE | FALSE | -0.098638 | -0.13754 | -0.52236 | -0.72214 | 0 |  |  | none | FALSE | 3 | 71.7138 | FALSE | FALSE | 0.1767 |  | 72.0243 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.15525 | Normal | 72.3348 | -1.3646 | Night | 202601 | 2026-01-15 | 1.3646
2026-01-15 07:07 | 71.8124 | FALSE | FALSE | -0.092897 | -0.12953 | -0.46028 | -0.63686 | 0 |  |  | none | FALSE | 3 | 71.7195 | FALSE | FALSE | 0.1743 |  | 71.9961 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.13829 | Normal | 72.2727 | -1.3283 | Night | 202601 | 2026-01-15 | 1.3283
2026-01-15 07:22 | 71.8124 | FALSE | FALSE | -0.11452 | -0.15973 | -0.45364 | -0.62774 | 0 |  |  | none | FALSE | 2 | 71.6979 | FALSE | FALSE | 0.1367 |  | 71.982 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14204 | Normal | 72.266 | -1.1937 | Day | 202601 | 2026-01-15 | 1.1937
2026-01-15 07:30 | 71.8124 | FALSE | FALSE | -0.13306 | -0.18563 | -0.44392 | -0.61437 | 0 |  |  | none | FALSE | 1 | 71.6793 | FALSE | FALSE | 0.1004 |  | 71.9678 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14424 | Normal | 72.2563 | -1.0775 | Day | 202601 | 2026-01-15 | 1.0775
2026-01-15 07:45 | 71.8124 | FALSE | FALSE | -0.14864 | -0.20742 | -0.43124 | -0.59693 | 0 |  |  | none | FALSE | 1 | 71.6638 | FALSE | FALSE | 0.0936 |  | 71.9537 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14497 | Normal | 72.2436 | -0.97468 | Day | 202601 | 2026-01-15 | 0.97468
2026-01-15 08:00 | 71.8124 | FALSE | FALSE | -0.16132 | -0.22514 | -0.41566 | -0.57548 | 0 |  |  | none | FALSE | 1 | 71.6511 | FALSE | FALSE | 0.0873 |  | 71.9396 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14424 | Normal | 72.2281 | -0.88163 | Day | 202601 | 2026-01-15 | 0.88163
2026-01-15 08:15 | 71.8124 | FALSE | FALSE | -0.17104 | -0.23875 | -0.39712 | -0.54996 | 0 |  |  | none | FALSE | 0 | 71.6414 | FALSE | FALSE | 0.0531 |  | 71.9254 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14204 | Normal | 72.2095 | -0.79582 | Day | 202601 | 2026-01-15 | 0.79582
2026-01-15 08:30 | 71.5298 | TRUE | FALSE | 0.044515 | 0.062194 | -0.69025 | -0.95575 | -0.2826 | 2026-01-15 08:45 | 2026-01-15 08:30 | lower | TRUE | 1 | 71.5743 | FALSE | FALSE | 0.2374 | 2.2757 | 71.8972 | 1 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.16143 | Extreme triggered | 72.22 | -2.2757 | Day | 202601 | 2026-01-15 | 2.2757
2026-01-15 08:45 | 71.8124 | TRUE | FALSE | -0.24028 | -0.33571 | -0.38158 | -0.52854 | 0.2826 |  |  | none | FALSE | 2 | 71.5721 | TRUE | FALSE | 0.0874 |  | 71.883 | 0 | 0.2826 | -0.01413 | 0.14424 | 2.0571 | 0.15546 | Persistence ends | 72.194 | -0.45445 | Day | 202601 | 2026-01-15 | 0.45445
2026-01-15 08:45 | 71.8124 | FALSE | FALSE | -0.23916 | -0.33415 | -0.3522 | -0.48806 | 0 |  |  | none | FALSE | 2 | 71.5732 | FALSE | FALSE | 0.0826 |  | 71.8689 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.14784 | Normal | 72.1646 | -0.3823 | Day | 202601 | 2026-01-15 | 0.3823
2026-01-15 09:00 | 71.5298 | FALSE | FALSE | -0.0014165 | -0.0019804 | -0.62314 | -0.86363 | -0.2826 |  |  | none | FALSE | 2 | 71.5284 | FALSE | FALSE | 0.1899 |  | 71.8407 | 0 | -0.2826 | -0.02826 | 0.15614 | -1.6289 | 0.15614 | Normal | 72.1529 | -1.9909 | Day | 202601 | 2026-01-15 | 1.9909
2026-01-15 09:15 | 71.8124 | FALSE | FALSE | -0.27436 | -0.38351 | -0.30262 | -0.41963 | 0.2826 |  |  | none | FALSE | 2 | 71.538 | FALSE | FALSE | 0.0637 |  | 71.8265 | 0 | 0.2826 | -0.01413 | 0.17092 | 1.7361 | 0.14424 | Normal | 72.115 | -0.097959 | Day | 202601 | 2026-01-15 | 0.097959
2026-01-15 09:30 | 71.8124 | FALSE | FALSE | -0.27436 | -0.38351 | -0.30262 | -0.41963 | 0 |  |  | none | FALSE | 2 | 71.538 | FALSE | FALSE | 0.0637 |  | 71.8265 | 0 | 0 | 0 | 0.15881 | 0 | 0.14424 | Normal | 72.115 | -0.097959 | Day | 202601 | 2026-01-15 | 0.097959
2026-01-15 09:44 | 71.8124 | FALSE | FALSE | -0.25933 | -0.36243 | -0.25933 | -0.35982 | 0 |  |  | none | FALSE | 2 | 71.5531 | FALSE | FALSE | 0.0571 |  | 71.8124 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.12967 | Normal | 72.0717 | 0 | Day | 202601 | 2026-01-15 | 0
2026-01-15 09:59 | 71.8124 | FALSE | FALSE | -0.23684 | -0.33089 | -0.20858 | -0.28961 | 0 |  |  | none | FALSE | 2 | 71.5756 | FALSE | FALSE | 0.0656 |  | 71.7983 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.11135 | Normal | 72.021 | 0.12689 | Day | 202601 | 2026-01-15 | 0.12689
2026-01-15 10:14 | 72.095 | FALSE | FALSE | -0.51944 | -0.72572 | 0.074022 | 0.10278 | 0.2826 | 2026-01-15 12:59 | 2026-01-15 10:14 | upper | TRUE | 2 | 71.5756 | FALSE | FALSE | 0.2919 | 2.6647 | 71.7983 | 1 | 0.2826 | 0 | 0.15881 | 1.7795 | 0.11135 | Extreme triggered | 72.021 | 2.6647 | Day | 202601 | 2026-01-15 | 2.6647
2026-01-15 10:30 | 72.3758 | FALSE | FALSE | -0.89059 | -1.2458 | 0.20813 | 0.2884 | 0.2808 |  | 2026-01-15 10:14 | upper | TRUE | 2 | 71.4852 | FALSE | FALSE | 0.3861 | 2.9423 | 71.8264 | 2 | 0.2808 | 0.02817 | 0.15598 | 1.6196 | 0.17061 | Extreme/elevated | 72.1677 | 3.2199 | Day | 202601 | 2026-01-15 | 3.2199
2026-01-15 10:44 | 72.3758 | FALSE | FALSE | -0.94141 | -1.3179 | 0.10097 | 0.1397 | 0 |  | 2026-01-15 10:14 | upper | TRUE | 1 | 71.4344 | FALSE | TRUE | 0.3654 | 2.7884 | 71.8546 | 3 | 0 | 0.02817 | 0.15598 | -0.18059 | 0.21011 | Persistent | 72.2748 | 2.4805 | Day | 202601 | 2026-01-15 | 2.4805
2026-01-15 10:59 | 72.941 | TRUE | FALSE | -1.6713 | -2.345 | 0.38865 | 0.53568 | 0.5652 |  | 2026-01-15 10:14 | upper | TRUE | 1 | 71.2697 | FALSE | TRUE | 0.4713 | 2.8943 | 71.911 | 4 | 0.5652 | 0.05643 | 0.19654 | 2.5886 | 0.32065 | Persistent | 72.5523 | 3.2121 | Day | 202601 | 2026-01-15 | 3.2121
2026-01-15 11:14 | 72.941 | FALSE | FALSE | -1.7604 | -2.4731 | 0.18667 | 0.25657 | 0 |  | 2026-01-15 10:14 | upper | TRUE | 1 | 71.1806 | FALSE | TRUE | 0.4792 | 2.8103 | 71.9675 | 5 | 0 | 0.05643 | 0.19654 | -0.28712 | 0.39343 | Persistent | 72.7543 | 2.4745 | Day | 202601 | 2026-01-15 | 2.4745
2026-01-15 11:29 | 72.941 | FALSE | FALSE | -1.8116 | -2.547 | 0.022556 | 0.030933 | 0 |  | 2026-01-15 10:14 | upper | TRUE | 1 | 71.1294 | FALSE | TRUE | 0.5081 | 2.6837 | 72.0239 | 6 | 0 | 0.05643 | 0.19654 | -0.28712 | 0.44727 | Persistent | 72.9184 | 2.0504 | Day | 202601 | 2026-01-15 | 2.0504
2026-01-15 11:44 | 73.2236 | FALSE | TRUE | -2.1649 | -3.0467 | 0.093362 | 0.12767 | 0.2826 |  | 2026-01-15 10:14 | upper | TRUE | 1 | 71.0587 | FALSE | TRUE | 0.5739 | 2.6118 | 72.0945 | 7 | 0.2826 | 0.07056 | 0.20234 | 1.0479 | 0.51789 | Confirmed/Materialized Shift | 73.1302 | 2.1803 | Day | 202601 | 2026-01-15 | 2.1803
2026-01-15 11:59 | 73.5062 | FALSE | TRUE | -2.5293 | -3.5636 | 0.12477 | 0.17003 | 0.2826 |  | 2026-01-15 10:14 | upper | TRUE | 1 | 70.9769 | FALSE | TRUE | 0.5757 | 2.5612 | 72.1792 | 8 | 0.2826 | 0.08469 | 0.20697 | 0.95623 | 0.60114 | Confirmed/Materialized Shift | 73.3814 | 2.2076 | Day | 202601 | 2026-01-15 | 2.2076
2026-01-15 12:14 | 73.5062 | FALSE | TRUE | -2.5681 | -3.6203 | -0.083423 | -0.11336 | 0 |  | 2026-01-15 10:14 | none | FALSE | 1 | 70.9381 | FALSE | FALSE | 0.5535 | 2.4849 | 72.2638 | 9 | 0 | 0.08469 | 0.20697 | -0.40919 | 0.66289 | Confirmed/Materialized Shift | 73.5896 | 1.8742 | Day | 202601 | 2026-01-15 | 1.8742
2026-01-15 12:29 | 73.5062 | FALSE | TRUE | -2.5753 | -3.6306 | -0.25991 | -0.35234 | 0 |  | 2026-01-15 10:14 | none | FALSE | 1 | 70.9309 | FALSE | FALSE | 0.5375 | 2.3997 | 72.3485 | 10 | 0 | 0.08469 | 0.20697 | -0.40919 | 0.70879 | Confirmed/Materialized Shift | 73.7661 | 1.6333 | Day | 202601 | 2026-01-15 | 1.6333
2026-01-15 12:44 | 73.7888 | FALSE | TRUE | -2.8727 | -4.0508 | -0.18976 | -0.25651 | 0.2826 |  | 2026-01-15 10:14 | none | FALSE | 1 | 70.9161 | FALSE | FALSE | 0.5454 | 2.3409 | 72.4474 | 11 | 0.2826 | 0.09882 | 0.2105 | 0.87306 | 0.76561 | Confirmed/Materialized Shift | 73.9786 | 1.7521 | Day | 202601 | 2026-01-15 | 1.7521
2026-01-15 12:59 | 73.2236 | TRUE | FALSE | -2.2438 | -3.1611 | -0.83237 | -1.124 | -0.5652 |  |  | none | FALSE | 2 | 70.9798 | TRUE | FALSE | 0.1183 |  | 72.5179 | 0 | -0.5652 | 0.07056 | 0.25722 | -2.4717 | 0.76903 | Persistence ends | 74.056 | 0.91764 | Day | 202601 | 2026-01-15 | 0.91764
2026-01-15 13:14 | 72.941 | FALSE | FALSE | -1.8279 | -2.5705 | -1.1229 | -1.5161 | -0.2826 |  |  | none | FALSE | 2 | 71.1131 | FALSE | FALSE | 0.089 |  | 72.5885 | 0 | -0.2826 | 0.07056 | 0.25722 | -1.373 | 0.7377 | Normal | 74.0639 | 0.47788 | Day | 202601 | 2026-01-15 | 0.47788
2026-01-15 13:29 | 72.941 | FALSE | FALSE | -1.7323 | -2.4328 | -1.1401 | -1.539 | 0 |  |  | none | FALSE | 1 | 71.2087 | FALSE | FALSE | 0.0561 |  | 72.6449 | 0 | 0 | 0.05643 | 0.25268 | -0.22333 | 0.71812 | Normal | 74.0811 | 0.41233 | Day | 202601 | 2026-01-15 | 0.41233
2026-01-15 13:43 | 72.6584 | FALSE | FALSE | -1.353 | -1.8975 | -1.4106 | -1.9044 | -0.2826 |  |  | none | FALSE | 1 | 71.3054 | FALSE | FALSE | 0.0314 |  | 72.6872 | 0 | -0.2826 | 0.0423 | 0.26367 | -1.2322 | 0.6909 | Normal | 74.069 | -0.041685 | Day | 202601 | 2026-01-15 | 0.041685
2026-01-15 13:51 | 72.6584 | FALSE | FALSE | -1.1852 | -1.6583 | -1.3557 | -1.8317 | 0 |  |  | none | FALSE | 1 | 71.4732 | FALSE | FALSE | 0.0375 |  | 72.7436 | 0 | 0 | 0.05643 | 0.25268 | -0.22333 | 0.63524 | Normal | 74.0141 | -0.13417 | Day | 202601 | 2026-01-15 | 0.13417
2026-01-15 13:51 | 72.6584 | FALSE | FALSE | -1.0664 | -1.4896 | -1.3215 | -1.7863 | 0 |  |  | none | FALSE | 1 | 71.592 | FALSE | FALSE | 0.0428 |  | 72.7859 | 0 | 0 | 0.0423 | 0.24721 | -0.17111 | 0.59698 | Normal | 73.9799 | -0.21363 | Day | 202601 | 2026-01-15 | 0.21363
2026-01-15 13:54 | 72.6584 | FALSE | FALSE | -0.93557 | -1.3044 | -1.2752 | -1.7248 | 0 |  |  | none | FALSE | 1 | 71.7228 | FALSE | FALSE | 0.0491 |  | 72.8282 | 0 | 0 | 0.0423 | 0.24721 | -0.17111 | 0.5527 | Normal | 73.9336 | -0.30727 | Day | 202601 | 2026-01-15 | 0.30727
2026-01-15 14:02 | 71.8124 | TRUE | FALSE | -0.089568 | -0.12488 | -2.1212 | -2.8691 | -0.846 |  |  | none | FALSE | 2 | 71.7228 | TRUE | FALSE | 0.1797 |  | 72.8282 | 0 | -0.846 | 0 | 0.31728 | -2.6664 | 0.5527 | Normal | 73.9336 | -1.8379 | Day | 202601 | 2026-01-15 | 1.8379
2026-01-15 14:17 | 72.3758 | FALSE | FALSE | -0.54136 | -0.75363 | -1.5026 | -2.0338 | 0.5634 |  |  | none | FALSE | 2 | 71.8344 | FALSE | FALSE | 0.1198 |  | 72.8564 | 0 | 0.5634 | 0.02817 | 0.34137 | 1.5679 | 0.51098 | Normal | 73.8784 | -0.94054 | Day | 202601 | 2026-01-15 | 0.94054
2026-01-15 14:32 | 72.3758 | FALSE | FALSE | -0.49033 | -0.6821 | -1.4796 | -2.0034 | 0 |  |  | none | FALSE | 2 | 71.8855 | FALSE | FALSE | 0.1241 |  | 72.8704 | 0 | 0 | 0.01404 | 0.3361 | -0.041774 | 0.49248 | Normal | 73.8554 | -1.0044 | Day | 202601 | 2026-01-15 | 1.0044
2026-01-15 14:48 | 72.6584 | FALSE | FALSE | -0.73678 | -1.0244 | -1.1891 | -1.6102 | 0.2826 |  |  | none | FALSE | 1 | 71.9216 | FALSE | FALSE | 0.0599 |  | 72.8846 | 0 | 0.2826 | 0.01413 | 0.33617 | 0.79861 | 0.48148 | Normal | 73.8475 | -0.46974 | Day | 202601 | 2026-01-15 | 0.46974
2026-01-15 14:51 | 72.941 | FALSE | FALSE | -0.96096 | -1.335 | -0.90462 | -1.225 | 0.2826 |  |  | none | FALSE | 1 | 71.98 | FALSE | FALSE | 0.0326 |  | 72.9128 | 0 | 0.2826 | 0.02826 | 0.34144 | 0.74489 | 0.46639 | Normal | 73.8456 | 0.0604 | Day | 202601 | 2026-01-15 | 0.0604
2026-01-15 15:06 | 72.941 | FALSE | FALSE | -0.96096 | -1.335 | -0.90462 | -1.225 | 0 |  |  | none | FALSE | 1 | 71.98 | FALSE | FALSE | 0.0326 |  | 72.9128 | 0 | 0 | 0 | 0.31719 | 0 | 0.46639 | Normal | 73.8456 | 0.0604 | Day | 202601 | 2026-01-15 | 0.0604
2026-01-15 15:21 | 72.941 | FALSE | FALSE | -0.96096 | -1.335 | -0.90462 | -1.225 | 0 |  |  | none | FALSE | 1 | 71.98 | FALSE | FALSE | 0.0326 |  | 72.9128 | 0 | 0 | 0 | 0.31719 | 0 | 0.46639 | Normal | 73.8456 | 0.0604 | Day | 202601 | 2026-01-15 | 0.0604
2026-01-15 15:36 | 72.941 | FALSE | FALSE | -0.96096 | -1.335 | -0.90462 | -1.225 | 0 |  |  | none | FALSE | 1 | 71.98 | FALSE | FALSE | 0.0326 |  | 72.9128 | 0 | 0 | 0 | 0.31719 | 0 | 0.46639 | Normal | 73.8456 | 0.0604 | Day | 202601 | 2026-01-15 | 0.0604
2026-01-15 15:50 | 73.2236 | FALSE | FALSE | -1.2436 | -1.7276 | -0.62202 | -0.84232 | 0.2826 |  |  | none | FALSE | 1 | 71.98 | FALSE | FALSE | 0.073 |  | 72.9128 | 0 | 0.2826 | 0 | 0.31719 | 0.89094 | 0.46639 | Normal | 73.8456 | 0.66633 | Day | 202601 | 2026-01-15 | 0.66633
2026-01-15 16:05 | 73.2236 | FALSE | FALSE | -1.2279 | -1.7056 | -0.57813 | -0.78335 | 0 |  |  | none | FALSE | 1 | 71.9957 | FALSE | FALSE | 0.0765 |  | 72.8987 | 0 | 0 | -0.01413 | 0.31016 | 0.045557 | 0.45151 | Normal | 73.8017 | 0.71958 | Day | 202601 | 2026-01-15 | 0.71958
2026-01-15 16:20 | 73.2236 | FALSE | FALSE | -1.2103 | -1.6807 | -0.53226 | -0.72165 | 0 |  |  | none | FALSE | 0 | 72.0133 | FALSE | FALSE | 0.0519 |  | 72.8846 | 0 | 0 | -0.01413 | 0.31016 | 0.045557 | 0.43564 | Normal | 73.7559 | 0.77823 | Day | 202601 | 2026-01-15 | 0.77823
2026-01-15 16:35 | 73.2236 | FALSE | FALSE | -1.1905 | -1.6527 | -0.48419 | -0.6569 | 0 |  |  | none | FALSE | 0 | 72.0331 | FALSE | FALSE | 0.0562 |  | 72.8704 | 0 | 0 | -0.01413 | 0.31016 | 0.045557 | 0.41867 | Normal | 73.7078 | 0.84352 | Day | 202601 | 2026-01-15 | 0.84352
2026-01-15 16:50 | 73.2236 | FALSE | FALSE | -1.1207 | -1.5543 | -0.35783 | -0.4863 | 0 |  |  | none | FALSE | 0 | 72.1029 | FALSE | FALSE | 0.0688 |  | 72.8422 | 0 | 0 | -0.02826 | 0.30227 | 0.093494 | 0.36962 | Normal | 73.5814 | 1.0319 | Day | 202601 | 2026-01-15 | 1.0319
2026-01-15 17:05 | 73.2236 | FALSE | FALSE | -1.1207 | -1.5543 | -0.35783 | -0.4863 | 0 |  |  | none | FALSE | 0 | 72.1029 | FALSE | FALSE | 0.0688 |  | 72.8422 | 0 | 0 | 0 | 0.27458 | 0 | 0.36962 | Normal | 73.5814 | 1.0319 | Day | 202601 | 2026-01-15 | 1.0319
2026-01-15 17:20 | 73.2236 | FALSE | FALSE | -1.1251 | -1.5605 | -0.39048 | -0.53045 | 0 |  |  | none | FALSE | 0 | 72.0985 | FALSE | FALSE | 0.0646 |  | 72.8563 | 0 | 0 | 0.01413 | 0.26642 | -0.053037 | 0.37889 | Normal | 73.6141 | 0.96939 | Day | 202601 | 2026-01-15 | 0.96939
2026-01-15 17:35 | 73.2236 | FALSE | FALSE | -1.1279 | -1.5645 | -0.42161 | -0.57249 | 0 |  |  | none | FALSE | 0 | 72.0957 | FALSE | FALSE | 0.0608 |  | 72.8704 | 0 | 0 | 0.01413 | 0.26642 | -0.053037 | 0.38739 | Normal | 73.6452 | 0.91165 | Day | 202601 | 2026-01-15 | 0.91165
2026-01-15 17:50 | 73.2236 | FALSE | FALSE | -1.1083 | -1.5368 | -0.45849 | -0.62225 | 0 |  |  | none | FALSE | 0 | 72.1153 | FALSE | FALSE | 0.0553 |  | 72.8987 | 0 | 0 | 0.02826 | 0.25719 | -0.10988 | 0.39169 | Normal | 73.6821 | 0.82947 | Day | 202601 | 2026-01-15 | 0.82947
2026-01-15 18:05 | 73.2236 | FALSE | FALSE | -1.0843 | -1.5031 | -0.49102 | -0.6661 | 0 |  |  | none | FALSE | 0 | 72.1393 | FALSE | FALSE | 0.0502 |  | 72.927 | 0 | 0 | 0.02826 | 0.25719 | -0.10988 | 0.39383 | Normal | 73.7146 | 0.75322 | Night | 202601 | 2026-01-15 | 0.75322
2026-01-15 18:20 | 73.2236 | FALSE | FALSE | -1.056 | -1.4633 | -0.51926 | -0.70415 | 0 |  |  | none | FALSE | 0 | 72.1676 | FALSE | FALSE | 0.0454 |  | 72.9552 | 0 | 0 | 0.02826 | 0.25719 | -0.10988 | 0.39382 | Normal | 73.7429 | 0.68148 | Night | 202601 | 2026-01-15 | 0.68148
2026-01-15 18:30 | 72.941 | FALSE | FALSE | -0.74691 | -1.0346 | -0.80361 | -1.0897 | -0.2826 |  |  | none | FALSE | 0 | 72.1941 | FALSE | FALSE | 0.0049 |  | 72.9694 | 0 | -0.2826 | 0.01413 | 0.26642 | -1.1138 | 0.38763 | Normal | 73.7446 | -0.073136 | Night | 202601 | 2026-01-15 | 0.073136
2026-01-15 18:31 | 73.2236 | FALSE | FALSE | -0.74216 | -1.0239 | -0.37478 | -0.50922 | 0.2826 |  |  | none | FALSE | 0 | 72.4814 | FALSE | FALSE | 0.0439 |  | 73.0399 | 0 | 0.2826 | 0.07056 | 0.18023 | 1.1765 | 0.27923 | Normal | 73.5984 | 0.65784 | Night | 202601 | 2026-01-15 | 0.65784
2026-01-15 18:46 | 72.941 | FALSE | FALSE | -0.33945 | -0.46755 | -0.59379 | -0.80749 | -0.2826 |  |  | none | FALSE | 0 | 72.6016 | FALSE | FALSE | 0.0363 |  | 73.0682 | 0 | -0.2826 | 0.02826 | 0.15614 | -1.9909 | 0.23331 | Normal | 73.5348 | -0.54507 | Night | 202601 | 2026-01-15 | 0.54507
2026-01-15 19:01 | 72.941 | FALSE | FALSE | -0.18641 | -0.25621 | -0.49727 | -0.67712 | 0 |  |  | none | FALSE | 0 | 72.7546 | FALSE | FALSE | 0.0606 |  | 73.0964 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.17092 | Normal | 73.4383 | -0.90938 | Night | 202601 | 2026-01-15 | 0.90938
2026-01-15 19:16 | 72.6584 | FALSE | FALSE | 0.096194 | 0.13222 | -0.77987 | -1.0619 | -0.2826 | 2026-01-16 10:03 | 2026-01-15 19:16 | lower | TRUE | 0 | 72.7546 | FALSE | FALSE | 0.228 | 2.5628 | 73.0964 | 1 | -0.2826 | 0 | 0.15881 | -1.7795 | 0.17092 | Extreme triggered | 73.4383 | -2.5628 | Night | 202601 | 2026-01-15 | 2.5628
2026-01-15 19:30 | 72.3758 | FALSE | FALSE | 0.22575 | 0.31095 | -1.159 | -1.5761 | -0.2826 |  | 2026-01-15 19:16 | lower | TRUE | 0 | 72.6016 | FALSE | FALSE | 0.3121 | 2.7652 | 73.0682 | 2 | -0.2826 | -0.02826 | 0.15614 | -1.6289 | 0.23331 | Extreme/elevated | 73.5348 | -2.9676 | Night | 202601 | 2026-01-15 | 2.9676
2026-01-15 19:45 | 72.095 | FALSE | FALSE | 0.29355 | 0.40552 | -1.5682 | -2.1289 | -0.2808 |  | 2026-01-15 19:16 | lower | TRUE | 0 | 72.3886 | FALSE | TRUE | 0.3662 | 2.8172 | 73.0259 | 3 | -0.2808 | -0.0423 | 0.16579 | -1.4386 | 0.31866 | Persistent | 73.6632 | -2.9212 | Night | 202601 | 2026-01-15 | 2.9212
2026-01-15 20:00 | 72.095 | FALSE | FALSE | 0.12729 | 0.17625 | -1.6499 | -2.2372 | 0 |  | 2026-01-15 19:16 | lower | TRUE | 0 | 72.2223 | FALSE | TRUE | 0.3842 | 2.6965 | 72.9836 | 4 | 0 | -0.0423 | 0.16579 | 0.25514 | 0.38064 | Persistent | 73.7449 | -2.3344 | Night | 202601 | 2026-01-15 | 2.3344
2026-01-15 20:15 | 71.8124 | FALSE | FALSE | 0.19033 | 0.26434 | -2.0391 | -2.7611 | -0.2826 |  | 2026-01-15 19:16 | lower | TRUE | 0 | 72.0027 | FALSE | TRUE | 0.4465 | 2.6396 | 72.9271 | 5 | -0.2826 | -0.05643 | 0.17384 | -1.301 | 0.4622 | Persistent | 73.8515 | -2.4118 | Night | 202601 | 2026-01-15 | 2.4118
2026-01-15 20:29 | 71.5298 | FALSE | FALSE | 0.20952 | 0.29206 | -2.4158 | -3.267 | -0.2826 |  | 2026-01-15 19:16 | lower | TRUE | 0 | 71.7393 | FALSE | TRUE | 0.5015 | 2.5963 | 72.8424 | 6 | -0.2826 | -0.08469 | 0.16132 | -1.2268 | 0.55156 | Persistent | 73.9456 | -2.3799 | Night | 202601 | 2026-01-15 | 2.3799
2026-01-15 20:44 | 71.2472 | FALSE | TRUE | 0.19992 | 0.27982 | -2.7929 | -3.7722 | -0.2826 |  | 2026-01-15 19:16 | lower | TRUE | 0 | 71.4471 | FALSE | TRUE | 0.5539 | 2.5552 | 72.7436 | 7 | -0.2826 | -0.09882 | 0.16582 | -1.1083 | 0.64826 | Confirmed/Materialized Shift | 74.0401 | -2.3084 | Night | 202601 | 2026-01-15 | 2.3084
2026-01-15 20:59 | 71.2472 | FALSE | TRUE | -0.038619 | -0.054234 | -2.8338 | -3.8253 | 0 |  | 2026-01-15 19:16 | none | FALSE | 0 | 71.2086 | FALSE | FALSE | 0.5297 | 2.479 | 72.6448 | 8 | 0 | -0.09882 | 0.16582 | 0.59594 | 0.71811 | Confirmed/Materialized Shift | 74.081 | -1.9462 | Night | 202601 | 2026-01-15 | 1.9462
2026-01-15 21:14 | 70.9646 | FALSE | TRUE | -0.024233 | -0.034159 | -3.1588 | -4.2615 | -0.2826 |  | 2026-01-15 19:16 | none | FALSE | 0 | 70.9404 | FALSE | FALSE | 0.5313 | 2.4224 | 72.5319 | 9 | -0.2826 | -0.11295 | 0.16897 | -1.004 | 0.79575 | Confirmed/Materialized Shift | 74.1234 | -1.9695 | Night | 202601 | 2026-01-15 | 1.9695
2026-01-15 21:29 | 70.682 | FALSE | TRUE | -0.033503 | -0.047423 | -3.4791 | -4.6912 | -0.2826 |  | 2026-01-15 19:16 | none | FALSE | 0 | 70.6485 | FALSE | FALSE | 0.5308 | 2.3764 | 72.4048 | 10 | -0.2826 | -0.12708 | 0.17083 | -0.91037 | 0.87814 | Confirmed/Materialized Shift | 74.1611 | -1.9618 | Night | 202601 | 2026-01-15 | 1.9618
2026-01-15 21:44 | 70.682 | FALSE | TRUE | -0.27519 | -0.39085 | -3.4666 | -4.6752 | 0 |  | 2026-01-15 19:16 | none | FALSE | 0 | 70.4068 | FALSE | FALSE | 0.5137 | 2.3154 | 72.2777 | 11 | 0 | -0.12708 | 0.17083 | 0.74389 | 0.93544 | Confirmed/Materialized Shift | 74.1486 | -1.7058 | Night | 202601 | 2026-01-15 | 1.7058
2026-01-15 21:59 | 70.3994 | FALSE | TRUE | -0.25556 | -0.36433 | -3.7297 | -5.0314 | -0.2826 |  | 2026-01-15 19:16 | none | FALSE | 0 | 70.1438 | FALSE | FALSE | 0.5162 | 2.2678 | 72.1365 | 12 | -0.2826 | -0.14121 | 0.17145 | -0.82465 | 0.99632 | Confirmed/Materialized Shift | 74.1291 | -1.7435 | Night | 202601 | 2026-01-15 | 1.7435
2026-01-15 22:14 | 70.3994 | FALSE | TRUE | -0.47128 | -0.67394 | -3.663 | -4.9459 | 0 |  | 2026-01-15 19:16 | none | FALSE | 0 | 69.9281 | FALSE | FALSE | 0.5029 | 2.2121 | 71.9953 | 13 | 0 | -0.14121 | 0.17145 | 0.8236 | 1.0336 | Confirmed/Materialized Shift | 74.0624 | -1.544 | Night | 202601 | 2026-01-15 | 1.544
2026-01-15 22:29 | 70.1168 | FALSE | TRUE | -0.42087 | -0.60387 | -3.8671 | -5.227 | -0.2826 |  | 2026-01-15 19:16 | none | FALSE | 0 | 69.6959 | FALSE | FALSE | 0.5072 | 2.1689 | 71.8399 | 14 | -0.2826 | -0.15534 | 0.17085 | -0.74487 | 1.072 | Confirmed/Materialized Shift | 73.9839 | -1.6074 | Night | 202601 | 2026-01-15 | 1.6074
2026-01-15 22:44 | 70.1168 | FALSE | TRUE | -0.60412 | -0.86907 | -3.7397 | -5.0635 | 0 |  | 2026-01-15 19:16 | none | FALSE | 0 | 69.5127 | FALSE | FALSE | 0.4962 | 2.1205 | 71.6846 | 15 | 0 | -0.15534 | 0.17085 | 0.90923 | 1.086 | Confirmed/Materialized Shift | 73.8565 | -1.4437 | Night | 202601 | 2026-01-15 | 1.4437
2026-01-15 22:59 | 69.836 | FALSE | TRUE | -0.5156 | -0.74379 | -3.874 | -5.2558 | -0.2808 |  | 2026-01-15 19:16 | none | FALSE | 0 | 69.3204 | FALSE | FALSE | 0.502 | 2.0836 | 71.5152 | 16 | -0.2808 | -0.16938 | 0.16894 | -0.65953 | 1.0974 | Confirmed/Materialized Shift | 73.71 | -1.5302 | Night | 202601 | 2026-01-15 | 1.5302
2026-01-15 23:14 | 69.836 | FALSE | TRUE | -0.68542 | -0.9912 | -3.7334 | -5.0746 | 0 |  | 2026-01-15 19:16 | none | FALSE | 0 | 69.1506 | FALSE | FALSE | 0.492 | 2.0422 | 71.36 | 17 | 0 | -0.15525 | 0.17078 | 0.90908 | 1.1047 | Confirmed/Materialized Shift | 73.5694 | -1.3795 | Night | 202601 | 2026-01-15 | 1.3795
2026-01-15 23:28 | 69.5534 | FALSE | TRUE | -0.54386 | -0.78809 | -3.79 | -5.1674 | -0.2826 |  | 2026-01-15 19:16 | none | FALSE | 0 | 69.0095 | FALSE | FALSE | 0.4999 | 2.012 | 71.1765 | 18 | -0.2826 | -0.18351 | 0.13816 | -0.71722 | 1.0835 | Confirmed/Materialized Shift | 73.3434 | -1.498 | Night | 202601 | 2026-01-15 | 1.498
2026-01-15 23:43 | 69.2708 | FALSE | TRUE | -0.43719 | -0.63515 | -3.8815 | -5.306 | -0.2826 |  | 2026-01-15 19:16 | none | FALSE | 0 | 68.8336 | FALSE | FALSE | 0.5063 | 1.9901 | 70.9929 | 19 | -0.2826 | -0.18351 | 0.13816 | -0.71722 | 1.0797 | Confirmed/Materialized Shift | 73.1523 | -1.5951 | Night | 202601 | 2026-01-15 | 1.5951
2026-01-15 23:59 | 69.2708 | FALSE | TRUE | -0.54617 | -0.79472 | -3.6234 | -4.9708 | 0 |  | 2026-01-15 19:16 | none | FALSE | 0 | 68.7246 | FALSE | FALSE | 0.4984 | 1.9644 | 70.8094 | 20 | 0 | -0.18351 | 0.13816 | 1.3283 | 1.0424 | Confirmed/Materialized Shift | 72.8942 | -1.476 | Night | 202601 | 2026-01-15 | 1.476
2026-01-16 00:14 | 68.9882 | FALSE | TRUE | -0.40756 | -0.59428 | -3.683 | -5.0681 | -0.2826 |  | 2026-01-15 19:16 | none | FALSE | 0 | 68.5806 | FALSE | FALSE | 0.5068 | 1.9471 | 70.6259 | 21 | -0.2826 | -0.18351 | 0.13816 | -0.71722 | 1.0226 | Confirmed/Materialized Shift | 72.6712 | -1.6015 | Night | 202601 | 2026-01-16 | 1.6015
2026-01-16 00:28 | 68.9882 | FALSE | TRUE | -0.52726 | -0.77016 | -3.464 | -4.781 | 0 |  | 2026-01-15 19:16 | none | FALSE | 0 | 68.4609 | FALSE | FALSE | 0.4981 | 1.9255 | 70.4565 | 22 | 0 | -0.16938 | 0.14189 | 1.1937 | 0.9978 | Confirmed/Materialized Shift | 72.4522 | -1.4716 | Night | 202601 | 2026-01-16 | 1.4716
2026-01-16 00:43 | 68.7056 | FALSE | TRUE | -0.40391 | -0.59137 | -3.5669 | -4.9353 | -0.2826 |  | 2026-01-15 19:16 | none | FALSE | 0 | 68.3017 | FALSE | FALSE | 0.5062 | 1.911 | 70.2871 | 23 | -0.2826 | -0.16947 | 0.14197 | -0.79688 | 0.9927 | Confirmed/Materialized Shift | 72.2725 | -1.5931 | Night | 202601 | 2026-01-16 | 1.5931
2026-01-16 00:58 | 68.7056 | FALSE | TRUE | -0.50092 | -0.73443 | -3.3249 | -4.616 | 0 |  | 2026-01-15 19:16 | none | FALSE | 0 | 68.2047 | FALSE | FALSE | 0.4984 | 1.8929 | 70.1176 | 24 | 0 | -0.16947 | 0.14197 | 1.1937 | 0.95646 | Confirmed/Materialized Shift | 72.0305 | -1.4763 | Night | 202601 | 2026-01-16 | 1.4763
2026-01-16 01:13 | 68.7056 | FALSE | TRUE | -0.57983 | -0.85112 | -3.0932 | -4.3081 | 0 |  | 2026-01-15 19:16 | none | FALSE | 0 | 68.1258 | FALSE | FALSE | 0.4912 | 1.8719 | 69.9623 | 25 | 0 | -0.15534 | 0.14416 | 1.0775 | 0.91825 | Confirmed/Materialized Shift | 71.7988 | -1.3685 | Night | 202601 | 2026-01-16 | 1.3685
2026-01-16 01:28 | 68.423 | FALSE | TRUE | -0.41958 | -0.617 | -3.1874 | -4.4511 | -0.2826 |  | 2026-01-15 19:16 | none | FALSE | 0 | 68.0034 | FALSE | FALSE | 0.5023 | 1.859 | 69.8069 | 26 | -0.2826 | -0.15534 | 0.14416 | -0.88276 | 0.90175 | Confirmed/Materialized Shift | 71.6104 | -1.5347 | Night | 202601 | 2026-01-16 | 1.5347
2026-01-16 01:43 | 68.423 | FALSE | TRUE | -0.52793 | -0.77756 | -3.0134 | -4.2183 | 0 |  | 2026-01-15 19:16 | none | FALSE | 0 | 67.8951 | FALSE | FALSE | 0.4936 | 1.8421 | 69.6657 | 27 | 0 | -0.14121 | 0.14488 | 0.97468 | 0.88532 | Confirmed/Materialized Shift | 71.4364 | -1.4037 | Night | 202601 | 2026-01-16 | 1.4037
2026-01-16 01:58 | 68.1404 | FALSE | TRUE | -0.36116 | -0.53285 | -3.1011 | -4.353 | -0.2826 |  | 2026-01-15 19:16 | none | FALSE | 0 | 67.7792 | FALSE | FALSE | 0.5055 | 1.8328 | 69.5104 | 28 | -0.2826 | -0.15534 | 0.14416 | -0.88276 | 0.86557 | Confirmed/Materialized Shift | 71.2415 | -1.5827 | Night | 202601 | 2026-01-16 | 1.5827
2026-01-16 02:13 | 68.1404 | FALSE | TRUE | -0.46321 | -0.68444 | -2.9208 | -4.1102 | 0 |  | 2026-01-15 19:16 | none | FALSE | 0 | 67.6772 | FALSE | FALSE | 0.4968 | 1.8197 | 69.3692 | 29 | 0 | -0.14121 | 0.14488 | 0.97468 | 0.84599 | Confirmed/Materialized Shift | 71.0612 | -1.4525 | Night | 202601 | 2026-01-16 | 1.4525
2026-01-16 02:28 | 67.8596 | FALSE | TRUE | -0.33327 | -0.49354 | -3.0702 | -4.3285 | -0.2808 |  | 2026-01-15 19:16 | none | FALSE | 0 | 67.5263 | FALSE | FALSE | 0.5072 | 1.8127 | 69.228 | 30 | -0.2808 | -0.14112 | 0.14479 | -0.96473 | 0.85086 | Confirmed/Materialized Shift | 70.9298 | -1.6083 | Night | 202601 | 2026-01-16 | 1.6083
2026-01-16 02:43 | 67.577 | FALSE | TRUE | -0.21394 | -0.31759 | -3.2055 | -4.5287 | -0.2826 |  | 2026-01-15 19:16 | none | FALSE | 0 | 67.3631 | FALSE | FALSE | 0.5166 | 1.8106 | 69.0728 | 31 | -0.2826 | -0.15525 | 0.14408 | -0.8839 | 0.85487 | Confirmed/Materialized Shift | 70.7825 | -1.7497 | Night | 202601 | 2026-01-16 | 1.7497
2026-01-16 02:58 | 67.577 | FALSE | TRUE | -0.35993 | -0.53548 | -3.0693 | -4.3446 | 0 |  | 2026-01-15 19:16 | none | FALSE | 0 | 67.2171 | FALSE | FALSE | 0.5053 | 1.8034 | 68.9317 | 32 | 0 | -0.14112 | 0.14479 | 0.97467 | 0.85731 | Confirmed/Materialized Shift | 70.6463 | -1.5802 | Night | 202601 | 2026-01-16 | 1.5802
2026-01-16 03:13 | 67.577 | FALSE | TRUE | -0.45643 | -0.68002 | -2.8836 | -4.0924 | 0 |  | 2026-01-15 19:16 | none | FALSE | 0 | 67.1206 | FALSE | FALSE | 0.4969 | 1.7928 | 68.7906 | 33 | 0 | -0.14112 | 0.14479 | 0.97467 | 0.835 | Confirmed/Materialized Shift | 70.4606 | -1.4534 | Night | 202601 | 2026-01-16 | 1.4534
2026-01-16 03:27 | 67.2944 | FALSE | TRUE | -0.32007 | -0.4779 | -3.0301 | -4.3088 | -0.2826 |  | 2026-01-15 19:16 | none | FALSE | 0 | 66.9743 | FALSE | FALSE | 0.5079 | 1.7877 | 68.6494 | 34 | -0.2826 | -0.14112 | 0.14479 | -0.97716 | 0.83755 | Confirmed/Materialized Shift | 70.3245 | -1.6179 | Night | 202601 | 2026-01-16 | 1.6179
2026-01-16 09:48 | 66.164 | TRUE | TRUE | 0.41998 | 0.63076 | -4.1556 | -5.9096 | -1.1304 |  | 2026-01-15 19:16 | lower | TRUE | 1 | 66.584 | FALSE | TRUE | 0.5919 | 1.8066 | 68.4518 | 35 | -1.1304 | -0.19764 | 0.26089 | -3.5753 | 0.93391 | Confirmed/Materialized Shift | 70.3196 | -2.4497 | Day | 202601 | 2026-01-16 | 2.4497
2026-01-16 09:48 | 66.164 | FALSE | TRUE | 0.092899 | 0.14021 | -4.1155 | -5.8559 | 0 |  | 2026-01-15 19:16 | lower | TRUE | 1 | 66.2569 | FALSE | TRUE | 0.5681 | 1.8145 | 68.2682 | 36 | 0 | -0.1836 | 0.26372 | 0.6962 | 1.0057 | Confirmed/Materialized Shift | 70.2795 | -2.0924 | Day | 202601 | 2026-01-16 | 2.0924
2026-01-16 10:03 | 67.2944 | TRUE | FALSE | -1.0663 | -1.61 | -2.7597 | -3.9394 | 1.1304 |  |  | none | FALSE | 2 | 66.2281 | TRUE | FALSE | 0.1162 |  | 68.1411 | 0 | 1.1304 | -0.12708 | 0.39406 | 3.1911 | 0.95649 | Persistence ends | 70.0541 | -0.88524 | Day | 202601 | 2026-01-16 | 0.88524
2026-01-16 10:18 | 67.8596 | FALSE | FALSE | -1.5993 | -2.4137 | -1.993 | -2.8531 | 0.5652 |  |  | none | FALSE | 2 | 66.2603 | FALSE | FALSE | 0.0718 |  | 68.0564 | 0 | 0.5652 | -0.08469 | 0.42112 | 1.5432 | 0.89807 | Normal | 69.8526 | -0.21917 | Day | 202601 | 2026-01-16 | 0.21917
2026-01-16 10:33 | 68.423 | FALSE | FALSE | -2.1225 | -3.2014 | -1.3046 | -1.871 | 0.5634 |  |  | none | FALSE | 2 | 66.3005 | FALSE | FALSE | 0.089 |  | 68.014 | 0 | 0.5634 | -0.04239 | 0.44216 | 1.3701 | 0.85679 | Normal | 69.7276 | 0.47732 | Day | 202601 | 2026-01-16 | 0.47732
2026-01-16 10:48 | 68.7056 | FALSE | FALSE | -2.3633 | -3.5623 | -0.9237 | -1.3266 | 0.2826 |  |  | none | FALSE | 2 | 66.3423 | FALSE | FALSE | 0.1155 |  | 67.9858 | 0 | 0.2826 | -0.02826 | 0.44806 | 0.69379 | 0.82176 | Normal | 69.6293 | 0.87595 | Day | 202601 | 2026-01-16 | 0.87595
2026-01-16 10:48 | 68.9882 | FALSE | FALSE | -2.6459 | -3.9883 | -0.6411 | -0.92073 | 0.2826 |  |  | none | FALSE | 2 | 66.3423 | FALSE | FALSE | 0.1385 |  | 67.9858 | 0 | 0.2826 | 0 | 0.449 | 0.6294 | 0.82176 | Normal | 69.6293 | 1.2198 | Day | 202601 | 2026-01-16 | 1.2198
2026-01-16 11:03 | 69.2708 | FALSE | FALSE | -2.9551 | -4.456 | -0.41327 | -0.59307 | 0.2826 |  |  | none | FALSE | 2 | 66.3157 | FALSE | FALSE | 0.1578 |  | 67.9999 | 0 | 0.2826 | 0.01413 | 0.45342 | 0.5921 | 0.84208 | Normal | 69.6841 | 1.5092 | Day | 202601 | 2026-01-16 | 1.5092
2026-01-16 11:18 | 69.5534 | FALSE | FALSE | -3.3089 | -4.995 | -0.28669 | -0.4105 | 0.2826 |  |  | none | FALSE | 2 | 66.2445 | FALSE | FALSE | 0.1692 |  | 68.0423 | 0 | 0.2826 | 0.04239 | 0.45156 | 0.53195 | 0.8989 | Normal | 69.8401 | 1.6811 | Day | 202601 | 2026-01-16 | 1.6811
2026-01-16 11:33 | 69.836 | FALSE | FALSE | -3.6874 | -5.5744 | -0.21303 | -0.30412 | 0.2826 |  |  | none | FALSE | 2 | 66.1486 | FALSE | FALSE | 0.1759 |  | 68.0988 | 0 | 0.2826 | 0.05652 | 0.45458 | 0.49734 | 0.97511 | Normal | 70.049 | 1.7815 | Day | 202601 | 2026-01-16 | 1.7815
2026-01-16 11:48 | 70.1168 | FALSE | FALSE | -4.0833 | -6.1837 | -0.1885 | -0.26812 | 0.2808 |  |  | none | FALSE | 1 | 66.0335 | FALSE | FALSE | 0.1501 |  | 68.1694 | 0 | 0.2808 | 0.07056 | 0.45707 | 0.45997 | 1.068 | Normal | 70.3053 | 1.8235 | Day | 202601 | 2026-01-16 | 1.8235
2026-01-16 12:03 | 70.3994 | FALSE | FALSE | -4.488 | -6.8091 | -0.22559 | -0.31942 | 0.2826 |  |  | none | FALSE | 1 | 65.9114 | FALSE | FALSE | 0.1491 |  | 68.2682 | 0 | 0.2826 | 0.09882 | 0.45153 | 0.40702 | 1.1784 | Normal | 70.625 | 1.8086 | Day | 202601 | 2026-01-16 | 1.8086
2026-01-16 12:18 | 70.682 | FALSE | FALSE | -4.8936 | -7.4384 | -0.29189 | -0.41127 | 0.2826 |  |  | none | FALSE | 0 | 65.7884 | FALSE | FALSE | 0.1183 |  | 68.3812 | 0 | 0.2826 | 0.11295 | 0.45269 | 0.37476 | 1.2964 | Normal | 70.9739 | 1.7748 | Day | 202601 | 2026-01-16 | 1.7748
2026-01-16 12:33 | 70.9646 | FALSE | FALSE | -5.2762 | -8.0321 | -0.39171 | -0.54894 | 0.2826 |  |  | none | FALSE | 0 | 65.6884 | FALSE | FALSE | 0.1149 |  | 68.5224 | 0 | 0.2826 | 0.14121 | 0.44426 | 0.31826 | 1.417 | Normal | 71.3563 | 1.7236 | Day | 202601 | 2026-01-16 | 1.7236
2026-01-16 12:48 | 71.2472 | FALSE | FALSE | -5.6455 | -8.6058 | -0.50654 | -0.70595 | 0.2826 |  |  | none | FALSE | 0 | 65.6017 | FALSE | FALSE | 0.1114 |  | 68.6777 | 0 | 0.2826 | 0.15534 | 0.44403 | 0.2866 | 1.538 | Normal | 71.7537 | 1.6707 | Day | 202601 | 2026-01-16 | 1.6707
2026-01-16 13:03 | 71.5298 | FALSE | FALSE | -5.9689 | -9.1043 | -0.63169 | -0.87539 | 0.2826 |  |  | none | FALSE | 0 | 65.5609 | FALSE | FALSE | 0.1078 |  | 68.8612 | 0 | 0.2826 | 0.18351 | 0.43263 | 0.22904 | 1.6501 | Normal | 72.1615 | 1.6172 | Day | 202601 | 2026-01-16 | 1.6172
2026-01-16 13:18 | 71.5298 | FALSE | FALSE | -5.9176 | -9.0191 | -0.9757 | -1.3457 | 0 |  |  | none | FALSE | 0 | 65.6122 | FALSE | FALSE | 0.0956 |  | 69.0589 | 0 | 0 | 0.19764 | 0.42106 | -0.46938 | 1.7233 | Normal | 72.5055 | 1.4338 | Day | 202601 | 2026-01-16 | 1.4338
2026-01-16 13:33 | 71.8124 | FALSE | FALSE | -6.1229 | -9.321 | -1.0394 | -1.4267 | 0.2826 |  |  | none | FALSE | 0 | 65.6895 | FALSE | FALSE | 0.0946 |  | 69.2706 | 0 | 0.2826 | 0.21177 | 0.41882 | 0.16912 | 1.7906 | Normal | 72.8518 | 1.4195 | Day | 202601 | 2026-01-16 | 1.4195
2026-01-16 13:47 | 72.095 | FALSE | FALSE | -6.2978 | -9.5716 | -1.1009 | -1.504 | 0.2826 |  |  | none | FALSE | 0 | 65.7972 | FALSE | FALSE | 0.0937 |  | 69.4965 | 0 | 0.2826 | 0.2259 | 0.41605 | 0.13628 | 1.8497 | Normal | 73.1959 | 1.4048 | Day | 202601 | 2026-01-16 | 1.4048
2026-01-16 14:02 | 72.095 | FALSE | FALSE | -6.0791 | -9.2085 | -1.3622 | -1.8544 | 0 |  |  | none | FALSE | 0 | 66.0159 | FALSE | FALSE | 0.0845 |  | 69.7365 | 0 | 0 | 0.24003 | 0.40245 | -0.59642 | 1.8603 | Normal | 73.4572 | 1.2678 | Day | 202601 | 2026-01-16 | 1.2678
2026-01-16 14:17 | 72.3758 | FALSE | FALSE | -5.8239 | -8.7509 | -1.1666 | -1.5862 | 0.2808 |  |  | none | FALSE | 0 | 66.5519 | FALSE | FALSE | 0.0888 |  | 70.0471 | 0 | 0.2808 | 0.31059 | 0.24077 | -0.12373 | 1.7476 | Normal | 73.5424 | 1.3325 | Day | 202601 | 2026-01-16 | 1.3325
2026-01-16 14:32 | 72.3758 | FALSE | FALSE | -5.145 | -7.6527 | -1.1088 | -1.5089 | 0 |  |  | none | FALSE | 0 | 67.2308 | FALSE | FALSE | 0.0861 |  | 70.3577 | 0 | 0 | 0.31059 | 0.24077 | -1.29 | 1.5634 | Normal | 73.4846 | 1.2908 | Day | 202601 | 2026-01-16 | 1.2908
2026-01-16 14:47 | 72.6584 | FALSE | FALSE | -4.9673 | -7.3382 | -0.90238 | -1.2267 | 0.2826 |  |  | none | FALSE | 0 | 67.6911 | FALSE | FALSE | 0.0923 |  | 70.6259 | 0 | 0.2826 | 0.2682 | 0.14403 | 0.099978 | 1.4674 | Normal | 73.5608 | 1.3851 | Day | 202601 | 2026-01-16 | 1.3851
2026-01-16 15:02 | 72.941 | FALSE | FALSE | -4.8644 | -7.1454 | -0.74236 | -1.0075 | 0.2826 |  |  | none | FALSE | 0 | 68.0766 | FALSE | FALSE | 0.098 |  | 70.88 | 0 | 0.2826 | 0.25407 | 0.12611 | 0.22623 | 1.4017 | Normal | 73.6834 | 1.4704 | Day | 202601 | 2026-01-16 | 1.4704
2026-01-16 15:17 | 72.941 | FALSE | FALSE | -4.5309 | -6.6231 | -0.86069 | -1.1662 | 0 |  |  | none | FALSE | 0 | 68.4101 | FALSE | FALSE | 0.0908 |  | 71.1059 | 0 | 0 | 0.2259 | 0.11589 | -1.9493 | 1.3479 | Normal | 73.8017 | 1.3615 | Day | 202601 | 2026-01-16 | 1.3615
2026-01-16 15:32 | 72.941 | FALSE | FALSE | -4.1874 | -6.0905 | -0.94075 | -1.2733 | 0 |  |  | none | FALSE | 0 | 68.7536 | FALSE | FALSE | 0.0844 |  | 71.3177 | 0 | 0 | 0.21177 | 0.12544 | -1.6882 | 1.282 | Normal | 73.8817 | 1.2662 | Day | 202601 | 2026-01-16 | 1.2662
2026-01-16 15:47 | 72.941 | FALSE | FALSE | -3.8387 | -5.555 | -0.98727 | -1.3354 | 0 |  |  | none | FALSE | 0 | 69.1023 | FALSE | FALSE | 0.0788 |  | 71.5153 | 0 | 0 | 0.19764 | 0.13275 | -1.4888 | 1.2065 | Normal | 73.9283 | 1.1817 | Day | 202601 | 2026-01-16 | 1.1817
2026-01-16 15:49 | 72.941 | FALSE | FALSE | -3.4889 | -5.0235 | -1.0046 | -1.3585 | 0 |  |  | none | FALSE | 0 | 69.4521 | FALSE | FALSE | 0.0737 |  | 71.6988 | 0 | 0 | 0.18351 | 0.13816 | -1.3283 | 1.1234 | Normal | 73.9456 | 1.1058 | Day | 202601 | 2026-01-16 | 1.1058
2026-01-16 15:50 | 72.941 | FALSE | FALSE | -3.1423 | -4.502 | -0.99673 | -1.3481 | 0 |  |  | none | FALSE | 0 | 69.7987 | FALSE | FALSE | 0.0691 |  | 71.8682 | 0 | 0 | 0.16938 | 0.14189 | -1.1937 | 1.0348 | Normal | 73.9377 | 1.0368 | Day | 202601 | 2026-01-16 | 1.0368
2026-01-16 15:52 | 72.941 | FALSE | FALSE | -2.8028 | -3.9962 | -0.96774 | -1.3094 | 0 |  |  | none | FALSE | 0 | 70.1382 | FALSE | FALSE | 0.0649 |  | 72.0234 | 0 | 0 | 0.15525 | 0.14408 | -1.0775 | 0.94264 | Normal | 73.9087 | 0.97338 | Day | 202601 | 2026-01-16 | 0.97338
2026-01-16 16:07 | 72.095 | TRUE | FALSE | -1.6306 | -2.3141 | -1.6853 | -2.2843 | -0.846 |  |  | none | FALSE | 1 | 70.4644 | FALSE | FALSE | 0.0308 |  | 72.1224 | 0 | -0.846 | 0.09891 | 0.26335 | -3.5881 | 0.82899 | Normal | 73.7803 | -0.033004 | Day | 202601 | 2026-01-16 | 0.033004
2026-01-16 16:16 | 71.8124 | FALSE | FALSE | -1.0765 | -1.5218 | -1.8377 | -2.4952 | -0.2826 |  |  | none | FALSE | 1 | 70.7359 | FALSE | FALSE | 0.0634 |  | 72.193 | 0 | -0.2826 | 0.07065 | 0.27275 | -1.2951 | 0.72854 | Normal | 73.6501 | -0.52242 | Day | 202601 | 2026-01-16 | 0.52242
2026-01-16 16:31 | 72.3758 | FALSE | FALSE | -1.3706 | -1.9303 | -1.1744 | -1.5967 | 0.5634 |  |  | none | FALSE | 1 | 71.0052 | FALSE | FALSE | 0.0389 |  | 72.2777 | 0 | 0.5634 | 0.08469 | 0.29086 | 1.6458 | 0.63626 | Normal | 73.5502 | 0.15418 | Day | 202601 | 2026-01-16 | 0.15418
2026-01-16 16:46 | 72.3758 | FALSE | FALSE | -1.1399 | -1.6002 | -1.0848 | -1.4767 | 0 |  |  | none | FALSE | 1 | 71.2359 | FALSE | FALSE | 0.0319 |  | 72.3483 | 0 | 0 | 0.07056 | 0.28759 | -0.24535 | 0.55618 | Normal | 73.4606 | 0.049516 | Day | 202601 | 2026-01-16 | 0.049516
2026-01-16 16:49 | 72.6584 | FALSE | FALSE | -1.2302 | -1.7223 | -0.75108 | -1.0231 | 0.2826 |  |  | none | FALSE | 1 | 71.4282 | FALSE | FALSE | 0.0608 |  | 72.4188 | 0 | 0.2826 | 0.07056 | 0.28759 | 0.7373 | 0.49533 | Normal | 73.4095 | 0.48368 | Day | 202601 | 2026-01-16 | 0.48368
2026-01-16 17:04 | 72.6584 | FALSE | FALSE | -1.0852 | -1.5162 | -0.7189 | -0.97973 | 0 |  |  | none | FALSE | 1 | 71.5732 | FALSE | FALSE | 0.0556 |  | 72.4753 | 0 | 0 | 0.05643 | 0.28354 | -0.19902 | 0.45102 | Normal | 73.3773 | 0.40608 | Day | 202601 | 2026-01-16 | 0.40608
2026-01-16 17:05 | 72.6584 | FALSE | FALSE | -0.91359 | -1.2734 | -0.66015 | -0.90038 | 0 |  |  | none | FALSE | 1 | 71.7448 | FALSE | FALSE | 0.05 |  | 72.5317 | 0 | 0 | 0.05643 | 0.28354 | -0.19902 | 0.39343 | Normal | 73.3185 | 0.32209 | Day | 202601 | 2026-01-16 | 0.32209
2026-01-16 17:06 | 72.6584 | FALSE | FALSE | -0.79582 | -1.1074 | -0.62698 | -0.85553 | 0 |  |  | none | FALSE | 1 | 71.8626 | FALSE | FALSE | 0.0444 |  | 72.574 | 0 | 0 | 0.0423 | 0.27867 | -0.15179 | 0.3557 | Normal | 73.2854 | 0.23733 | Day | 202601 | 2026-01-16 | 0.23733
2026-01-16 17:08 | 72.941 | FALSE | FALSE | -1.0165 | -1.4133 | -0.3671 | -0.50076 | 0.2826 |  |  | none | FALSE | 1 | 71.9245 | FALSE | FALSE | 0.0912 |  | 72.6163 | 0 | 0.2826 | 0.0423 | 0.27867 | 0.8623 | 0.34591 | Normal | 73.3081 | 0.93874 | Day | 202601 | 2026-01-16 | 0.93874
2026-01-16 17:18 | 71.8124 | TRUE | FALSE | 0.043683 | 0.060793 | -1.5358 | -2.0939 | -1.1286 | 2026-01-16 17:48 | 2026-01-16 17:18 | lower | TRUE | 2 | 71.8561 | TRUE | FALSE | 0.2554 | 2.1171 | 72.6021 | 1 | -1.1286 | -0.01413 | 0.38258 | -2.913 | 0.37303 | Extreme triggered | 73.3482 | -2.1171 | Day | 202601 | 2026-01-16 | 2.1171
2026-01-16 17:33 | 72.095 | FALSE | FALSE | -0.28094 | -0.3912 | -1.2672 | -1.7273 | 0.2826 |  | 2026-01-16 17:18 | none | FALSE | 1 | 71.8141 | FALSE | FALSE | 0.2278 | 1.6956 | 72.5881 | 2 | 0.2826 | -0.01404 | 0.38266 | 0.77521 | 0.38702 | Extreme/elevated | 73.3622 | -1.2741 | Day | 202601 | 2026-01-16 | 1.2741
2026-01-16 17:48 | 72.3758 | FALSE | FALSE | -0.56174 | -0.78221 | -0.98636 | -1.3445 | 0.2808 |  |  | none | FALSE | 1 | 71.8141 | FALSE | FALSE | 0.0651 |  | 72.5881 | 0 | 0.2808 | 0 | 0.38831 | 0.72313 | 0.38702 | Persistence ends | 73.3622 | -0.54857 | Day | 202601 | 2026-01-16 | 0.54857
2026-01-16 18:03 | 72.3758 | FALSE | FALSE | -0.58077 | -0.80892 | -0.97713 | -1.3321 | 0 |  |  | none | FALSE | 1 | 71.795 | FALSE | FALSE | 0.0625 |  | 72.574 | 0 | 0 | -0.01413 | 0.38258 | 0.036933 | 0.38947 | Normal | 73.3529 | -0.50884 | Night | 202601 | 2026-01-16 | 0.50884
2026-01-16 18:05 | 72.3758 | FALSE | FALSE | -0.59382 | -0.82726 | -0.93366 | -1.2736 | 0 |  |  | none | FALSE | 1 | 71.782 | FALSE | FALSE | 0.0582 |  | 72.5457 | 0 | 0 | -0.02826 | 0.37621 | 0.075117 | 0.38187 | Normal | 73.3095 | -0.44497 | Night | 202601 | 2026-01-16 | 0.44497
2026-01-16 18:20 | 72.3758 | FALSE | FALSE | -0.60206 | -0.83884 | -0.88538 | -1.2085 | 0 |  |  | none | FALSE | 1 | 71.7737 | FALSE | FALSE | 0.054 |  | 72.5175 | 0 | 0 | -0.02826 | 0.37621 | 0.075117 | 0.37186 | Normal | 73.2612 | -0.38095 | Night | 202601 | 2026-01-16 | 0.38095
2026-01-16 18:30 | 72.3758 | FALSE | FALSE | -0.60509 | -0.84308 | -0.83189 | -1.1363 | 0 |  |  | none | FALSE | 1 | 71.7707 | FALSE | FALSE | 0.0496 |  | 72.4892 | 0 | 0 | -0.02826 | 0.37621 | 0.075117 | 0.35924 | Normal | 73.2077 | -0.31566 | Night | 202601 | 2026-01-16 | 0.31566
2026-01-16 18:31 | 72.3758 | FALSE | FALSE | -0.60231 | -0.83919 | -0.77259 | -1.0562 | 0 |  |  | none | FALSE | 1 | 71.7735 | FALSE | FALSE | 0.0451 |  | 72.4609 | 0 | 0 | -0.02826 | 0.37621 | 0.075117 | 0.34373 | Normal | 73.1484 | -0.2477 | Night | 202601 | 2026-01-16 | 0.2477
2026-01-16 18:46 | 72.3758 | FALSE | FALSE | -0.59292 | -0.82599 | -0.70668 | -0.96696 | 0 |  |  | none | FALSE | 1 | 71.7829 | FALSE | FALSE | 0.0402 |  | 72.4327 | 0 | 0 | -0.02826 | 0.37621 | 0.075117 | 0.3249 | Normal | 73.0825 | -0.17507 | Night | 202601 | 2026-01-16 | 0.17507
2026-01-16 19:01 | 72.3758 | FALSE | FALSE | -0.57566 | -0.80176 | -0.6329 | -0.86689 | 0 |  |  | none | FALSE | 1 | 71.8001 | FALSE | FALSE | 0.0349 |  | 72.4044 | 0 | 0 | -0.02826 | 0.37621 | 0.075117 | 0.30214 | Normal | 73.0087 | -0.094724 | Night | 202601 | 2026-01-16 | 0.094724
2026-01-16 19:16 | 72.3758 | FALSE | FALSE | -0.5486 | -0.76377 | -0.54932 | -0.75326 | 0 |  |  | none | FALSE | 0 | 71.8272 | FALSE | FALSE | 0.0001 |  | 72.3762 | 0 | 0 | -0.02826 | 0.37621 | 0.075117 | 0.27448 | Normal | 72.9251 | -0.0013116 | Night | 202601 | 2026-01-16 | 0.0013116
2026-01-16 19:30 | 72.095 | FALSE | FALSE | -0.2678 | -0.37284 | -0.83012 | -1.1383 | -0.2808 |  |  | none | FALSE | 0 | 71.8272 | FALSE | FALSE | 0.0683 |  | 72.3762 | 0 | -0.2808 | 0 | 0.32994 | -0.85107 | 0.27448 | Normal | 72.9251 | -1.0243 | Night | 202601 | 2026-01-16 | 1.0243
2026-01-16 19:45 | 72.095 | FALSE | FALSE | -0.20496 | -0.2851 | -0.79554 | -1.0914 | 0 |  |  | none | FALSE | 0 | 71.89 | FALSE | FALSE | 0.0787 |  | 72.3903 | 0 | 0 | 0.01413 | 0.32318 | -0.043722 | 0.25012 | Normal | 72.8905 | -1.1806 | Night | 202601 | 2026-01-16 | 1.1806
2026-01-16 20:00 | 71.8124 | FALSE | FALSE | -0.013456 | -0.018741 | -1.1129 | -1.5261 | -0.2826 |  |  | none | FALSE | 0 | 71.7989 | FALSE | FALSE | 0.1301 |  | 72.3621 | 0 | -0.2826 | -0.02817 | 0.30219 | -0.84196 | 0.28159 | Normal | 72.9253 | -1.9522 | Night | 202601 | 2026-01-16 | 1.9522
2026-01-16 20:15 | 71.5298 | FALSE | FALSE | 0.11516 | 0.16074 | -1.4649 | -2.0068 | -0.2826 | 2026-01-17 00:14 | 2026-01-16 20:15 | lower | TRUE | 0 | 71.645 | FALSE | FALSE | 0.2132 | 2.3413 | 72.3198 | 1 | -0.2826 | -0.0423 | 0.30736 | -0.78181 | 0.33743 | Extreme triggered | 72.9947 | -2.3413 | Night | 202601 | 2026-01-16 | 2.3413
2026-01-16 20:29 | 71.5298 | FALSE | FALSE | -0.0075522 | -0.010559 | -1.4747 | -2.0201 | 0 |  | 2026-01-16 20:15 | none | FALSE | 0 | 71.5222 | FALSE | FALSE | 0.2463 | 2.1605 | 72.2634 | 2 | 0 | -0.05643 | 0.29799 | 0.18937 | 0.37057 | Extreme/elevated | 73.0045 | -1.9796 | Night | 202601 | 2026-01-16 | 1.9796
2026-01-16 20:44 | 71.2472 | FALSE | FALSE | 0.10131 | 0.14199 | -1.79 | -2.4507 | -0.2826 |  | 2026-01-16 20:15 | lower | TRUE | 0 | 71.3485 | FALSE | TRUE | 0.3208 | 2.187 | 72.1928 | 3 | -0.2826 | -0.07056 | 0.30185 | -0.70246 | 0.42216 | Persistent | 73.0372 | -2.24 | Night | 202601 | 2026-01-16 | 2.24
2026-01-16 20:59 | 71.2472 | FALSE | FALSE | -0.038461 | -0.054011 | -1.7886 | -2.4489 | 0 |  | 2026-01-16 20:15 | none | FALSE | 0 | 71.2087 | FALSE | FALSE | 0.3563 | 2.1192 | 72.1223 | 4 | 0 | -0.07056 | 0.30185 | 0.23376 | 0.45677 | Persistent | 73.0358 | -1.9158 | Night | 202601 | 2026-01-16 | 1.9158
2026-01-16 21:14 | 70.9646 | FALSE | FALSE | 0.060077 | 0.084585 | -2.0859 | -2.8554 | -0.2826 |  | 2026-01-16 20:15 | lower | TRUE | 0 | 71.0247 | FALSE | TRUE | 0.427 | 2.1191 | 72.0376 | 5 | -0.2826 | -0.08469 | 0.30497 | -0.64894 | 0.50645 | Persistent | 73.0505 | -2.1186 | Night | 202601 | 2026-01-16 | 2.1186
2026-01-16 21:29 | 70.9646 | FALSE | FALSE | -0.05317 | -0.074981 | -2.0015 | -2.743 | 0 |  | 2026-01-16 20:15 | none | FALSE | 0 | 70.9114 | FALSE | FALSE | 0.4693 | 2.082 | 71.9388 | 6 | 0 | -0.09882 | 0.29339 | 0.33682 | 0.51367 | Persistent | 72.9661 | -1.8965 | Night | 202601 | 2026-01-16 | 1.8965
2026-01-16 21:44 | 70.9646 | FALSE | TRUE | -0.1837 | -0.25953 | -2.0472 | -2.804 | 0 |  | 2026-01-16 20:15 | none | FALSE | 0 | 70.7809 | FALSE | FALSE | 0.5114 | 2.0232 | 71.8964 | 7 | 0 | -0.04239 | 0.1656 | 0.25597 | 0.55773 | Confirmed/Materialized Shift | 73.0118 | -1.6706 | Night | 202601 | 2026-01-16 | 1.6706
2026-01-16 21:59 | 70.682 | FALSE | TRUE | -0.091353 | -0.12941 | -2.3788 | -3.2559 | -0.2826 |  | 2026-01-16 20:15 | none | FALSE | 0 | 70.5906 | FALSE | FALSE | 0.5235 | 2.0018 | 71.8257 | 8 | -0.2826 | -0.07065 | 0.15512 | -1.3664 | 0.61754 | Confirmed/Materialized Shift | 73.0608 | -1.8521 | Night | 202601 | 2026-01-16 | 1.8521
2026-01-16 22:14 | 70.682 | FALSE | TRUE | -0.24745 | -0.35132 | -2.3655 | -3.2383 | 0 |  | 2026-01-16 20:15 | none | FALSE | 0 | 70.4345 | FALSE | FALSE | 0.5081 | 1.9595 | 71.741 | 9 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.65324 | Confirmed/Materialized Shift | 73.0475 | -1.6212 | Night | 202601 | 2026-01-16 | 1.6212
2026-01-16 22:29 | 70.682 | FALSE | TRUE | -0.37769 | -0.53722 | -2.3264 | -3.1864 | 0 |  | 2026-01-16 20:15 | none | FALSE | 0 | 70.3043 | FALSE | FALSE | 0.4961 | 1.9077 | 71.6563 | 10 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.67601 | Confirmed/Materialized Shift | 73.0084 | -1.4413 | Night | 202601 | 2026-01-16 | 1.4413
2026-01-16 22:44 | 70.3994 | FALSE | TRUE | -0.2598 | -0.37041 | -2.576 | -3.53 | -0.2826 |  | 2026-01-16 20:15 | none | FALSE | 0 | 70.1396 | FALSE | FALSE | 0.5089 | 1.8828 | 71.5575 | 11 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.70896 | Confirmed/Materialized Shift | 72.9754 | -1.6335 | Night | 202601 | 2026-01-16 | 1.6335
2026-01-16 22:59 | 70.3994 | FALSE | TRUE | -0.39355 | -0.56217 | -2.5122 | -3.4455 | 0 |  | 2026-01-16 20:15 | none | FALSE | 0 | 70.0058 | FALSE | FALSE | 0.4972 | 1.8474 | 71.4587 | 12 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.72643 | Confirmed/Materialized Shift | 72.9116 | -1.4582 | Night | 202601 | 2026-01-16 | 1.4582
2026-01-16 23:14 | 70.3994 | FALSE | TRUE | -0.49857 | -0.71326 | -2.4195 | -3.3227 | 0 |  | 2026-01-16 20:15 | none | FALSE | 0 | 69.9008 | FALSE | FALSE | 0.4878 | 1.8066 | 71.3599 | 13 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.72953 | Confirmed/Materialized Shift | 72.8189 | -1.3166 | Night | 202601 | 2026-01-16 | 1.3166
2026-01-16 23:28 | 70.3994 | FALSE | TRUE | -0.57523 | -0.82382 | -2.2985 | -3.1618 | 0 |  | 2026-01-16 20:15 | none | FALSE | 0 | 69.8242 | FALSE | FALSE | 0.48 | 1.7632 | 71.2611 | 14 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.71844 | Confirmed/Materialized Shift | 72.6979 | -1.1993 | Night | 202601 | 2026-01-16 | 1.1993
2026-01-16 23:43 | 70.3994 | FALSE | TRUE | -0.62216 | -0.89164 | -2.1478 | -2.9606 | 0 |  | 2026-01-16 20:15 | none | FALSE | 0 | 69.7772 | FALSE | FALSE | 0.4734 | 1.7191 | 71.1622 | 15 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.6925 | Confirmed/Materialized Shift | 72.5472 | -1.1016 | Night | 202601 | 2026-01-16 | 1.1016
2026-01-16 23:59 | 70.3994 | FALSE | TRUE | -0.63582 | -0.91139 | -1.9639 | -2.7139 | 0 |  | 2026-01-16 20:15 | none | FALSE | 0 | 69.7636 | FALSE | FALSE | 0.4681 | 1.6755 | 71.0634 | 16 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.64992 | Confirmed/Materialized Shift | 72.3633 | -1.0217 | Night | 202601 | 2026-01-16 | 1.0217
2026-01-17 00:14 | 70.3994 | FALSE | FALSE | -0.60897 | -0.87257 | -1.7394 | -2.4111 | 0 |  |  | none | FALSE | 0 | 69.7904 | FALSE | FALSE | 0.0642 |  | 70.9646 | 0 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.58709 | Persistence ends | 72.1388 | -0.96272 | Night | 202601 | 2026-01-17 | 0.96272
2026-01-17 00:28 | 70.3994 | FALSE | FALSE | -0.5904 | -0.84574 | -1.5512 | -2.156 | 0 |  |  | none | FALSE | 0 | 69.809 | FALSE | FALSE | 0.0598 |  | 70.8798 | 0 | 0 | -0.08478 | 0.13287 | 0.63808 | 0.53541 | Normal | 71.9506 | -0.89729 | Night | 202601 | 2026-01-17 | 0.89729
2026-01-17 00:43 | 70.1168 | FALSE | FALSE | -0.29358 | -0.42045 | -1.6218 | -2.2607 | -0.2826 |  |  | none | FALSE | 0 | 69.8232 | FALSE | FALSE | 0.0925 |  | 70.7809 | 0 | -0.2826 | -0.09891 | 0.13829 | -1.3283 | 0.47884 | Normal | 71.7386 | -1.3869 | Night | 202601 | 2026-01-17 | 1.3869
2026-01-17 00:58 | 70.1168 | FALSE | FALSE | -0.29001 | -0.41533 | -1.4487 | -2.0243 | 0 |  |  | none | FALSE | 0 | 69.8268 | FALSE | FALSE | 0.0889 |  | 70.6961 | 0 | 0 | -0.08478 | 0.13287 | 0.63808 | 0.43467 | Normal | 71.5655 | -1.3328 | Night | 202601 | 2026-01-17 | 1.3328
2026-01-17 01:13 | 70.1168 | FALSE | FALSE | -0.30316 | -0.43424 | -1.3205 | -1.8485 | 0 |  |  | none | FALSE | 0 | 69.8136 | FALSE | FALSE | 0.0835 |  | 70.6255 | 0 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.40592 | Normal | 71.4373 | -1.2532 | Night | 202601 | 2026-01-17 | 1.2532
2026-01-17 01:28 | 70.1168 | FALSE | FALSE | -0.28334 | -0.40573 | -1.1594 | -1.6266 | 0 |  |  | none | FALSE | 0 | 69.8335 | FALSE | FALSE | 0.081 |  | 70.5548 | 0 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.36068 | Normal | 71.2762 | -1.2144 | Night | 202601 | 2026-01-17 | 1.2144
2026-01-17 01:43 | 70.1168 | FALSE | FALSE | -0.28661 | -0.41045 | -1.0496 | -1.4749 | 0 |  |  | none | FALSE | 0 | 69.8302 | FALSE | FALSE | 0.0761 |  | 70.4983 | 0 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.33406 | Normal | 71.1664 | -1.142 | Night | 202601 | 2026-01-17 | 1.142
2026-01-17 01:58 | 70.1168 | FALSE | FALSE | -0.26281 | -0.37623 | -0.91279 | -1.2851 | 0 |  |  | none | FALSE | 0 | 69.854 | FALSE | FALSE | 0.0737 |  | 70.4418 | 0 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.2939 | Normal | 71.0296 | -1.1058 | Night | 202601 | 2026-01-17 | 1.1058
2026-01-17 02:13 | 70.1168 | FALSE | FALSE | -0.26753 | -0.383 | -0.83273 | -1.1737 | 0 |  |  | none | FALSE | 0 | 69.8493 | FALSE | FALSE | 0.0685 |  | 70.3994 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27506 | Normal | 70.9495 | -1.0274 | Night | 202601 | 2026-01-17 | 1.0274
2026-01-17 02:27 | 69.836 | FALSE | FALSE | -0.030433 | -0.043597 | -1.0444 | -1.4734 | -0.2808 |  |  | none | FALSE | 0 | 69.8056 | FALSE | FALSE | 0.1258 |  | 70.343 | 0 | -0.2808 | -0.05643 | 0.11579 | -1.9377 | 0.2687 | Normal | 70.8804 | -1.8867 | Night | 202601 | 2026-01-17 | 1.8867
2026-01-17 02:43 | 69.836 | FALSE | FALSE | -0.047608 | -0.068218 | -0.94869 | -1.3402 | 0 |  |  | none | FALSE | 0 | 69.7884 | FALSE | FALSE | 0.1206 |  | 70.2865 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.24907 | Normal | 70.7847 | -1.8089 | Night | 202601 | 2026-01-17 | 1.8089
2026-01-17 02:58 | 69.836 | FALSE | FALSE | -0.092187 | -0.13218 | -0.90867 | -1.2844 | 0 |  |  | none | FALSE | 0 | 69.7438 | FALSE | FALSE | 0.1088 |  | 70.2442 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.25021 | Normal | 70.7447 | -1.6316 | Night | 202601 | 2026-01-17 | 1.6316
2026-01-17 03:13 | 69.836 | FALSE | FALSE | -0.12154 | -0.17434 | -0.85342 | -1.2073 | 0 |  |  | none | FALSE | 0 | 69.7145 | FALSE | FALSE | 0.1001 |  | 70.2019 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.24374 | Normal | 70.6894 | -1.5014 | Night | 202601 | 2026-01-17 | 1.5014
2026-01-17 03:27 | 69.836 | FALSE | FALSE | -0.13437 | -0.19278 | -0.78165 | -1.1069 | 0 |  |  | none | FALSE | 0 | 69.7016 | FALSE | FALSE | 0.0942 |  | 70.1596 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.22901 | Normal | 70.6177 | -1.4132 | Night | 202601 | 2026-01-17 | 1.4132
2026-01-17 03:42 | 69.836 | FALSE | FALSE | -0.1697 | -0.24359 | -0.76064 | -1.0774 | 0 |  |  | none | FALSE | 0 | 69.6663 | FALSE | FALSE | 0.0847 |  | 70.1315 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.23259 | Normal | 70.5966 | -1.2704 | Night | 202601 | 2026-01-17 | 1.2704
2026-01-17 03:57 | 69.836 | FALSE | FALSE | -0.19779 | -0.28403 | -0.73239 | -1.0378 | 0 |  |  | none | FALSE | 0 | 69.6382 | FALSE | FALSE | 0.0766 |  | 70.1033 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.23255 | Normal | 70.5684 | -1.1495 | Night | 202601 | 2026-01-17 | 1.1495
2026-01-17 04:12 | 69.5534 | TRUE | FALSE | 0.0036365 | 0.0052281 | -1.0116 | -1.4335 | -0.2826 | 2026-01-17 06:12 | 2026-01-17 04:12 | lower | TRUE | 1 | 69.557 | FALSE | FALSE | 0.22 | 2.0144 | 70.061 | 1 | -0.2826 | -0.0423 | 0.10331 | -2.326 | 0.25198 | Extreme triggered | 70.565 | -2.0144 | Night | 202601 | 2026-01-17 | 2.0144
2026-01-17 04:27 | 69.5534 | FALSE | FALSE | -0.060609 | -0.087217 | -0.99121 | -1.4051 | 0 |  | 2026-01-17 04:12 | none | FALSE | 1 | 69.4928 | FALSE | FALSE | 0.2608 | 1.892 | 70.0187 | 2 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.26295 | Extreme/elevated | 70.5446 | -1.7695 | Night | 202601 | 2026-01-17 | 1.7695
2026-01-17 04:42 | 69.5534 | FALSE | FALSE | -0.11002 | -0.15844 | -0.95602 | -1.3559 | 0 |  | 2026-01-17 04:12 | none | FALSE | 1 | 69.4434 | FALSE | FALSE | 0.3058 | 1.7904 | 69.9764 | 3 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.26651 | Persistent | 70.5094 | -1.5872 | Night | 202601 | 2026-01-17 | 1.5872
2026-01-17 04:57 | 69.5534 | FALSE | FALSE | -0.14521 | -0.20921 | -0.90661 | -1.2867 | 0 |  | 2026-01-17 04:12 | none | FALSE | 1 | 69.4082 | FALSE | FALSE | 0.3537 | 1.7047 | 69.9341 | 4 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.26295 | Persistent | 70.46 | -1.4478 | Night | 202601 | 2026-01-17 | 1.4478
2026-01-17 05:12 | 69.5534 | FALSE | FALSE | -0.16556 | -0.23861 | -0.84236 | -1.1966 | 0 |  | 2026-01-17 04:12 | none | FALSE | 1 | 69.3878 | FALSE | FALSE | 0.4038 | 1.6324 | 69.8918 | 5 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.25198 | Persistent | 70.3958 | -1.343 | Night | 202601 | 2026-01-17 | 1.343
2026-01-17 05:27 | 69.5534 | FALSE | FALSE | -0.16899 | -0.24356 | -0.76119 | -1.0826 | 0 |  | 2026-01-17 04:12 | none | FALSE | 1 | 69.3844 | FALSE | FALSE | 0.4563 | 1.5725 | 69.8495 | 6 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.23255 | Persistent | 70.3146 | -1.2733 | Night | 202601 | 2026-01-17 | 1.2733
2026-01-17 05:42 | 69.5534 | FALSE | TRUE | -0.19724 | -0.28439 | -0.7331 | -1.043 | 0 |  | 2026-01-17 04:12 | none | FALSE | 1 | 69.3562 | FALSE | FALSE | 0.5054 | 1.5124 | 69.8213 | 7 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.23259 | Confirmed/Materialized Shift | 70.2865 | -1.152 | Night | 202601 | 2026-01-17 | 1.152
2026-01-17 05:57 | 69.5534 | FALSE | TRUE | -0.21825 | -0.31478 | -0.69777 | -0.99326 | 0 |  | 2026-01-17 04:12 | none | FALSE | 1 | 69.3351 | FALSE | FALSE | 0.4984 | 1.4543 | 69.7932 | 8 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.22901 | Confirmed/Materialized Shift | 70.2512 | -1.047 | Night | 202601 | 2026-01-17 | 1.047
2026-01-17 06:12 | 69.5534 | FALSE | FALSE | -0.23168 | -0.33421 | -0.65486 | -0.93274 | 0 |  |  | none | FALSE | 1 | 69.3217 | FALSE | FALSE | 0.0922 |  | 69.765 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.22163 | Persistence ends | 70.2083 | -0.95468 | Night | 202601 | 2026-01-17 | 0.95468
2026-01-17 06:26 | 69.5534 | FALSE | FALSE | -0.23672 | -0.3415 | -0.60356 | -0.86029 | 0 |  |  | none | FALSE | 1 | 69.3167 | FALSE | FALSE | 0.0868 |  | 69.7368 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.21007 | Normal | 70.157 | -0.87315 | Night | 202601 | 2026-01-17 | 0.87315
2026-01-17 06:41 | 69.5534 | FALSE | FALSE | -0.23187 | -0.33448 | -0.54237 | -0.77375 | 0 |  |  | none | FALSE | 0 | 69.3215 | FALSE | FALSE | 0.0535 |  | 69.7087 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.19356 | Normal | 70.0958 | -0.80209 | Night | 202601 | 2026-01-17 | 0.80209
2026-01-17 06:56 | 69.5534 | FALSE | FALSE | -0.21427 | -0.30902 | -0.46843 | -0.66898 | 0 |  |  | none | FALSE | 0 | 69.3391 | FALSE | FALSE | 0.0496 |  | 69.6805 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.17068 | Normal | 70.0218 | -0.74457 | Night | 202601 | 2026-01-17 | 0.74457
2026-01-17 07:11 | 69.2708 | TRUE | FALSE | 0.044515 | 0.064221 | -0.69025 | -0.98661 | -0.2826 | 2026-01-17 07:45 | 2026-01-17 07:11 | lower | TRUE | 1 | 69.3153 | FALSE | FALSE | 0.2374 | 2.2757 | 69.6382 | 1 | -0.2826 | -0.0423 | 0.10331 | -2.326 | 0.16143 | Extreme triggered | 69.961 | -2.2757 | Night | 202601 | 2026-01-17 | 2.2757
2026-01-17 07:26 | 69.2708 | FALSE | FALSE | -0.0088098 | -0.012719 | -0.68705 | -0.98209 | 0 |  | 2026-01-17 07:11 | none | FALSE | 1 | 69.262 | FALSE | FALSE | 0.2728 | 2.1126 | 69.6099 | 2 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.17396 | Extreme/elevated | 69.9578 | -1.9494 | Day | 202601 | 2026-01-17 | 1.9494
2026-01-17 07:30 | 69.2708 | FALSE | FALSE | -0.051277 | -0.074079 | -0.673 | -0.9622 | 0 |  | 2026-01-17 07:11 | none | FALSE | 1 | 69.2195 | FALSE | FALSE | 0.3145 | 1.9806 | 69.5817 | 3 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18107 | Persistent | 69.9438 | -1.7168 | Day | 202601 | 2026-01-17 | 1.7168
2026-01-17 07:45 | 69.5534 | TRUE | FALSE | -0.32771 | -0.47339 | -0.35597 | -0.50918 | 0.2826 |  |  | none | FALSE | 2 | 69.2257 | TRUE | FALSE | 0.0627 |  | 69.5675 | 0 | 0.2826 | -0.01413 | 0.11135 | 2.6647 | 0.17092 | Persistence ends | 69.9094 | -0.082671 | Day | 202601 | 2026-01-17 | 0.082671
2026-01-17 08:00 | 69.5534 | FALSE | FALSE | -0.31761 | -0.45874 | -0.31761 | -0.45457 | 0 |  |  | none | FALSE | 2 | 69.2358 | FALSE | FALSE | 0.0571 |  | 69.5534 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.15881 | Normal | 69.871 | 0 | Day | 202601 | 2026-01-17 | 0
2026-01-17 08:16 | 69.5534 | FALSE | FALSE | -0.30262 | -0.43699 | -0.27436 | -0.39291 | 0 |  |  | none | FALSE | 2 | 69.2508 | FALSE | FALSE | 0.0637 |  | 69.5393 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14424 | Normal | 69.8278 | 0.097959 | Day | 202601 | 2026-01-17 | 0.097959
2026-01-17 08:30 | 69.5534 | FALSE | FALSE | -0.28103 | -0.40568 | -0.22451 | -0.32174 | 0 |  |  | none | FALSE | 2 | 69.2724 | FALSE | FALSE | 0.072 |  | 69.5251 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.12638 | Normal | 69.7779 | 0.22361 | Day | 202601 | 2026-01-17 | 0.22361
2026-01-17 08:30 | 69.5534 | FALSE | FALSE | -0.24945 | -0.35994 | -0.16467 | -0.23619 | 0 |  |  | none | FALSE | 2 | 69.304 | FALSE | FALSE | 0.0844 |  | 69.511 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.10353 | Normal | 69.7181 | 0.40945 | Day | 202601 | 2026-01-17 | 0.40945
2026-01-17 08:45 | 69.5534 | FALSE | FALSE | -0.24945 | -0.35994 | -0.16467 | -0.23619 | 0 |  |  | none | FALSE | 2 | 69.304 | FALSE | FALSE | 0.0844 |  | 69.511 | 0 | 0 | 0 | 0.091688 | 0 | 0.10353 | Normal | 69.7181 | 0.40945 | Day | 202601 | 2026-01-17 | 0.40945
2026-01-17 09:00 | 70.1168 | TRUE | FALSE | -0.91881 | -1.3278 | 0.23643 | 0.33833 | 0.5634 | 2026-01-17 13:28 | 2026-01-17 09:00 | upper | TRUE | 3 | 69.198 | TRUE | FALSE | 0.3686 | 3.3859 | 69.5392 | 1 | 0.5634 | 0.02817 | 0.15581 | 3.4351 | 0.1706 | Extreme triggered | 69.8804 | 3.3859 | Day | 202601 | 2026-01-17 | 3.3859
2026-01-17 09:15 | 70.3994 | FALSE | FALSE | -1.3323 | -1.929 | 0.30351 | 0.43299 | 0.2826 |  | 2026-01-17 09:00 | upper | TRUE | 2 | 69.0671 | FALSE | FALSE | 0.3834 | 3.2829 | 69.5815 | 2 | 0.2826 | 0.0423 | 0.16563 | 1.4508 | 0.25721 | Extreme/elevated | 70.0959 | 3.18 | Day | 202601 | 2026-01-17 | 3.18
2026-01-17 09:30 | 70.682 | FALSE | FALSE | -1.7554 | -2.5468 | 0.33274 | 0.47298 | 0.2826 |  | 2026-01-17 09:00 | upper | TRUE | 2 | 68.9266 | FALSE | TRUE | 0.4243 | 3.1671 | 69.6379 | 3 | 0.2826 | 0.05643 | 0.17369 | 1.3022 | 0.35568 | Persistent | 70.3493 | 2.9355 | Day | 202601 | 2026-01-17 | 2.9355
2026-01-17 09:45 | 70.9646 | FALSE | FALSE | -2.1803 | -3.1698 | 0.33195 | 0.46997 | 0.2826 |  | 2026-01-17 09:00 | upper | TRUE | 2 | 68.7843 | FALSE | TRUE | 0.4669 | 3.0549 | 69.7085 | 4 | 0.2826 | 0.07056 | 0.18023 | 1.1765 | 0.46209 | Persistent | 70.6326 | 2.7184 | Day | 202601 | 2026-01-17 | 2.7184
2026-01-17 10:00 | 71.2472 | FALSE | FALSE | -2.6018 | -3.7902 | 0.3063 | 0.43177 | 0.2826 |  | 2026-01-17 09:00 | upper | TRUE | 1 | 68.6454 | FALSE | TRUE | 0.4832 | 2.9507 | 69.7932 | 5 | 0.2826 | 0.08469 | 0.18541 | 1.0674 | 0.57387 | Persistent | 70.9409 | 2.5337 | Day | 202601 | 2026-01-17 | 2.5337
2026-01-17 10:15 | 71.5298 | FALSE | FALSE | -3.0159 | -4.4018 | 0.25977 | 0.36449 | 0.2826 |  | 2026-01-17 09:00 | upper | TRUE | 1 | 68.5139 | FALSE | TRUE | 0.5299 | 2.8551 | 69.892 | 6 | 0.2826 | 0.09882 | 0.18934 | 0.97063 | 0.68902 | Persistent | 71.27 | 2.377 | Day | 202601 | 2026-01-17 | 2.377
2026-01-17 10:29 | 71.8124 | FALSE | TRUE | -3.4192 | -4.9993 | 0.19577 | 0.27335 | 0.2826 |  | 2026-01-17 09:00 | upper | TRUE | 1 | 68.3932 | FALSE | TRUE | 0.5781 | 2.7676 | 70.0049 | 7 | 0.2826 | 0.11295 | 0.1921 | 0.88312 | 0.80585 | Confirmed/Materialized Shift | 71.6166 | 2.2429 | Day | 202601 | 2026-01-17 | 2.2429
2026-01-17 10:44 | 72.095 | FALSE | TRUE | -3.8086 | -5.5774 | 0.11736 | 0.16306 | 0.2826 |  | 2026-01-17 09:00 | upper | TRUE | 1 | 68.2864 | FALSE | TRUE | 0.5704 | 2.6876 | 70.132 | 8 | 0.2826 | 0.12708 | 0.19374 | 0.80271 | 0.92281 | Confirmed/Materialized Shift | 71.9776 | 2.1272 | Day | 202601 | 2026-01-17 | 2.1272
2026-01-17 10:59 | 72.095 | FALSE | TRUE | -3.8556 | -5.6501 | -0.18376 | -0.25424 | 0 |  | 2026-01-17 09:00 | none | FALSE | 1 | 68.2394 | FALSE | FALSE | 0.5498 | 2.591 | 70.2591 | 9 | 0 | 0.12708 | 0.19374 | -0.65592 | 1.0098 | Confirmed/Materialized Shift | 72.2788 | 1.818 | Day | 202601 | 2026-01-17 | 1.818
2026-01-17 11:14 | 72.3758 | FALSE | TRUE | -4.1741 | -6.1203 | -0.22296 | -0.30712 | 0.2808 |  | 2026-01-17 09:00 | none | FALSE | 1 | 68.2017 | FALSE | FALSE | 0.5484 | 2.5116 | 70.4002 | 10 | 0.2808 | 0.14112 | 0.19422 | 0.71917 | 1.0993 | Confirmed/Materialized Shift | 72.5988 | 1.7972 | Day | 202601 | 2026-01-17 | 1.7972
2026-01-17 11:29 | 72.6584 | FALSE | TRUE | -4.4809 | -6.5724 | -0.27503 | -0.3771 | 0.2826 |  | 2026-01-17 09:00 | none | FALSE | 0 | 68.1775 | FALSE | FALSE | 0.5179 | 2.444 | 70.5555 | 11 | 0.2826 | 0.15525 | 0.1937 | 0.65747 | 1.189 | Confirmed/Materialized Shift | 72.9334 | 1.7687 | Day | 202601 | 2026-01-17 | 1.7687
2026-01-17 11:44 | 72.6584 | FALSE | TRUE | -4.4069 | -6.4569 | -0.53981 | -0.73746 | 0 |  | 2026-01-17 09:00 | none | FALSE | 0 | 68.2515 | FALSE | FALSE | 0.5042 | 2.3707 | 70.7248 | 12 | 0 | 0.16938 | 0.16878 | -1.0036 | 1.2367 | Confirmed/Materialized Shift | 73.1982 | 1.5635 | Day | 202601 | 2026-01-17 | 1.5635
2026-01-17 11:59 | 72.941 | FALSE | TRUE | -4.5948 | -6.7228 | -0.5295 | -0.7207 | 0.2826 |  | 2026-01-17 09:00 | none | FALSE | 0 | 68.3462 | FALSE | FALSE | 0.5058 | 2.3104 | 70.9083 | 13 | 0.2826 | 0.18351 | 0.16565 | 0.59818 | 1.2811 | Confirmed/Materialized Shift | 73.4705 | 1.5867 | Day | 202601 | 2026-01-17 | 1.5867
2026-01-17 12:14 | 73.2236 | FALSE | TRUE | -4.7566 | -6.9472 | -0.52135 | -0.70696 | 0.2826 |  | 2026-01-17 09:00 | none | FALSE | 0 | 68.467 | FALSE | FALSE | 0.507 | 2.26 | 71.106 | 14 | 0.2826 | 0.19764 | 0.16117 | 0.52715 | 1.3195 | Confirmed/Materialized Shift | 73.7449 | 1.6049 | Day | 202601 | 2026-01-17 | 1.6049
2026-01-17 12:29 | 73.5062 | FALSE | TRUE | -4.9421 | -7.208 | -0.53696 | -0.72519 | 0.2826 |  | 2026-01-17 09:00 | none | FALSE | 0 | 68.5641 | FALSE | FALSE | 0.5072 | 2.2165 | 71.3036 | 15 | 0.2826 | 0.19764 | 0.16117 | 0.52715 | 1.3698 | Confirmed/Materialized Shift | 74.0432 | 1.608 | Day | 202601 | 2026-01-17 | 1.608
2026-01-17 12:44 | 73.5062 | FALSE | TRUE | -4.7829 | -6.9596 | -0.77301 | -1.0407 | 0 |  | 2026-01-17 09:00 | none | FALSE | 0 | 68.7233 | FALSE | FALSE | 0.4962 | 2.1682 | 71.5013 | 16 | 0 | 0.19764 | 0.16117 | -1.2263 | 1.389 | Confirmed/Materialized Shift | 74.2792 | 1.4435 | Day | 202601 | 2026-01-17 | 1.4435
2026-01-17 12:59 | 73.2236 | TRUE | TRUE | -4.2593 | -6.1761 | -1.1816 | -1.5881 | -0.2826 |  | 2026-01-17 09:00 | none | FALSE | 1 | 68.9643 | FALSE | FALSE | 0.504 | 2.1072 | 71.6848 | 17 | -0.2826 | 0.18351 | 0.18933 | -2.4618 | 1.3602 | Confirmed/Materialized Shift | 74.4052 | 1.1313 | Day | 202601 | 2026-01-17 | 1.1313
2026-01-17 13:14 | 73.2236 | FALSE | TRUE | -3.9632 | -5.7222 | -1.2526 | -1.6819 | 0 |  | 2026-01-17 09:00 | none | FALSE | 1 | 69.2604 | FALSE | FALSE | 0.4979 | 2.0479 | 71.8683 | 18 | 0 | 0.18351 | 0.18933 | -0.96924 | 1.304 | Confirmed/Materialized Shift | 74.4762 | 1.0394 | Day | 202601 | 2026-01-17 | 1.0394
2026-01-17 13:28 | 73.2236 | FALSE | FALSE | -3.6045 | -5.1775 | -1.2609 | -1.6928 | 0 |  |  | none | FALSE | 1 | 69.6191 | FALSE | FALSE | 0.0928 |  | 72.0518 | 0 | 0 | 0.18351 | 0.18933 | -0.96924 | 1.2163 | Persistence ends | 74.4845 | 0.96338 | Day | 202601 | 2026-01-17 | 0.96338
2026-01-17 13:43 | 73.2236 | FALSE | FALSE | -3.168 | -4.5221 | -1.1914 | -1.6011 | 0 |  |  | none | FALSE | 1 | 70.0556 | FALSE | FALSE | 0.089 |  | 72.2353 | 0 | 0 | 0.18351 | 0.18933 | -0.96924 | 1.0899 | Normal | 74.415 | 0.9068 | Day | 202601 | 2026-01-17 | 0.9068
2026-01-17 13:59 | 73.2236 | FALSE | FALSE | -2.8104 | -3.9913 | -1.1445 | -1.539 | 0 |  |  | none | FALSE | 1 | 70.4132 | FALSE | FALSE | 0.0847 |  | 72.3906 | 0 | 0 | 0.15534 | 0.17085 | -0.90923 | 0.98873 | Normal | 74.3681 | 0.84244 | Day | 202601 | 2026-01-17 | 0.84244
2026-01-17 14:14 | 73.2236 | FALSE | FALSE | -2.4631 | -3.4809 | -1.0796 | -1.453 | 0 |  |  | none | FALSE | 1 | 70.7605 | FALSE | FALSE | 0.0806 |  | 72.5319 | 0 | 0 | 0.14121 | 0.17145 | -0.8236 | 0.88568 | Normal | 74.3032 | 0.78103 | Day | 202601 | 2026-01-17 | 0.78103
2026-01-17 14:28 | 73.2236 | FALSE | FALSE | -2.1299 | -2.9959 | -1.0006 | -1.3481 | 0 |  |  | none | FALSE | 1 | 71.0937 | FALSE | FALSE | 0.0767 |  | 72.6589 | 0 | 0 | 0.12708 | 0.17083 | -0.74389 | 0.78263 | Normal | 74.2242 | 0.72149 | Day | 202601 | 2026-01-17 | 0.72149
2026-01-17 14:43 | 73.2236 | FALSE | FALSE | -1.8152 | -2.542 | -0.91176 | -1.2299 | 0 |  |  | none | FALSE | 1 | 71.4084 | FALSE | FALSE | 0.0727 |  | 72.7719 | 0 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.68174 | Normal | 74.1354 | 0.66259 | Day | 202601 | 2026-01-17 | 0.66259
2026-01-17 14:58 | 73.2236 | FALSE | FALSE | -1.524 | -2.1255 | -0.81821 | -1.1051 | 0 |  |  | none | FALSE | 1 | 71.6996 | FALSE | FALSE | 0.0687 |  | 72.8707 | 0 | 0 | 0.09882 | 0.16582 | -0.59594 | 0.58555 | Normal | 74.0418 | 0.60266 | Day | 202601 | 2026-01-17 | 0.60266
2026-01-17 15:13 | 73.5062 | FALSE | FALSE | -1.5549 | -2.1611 | -0.48159 | -0.6509 | 0.2826 |  |  | none | FALSE | 1 | 71.9513 | FALSE | FALSE | 0.0988 |  | 72.9695 | 0 | 0.2826 | 0.09882 | 0.16582 | 1.1083 | 0.50913 | Normal | 73.9878 | 1.0541 | Day | 202601 | 2026-01-17 | 1.0541
2026-01-17 15:28 | 73.5062 | FALSE | FALSE | -1.3382 | -1.8543 | -0.43425 | -0.5873 | 0 |  |  | none | FALSE | 0 | 72.168 | FALSE | FALSE | 0.068 |  | 73.0542 | 0 | 0 | 0.08469 | 0.16132 | -0.52499 | 0.44311 | Normal | 73.9404 | 1.02 | Day | 202601 | 2026-01-17 | 1.02
2026-01-17 15:43 | 73.5062 | FALSE | FALSE | -1.1648 | -1.6102 | -0.402 | -0.54391 | 0 |  |  | none | FALSE | 0 | 72.3414 | FALSE | FALSE | 0.0649 |  | 73.1248 | 0 | 0 | 0.07056 | 0.15534 | -0.45424 | 0.39171 | Normal | 73.9082 | 0.97373 | Day | 202601 | 2026-01-17 | 0.97373
2026-01-17 15:58 | 73.5062 | FALSE | FALSE | -0.94344 | -1.3002 | -0.32172 | -0.43577 | 0 |  |  | none | FALSE | 0 | 72.5628 | FALSE | FALSE | 0.0655 |  | 73.1953 | 0 | 0 | 0.07056 | 0.15534 | -0.45424 | 0.31629 | Normal | 73.8279 | 0.98284 | Day | 202601 | 2026-01-17 | 0.98284
2026-01-17 16:13 | 73.5062 | FALSE | FALSE | -0.76975 | -1.0583 | -0.26107 | -0.35391 | 0 |  |  | none | FALSE | 0 | 72.7364 | FALSE | FALSE | 0.0658 |  | 73.2519 | 0 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.25771 | Normal | 73.7673 | 0.98694 | Day | 202601 | 2026-01-17 | 0.98694
2026-01-17 16:28 | 73.5062 | FALSE | FALSE | -0.65642 | -0.90106 | -0.23252 | -0.31533 | 0 |  |  | none | FALSE | 0 | 72.8498 | FALSE | FALSE | 0.0636 |  | 73.2943 | 0 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.22224 | Normal | 73.7387 | 0.95372 | Day | 202601 | 2026-01-17 | 0.95372
2026-01-17 16:43 | 73.5062 | FALSE | FALSE | -0.50769 | -0.69548 | -0.16857 | -0.2288 | 0 |  |  | none | FALSE | 0 | 72.9985 | FALSE | FALSE | 0.0669 |  | 73.3366 | 0 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.16906 | Normal | 73.6748 | 1.0029 | Day | 202601 | 2026-01-17 | 1.0029
2026-01-17 16:58 | 73.2236 | TRUE | FALSE | -0.16132 | -0.2208 | -0.41566 | -0.56445 | -0.2826 |  |  | none | FALSE | 1 | 73.0623 | FALSE | FALSE | 0.0873 |  | 73.3508 | 0 | -0.2826 | 0.01413 | 0.14424 | -2.0571 | 0.14424 | Normal | 73.6393 | -0.88163 | Day | 202601 | 2026-01-17 | 0.88163
2026-01-17 17:13 | 73.2236 | FALSE | FALSE | -0.16132 | -0.2208 | -0.41566 | -0.56445 | 0 |  |  | none | FALSE | 1 | 73.0623 | FALSE | FALSE | 0.0873 |  | 73.3508 | 0 | 0 | 0 | 0.12967 | 0 | 0.14424 | Normal | 73.6393 | -0.88163 | Day | 202601 | 2026-01-17 | 0.88163
2026-01-17 17:27 | 73.2236 | FALSE | FALSE | -0.17104 | -0.23414 | -0.39712 | -0.53942 | 0 |  |  | none | FALSE | 1 | 73.0526 | FALSE | FALSE | 0.0816 |  | 73.3366 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14204 | Normal | 73.6207 | -0.79582 | Day | 202601 | 2026-01-17 | 0.79582
2026-01-17 17:30 | 73.2236 | FALSE | FALSE | -0.17768 | -0.24324 | -0.3755 | -0.51019 | 0 |  |  | none | FALSE | 1 | 73.0459 | FALSE | FALSE | 0.0763 |  | 73.3225 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13829 | Normal | 73.5991 | -0.71522 | Day | 202601 | 2026-01-17 | 0.71522
2026-01-17 17:31 | 73.2236 | FALSE | FALSE | -0.17768 | -0.24324 | -0.3755 | -0.51019 | 0 |  |  | none | FALSE | 1 | 73.0459 | FALSE | FALSE | 0.0763 |  | 73.3225 | 0 | 0 | 0 | 0.091688 | 0 | 0.13829 | Normal | 73.5991 | -0.71522 | Day | 202601 | 2026-01-17 | 0.71522
2026-01-17 17:46 | 73.2236 | FALSE | FALSE | -0.17768 | -0.24324 | -0.3755 | -0.51019 | 0 |  |  | none | FALSE | 1 | 73.0459 | FALSE | FALSE | 0.0763 |  | 73.3225 | 0 | 0 | 0 | 0.091688 | 0 | 0.13829 | Normal | 73.5991 | -0.71522 | Day | 202601 | 2026-01-17 | 0.71522
2026-01-17 18:01 | 73.5062 | TRUE | FALSE | -0.45364 | -0.62098 | -0.11452 | -0.15556 | 0.2826 |  |  | none | FALSE | 2 | 73.0526 | TRUE | FALSE | 0.1367 |  | 73.3366 | 0 | 0.2826 | 0.01413 | 0.11135 | 2.411 | 0.14204 | Normal | 73.6207 | 1.1937 | Night | 202601 | 2026-01-17 | 1.1937
2026-01-17 18:16 | 73.7888 | TRUE | FALSE | -0.76696 | -1.0503 | 0.080837 | 0.10967 | 0.2826 | 2026-01-17 19:29 | 2026-01-17 18:16 | upper | TRUE | 3 | 73.0218 | TRUE | FALSE | 0.3076 | 2.4713 | 73.3649 | 1 | 0.2826 | 0.02826 | 0.12638 | 2.0125 | 0.17153 | Extreme triggered | 73.708 | 2.4713 | Night | 202601 | 2026-01-17 | 2.4713
2026-01-17 18:30 | 73.7888 | FALSE | FALSE | -0.78029 | -1.0688 | 0.010989 | 0.014895 | 0 |  | 2026-01-17 18:16 | upper | TRUE | 3 | 73.0085 | FALSE | FALSE | 0.3371 | 2.2642 | 73.3932 | 2 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.19233 | Extreme/elevated | 73.7778 | 2.0571 | Night | 202601 | 2026-01-17 | 2.0571
2026-01-17 18:45 | 73.7888 | FALSE | FALSE | -0.7815 | -1.0704 | -0.046739 | -0.063302 | 0 |  | 2026-01-17 18:16 | none | FALSE | 3 | 73.0073 | FALSE | FALSE | 0.3754 | 2.1009 | 73.4214 | 3 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.20706 | Persistent | 73.8355 | 1.7743 | Night | 202601 | 2026-01-17 | 1.7743
2026-01-17 19:00 | 73.7888 | FALSE | FALSE | -0.77306 | -1.0588 | -0.094825 | -0.12834 | 0 |  | 2026-01-17 18:16 | none | FALSE | 2 | 73.0157 | FALSE | FALSE | 0.3899 | 1.9664 | 73.4497 | 4 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.21697 | Persistent | 73.8836 | 1.563 | Night | 202601 | 2026-01-17 | 1.563
2026-01-17 19:15 | 73.7888 | FALSE | FALSE | -0.75628 | -1.0355 | -0.13456 | -0.18202 | 0 |  | 2026-01-17 18:16 | none | FALSE | 2 | 73.0325 | FALSE | FALSE | 0.4359 | 1.8523 | 73.4779 | 5 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.22271 | Persistent | 73.9234 | 1.3958 | Night | 202601 | 2026-01-17 | 1.3958
2026-01-17 19:29 | 73.5062 | TRUE | FALSE | -0.4432 | -0.60661 | -0.41494 | -0.56133 | -0.2826 |  |  | none | FALSE | 3 | 73.063 | TRUE | FALSE | 0.0901 |  | 73.4921 | 0 | -0.2826 | 0.01413 | 0.14424 | -2.0571 | 0.21454 | Persistence ends | 73.9211 | 0.065863 | Night | 202601 | 2026-01-17 | 0.065863
2026-01-17 19:44 | 73.5062 | FALSE | FALSE | -0.4432 | -0.60661 | -0.41494 | -0.56133 | 0 |  |  | none | FALSE | 3 | 73.063 | FALSE | FALSE | 0.0901 |  | 73.4921 | 0 | 0 | 0 | 0.12967 | 0 | 0.21454 | Normal | 73.9211 | 0.065863 | Night | 202601 | 2026-01-17 | 0.065863
2026-01-17 19:59 | 73.5062 | FALSE | FALSE | -0.4432 | -0.60661 | -0.41494 | -0.56133 | 0 |  |  | none | FALSE | 3 | 73.063 | FALSE | FALSE | 0.0901 |  | 73.4921 | 0 | 0 | 0 | 0.12967 | 0 | 0.21454 | Normal | 73.9211 | 0.065863 | Night | 202601 | 2026-01-17 | 0.065863
2026-01-17 20:15 | 73.2236 | FALSE | FALSE | -0.19108 | -0.26163 | -0.69976 | -0.9466 | -0.2826 |  |  | none | FALSE | 3 | 73.0325 | FALSE | FALSE | 0.1618 |  | 73.4779 | 0 | -0.2826 | -0.01413 | 0.14424 | -1.8612 | 0.22271 | Normal | 73.9234 | -1.142 | Night | 202601 | 2026-01-17 | 1.142
2026-01-17 20:29 | 73.2236 | FALSE | FALSE | -0.21914 | -0.30018 | -0.69956 | -0.94634 | 0 |  |  | none | FALSE | 2 | 73.0045 | FALSE | FALSE | 0.1269 |  | 73.4638 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.22968 | Normal | 73.9232 | -1.0459 | Night | 202601 | 2026-01-17 | 1.0459
2026-01-17 20:44 | 73.2236 | FALSE | FALSE | -0.24502 | -0.33574 | -0.69718 | -0.94314 | 0 |  |  | none | FALSE | 1 | 72.9786 | FALSE | FALSE | 0.0926 |  | 73.4497 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.23555 | Normal | 73.9208 | -0.9598 | Night | 202601 | 2026-01-17 | 0.9598
2026-01-17 20:59 | 73.2236 | FALSE | FALSE | -0.26886 | -0.36853 | -0.69276 | -0.93723 | 0 |  |  | none | FALSE | 1 | 72.9547 | FALSE | FALSE | 0.0873 |  | 73.4356 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.24041 | Normal | 73.9164 | -0.88163 | Night | 202601 | 2026-01-17 | 0.88163
2026-01-17 21:14 | 73.2236 | FALSE | FALSE | -0.2908 | -0.39872 | -0.68644 | -0.92875 | 0 |  |  | none | FALSE | 1 | 72.9328 | FALSE | FALSE | 0.0826 |  | 73.4214 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.24431 | Normal | 73.91 | -0.80971 | Night | 202601 | 2026-01-17 | 0.80971
2026-01-17 21:29 | 73.2236 | FALSE | FALSE | -0.2908 | -0.39872 | -0.68644 | -0.92875 | 0 |  |  | none | FALSE | 1 | 72.9328 | FALSE | FALSE | 0.0826 |  | 73.4214 | 0 | 0 | 0 | 0.12967 | 0 | 0.24431 | Normal | 73.91 | -0.80971 | Night | 202601 | 2026-01-17 | 0.80971
2026-01-17 21:44 | 72.941 | FALSE | FALSE | -0.061212 | -0.083991 | -0.99379 | -1.3441 | -0.2826 |  |  | none | FALSE | 1 | 72.8798 | FALSE | FALSE | 0.1464 |  | 73.4073 | 0 | -0.2826 | -0.01413 | 0.14424 | -1.8612 | 0.26375 | Normal | 73.9348 | -1.7679 | Night | 202601 | 2026-01-17 | 1.7679
2026-01-17 21:59 | 72.941 | FALSE | FALSE | -0.11006 | -0.15111 | -1.0144 | -1.3716 | 0 |  |  | none | FALSE | 0 | 72.8309 | FALSE | FALSE | 0.1072 |  | 73.3932 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.28111 | Normal | 73.9554 | -1.6085 | Night | 202601 | 2026-01-17 | 1.6085
2026-01-17 22:14 | 72.941 | FALSE | FALSE | -0.15547 | -0.21359 | -1.0315 | -1.3945 | 0 |  |  | none | FALSE | 0 | 72.7855 | FALSE | FALSE | 0.0984 |  | 73.379 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.29675 | Normal | 73.9725 | -1.4761 | Night | 202601 | 2026-01-17 | 1.4761
2026-01-17 22:28 | 72.941 | FALSE | FALSE | -0.19796 | -0.27213 | -1.0458 | -1.4134 | 0 |  |  | none | FALSE | 0 | 72.743 | FALSE | FALSE | 0.0909 |  | 73.3649 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.31093 | Normal | 73.9868 | -1.3633 | Night | 202601 | 2026-01-17 | 1.3633
2026-01-17 22:43 | 72.941 | FALSE | FALSE | -0.23791 | -0.32724 | -1.0575 | -1.429 | 0 |  |  | none | FALSE | 0 | 72.7031 | FALSE | FALSE | 0.0844 |  | 73.3508 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.32384 | Normal | 73.9985 | -1.2653 | Night | 202601 | 2026-01-17 | 1.2653
2026-01-17 22:59 | 72.6584 | FALSE | FALSE | -0.062592 | -0.08622 | -1.3626 | -1.8408 | -0.2826 |  |  | none | FALSE | 0 | 72.5958 | FALSE | FALSE | 0.1216 |  | 73.3084 | 0 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.35629 | Normal | 74.021 | -1.8243 | Night | 202601 | 2026-01-17 | 1.8243
2026-01-17 23:14 | 72.6584 | FALSE | FALSE | -0.13774 | -0.18994 | -1.3247 | -1.7905 | 0 |  |  | none | FALSE | 0 | 72.5207 | FALSE | FALSE | 0.1082 |  | 73.2519 | 0 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.3656 | Normal | 73.9831 | -1.6232 | Night | 202601 | 2026-01-17 | 1.6232
2026-01-17 23:28 | 72.3758 | FALSE | FALSE | 0.021495 | 0.02969 | -1.5893 | -2.1487 | -0.2826 | 2026-01-18 02:57 | 2026-01-17 23:28 | lower | TRUE | 0 | 72.3973 | FALSE | FALSE | 0.1941 | 2.0548 | 73.1812 | 1 | -0.2826 | -0.07065 | 0.12555 | -1.6882 | 0.39196 | Extreme triggered | 73.9651 | -2.0548 | Night | 202601 | 2026-01-17 | 2.0548
2026-01-17 23:43 | 72.3758 | FALSE | FALSE | -0.072924 | -0.10086 | -1.5424 | -2.0867 | 0 |  | 2026-01-17 23:28 | none | FALSE | 0 | 72.3029 | FALSE | FALSE | 0.2356 | 1.9371 | 73.1106 | 2 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.40384 | Extreme/elevated | 73.9182 | -1.8194 | Night | 202601 | 2026-01-17 | 1.8194
2026-01-17 23:58 | 72.3758 | FALSE | FALSE | -0.14097 | -0.19515 | -1.4692 | -1.9896 | 0 |  | 2026-01-17 23:28 | none | FALSE | 0 | 72.2348 | FALSE | FALSE | 0.2814 | 1.8414 | 73.0399 | 3 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.40254 | Persistent | 73.845 | -1.6498 | Night | 202601 | 2026-01-17 | 1.6498
2026-01-18 00:13 | 72.3758 | FALSE | FALSE | -0.18237 | -0.25261 | -1.3693 | -1.8568 | 0 |  | 2026-01-17 23:28 | none | FALSE | 0 | 72.1934 | FALSE | FALSE | 0.3306 | 1.7635 | 72.9693 | 4 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.38792 | Persistent | 73.7451 | -1.5299 | Night | 202601 | 2026-01-18 | 1.5299
2026-01-18 00:28 | 72.3758 | FALSE | FALSE | -0.23889 | -0.33116 | -1.3128 | -1.7815 | 0 |  | 2026-01-17 23:28 | none | FALSE | 0 | 72.1369 | FALSE | FALSE | 0.378 | 1.6876 | 72.9127 | 5 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.38792 | Persistent | 73.6886 | -1.3842 | Night | 202601 | 2026-01-18 | 1.3842
2026-01-18 00:43 | 72.3758 | FALSE | FALSE | -0.27788 | -0.38541 | -1.2387 | -1.6827 | 0 |  | 2026-01-17 23:28 | none | FALSE | 0 | 72.0979 | FALSE | FALSE | 0.4273 | 1.6175 | 72.8562 | 6 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.37915 | Persistent | 73.6145 | -1.2671 | Night | 202601 | 2026-01-18 | 1.2671
2026-01-18 00:58 | 72.3758 | FALSE | TRUE | -0.29805 | -0.41351 | -1.1458 | -1.5585 | 0 |  | 2026-01-17 23:28 | none | FALSE | 0 | 72.0778 | FALSE | FALSE | 0.4783 | 1.5542 | 72.7997 | 7 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.36097 | Confirmed/Materialized Shift | 73.5216 | -1.1743 | Night | 202601 | 2026-01-18 | 1.1743
2026-01-18 01:13 | 72.3758 | FALSE | TRUE | -0.33518 | -0.46526 | -1.0982 | -1.4947 | 0 |  | 2026-01-17 23:28 | none | FALSE | 0 | 72.0406 | FALSE | FALSE | 0.471 | 1.493 | 72.7573 | 8 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.35834 | Confirmed/Materialized Shift | 73.474 | -1.0646 | Night | 202601 | 2026-01-18 | 1.0646
2026-01-18 01:28 | 72.095 | FALSE | TRUE | -0.13359 | -0.18564 | -1.3453 | -1.8319 | -0.2808 |  | 2026-01-17 23:28 | none | FALSE | 0 | 71.9614 | FALSE | FALSE | 0.5092 | 1.5092 | 72.7009 | 9 | -0.2808 | -0.05643 | 0.11579 | -1.9377 | 0.36973 | Confirmed/Materialized Shift | 73.4403 | -1.6387 | Night | 202601 | 2026-01-18 | 1.6387
2026-01-18 01:43 | 72.095 | FALSE | TRUE | -0.1943 | -0.27023 | -1.2932 | -1.7621 | 0 |  | 2026-01-17 23:28 | none | FALSE | 0 | 71.9007 | FALSE | FALSE | 0.4985 | 1.506 | 72.6445 | 10 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.37187 | Confirmed/Materialized Shift | 73.3882 | -1.4775 | Night | 202601 | 2026-01-18 | 1.4775
2026-01-18 01:58 | 72.095 | FALSE | TRUE | -0.23684 | -0.32959 | -1.2229 | -1.6679 | 0 |  | 2026-01-17 23:28 | none | FALSE | 0 | 71.8582 | FALSE | FALSE | 0.4901 | 1.4919 | 72.588 | 11 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.36493 | Confirmed/Materialized Shift | 73.3179 | -1.351 | Night | 202601 | 2026-01-18 | 1.351
2026-01-18 02:13 | 72.095 | FALSE | TRUE | -0.26013 | -0.36212 | -1.1333 | -1.5476 | 0 |  | 2026-01-17 23:28 | none | FALSE | 0 | 71.8349 | FALSE | FALSE | 0.4836 | 1.4721 | 72.5316 | 12 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.34836 | Confirmed/Materialized Shift | 73.2283 | -1.2533 | Night | 202601 | 2026-01-18 | 1.2533
2026-01-18 02:27 | 72.095 | FALSE | TRUE | -0.26118 | -0.36359 | -1.0215 | -1.3971 | 0 |  | 2026-01-17 23:28 | none | FALSE | 0 | 71.8338 | FALSE | FALSE | 0.479 | 1.45 | 72.4752 | 13 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.32067 | Confirmed/Materialized Shift | 73.1165 | -1.1855 | Night | 202601 | 2026-01-18 | 1.1855
2026-01-18 02:42 | 72.095 | FALSE | TRUE | -0.28546 | -0.39752 | -0.96118 | -1.3157 | 0 |  | 2026-01-17 23:28 | none | FALSE | 0 | 71.8095 | FALSE | FALSE | 0.4723 | 1.4239 | 72.4329 | 14 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.31166 | Confirmed/Materialized Shift | 73.0562 | -1.0841 | Night | 202601 | 2026-01-18 | 1.0841
2026-01-18 02:57 | 72.095 | FALSE | FALSE | -0.29661 | -0.41312 | -0.88773 | -1.2164 | 0 |  |  | none | FALSE | 0 | 71.7984 | FALSE | FALSE | 0.0665 |  | 72.3906 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.29609 | Persistence ends | 72.9827 | -0.99823 | Night | 202601 | 2026-01-18 | 0.99823
2026-01-18 03:12 | 72.095 | FALSE | FALSE | -0.29239 | -0.40722 | -0.79891 | -1.096 | 0 |  |  | none | FALSE | 0 | 71.8026 | FALSE | FALSE | 0.0619 |  | 72.3483 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.27283 | Normal | 72.8939 | -0.92828 | Night | 202601 | 2026-01-18 | 0.92828
2026-01-18 03:27 | 72.095 | FALSE | FALSE | -0.26835 | -0.37361 | -0.69027 | -0.94837 | 0 |  |  | none | FALSE | 0 | 71.8266 | FALSE | FALSE | 0.0587 |  | 72.306 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.23966 | Normal | 72.7853 | -0.88026 | Night | 202601 | 2026-01-18 | 0.88026
2026-01-18 03:42 | 72.095 | FALSE | FALSE | -0.21432 | -0.29816 | -0.55164 | -0.75935 | 0 |  |  | none | FALSE | 0 | 71.8807 | FALSE | FALSE | 0.0587 |  | 72.2637 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.19149 | Normal | 72.6466 | -0.88077 | Night | 202601 | 2026-01-18 | 0.88077
2026-01-18 03:57 | 71.8124 | TRUE | FALSE | 0.022686 | 0.031581 | -0.79523 | -1.0952 | -0.2826 | 2026-01-18 06:26 | 2026-01-18 03:57 | lower | TRUE | 1 | 71.8351 | FALSE | FALSE | 0.2269 | 2.1175 | 72.2214 | 1 | -0.2826 | -0.0423 | 0.10331 | -2.326 | 0.19314 | Extreme triggered | 72.6076 | -2.1175 | Night | 202601 | 2026-01-18 | 2.1175
2026-01-18 04:12 | 71.8124 | FALSE | FALSE | -0.003032 | -0.0042223 | -0.73635 | -1.015 | 0 |  | 2026-01-18 03:57 | none | FALSE | 1 | 71.8094 | FALSE | FALSE | 0.2751 | 2.0505 | 72.1791 | 2 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.18485 | Extreme/elevated | 72.5488 | -1.9836 | Night | 202601 | 2026-01-18 | 1.9836
2026-01-18 04:27 | 71.8124 | FALSE | FALSE | -0.053282 | -0.074251 | -0.73026 | -1.0067 | 0 |  | 2026-01-18 03:57 | none | FALSE | 1 | 71.7591 | FALSE | FALSE | 0.3152 | 1.943 | 72.1509 | 3 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.19589 | Persistent | 72.5427 | -1.728 | Night | 202601 | 2026-01-18 | 1.728
2026-01-18 04:42 | 71.8124 | FALSE | FALSE | -0.094174 | -0.13131 | -0.71481 | -0.98558 | 0 |  | 2026-01-18 03:57 | none | FALSE | 1 | 71.7182 | FALSE | FALSE | 0.3594 | 1.8409 | 72.1227 | 4 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.20225 | Persistent | 72.5272 | -1.5344 | Night | 202601 | 2026-01-18 | 1.5344
2026-01-18 04:57 | 71.8124 | FALSE | FALSE | -0.12658 | -0.17658 | -0.69088 | -0.9529 | 0 |  | 2026-01-18 03:57 | none | FALSE | 1 | 71.6858 | FALSE | FALSE | 0.4063 | 1.7488 | 72.0945 | 5 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.20437 | Persistent | 72.5033 | -1.3806 | Night | 202601 | 2026-01-18 | 1.3806
2026-01-18 05:12 | 71.8124 | FALSE | FALSE | -0.15078 | -0.2104 | -0.65874 | -0.90897 | 0 |  | 2026-01-18 03:57 | none | FALSE | 1 | 71.6616 | FALSE | FALSE | 0.4551 | 1.6665 | 72.0664 | 6 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.20238 | Persistent | 72.4711 | -1.255 | Night | 202601 | 2026-01-18 | 1.255
2026-01-18 05:26 | 71.8124 | FALSE | TRUE | -0.16651 | -0.2324 | -0.61813 | -0.85341 | 0 |  | 2026-01-18 03:57 | none | FALSE | 1 | 71.6459 | FALSE | FALSE | 0.5053 | 1.5929 | 72.0382 | 7 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.19616 | Confirmed/Materialized Shift | 72.4305 | -1.1512 | Night | 202601 | 2026-01-18 | 1.1512
2026-01-18 05:41 | 71.8124 | FALSE | TRUE | -0.17292 | -0.24137 | -0.5682 | -0.78501 | 0 |  | 2026-01-18 03:57 | none | FALSE | 1 | 71.6395 | FALSE | FALSE | 0.4997 | 1.5271 | 72.01 | 8 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.18528 | Confirmed/Materialized Shift | 72.3806 | -1.0667 | Night | 202601 | 2026-01-18 | 1.0667
2026-01-18 05:56 | 71.8124 | FALSE | TRUE | -0.16821 | -0.23479 | -0.50715 | -0.70127 | 0 |  | 2026-01-18 03:57 | none | FALSE | 1 | 71.6442 | FALSE | FALSE | 0.4955 | 1.469 | 71.9819 | 9 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.16884 | Confirmed/Materialized Shift | 72.3196 | -1.0037 | Night | 202601 | 2026-01-18 | 1.0037
2026-01-18 06:11 | 71.5298 | TRUE | TRUE | 0.067934 | 0.094883 | -0.75161 | -1.0398 | -0.2826 |  | 2026-01-18 03:57 | lower | TRUE | 2 | 71.5977 | TRUE | TRUE | 0.617 | 1.5618 | 71.9396 | 10 | -0.2826 | -0.0423 | 0.10331 | -2.326 | 0.17092 | Confirmed/Materialized Shift | 72.2814 | -2.3975 | Night | 202601 | 2026-01-18 | 2.3975
2026-01-18 06:26 | 71.8124 | TRUE | FALSE | -0.22509 | -0.31442 | -0.45117 | -0.62434 | 0.2826 |  |  | none | FALSE | 2 | 71.5873 | TRUE | FALSE | 0.1017 |  | 71.9254 | 0 | 0.2826 | -0.01413 | 0.11135 | 2.6647 | 0.16906 | Persistence ends | 72.2636 | -0.66862 | Night | 202601 | 2026-01-18 | 0.66862
2026-01-18 06:41 | 71.8124 | FALSE | FALSE | -0.23294 | -0.32543 | -0.43076 | -0.59627 | 0 |  |  | none | FALSE | 2 | 71.5795 | FALSE | FALSE | 0.0969 |  | 71.9113 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.16593 | Normal | 72.2432 | -0.59611 | Night | 202601 | 2026-01-18 | 0.59611
2026-01-18 06:56 | 71.8124 | FALSE | FALSE | -0.23809 | -0.33264 | -0.40765 | -0.56445 | 0 |  |  | none | FALSE | 2 | 71.5743 | FALSE | FALSE | 0.0922 |  | 71.8972 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.16143 | Normal | 72.22 | -0.52517 | Night | 202601 | 2026-01-18 | 0.52517
2026-01-18 07:11 | 71.8124 | FALSE | FALSE | -0.24028 | -0.33571 | -0.38158 | -0.52854 | 0 |  |  | none | FALSE | 2 | 71.5721 | FALSE | FALSE | 0.0874 |  | 71.883 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.15546 | Normal | 72.194 | -0.45445 | Night | 202601 | 2026-01-18 | 0.45445
2026-01-18 07:26 | 71.8124 | FALSE | FALSE | -0.23916 | -0.33415 | -0.3522 | -0.48806 | 0 |  |  | none | FALSE | 2 | 71.5732 | FALSE | FALSE | 0.0826 |  | 71.8689 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14784 | Normal | 72.1646 | -0.3823 | Day | 202601 | 2026-01-18 | 0.3823
2026-01-18 07:41 | 71.8124 | FALSE | FALSE | -0.2342 | -0.32719 | -0.31898 | -0.44222 | 0 |  |  | none | FALSE | 2 | 71.5782 | FALSE | FALSE | 0.0776 |  | 71.8548 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13829 | Normal | 72.1314 | -0.30652 | Day | 202601 | 2026-01-18 | 0.30652
2026-01-18 07:56 | 71.8124 | FALSE | FALSE | -0.22451 | -0.31361 | -0.28103 | -0.38981 | 0 |  |  | none | FALSE | 2 | 71.5879 | FALSE | FALSE | 0.072 |  | 71.8407 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.12638 | Normal | 72.0934 | -0.22361 | Day | 202601 | 2026-01-18 | 0.22361
2026-01-18 08:11 | 71.8124 | FALSE | FALSE | -0.20858 | -0.29129 | -0.23684 | -0.32872 | 0 |  |  | none | FALSE | 2 | 71.6038 | FALSE | FALSE | 0.0656 |  | 71.8265 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.11135 | Normal | 72.0492 | -0.12689 | Day | 202601 | 2026-01-18 | 0.12689
2026-01-18 08:25 | 71.8124 | FALSE | FALSE | -0.18338 | -0.25601 | -0.18338 | -0.2547 | 0 |  |  | none | FALSE | 2 | 71.629 | FALSE | FALSE | 0.0571 |  | 71.8124 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.091688 | Normal | 71.9958 | 0 | Day | 202601 | 2026-01-18 | 0
2026-01-18 08:30 | 71.8124 | FALSE | FALSE | -0.14051 | -0.19605 | -0.11225 | -0.15607 | 0 |  |  | none | FALSE | 1 | 71.6719 | FALSE | FALSE | 0.0435 |  | 71.7983 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.063191 | Normal | 71.9247 | 0.22361 | Day | 202601 | 2026-01-18 | 0.22361
2026-01-18 08:45 | 71.8124 | FALSE | FALSE | -0.14051 | -0.19605 | -0.11225 | -0.15607 | 0 |  |  | none | FALSE | 0 | 71.6719 | FALSE | FALSE | 0.0149 |  | 71.7983 | 0 | 0 | 0 | 0.091688 | 0 | 0.063191 | Normal | 71.9247 | 0.22361 | Day | 202601 | 2026-01-18 | 0.22361
2026-01-18 09:00 | 71.8124 | FALSE | FALSE | -0.14051 | -0.19605 | -0.11225 | -0.15607 | 0 |  |  | none | FALSE | 0 | 71.6719 | FALSE | FALSE | 0.0149 |  | 71.7983 | 0 | 0 | 0 | 0.091688 | 0 | 0.063191 | Normal | 71.9247 | 0.22361 | Day | 202601 | 2026-01-18 | 0.22361
2026-01-18 09:16 | 72.095 | TRUE | FALSE | -0.46598 | -0.65054 | 0.099225 | 0.13782 | 0.2826 | 2026-01-18 13:14 | 2026-01-18 09:16 | upper | TRUE | 1 | 71.629 | FALSE | FALSE | 0.2912 | 3.0822 | 71.8124 | 1 | 0.2826 | 0.01413 | 0.11135 | 2.411 | 0.091688 | Extreme triggered | 71.9958 | 3.0822 | Day | 202601 | 2026-01-18 | 3.0822
2026-01-18 09:30 | 72.095 | FALSE | FALSE | -0.49118 | -0.68597 | 0.045762 | 0.063515 | 0 |  | 2026-01-18 09:16 | upper | TRUE | 1 | 71.6038 | FALSE | FALSE | 0.3036 | 2.7466 | 71.8265 | 2 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.11135 | Extreme/elevated | 72.0492 | 2.411 | Day | 202601 | 2026-01-18 | 2.411
2026-01-18 09:30 | 72.095 | FALSE | FALSE | -0.50711 | -0.70837 | 0.0015749 | 0.0021845 | 0 |  | 2026-01-18 09:16 | upper | TRUE | 1 | 71.5879 | FALSE | TRUE | 0.3342 | 2.5019 | 71.8407 | 3 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.12638 | Persistent | 72.0934 | 2.0125 | Day | 202601 | 2026-01-18 | 2.0125
2026-01-18 09:45 | 72.3758 | TRUE | FALSE | -0.85435 | -1.1945 | 0.15959 | 0.22099 | 0.2808 |  | 2026-01-18 09:16 | upper | TRUE | 2 | 71.5215 | TRUE | TRUE | 0.4803 | 2.6061 | 71.8688 | 4 | 0.2808 | 0.02817 | 0.12619 | 2.0019 | 0.17369 | Persistent | 72.2162 | 2.9189 | Day | 202601 | 2026-01-18 | 2.9189
2026-01-18 10:00 | 72.3758 | FALSE | FALSE | -0.89204 | -1.2479 | 0.065559 | 0.090664 | 0 |  | 2026-01-18 09:16 | upper | TRUE | 2 | 71.4838 | FALSE | TRUE | 0.4973 | 2.5484 | 71.897 | 5 | 0 | 0.02817 | 0.12619 | -0.22323 | 0.20662 | Persistent | 72.3102 | 2.3173 | Day | 202601 | 2026-01-18 | 2.3173
2026-01-18 10:15 | 72.6584 | FALSE | FALSE | -1.2518 | -1.7531 | 0.18639 | 0.25719 | 0.2826 |  | 2026-01-18 09:16 | upper | TRUE | 2 | 71.4066 | FALSE | TRUE | 0.58 | 2.5736 | 71.9393 | 6 | 0.2826 | 0.0423 | 0.13813 | 1.7397 | 0.26635 | Persistent | 72.472 | 2.6998 | Day | 202601 | 2026-01-18 | 2.6998
2026-01-18 10:30 | 72.941 | FALSE | TRUE | -1.6368 | -2.2955 | 0.25374 | 0.34908 | 0.2826 |  | 2026-01-18 09:16 | upper | TRUE | 2 | 71.3042 | FALSE | TRUE | 0.6394 | 2.5965 | 71.9957 | 7 | 0.2826 | 0.05643 | 0.1477 | 1.5313 | 0.34577 | Confirmed/Materialized Shift | 72.6873 | 2.7338 | Day | 202601 | 2026-01-18 | 2.7338
2026-01-18 10:45 | 72.941 | FALSE | TRUE | -1.6491 | -2.3132 | 0.10033 | 0.13774 | 0 |  | 2026-01-18 09:16 | upper | TRUE | 2 | 71.2919 | FALSE | TRUE | 0.6078 | 2.5543 | 72.0663 | 8 | 0 | 0.07056 | 0.12539 | -0.56273 | 0.38719 | Confirmed/Materialized Shift | 72.8407 | 2.2591 | Day | 202601 | 2026-01-18 | 2.2591
2026-01-18 11:00 | 73.2236 | FALSE | TRUE | -2.0071 | -2.8184 | 0.16637 | 0.22772 | 0.2826 |  | 2026-01-18 09:16 | upper | TRUE | 2 | 71.2165 | FALSE | TRUE | 0.6146 | 2.5329 | 72.1368 | 9 | 0.2826 | 0.07056 | 0.12539 | 1.6911 | 0.46019 | Confirmed/Materialized Shift | 73.0572 | 2.3615 | Day | 202601 | 2026-01-18 | 2.3615
2026-01-18 11:15 | 73.5062 | FALSE | TRUE | -2.3753 | -3.3393 | 0.19402 | 0.26464 | 0.2826 |  | 2026-01-18 09:16 | upper | TRUE | 2 | 71.1309 | FALSE | TRUE | 0.6142 | 2.5152 | 72.2215 | 10 | 0.2826 | 0.08469 | 0.13273 | 1.4911 | 0.54532 | Confirmed/Materialized Shift | 73.3122 | 2.3558 | Day | 202601 | 2026-01-18 | 2.3558
2026-01-18 11:29 | 73.5062 | FALSE | TRUE | -2.413 | -3.3942 | -0.013087 | -0.017801 | 0 |  | 2026-01-18 09:16 | none | FALSE | 1 | 71.0932 | FALSE | FALSE | 0.5605 | 2.4664 | 72.3062 | 11 | 0 | 0.08469 | 0.13273 | -0.63807 | 0.60653 | Confirmed/Materialized Shift | 73.5193 | 1.9784 | Day | 202601 | 2026-01-18 | 1.9784
2026-01-18 11:44 | 73.5062 | FALSE | TRUE | -2.4165 | -3.3992 | -0.18592 | -0.25229 | 0 |  | 2026-01-18 09:16 | none | FALSE | 1 | 71.0897 | FALSE | FALSE | 0.5429 | 2.4037 | 72.3909 | 12 | 0 | 0.08469 | 0.13273 | -0.63807 | 0.6506 | Confirmed/Materialized Shift | 73.6921 | 1.7142 | Day | 202601 | 2026-01-18 | 1.7142
2026-01-18 11:59 | 73.5062 | FALSE | TRUE | -2.3923 | -3.3641 | -0.33114 | -0.44847 | 0 |  | 2026-01-18 09:16 | none | FALSE | 1 | 71.1139 | FALSE | FALSE | 0.5295 | 2.3352 | 72.4756 | 13 | 0 | 0.08469 | 0.13273 | -0.63807 | 0.68087 | Confirmed/Materialized Shift | 73.8373 | 1.5136 | Day | 202601 | 2026-01-18 | 1.5136
2026-01-18 12:14 | 73.5062 | FALSE | TRUE | -2.3442 | -3.2941 | -0.45236 | -0.61163 | 0 |  | 2026-01-18 09:16 | none | FALSE | 0 | 71.162 | FALSE | FALSE | 0.4902 | 2.2651 | 72.5603 | 14 | 0 | 0.08469 | 0.13273 | -0.63807 | 0.69913 | Confirmed/Materialized Shift | 73.9586 | 1.353 | Day | 202601 | 2026-01-18 | 1.353
2026-01-18 12:29 | 73.7888 | FALSE | TRUE | -2.5836 | -3.6284 | -0.32427 | -0.43753 | 0.2826 |  | 2026-01-18 09:16 | none | FALSE | 0 | 71.2052 | FALSE | FALSE | 0.5036 | 2.2177 | 72.6591 | 15 | 0.2826 | 0.09882 | 0.13817 | 1.3301 | 0.72697 | Confirmed/Materialized Shift | 74.1131 | 1.5539 | Day | 202601 | 2026-01-18 | 1.5539
2026-01-18 12:44 | 73.5062 | TRUE | TRUE | -2.206 | -3.0939 | -0.68118 | -0.91819 | -0.2826 |  | 2026-01-18 09:16 | none | FALSE | 1 | 71.3002 | FALSE | FALSE | 0.499 | 2.1451 | 72.7438 | 16 | -0.2826 | 0.08469 | 0.16132 | -2.2768 | 0.72179 | Confirmed/Materialized Shift | 74.1874 | 1.0563 | Day | 202601 | 2026-01-18 | 1.0563
2026-01-18 12:59 | 73.7888 | FALSE | TRUE | -2.3919 | -3.3501 | -0.49953 | -0.67242 | 0.2826 |  | 2026-01-18 09:16 | none | FALSE | 1 | 71.3969 | FALSE | FALSE | 0.5158 | 2.0959 | 72.8426 | 17 | 0.2826 | 0.09882 | 0.16582 | 1.1083 | 0.72285 | Confirmed/Materialized Shift | 74.2883 | 1.3089 | Day | 202601 | 2026-01-18 | 1.3089
2026-01-18 13:14 | 73.2236 | TRUE | FALSE | -1.6801 | -2.3484 | -1.0593 | -1.4261 | -0.5652 |  |  | none | FALSE | 2 | 71.5435 | TRUE | FALSE | 0.0874 |  | 72.9132 | 0 | -0.5652 | 0.07056 | 0.22215 | -2.8619 | 0.68487 | Persistence ends | 74.2829 | 0.45324 | Day | 202601 | 2026-01-18 | 0.45324
2026-01-18 13:29 | 72.941 | FALSE | FALSE | -1.2394 | -1.7285 | -1.2966 | -1.7466 | -0.2826 |  |  | none | FALSE | 2 | 71.7016 | FALSE | FALSE | 0.0602 |  | 72.9696 | 0 | -0.2826 | 0.05643 | 0.23546 | -1.4399 | 0.634 | Normal | 74.2376 | -0.045142 | Day | 202601 | 2026-01-18 | 0.045142
2026-01-18 13:44 | 73.2236 | FALSE | FALSE | -1.3317 | -1.8524 | -0.96485 | -1.3005 | 0.2826 |  |  | none | FALSE | 2 | 71.8919 | FALSE | FALSE | 0.0784 |  | 73.0402 | 0 | 0.2826 | 0.07056 | 0.24032 | 0.88231 | 0.57414 | Normal | 74.1885 | 0.31947 | Day | 202601 | 2026-01-18 | 0.31947
2026-01-18 13:59 | 73.2236 | FALSE | FALSE | -1.1872 | -1.6481 | -0.93326 | -1.2585 | 0 |  |  | none | FALSE | 2 | 72.0364 | FALSE | FALSE | 0.0731 |  | 73.0966 | 0 | 0 | 0.05643 | 0.23546 | -0.23966 | 0.53012 | Normal | 74.1569 | 0.23955 | Day | 202601 | 2026-01-18 | 0.23955
2026-01-18 14:14 | 73.7888 | FALSE | FALSE | -1.5993 | -2.2154 | -0.38426 | -0.51806 | 0.5652 |  |  | none | FALSE | 2 | 72.1895 | FALSE | FALSE | 0.1388 |  | 73.1813 | 0 | 0.5652 | 0.08469 | 0.26088 | 1.8419 | 0.49588 | Normal | 74.1731 | 1.2251 | Day | 202601 | 2026-01-18 | 1.2251
2026-01-18 14:28 | 73.7888 | FALSE | FALSE | -1.4075 | -1.9445 | -0.36187 | -0.48802 | 0 |  |  | none | FALSE | 2 | 72.3813 | FALSE | FALSE | 0.1359 |  | 73.266 | 0 | 0 | 0.08469 | 0.26088 | -0.32464 | 0.44234 | Normal | 74.1507 | 1.1819 | Day | 202601 | 2026-01-18 | 1.1819
2026-01-18 14:43 | 73.7888 | FALSE | FALSE | -1.2598 | -1.737 | -0.35552 | -0.4795 | 0 |  |  | none | FALSE | 2 | 72.529 | FALSE | FALSE | 0.1318 |  | 73.3366 | 0 | 0 | 0.07065 | 0.2573 | -0.27458 | 0.40384 | Normal | 74.1443 | 1.1196 | Day | 202601 | 2026-01-18 | 1.1196
2026-01-18 14:46 | 74.0714 | FALSE | FALSE | -1.3858 | -1.9065 | -0.085809 | -0.11571 | 0.2826 |  |  | none | FALSE | 2 | 72.6856 | FALSE | FALSE | 0.1749 |  | 73.4214 | 0 | 0.2826 | 0.08478 | 0.26095 | 0.75808 | 0.36789 | Normal | 74.1572 | 1.7668 | Day | 202601 | 2026-01-18 | 1.7668
2026-01-18 14:49 | 74.0714 | FALSE | FALSE | -1.277 | -1.7543 | -0.11834 | -0.15951 | 0 |  |  | none | FALSE | 1 | 72.7944 | FALSE | FALSE | 0.1393 |  | 73.4921 | 0 | 0 | 0.07065 | 0.2573 | -0.27458 | 0.34883 | Normal | 74.1897 | 1.6608 | Day | 202601 | 2026-01-18 | 1.6608
2026-01-18 15:01 | 72.941 | TRUE | FALSE | -0.1466 | -0.20139 | -1.2487 | -1.6832 | -1.1304 |  |  | none | FALSE | 2 | 72.7944 | TRUE | FALSE | 0.1625 |  | 73.4921 | 0 | -1.1304 | 0 | 0.36675 | -3.0822 | 0.34883 | Normal | 74.1897 | -1.5797 | Day | 202601 | 2026-01-18 | 1.5797
2026-01-18 15:16 | 72.095 | FALSE | FALSE | 0.44582 | 0.61458 | -2.2637 | -3.0443 | -0.846 | 2026-01-18 16:11 | 2026-01-18 15:16 | lower | TRUE | 1 | 72.5408 | FALSE | FALSE | 0.2844 | 2.981 | 73.4498 | 1 | -0.846 | -0.0423 | 0.41266 | -1.9476 | 0.45447 | Extreme triggered | 74.3587 | -2.981 | Day | 202601 | 2026-01-18 | 2.981
2026-01-18 15:28 | 72.095 | FALSE | FALSE | 0.2082 | 0.28795 | -2.3885 | -3.2067 | 0 |  | 2026-01-18 15:16 | lower | TRUE | 1 | 72.3032 | FALSE | FALSE | 0.3017 | 2.6815 | 73.3933 | 2 | 0 | -0.05643 | 0.40573 | 0.13908 | 0.54507 | Extreme/elevated | 74.4835 | -2.382 | Day | 202601 | 2026-01-18 | 2.382
2026-01-18 15:41 | 71.8124 | FALSE | FALSE | 0.19944 | 0.27696 | -2.7931 | -3.7438 | -0.2826 |  | 2026-01-18 15:16 | lower | TRUE | 1 | 72.0118 | FALSE | TRUE | 0.3538 | 2.5568 | 73.3087 | 3 | -0.2826 | -0.08469 | 0.40053 | -0.49412 | 0.6484 | Persistent | 74.6055 | -2.3076 | Day | 202601 | 2026-01-18 | 2.3076
2026-01-18 15:56 | 72.3758 | FALSE | FALSE | -0.48133 | -0.6695 | -2.234 | -2.9942 | 0.5634 |  | 2026-01-18 15:16 | none | FALSE | 1 | 71.8945 | FALSE | FALSE | 0.3432 | 2.2404 | 73.2521 | 4 | 0.5634 | -0.05652 | 0.42581 | 1.4559 | 0.67883 | Persistent | 74.6098 | -1.2909 | Day | 202601 | 2026-01-18 | 1.2909
2026-01-18 16:11 | 72.6584 | FALSE | FALSE | -0.82572 | -1.1495 | -1.9284 | -2.5854 | 0.2826 |  |  | none | FALSE | 1 | 71.8327 | FALSE | FALSE | 0.082 |  | 73.2097 | 0 | 0.2826 | -0.04239 | 0.43242 | 0.75156 | 0.68853 | Persistence ends | 74.5868 | -0.80075 | Day | 202601 | 2026-01-18 | 0.80075
2026-01-18 16:26 | 72.6584 | FALSE | FALSE | -0.88182 | -1.2286 | -1.8997 | -2.548 | 0 |  |  | none | FALSE | 1 | 71.7766 | FALSE | FALSE | 0.0774 |  | 73.1673 | 0 | 0 | -0.04239 | 0.43242 | 0.098029 | 0.69538 | Normal | 74.5581 | -0.7319 | Day | 202601 | 2026-01-18 | 0.7319
2026-01-18 16:28 | 72.6584 | FALSE | FALSE | -0.93238 | -1.2999 | -1.8655 | -2.5032 | 0 |  |  | none | FALSE | 1 | 71.726 | FALSE | FALSE | 0.073 |  | 73.125 | 0 | 0 | -0.04239 | 0.43242 | 0.098029 | 0.69947 | Normal | 74.5239 | -0.66702 | Day | 202601 | 2026-01-18 | 0.66702
2026-01-18 16:43 | 72.6584 | FALSE | FALSE | -0.96714 | -1.349 | -1.7872 | -2.4007 | 0 |  |  | none | FALSE | 1 | 71.6913 | FALSE | FALSE | 0.0683 |  | 73.0684 | 0 | 0 | -0.05652 | 0.42581 | 0.13273 | 0.68859 | Normal | 74.4456 | -0.59548 | Day | 202601 | 2026-01-18 | 0.59548
2026-01-18 16:58 | 72.3758 | FALSE | FALSE | -0.75809 | -1.0585 | -2.0303 | -2.7287 | -0.2826 |  |  | none | FALSE | 1 | 71.6177 | FALSE | FALSE | 0.0894 |  | 73.0119 | 0 | -0.2826 | -0.05652 | 0.42581 | -0.53094 | 0.69711 | Normal | 74.4061 | -0.91252 | Day | 202601 | 2026-01-18 | 0.91252
2026-01-18 17:13 | 72.3758 | FALSE | FALSE | -0.806 | -1.1262 | -1.9369 | -2.6065 | 0 |  |  | none | FALSE | 0 | 71.5698 | FALSE | FALSE | 0.055 |  | 72.9413 | 0 | 0 | -0.07065 | 0.41859 | 0.16878 | 0.68574 | Normal | 74.3127 | -0.82462 | Day | 202601 | 2026-01-18 | 0.82462
2026-01-18 17:28 | 72.3758 | FALSE | FALSE | -0.86397 | -1.2082 | -1.9101 | -2.5713 | 0 |  |  | none | FALSE | 0 | 71.5118 | FALSE | FALSE | 0.0503 |  | 72.8989 | 0 | 0 | -0.04239 | 0.40221 | 0.10539 | 0.69353 | Normal | 74.2859 | -0.75423 | Day | 202601 | 2026-01-18 | 0.75423
2026-01-18 17:43 | 72.3758 | FALSE | FALSE | -0.91151 | -1.2755 | -1.9012 | -2.5595 | 0 |  |  | none | FALSE | 0 | 71.4643 | FALSE | FALSE | 0.0469 |  | 72.8706 | 0 | 0 | -0.02826 | 0.39827 | 0.070957 | 0.70317 | Normal | 74.277 | -0.7037 | Day | 202601 | 2026-01-18 | 0.7037
2026-01-18 17:43 | 72.3758 | FALSE | FALSE | -0.9602 | -1.3445 | -1.8651 | -2.5122 | 0 |  |  | none | FALSE | 0 | 71.4156 | FALSE | FALSE | 0.0427 |  | 72.8282 | 0 | 0 | -0.04239 | 0.39162 | 0.10824 | 0.70632 | Normal | 74.2409 | -0.64055 | Day | 202601 | 2026-01-18 | 0.64055
2026-01-18 17:58 | 72.6584 | FALSE | FALSE | -1.2603 | -1.7652 | -1.5435 | -2.0801 | 0.2826 |  |  | none | FALSE | 0 | 71.3981 | FALSE | FALSE | 0.0135 |  | 72.8 | 0 | 0.2826 | -0.02826 | 0.39827 | 0.78053 | 0.70095 | Normal | 74.2019 | -0.20197 | Night | 202601 | 2026-01-18 | 0.20197
2026-01-18 18:13 | 72.941 | FALSE | FALSE | -1.5086 | -2.1119 | -1.1418 | -1.5412 | 0.2826 |  |  | none | FALSE | 0 | 71.4324 | FALSE | FALSE | 0.0185 |  | 72.7576 | 0 | 0.2826 | -0.04239 | 0.38073 | 0.85359 | 0.66259 | Normal | 74.0828 | 0.27682 | Night | 202601 | 2026-01-18 | 0.27682
2026-01-18 18:28 | 72.941 | FALSE | FALSE | -1.4634 | -2.0474 | -1.0118 | -1.3682 | 0 |  |  | none | FALSE | 0 | 71.4776 | FALSE | FALSE | 0.0243 |  | 72.7152 | 0 | 0 | -0.04239 | 0.38073 | 0.11134 | 0.61882 | Normal | 73.9528 | 0.36491 | Night | 202601 | 2026-01-18 | 0.36491
2026-01-18 18:42 | 72.941 | FALSE | FALSE | -1.405 | -1.964 | -0.86857 | -1.1768 | 0 |  |  | none | FALSE | 0 | 71.536 | FALSE | FALSE | 0.0315 |  | 72.6728 | 0 | 0 | -0.04239 | 0.38073 | 0.11134 | 0.56839 | Normal | 73.8096 | 0.47186 | Night | 202601 | 2026-01-18 | 0.47186
2026-01-18 18:57 | 72.941 | FALSE | FALSE | -1.2639 | -1.7634 | -0.6145 | -0.83542 | 0 |  |  | none | FALSE | 0 | 71.6771 | FALSE | FALSE | 0.0461 |  | 72.6163 | 0 | 0 | -0.05652 | 0.37321 | 0.15144 | 0.46961 | Normal | 73.5555 | 0.69147 | Night | 202601 | 2026-01-18 | 0.69147
2026-01-18 19:12 | 72.6584 | FALSE | FALSE | -0.75754 | -1.0536 | -0.532 | -0.72687 | -0.2826 |  |  | none | FALSE | 0 | 71.9009 | FALSE | FALSE | 0.0233 |  | 72.5456 | 0 | -0.2826 | -0.07065 | 0.37629 | -0.56326 | 0.32238 | Normal | 73.1904 | 0.3498 | Night | 202601 | 2026-01-18 | 0.3498
2026-01-18 19:27 | 72.6584 | FALSE | FALSE | -0.74711 | -1.0389 | -0.49331 | -0.67436 | 0 |  |  | none | FALSE | 0 | 71.9113 | FALSE | FALSE | 0.0273 |  | 72.5315 | 0 | 0 | -0.01413 | 0.28175 | 0.05015 | 0.3101 | Normal | 73.1517 | 0.40922 | Night | 202601 | 2026-01-18 | 0.40922
2026-01-18 19:42 | 72.3758 | FALSE | FALSE | -0.42087 | -0.5849 | -0.76035 | -1.0396 | -0.2826 |  |  | none | FALSE | 0 | 71.9549 | FALSE | FALSE | 0.0383 |  | 72.5455 | 0 | -0.2826 | 0.01404 | 0.21429 | -1.3843 | 0.2953 | Normal | 73.1361 | -0.5748 | Night | 202601 | 2026-01-18 | 0.5748
2026-01-18 19:57 | 72.3758 | FALSE | FALSE | -0.37418 | -0.51968 | -0.74174 | -1.0144 | 0 |  |  | none | FALSE | 0 | 72.0016 | FALSE | FALSE | 0.0439 |  | 72.5596 | 0 | 0 | 0.01404 | 0.21429 | -0.065517 | 0.27898 | Normal | 73.1175 | -0.65876 | Night | 202601 | 2026-01-18 | 0.65876
2026-01-18 20:12 | 72.3758 | FALSE | FALSE | -0.23252 | -0.32231 | -0.65642 | -0.89881 | 0 |  |  | none | FALSE | 0 | 72.1433 | FALSE | FALSE | 0.0636 |  | 72.5877 | 0 | 0 | 0.02817 | 0.20271 | -0.13897 | 0.22224 | Normal | 73.0322 | -0.95372 | Night | 202601 | 2026-01-18 | 0.95372
2026-01-18 20:27 | 72.3758 | FALSE | FALSE | -0.23252 | -0.32231 | -0.65642 | -0.89881 | 0 |  |  | none | FALSE | 0 | 72.1433 | FALSE | FALSE | 0.0636 |  | 72.5877 | 0 | 0 | 0 | 0.15881 | 0 | 0.22224 | Normal | 73.0322 | -0.95372 | Night | 202601 | 2026-01-18 | 0.95372
2026-01-18 20:42 | 72.095 | FALSE | FALSE | -0.029666 | -0.041166 | -0.95883 | -1.3125 | -0.2808 |  |  | none | FALSE | 0 | 72.0653 | FALSE | FALSE | 0.1253 |  | 72.5596 | 0 | -0.2808 | -0.02817 | 0.15598 | -1.6196 | 0.24712 | Normal | 73.0538 | -1.88 | Night | 202601 | 2026-01-18 | 1.88
2026-01-18 20:57 | 72.095 | FALSE | FALSE | -0.096808 | -0.13446 | -0.96963 | -1.3271 | 0 |  |  | none | FALSE | 0 | 71.9982 | FALSE | FALSE | 0.1091 |  | 72.5314 | 0 | 0 | -0.02817 | 0.15598 | 0.18059 | 0.26661 | Normal | 73.0646 | -1.6369 | Night | 202601 | 2026-01-18 | 1.6369
2026-01-18 21:12 | 72.095 | FALSE | FALSE | -0.15539 | -0.216 | -0.97187 | -1.3301 | 0 |  |  | none | FALSE | 0 | 71.9396 | FALSE | FALSE | 0.0966 |  | 72.5032 | 0 | 0 | -0.02817 | 0.15598 | 0.18059 | 0.28182 | Normal | 73.0669 | -1.4486 | Night | 202601 | 2026-01-18 | 1.4486
2026-01-18 21:27 | 71.8124 | FALSE | FALSE | 0.011709 | 0.016302 | -1.2854 | -1.7584 | -0.2826 | 2026-01-20 15:01 | 2026-01-18 21:27 | lower | TRUE | 0 | 71.8241 | FALSE | FALSE | 0.1929 | 2.0368 | 72.4609 | 1 | -0.2826 | -0.0423 | 0.16579 | -1.4494 | 0.31842 | Extreme triggered | 73.0978 | -2.0368 | Night | 202601 | 2026-01-18 | 2.0368
2026-01-18 21:41 | 71.8124 | FALSE | FALSE | -0.079083 | -0.11025 | -1.3198 | -1.8047 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 71.7333 | FALSE | FALSE | 0.2325 | 1.9053 | 72.4328 | 2 | 0 | -0.02817 | 0.15598 | 0.18059 | 0.34973 | Extreme/elevated | 73.1322 | -1.7739 | Night | 202601 | 2026-01-18 | 1.7739
2026-01-18 21:56 | 71.8124 | FALSE | FALSE | -0.16028 | -0.2237 | -1.3447 | -1.8381 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 71.6521 | FALSE | FALSE | 0.2764 | 1.7949 | 72.4046 | 3 | 0 | -0.02817 | 0.15598 | 0.18059 | 0.37624 | Persistent | 73.1571 | -1.574 | Night | 202601 | 2026-01-18 | 1.574
2026-01-18 22:11 | 71.8124 | FALSE | FALSE | -0.23381 | -0.32665 | -1.3619 | -1.8611 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 71.5786 | FALSE | FALSE | 0.3228 | 1.6996 | 72.3764 | 4 | 0 | -0.02817 | 0.15598 | 0.18059 | 0.39892 | Persistent | 73.1743 | -1.4139 | Night | 202601 | 2026-01-18 | 1.4139
2026-01-18 22:26 | 71.5298 | FALSE | FALSE | -0.078799 | -0.11028 | -1.6875 | -2.3047 | -0.2826 |  | 2026-01-18 21:27 | none | FALSE | 0 | 71.451 | FALSE | FALSE | 0.4072 | 1.724 | 72.3341 | 5 | -0.2826 | -0.0423 | 0.16579 | -1.4494 | 0.44156 | Persistent | 73.2173 | -1.8215 | Night | 202601 | 2026-01-18 | 1.8215
2026-01-18 22:41 | 71.5298 | FALSE | FALSE | -0.19097 | -0.2677 | -1.715 | -2.3415 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 71.3388 | FALSE | FALSE | 0.4495 | 1.7032 | 72.2918 | 6 | 0 | -0.0423 | 0.16579 | 0.25514 | 0.4765 | Persistent | 73.2448 | -1.5992 | Night | 202601 | 2026-01-18 | 1.5992
2026-01-18 22:56 | 71.5298 | FALSE | TRUE | -0.28877 | -0.40534 | -1.7 | -2.3214 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 71.241 | FALSE | FALSE | 0.4946 | 1.6626 | 72.2354 | 7 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.49718 | Confirmed/Materialized Shift | 73.2298 | -1.4192 | Night | 202601 | 2026-01-18 | 1.4192
2026-01-18 23:11 | 71.2472 | FALSE | TRUE | -0.12573 | -0.17679 | -1.9328 | -2.6411 | -0.2826 |  | 2026-01-18 21:27 | none | FALSE | 0 | 71.1215 | FALSE | FALSE | 0.517 | 1.6743 | 72.1507 | 8 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.51462 | Confirmed/Materialized Shift | 73.18 | -1.7557 | Night | 202601 | 2026-01-18 | 1.7557
2026-01-18 23:26 | 71.2472 | FALSE | TRUE | -0.21535 | -0.30318 | -1.853 | -2.5349 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 71.0318 | FALSE | FALSE | 0.5056 | 1.6642 | 72.066 | 9 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.51709 | Confirmed/Materialized Shift | 73.1002 | -1.5835 | Night | 202601 | 2026-01-18 | 1.5835
2026-01-18 23:41 | 70.9646 | FALSE | TRUE | -0.056936 | -0.080296 | -2.0621 | -2.8238 | -0.2826 |  | 2026-01-18 21:27 | none | FALSE | 0 | 70.9077 | FALSE | FALSE | 0.5262 | 1.687 | 71.9672 | 10 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.52977 | Confirmed/Materialized Shift | 73.0267 | -1.8925 | Night | 202601 | 2026-01-18 | 1.8925
2026-01-18 23:56 | 70.9646 | FALSE | TRUE | -0.14192 | -0.20038 | -1.9495 | -2.6737 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 70.8227 | FALSE | FALSE | 0.5152 | 1.6908 | 71.8684 | 11 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.52285 | Confirmed/Materialized Shift | 72.9141 | -1.7286 | Night | 202601 | 2026-01-18 | 1.7286
2026-01-19 00:11 | 70.9646 | FALSE | TRUE | -0.23155 | -0.32736 | -1.8697 | -2.5671 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 70.733 | FALSE | FALSE | 0.5039 | 1.6798 | 71.7837 | 12 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.52532 | Confirmed/Materialized Shift | 72.8343 | -1.5592 | Night | 202601 | 2026-01-19 | 1.5592
2026-01-19 00:26 | 70.682 | FALSE | TRUE | -0.07285 | -0.10317 | -2.0786 | -2.8568 | -0.2826 |  | 2026-01-18 21:27 | none | FALSE | 0 | 70.6091 | FALSE | FALSE | 0.5243 | 1.694 | 71.6849 | 13 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.53786 | Confirmed/Materialized Shift | 72.7606 | -1.8646 | Night | 202601 | 2026-01-19 | 1.8646
2026-01-19 00:40 | 70.682 | FALSE | TRUE | -0.19457 | -0.27603 | -2.0309 | -2.7931 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 70.4874 | FALSE | FALSE | 0.51 | 1.6909 | 71.6002 | 14 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.55637 | Confirmed/Materialized Shift | 72.7129 | -1.6503 | Night | 202601 | 2026-01-19 | 1.6503
2026-01-19 00:55 | 70.3994 | FALSE | TRUE | -0.070215 | -0.099838 | -2.2741 | -3.1292 | -0.2826 |  | 2026-01-18 21:27 | none | FALSE | 0 | 70.3292 | FALSE | FALSE | 0.5253 | 1.7035 | 71.5014 | 15 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.58609 | Confirmed/Materialized Shift | 72.6735 | -1.8802 | Night | 202601 | 2026-01-19 | 1.8802
2026-01-19 01:11 | 70.3994 | FALSE | TRUE | -0.19166 | -0.27299 | -2.1979 | -3.0276 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 70.2077 | FALSE | FALSE | 0.5119 | 1.702 | 71.4025 | 16 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.5974 | Confirmed/Materialized Shift | 72.5973 | -1.6792 | Night | 202601 | 2026-01-19 | 1.6792
2026-01-19 01:26 | 70.3994 | FALSE | TRUE | -0.27841 | -0.39705 | -2.0871 | -2.8792 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 70.121 | FALSE | FALSE | 0.5019 | 1.6918 | 71.3037 | 17 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.59137 | Confirmed/Materialized Shift | 72.4865 | -1.5292 | Night | 202601 | 2026-01-19 | 1.5292
2026-01-19 01:40 | 70.1168 | FALSE | TRUE | -0.14586 | -0.20846 | -2.3219 | -3.2053 | -0.2826 |  | 2026-01-18 21:27 | none | FALSE | 0 | 69.9709 | FALSE | FALSE | 0.5176 | 1.6958 | 71.2048 | 18 | -0.2826 | -0.09891 | 0.13829 | -1.3283 | 0.61694 | Confirmed/Materialized Shift | 72.4387 | -1.7636 | Night | 202601 | 2026-01-19 | 1.7636
2026-01-19 01:55 | 70.1168 | FALSE | TRUE | -0.26135 | -0.37413 | -2.2396 | -3.0952 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 69.8554 | FALSE | FALSE | 0.5055 | 1.6898 | 71.1059 | 19 | 0 | -0.09891 | 0.13829 | 0.71522 | 0.62523 | Confirmed/Materialized Shift | 72.3564 | -1.582 | Night | 202601 | 2026-01-19 | 1.582
2026-01-19 02:10 | 69.836 | FALSE | TRUE | -0.12502 | -0.17934 | -2.4389 | -3.3745 | -0.2808 |  | 2026-01-18 21:27 | none | FALSE | 0 | 69.711 | FALSE | FALSE | 0.5203 | 1.6956 | 70.9929 | 20 | -0.2808 | -0.11295 | 0.14193 | -1.1826 | 0.64099 | Confirmed/Materialized Shift | 72.2749 | -1.805 | Night | 202601 | 2026-01-19 | 1.805
2026-01-19 02:25 | 69.836 | FALSE | TRUE | -0.26201 | -0.37659 | -2.3783 | -3.2933 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 69.574 | FALSE | FALSE | 0.5069 | 1.6912 | 70.8941 | 21 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.66007 | Confirmed/Materialized Shift | 72.2143 | -1.6031 | Night | 202601 | 2026-01-19 | 1.6031
2026-01-19 02:40 | 69.5534 | FALSE | TRUE | -0.14698 | -0.21177 | -2.6025 | -3.6068 | -0.2826 |  | 2026-01-18 21:27 | none | FALSE | 0 | 69.4064 | FALSE | FALSE | 0.5191 | 1.6955 | 70.7812 | 22 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.68738 | Confirmed/Materialized Shift | 72.1559 | -1.7862 | Night | 202601 | 2026-01-19 | 1.7862
2026-01-19 02:55 | 69.5534 | FALSE | TRUE | -0.27432 | -0.39596 | -2.504 | -3.475 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 69.2791 | FALSE | FALSE | 0.507 | 1.6916 | 70.6682 | 23 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.69457 | Confirmed/Materialized Shift | 72.0574 | -1.6051 | Night | 202601 | 2026-01-19 | 1.6051
2026-01-19 03:10 | 69.2708 | FALSE | TRUE | -0.14289 | -0.2067 | -2.6836 | -3.7296 | -0.2826 |  | 2026-01-18 21:27 | none | FALSE | 0 | 69.1279 | FALSE | FALSE | 0.5199 | 1.696 | 70.5412 | 24 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.70662 | Confirmed/Materialized Shift | 71.9544 | -1.7978 | Night | 202601 | 2026-01-19 | 1.7978
2026-01-19 03:25 | 69.2708 | FALSE | TRUE | -0.28395 | -0.4116 | -2.5988 | -3.6159 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 68.9868 | FALSE | FALSE | 0.5071 | 1.6924 | 70.4282 | 25 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.72068 | Confirmed/Materialized Shift | 71.8696 | -1.606 | Night | 202601 | 2026-01-19 | 1.606
2026-01-19 03:39 | 69.2708 | FALSE | TRUE | -0.38744 | -0.56246 | -2.4763 | -3.4515 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 68.8834 | FALSE | FALSE | 0.4973 | 1.6834 | 70.3153 | 26 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.71595 | Confirmed/Materialized Shift | 71.7471 | -1.4588 | Night | 202601 | 2026-01-19 | 1.4588
2026-01-19 03:55 | 68.9882 | FALSE | TRUE | -0.2292 | -0.33333 | -2.6291 | -3.6711 | -0.2826 |  | 2026-01-18 21:27 | none | FALSE | 0 | 68.759 | FALSE | FALSE | 0.512 | 1.6833 | 70.1882 | 27 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.71458 | Confirmed/Materialized Shift | 71.6173 | -1.6793 | Night | 202601 | 2026-01-19 | 1.6793
2026-01-19 04:10 | 68.7056 | FALSE | TRUE | -0.12813 | -0.18685 | -2.8391 | -3.9683 | -0.2826 |  | 2026-01-18 21:27 | none | FALSE | 0 | 68.5775 | FALSE | FALSE | 0.5218 | 1.6884 | 70.0611 | 28 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.74181 | Confirmed/Materialized Shift | 71.5447 | -1.8273 | Night | 202601 | 2026-01-19 | 1.8273
2026-01-19 04:25 | 68.7056 | FALSE | TRUE | -0.26282 | -0.384 | -2.7196 | -3.8077 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 68.4428 | FALSE | FALSE | 0.5098 | 1.687 | 69.934 | 29 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.74562 | Confirmed/Materialized Shift | 71.4252 | -1.6475 | Night | 202601 | 2026-01-19 | 1.6475
2026-01-19 04:39 | 68.7056 | FALSE | TRUE | -0.38925 | -0.56977 | -2.6202 | -3.6735 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 68.3164 | FALSE | FALSE | 0.4988 | 1.6802 | 69.8211 | 30 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.75235 | Confirmed/Materialized Shift | 71.3258 | -1.4826 | Night | 202601 | 2026-01-19 | 1.4826
2026-01-19 04:54 | 68.423 | FALSE | TRUE | -0.25622 | -0.37587 | -2.7982 | -3.9289 | -0.2826 |  | 2026-01-18 21:27 | none | FALSE | 0 | 68.1668 | FALSE | FALSE | 0.511 | 1.6797 | 69.694 | 31 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.7636 | Confirmed/Materialized Shift | 71.2212 | -1.6645 | Night | 202601 | 2026-01-19 | 1.6645
2026-01-19 05:09 | 68.423 | FALSE | TRUE | -0.36093 | -0.5303 | -2.6487 | -3.7268 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 68.0621 | FALSE | FALSE | 0.5014 | 1.6747 | 69.5669 | 32 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.75242 | Confirmed/Materialized Shift | 71.0717 | -1.5203 | Night | 202601 | 2026-01-19 | 1.5203
2026-01-19 05:24 | 68.423 | FALSE | TRUE | -0.46053 | -0.67762 | -2.5224 | -3.5554 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 67.9625 | FALSE | FALSE | 0.4922 | 1.6658 | 69.454 | 33 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.74574 | Confirmed/Materialized Shift | 70.9454 | -1.3825 | Night | 202601 | 2026-01-19 | 1.3825
2026-01-19 05:39 | 68.1404 | FALSE | TRUE | -0.29753 | -0.43856 | -2.6705 | -3.7713 | -0.2826 |  | 2026-01-18 21:27 | none | FALSE | 0 | 67.8429 | FALSE | FALSE | 0.5066 | 1.6639 | 69.3269 | 34 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.742 | Confirmed/Materialized Shift | 70.8109 | -1.599 | Night | 202601 | 2026-01-19 | 1.599
2026-01-19 05:54 | 67.8596 | FALSE | TRUE | -0.1912 | -0.28255 | -2.8718 | -4.0601 | -0.2808 |  | 2026-01-18 21:27 | none | FALSE | 0 | 67.6684 | FALSE | FALSE | 0.5167 | 1.6663 | 69.1999 | 35 | -0.2808 | -0.12699 | 0.14404 | -1.0678 | 0.76574 | Confirmed/Materialized Shift | 70.7314 | -1.7503 | Night | 202601 | 2026-01-19 | 1.7503
2026-01-19 06:09 | 67.8596 | FALSE | TRUE | -0.32059 | -0.47467 | -2.7472 | -3.8908 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 67.539 | FALSE | FALSE | 0.5055 | 1.664 | 69.0729 | 36 | 0 | -0.12699 | 0.14404 | 0.88163 | 0.76694 | Confirmed/Materialized Shift | 70.6068 | -1.582 | Night | 202601 | 2026-01-19 | 1.582
2026-01-19 06:24 | 67.577 | FALSE | TRUE | -0.18457 | -0.27388 | -2.8941 | -4.1068 | -0.2826 |  | 2026-01-18 21:27 | none | FALSE | 0 | 67.3924 | FALSE | FALSE | 0.5173 | 1.6666 | 68.9318 | 37 | -0.2826 | -0.14112 | 0.14479 | -0.97716 | 0.76967 | Confirmed/Materialized Shift | 70.4711 | -1.7602 | Night | 202601 | 2026-01-19 | 1.7602
2026-01-20 11:30 | 70.9646 | TRUE | TRUE | -3.704 | -5.507 | 0.27686 | 0.39167 | 3.3876 |  | 2026-01-18 21:27 | upper | TRUE | 1 | 67.2606 | FALSE | TRUE | 0.5834 | 1.6839 | 68.9742 | 38 | 3.3876 | 0.04239 | 0.79989 | 4.1821 | 0.85679 | Confirmed/Materialized Shift | 70.6877 | 2.3231 | Day | 202601 | 2026-01-20 | 2.3231
2026-01-20 11:31 | 70.9646 | FALSE | TRUE | -3.8157 | -5.6824 | 0.080435 | 0.11347 | 0 |  | 2026-01-18 21:27 | upper | TRUE | 1 | 67.1489 | FALSE | TRUE | 0.5676 | 1.6942 | 69.0165 | 39 | 0 | 0.04239 | 0.79989 | -0.052995 | 0.93381 | Confirmed/Materialized Shift | 70.8842 | 2.0861 | Day | 202601 | 2026-01-20 | 2.0861
2026-01-20 11:46 | 71.5298 | FALSE | TRUE | -4.5841 | -6.8474 | 0.27306 | 0.3832 | 0.5652 |  | 2026-01-18 21:27 | upper | TRUE | 1 | 66.9457 | FALSE | TRUE | 0.5788 | 1.7082 | 69.1012 | 40 | 0.5652 | 0.08469 | 0.80426 | 0.59746 | 1.0778 | Confirmed/Materialized Shift | 71.2567 | 2.2534 | Day | 202601 | 2026-01-20 | 2.2534
2026-01-20 12:01 | 71.8124 | FALSE | TRUE | -5.0698 | -7.596 | 0.15493 | 0.21621 | 0.2826 |  | 2026-01-18 21:27 | upper | TRUE | 1 | 66.7426 | FALSE | TRUE | 0.5703 | 1.7184 | 69.2001 | 41 | 0.2826 | 0.09882 | 0.80517 | 0.22825 | 1.2287 | Confirmed/Materialized Shift | 71.6575 | 2.1261 | Day | 202601 | 2026-01-20 | 2.1261
2026-01-20 12:16 | 71.8124 | FALSE | TRUE | -5.2189 | -7.8369 | -0.22009 | -0.30554 | 0 |  | 2026-01-18 21:27 | none | FALSE | 1 | 66.5935 | FALSE | FALSE | 0.5511 | 1.7212 | 69.313 | 42 | 0 | 0.11295 | 0.80059 | -0.14108 | 1.3597 | Confirmed/Materialized Shift | 72.0325 | 1.8381 | Day | 202601 | 2026-01-20 | 1.8381
2026-01-20 12:30 | 72.095 | FALSE | TRUE | -5.6457 | -8.4962 | -0.33587 | -0.46371 | 0.2826 |  | 2026-01-18 21:27 | none | FALSE | 1 | 66.4493 | FALSE | FALSE | 0.5469 | 1.7225 | 69.4401 | 43 | 0.2826 | 0.12708 | 0.80099 | 0.19416 | 1.4954 | Confirmed/Materialized Shift | 72.4309 | 1.7754 | Day | 202601 | 2026-01-20 | 1.7754
2026-01-20 12:45 | 72.3758 | FALSE | TRUE | -6.0441 | -9.112 | -0.48323 | -0.66323 | 0.2808 |  | 2026-01-18 21:27 | none | FALSE | 1 | 66.3317 | FALSE | FALSE | 0.5422 | 1.7221 | 69.5953 | 44 | 0.2808 | 0.15525 | 0.79571 | 0.15778 | 1.6318 | Confirmed/Materialized Shift | 72.859 | 1.7039 | Day | 202601 | 2026-01-20 | 1.7039
2026-01-20 13:00 | 72.6584 | FALSE | TRUE | -6.4269 | -9.7038 | -0.63958 | -0.87257 | 0.2826 |  | 2026-01-18 21:27 | none | FALSE | 1 | 66.2315 | FALSE | FALSE | 0.5378 | 1.7202 | 69.7647 | 45 | 0.2826 | 0.16938 | 0.79532 | 0.14236 | 1.7666 | Confirmed/Materialized Shift | 73.298 | 1.638 | Day | 202601 | 2026-01-20 | 1.638
2026-01-20 13:15 | 72.941 | FALSE | TRUE | -6.7894 | -10.2635 | -0.8039 | -1.0901 | 0.2826 |  | 2026-01-18 21:27 | none | FALSE | 1 | 66.1516 | FALSE | FALSE | 0.5337 | 1.7171 | 69.9482 | 46 | 0.2826 | 0.18351 | 0.79466 | 0.12469 | 1.8983 | Confirmed/Materialized Shift | 73.7449 | 1.5765 | Day | 202601 | 2026-01-20 | 1.5765
2026-01-20 13:30 | 73.2236 | FALSE | TRUE | -7.0997 | -10.737 | -0.97253 | -1.3108 | 0.2826 |  | 2026-01-18 21:27 | none | FALSE | 1 | 66.1239 | FALSE | FALSE | 0.5298 | 1.7128 | 70.16 | 47 | 0.2826 | 0.21177 | 0.78723 | 0.089974 | 2.0181 | Confirmed/Materialized Shift | 74.1961 | 1.5181 | Day | 202601 | 2026-01-20 | 1.5181
2026-01-20 13:45 | 73.2236 | FALSE | TRUE | -7.0337 | -10.6265 | -1.3583 | -1.8212 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 66.1899 | FALSE | FALSE | 0.4902 | 1.7053 | 70.3859 | 48 | 0 | 0.2259 | 0.78039 | -0.28947 | 2.098 | Confirmed/Materialized Shift | 74.5819 | 1.3526 | Day | 202601 | 2026-01-20 | 1.3526
2026-01-20 14:00 | 73.5062 | FALSE | TRUE | -7.2183 | -10.8894 | -1.4578 | -1.9447 | 0.2826 |  | 2026-01-18 21:27 | none | FALSE | 0 | 66.2879 | FALSE | FALSE | 0.4885 | 1.6976 | 70.6259 | 49 | 0.2826 | 0.24003 | 0.77864 | 0.054672 | 2.169 | Confirmed/Materialized Shift | 74.964 | 1.3279 | Day | 202601 | 2026-01-20 | 1.3279
2026-01-20 14:15 | 73.7888 | FALSE | TRUE | -7.367 | -11.0913 | -1.5496 | -2.0569 | 0.2826 |  | 2026-01-18 21:27 | none | FALSE | 0 | 66.4218 | FALSE | FALSE | 0.487 | 1.6898 | 70.8801 | 50 | 0.2826 | 0.25416 | 0.77662 | 0.03662 | 2.2292 | Confirmed/Materialized Shift | 75.3384 | 1.3048 | Day | 202601 | 2026-01-20 | 1.3048
2026-01-20 14:30 | 73.7888 | FALSE | TRUE | -7.1219 | -10.6828 | -1.8411 | -2.4343 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 66.6669 | FALSE | FALSE | 0.4786 | 1.6797 | 71.1484 | 51 | 0 | 0.26829 | 0.76887 | -0.34894 | 2.2407 | Confirmed/Materialized Shift | 75.6299 | 1.1784 | Day | 202601 | 2026-01-20 | 1.1784
2026-01-20 14:45 | 73.7888 | FALSE | TRUE | -6.8089 | -10.1655 | -2.0646 | -2.7218 | 0 |  | 2026-01-18 21:27 | none | FALSE | 0 | 66.9799 | FALSE | FALSE | 0.4713 | 1.668 | 71.4167 | 52 | 0 | 0.26829 | 0.76887 | -0.34894 | 2.2184 | Confirmed/Materialized Shift | 75.8534 | 1.0693 | Day | 202601 | 2026-01-20 | 1.0693
2026-01-20 14:58 | 74.0714 | FALSE | TRUE | -6.725 | -9.9857 | -1.9804 | -2.604 | 0.2826 |  | 2026-01-18 21:27 | none | FALSE | 0 | 67.3464 | FALSE | FALSE | 0.4727 | 1.6571 | 71.6991 | 53 | 0.2826 | 0.28242 | 0.76628 | 0.0002349 | 2.1763 | Confirmed/Materialized Shift | 76.0518 | 1.09 | Day | 202601 | 2026-01-20 | 1.09
2026-01-20 15:01 | 73.7888 | FALSE | FALSE | -5.9138 | -8.7127 | -2.2992 | -3.0217 | -0.2826 |  |  | none | FALSE | 0 | 67.875 | FALSE | FALSE | 0.0587 |  | 71.9815 | 0 | -0.2826 | 0.28242 | 0.76628 | -0.73736 | 2.0532 | Persistence ends | 76.088 | 0.88022 | Day | 202601 | 2026-01-20 | 0.88022
2026-01-20 15:16 | 72.941 | FALSE | FALSE | -4.3397 | -6.326 | -2.9289 | -3.8604 | -0.8478 |  |  | none | FALSE | 0 | 68.6013 | FALSE | FALSE | 0.0259 |  | 72.2356 | 0 | -0.8478 | 0.25407 | 0.79804 | -1.3807 | 1.8172 | Normal | 75.8699 | 0.3882 | Day | 202601 | 2026-01-20 | 0.3882
2026-01-20 15:29 | 72.095 | FALSE | FALSE | -2.6463 | -3.8105 | -3.351 | -4.4416 | -0.846 |  |  | none | FALSE | 0 | 69.4487 | FALSE | FALSE | 0.0157 |  | 72.4474 | 0 | -0.846 | 0.21177 | 0.83383 | -1.2686 | 1.4993 | Normal | 75.446 | -0.235 | Day | 202601 | 2026-01-20 | 0.235
2026-01-20 15:36 | 71.8124 | FALSE | FALSE | -1.1267 | -1.594 | -2.8202 | -3.7787 | -0.2826 |  |  | none | FALSE | 0 | 70.6857 | FALSE | FALSE | 0.0572 |  | 72.6591 | 0 | -0.2826 | 0.21177 | 0.83383 | -0.59289 | 0.98672 | Normal | 74.6326 | -0.85812 | Day | 202601 | 2026-01-20 | 0.85812
2026-01-20 15:51 | 72.6584 | FALSE | FALSE | -1.7201 | -2.4247 | -1.8909 | -2.5364 | 0.846 |  |  | none | FALSE | 0 | 70.9383 | FALSE | FALSE | 0.0063 |  | 72.7438 | 0 | 0.846 | 0.08469 | 0.41063 | 1.854 | 0.90274 | Normal | 74.5493 | -0.094612 | Day | 202601 | 2026-01-20 | 0.094612
2026-01-20 16:06 | 72.941 | FALSE | FALSE | -1.6985 | -2.3841 | -1.5017 | -2.0173 | 0.2826 |  |  | none | FALSE | 0 | 71.2425 | FALSE | FALSE | 0.0082 |  | 72.8426 | 0 | 0.2826 | 0.09882 | 0.41242 | 0.44562 | 0.80006 | Normal | 74.4427 | 0.12295 | Day | 202601 | 2026-01-20 | 0.12295
2026-01-20 16:21 | 73.2236 | FALSE | FALSE | -1.7788 | -2.4898 | -1.1862 | -1.5942 | 0.2826 |  |  | none | FALSE | 0 | 71.4448 | FALSE | FALSE | 0.0266 |  | 72.9273 | 0 | 0.2826 | 0.08469 | 0.40026 | 0.49445 | 0.74126 | Normal | 74.4098 | 0.3997 | Day | 202601 | 2026-01-20 | 0.3997
2026-01-20 16:29 | 73.2236 | FALSE | FALSE | -1.6163 | -2.2572 | -1.1649 | -1.5659 | 0 |  |  | none | FALSE | 0 | 71.6073 | FALSE | FALSE | 0.0216 |  | 72.9979 | 0 | 0 | 0.07056 | 0.39789 | -0.17734 | 0.69529 | Normal | 74.3885 | 0.32464 | Day | 202601 | 2026-01-20 | 0.32464
2026-01-20 16:44 | 73.5062 | FALSE | FALSE | -1.7128 | -2.3858 | -0.86557 | -1.1638 | 0.2826 |  |  | none | FALSE | 0 | 71.7934 | FALSE | FALSE | 0.0438 |  | 73.0826 | 0 | 0.2826 | 0.08469 | 0.40026 | 0.49445 | 0.6446 | Normal | 74.3718 | 0.6572 | Day | 202601 | 2026-01-20 | 0.6572
2026-01-20 16:59 | 73.5062 | FALSE | FALSE | -1.567 | -2.1782 | -0.86082 | -1.1575 | 0 |  |  | none | FALSE | 0 | 71.9392 | FALSE | FALSE | 0.0388 |  | 73.1531 | 0 | 0 | 0.07056 | 0.39789 | -0.17734 | 0.60695 | Normal | 74.367 | 0.58171 | Day | 202601 | 2026-01-20 | 0.58171
2026-01-20 17:14 | 73.7888 | FALSE | FALSE | -1.7526 | -2.433 | -0.62258 | -0.83667 | 0.2826 |  |  | none | FALSE | 0 | 72.0362 | FALSE | FALSE | 0.0634 |  | 73.2238 | 0 | 0.2826 | 0.07065 | 0.39794 | 0.53262 | 0.5938 | Normal | 74.4114 | 0.95154 | Day | 202601 | 2026-01-20 | 0.95154
2026-01-20 17:29 | 73.7888 | FALSE | FALSE | -1.6904 | -2.3445 | -0.67338 | -0.90433 | 0 |  |  | none | FALSE | 0 | 72.0984 | FALSE | FALSE | 0.0574 |  | 73.2803 | 0 | 0 | 0.05652 | 0.39502 | -0.14308 | 0.59094 | Normal | 74.4622 | 0.86049 | Day | 202601 | 2026-01-20 | 0.86049
2026-01-20 17:44 | 73.7888 | FALSE | FALSE | -1.6575 | -2.2979 | -0.72531 | -0.97339 | 0 |  |  | none | FALSE | 0 | 72.1313 | FALSE | FALSE | 0.0522 |  | 73.3227 | 0 | 0 | 0.04239 | 0.39155 | -0.10826 | 0.59571 | Normal | 74.5141 | 0.78244 | Day | 202601 | 2026-01-20 | 0.78244
2026-01-20 17:59 | 73.2236 | FALSE | FALSE | -1.0923 | -1.5144 | -1.2905 | -1.7319 | -0.5652 |  |  | none | FALSE | 0 | 72.1313 | FALSE | FALSE | 0.0111 |  | 73.3227 | 0 | -0.5652 | 0 | 0.40965 | -1.3797 | 0.59571 | Normal | 74.5141 | -0.16634 | Night | 202601 | 2026-01-20 | 0.16634
2026-01-20 18:14 | 72.941 | FALSE | FALSE | -0.83545 | -1.1587 | -1.5706 | -2.1078 | -0.2826 |  |  | none | FALSE | 0 | 72.1055 | FALSE | FALSE | 0.0407 |  | 73.3086 | 0 | -0.2826 | -0.01413 | 0.41449 | -0.64771 | 0.60151 | Normal | 74.5116 | -0.61106 | Night | 202601 | 2026-01-20 | 0.61106
2026-01-20 18:28 | 72.6584 | FALSE | FALSE | -0.62529 | -0.86806 | -1.8408 | -2.4709 | -0.2826 |  |  | none | FALSE | 0 | 72.0331 | FALSE | FALSE | 0.0657 |  | 73.2662 | 0 | -0.2826 | -0.04239 | 0.41246 | -0.58238 | 0.61653 | Normal | 74.4992 | -0.98579 | Night | 202601 | 2026-01-20 | 0.98579
2026-01-20 18:30 | 72.6584 | FALSE | FALSE | -0.68457 | -0.95114 | -1.7871 | -2.4005 | 0 |  |  | none | FALSE | 0 | 71.9738 | FALSE | FALSE | 0.0595 |  | 73.2096 | 0 | 0 | -0.05652 | 0.40552 | 0.13938 | 0.61791 | Normal | 74.4455 | -0.89212 | Night | 202601 | 2026-01-20 | 0.89212
2026-01-20 18:31 | 72.6584 | FALSE | FALSE | -0.73294 | -1.019 | -1.7224 | -2.3156 | 0 |  |  | none | FALSE | 0 | 71.9255 | FALSE | FALSE | 0.0537 |  | 73.1531 | 0 | 0 | -0.05652 | 0.40552 | 0.13938 | 0.61383 | Normal | 74.3808 | -0.80597 | Night | 202601 | 2026-01-20 | 0.80597
2026-01-20 18:46 | 72.3758 | FALSE | FALSE | -0.52956 | -0.73707 | -1.9429 | -2.6143 | -0.2826 |  |  | none | FALSE | 0 | 71.8462 | FALSE | FALSE | 0.0762 |  | 73.0825 | 0 | -0.2826 | -0.07065 | 0.40836 | -0.51902 | 0.61812 | Normal | 74.3187 | -1.1433 | Night | 202601 | 2026-01-20 | 1.1433
2026-01-20 19:01 | 72.941 | FALSE | FALSE | -1.061 | -1.476 | -1.2309 | -1.6595 | 0.5652 |  |  | none | FALSE | 0 | 71.88 | FALSE | FALSE | 0.0099 |  | 73.026 | 0 | 0.5652 | -0.05652 | 0.42575 | 1.4603 | 0.57297 | Normal | 74.1719 | -0.14828 | Night | 202601 | 2026-01-20 | 0.14828
2026-01-20 19:16 | 72.941 | FALSE | FALSE | -1.0458 | -1.4547 | -1.131 | -1.5268 | 0 |  |  | none | FALSE | 0 | 71.8952 | FALSE | FALSE | 0.0052 |  | 72.9836 | 0 | 0 | -0.04239 | 0.42253 | 0.10032 | 0.5442 | Normal | 74.072 | -0.078225 | Night | 202601 | 2026-01-20 | 0.078225
2026-01-20 19:30 | 72.941 | FALSE | FALSE | -1.0458 | -1.4547 | -1.131 | -1.5268 | 0 |  |  | none | FALSE | 0 | 71.8952 | FALSE | FALSE | 0.0052 |  | 72.9836 | 0 | 0 | 0 | 0.37761 | 0 | 0.5442 | Normal | 74.072 | -0.078225 | Night | 202601 | 2026-01-20 | 0.078225
2026-01-20 19:45 | 73.2236 | FALSE | FALSE | -1.1921 | -1.655 | -0.82492 | -1.114 | 0.2826 |  |  | none | FALSE | 0 | 72.0315 | FALSE | FALSE | 0.0243 |  | 73.04 | 0 | 0.2826 | 0.05643 | 0.32523 | 0.69542 | 0.50426 | Normal | 74.0485 | 0.3641 | Night | 202601 | 2026-01-20 | 0.3641
2026-01-20 20:00 | 73.2236 | FALSE | FALSE | -0.94128 | -1.3022 | -0.7152 | -0.96728 | 0 |  |  | none | FALSE | 0 | 72.2823 | FALSE | FALSE | 0.0182 |  | 73.1106 | 0 | 0 | 0.07056 | 0.31572 | -0.22349 | 0.41412 | Normal | 73.9388 | 0.27296 | Night | 202601 | 2026-01-20 | 0.27296
2026-01-20 20:15 | 72.941 | FALSE | FALSE | -0.62139 | -0.85922 | -0.98877 | -1.3374 | -0.2826 |  |  | none | FALSE | 0 | 72.3196 | FALSE | FALSE | 0.0304 |  | 73.1247 | 0 | -0.2826 | 0.01413 | 0.26692 | -1.1117 | 0.40254 | Normal | 73.9298 | -0.45633 | Night | 202601 | 2026-01-20 | 0.45633
2026-01-20 20:29 | 72.941 | FALSE | FALSE | -0.62139 | -0.85922 | -0.98877 | -1.3374 | 0 |  |  | none | FALSE | 0 | 72.3196 | FALSE | FALSE | 0.0304 |  | 73.1247 | 0 | 0 | 0 | 0.25933 | 0 | 0.40254 | Normal | 73.9298 | -0.45633 | Night | 202601 | 2026-01-20 | 0.45633
2026-01-20 20:44 | 72.6584 | FALSE | FALSE | -0.39173 | -0.54206 | -1.2678 | -1.7149 | -0.2826 |  |  | none | FALSE | 0 | 72.2667 | FALSE | FALSE | 0.0704 |  | 73.0964 | 0 | -0.2826 | -0.02826 | 0.25771 | -0.98694 | 0.41488 | Normal | 73.9262 | -1.0558 | Night | 202601 | 2026-01-20 | 1.0558
2026-01-20 20:59 | 72.6584 | FALSE | FALSE | -0.44001 | -0.60928 | -1.2596 | -1.704 | 0 |  |  | none | FALSE | 0 | 72.2184 | FALSE | FALSE | 0.0643 |  | 73.0682 | 0 | 0 | -0.02826 | 0.25771 | 0.10966 | 0.42489 | Normal | 73.918 | -0.96441 | Night | 202601 | 2026-01-20 | 0.96441
2026-01-20 21:29 | 72.3758 | FALSE | FALSE | -0.24119 | -0.33437 | -1.5129 | -2.0475 | -0.2826 |  |  | none | FALSE | 0 | 72.1346 | FALSE | FALSE | 0.0967 |  | 73.0117 | 0 | -0.2826 | -0.05652 | 0.25277 | -0.89443 | 0.43852 | Normal | 73.8887 | -1.45 | Night | 202601 | 2026-01-20 | 1.45
2026-01-20 21:44 | 72.3758 | FALSE | FALSE | -0.30914 | -0.42897 | -1.4678 | -1.9877 | 0 |  |  | none | FALSE | 0 | 72.0667 | FALSE | FALSE | 0.0869 |  | 72.9551 | 0 | 0 | -0.05652 | 0.25277 | 0.22361 | 0.44424 | Normal | 73.8436 | -1.3041 | Night | 202601 | 2026-01-20 | 1.3041
2026-01-20 21:59 | 72.3758 | FALSE | FALSE | -0.32361 | -0.44913 | -1.341 | -1.8191 | 0 |  |  | none | FALSE | 0 | 72.0522 | FALSE | FALSE | 0.0815 |  | 72.8845 | 0 | 0 | -0.07065 | 0.24041 | 0.29388 | 0.41614 | Normal | 73.7168 | -1.2224 | Night | 202601 | 2026-01-20 | 1.2224
2026-01-20 22:14 | 72.3758 | FALSE | FALSE | -0.30628 | -0.42498 | -1.1823 | -1.6074 | 0 |  |  | none | FALSE | 0 | 72.0695 | FALSE | FALSE | 0.0785 |  | 72.8138 | 0 | 0 | -0.07065 | 0.24041 | 0.29388 | 0.37215 | Normal | 73.5581 | -1.177 | Night | 202601 | 2026-01-20 | 1.177
2026-01-20 22:29 | 72.3758 | FALSE | FALSE | -0.24356 | -0.33766 | -0.97832 | -1.3337 | 0 |  |  | none | FALSE | 0 | 72.1322 | FALSE | FALSE | 0.0802 |  | 72.7432 | 0 | 0 | -0.07065 | 0.24041 | 0.29388 | 0.30547 | Normal | 73.3541 | -1.2027 | Night | 202601 | 2026-01-20 | 1.2027
2026-01-20 22:44 | 72.3758 | FALSE | FALSE | -0.26281 | -0.36445 | -0.91279 | -1.2455 | 0 |  |  | none | FALSE | 0 | 72.113 | FALSE | FALSE | 0.0737 |  | 72.7008 | 0 | 0 | -0.04239 | 0.21058 | 0.2013 | 0.2939 | Normal | 73.2886 | -1.1058 | Night | 202601 | 2026-01-20 | 1.1058
2026-01-20 22:59 | 72.3758 | FALSE | FALSE | -0.29677 | -0.41172 | -0.89023 | -1.2151 | 0 |  |  | none | FALSE | 0 | 72.079 | FALSE | FALSE | 0.0667 |  | 72.6725 | 0 | 0 | -0.02826 | 0.20296 | 0.13924 | 0.29675 | Normal | 73.266 | -0.99994 | Night | 202601 | 2026-01-20 | 0.99994
2026-01-20 23:14 | 72.095 | FALSE | FALSE | -0.097998 | -0.13611 | -1.1967 | -1.6328 | -0.2808 |  |  | none | FALSE | 0 | 71.997 | FALSE | FALSE | 0.1131 |  | 72.6444 | 0 | -0.2808 | -0.02817 | 0.20284 | -1.2455 | 0.32368 | Normal | 73.2917 | -1.6972 | Night | 202601 | 2026-01-20 | 1.6972
2026-01-20 23:28 | 72.095 | FALSE | FALSE | -0.17107 | -0.23785 | -1.2135 | -1.6553 | 0 |  |  | none | FALSE | 0 | 71.9239 | FALSE | FALSE | 0.1004 |  | 72.6162 | 0 | 0 | -0.02817 | 0.20284 | 0.13888 | 0.34613 | Normal | 73.3085 | -1.5058 | Night | 202601 | 2026-01-20 | 1.5058
2026-01-20 23:43 | 72.095 | FALSE | FALSE | -0.23684 | -0.32959 | -1.2229 | -1.6679 | 0 |  |  | none | FALSE | 0 | 71.8582 | FALSE | FALSE | 0.0901 |  | 72.588 | 0 | 0 | -0.02817 | 0.20284 | 0.13888 | 0.36493 | Normal | 73.3179 | -1.351 | Night | 202601 | 2026-01-20 | 1.351
2026-01-20 23:58 | 72.095 | FALSE | FALSE | -0.27836 | -0.38759 | -1.2363 | -1.6859 | 0 |  |  | none | FALSE | 0 | 71.8166 | FALSE | FALSE | 0.0843 |  | 72.574 | 0 | 0 | -0.01404 | 0.19383 | 0.072436 | 0.37867 | Normal | 73.3313 | -1.2649 | Night | 202601 | 2026-01-20 | 1.2649
2026-01-21 00:14 | 72.095 | FALSE | FALSE | -0.3288 | -0.45816 | -1.2022 | -1.6401 | 0 |  |  | none | FALSE | 0 | 71.7662 | FALSE | FALSE | 0.0761 |  | 72.5317 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.38274 | Normal | 73.2972 | -1.1409 | Night | 202601 | 2026-01-21 | 1.1409
2026-01-21 00:28 | 72.095 | FALSE | FALSE | -0.36936 | -0.51497 | -1.1581 | -1.581 | 0 |  |  | none | FALSE | 0 | 71.7256 | FALSE | FALSE | 0.0689 |  | 72.4894 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.38187 | Normal | 73.2531 | -1.0328 | Night | 202601 | 2026-01-21 | 1.0328
2026-01-21 00:43 | 72.095 | FALSE | FALSE | -0.39997 | -0.55787 | -1.1041 | -1.5084 | 0 |  |  | none | FALSE | 0 | 71.695 | FALSE | FALSE | 0.0624 |  | 72.4471 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.37602 | Normal | 73.1991 | -0.93632 | Night | 202601 | 2026-01-21 | 0.93632
2026-01-21 00:58 | 72.095 | FALSE | FALSE | -0.37615 | -0.52448 | -0.96745 | -1.3241 | 0 |  |  | none | FALSE | 0 | 71.7188 | FALSE | FALSE | 0.0587 |  | 72.3906 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.3359 | Normal | 73.0625 | -0.88017 | Night | 202601 | 2026-01-21 | 0.88017
2026-01-21 01:13 | 72.095 | FALSE | FALSE | -0.31778 | -0.44273 | -0.79622 | -1.0923 | 0 |  |  | none | FALSE | 0 | 71.7772 | FALSE | FALSE | 0.0573 |  | 72.3342 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.2785 | Normal | 72.8912 | -0.85896 | Night | 202601 | 2026-01-21 | 0.85896
2026-01-21 01:28 | 72.095 | FALSE | FALSE | -0.29016 | -0.4041 | -0.684 | -0.93984 | 0 |  |  | none | FALSE | 0 | 71.8048 | FALSE | FALSE | 0.0539 |  | 72.2919 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.24354 | Normal | 72.779 | -0.80857 | Night | 202601 | 2026-01-21 | 0.80857
2026-01-21 01:43 | 71.8124 | FALSE | FALSE | -0.005345 | -0.0074435 | -0.85152 | -1.1719 | -0.2826 |  |  | none | FALSE | 0 | 71.8071 | FALSE | FALSE | 0.1317 |  | 72.2355 | 0 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.21422 | Normal | 72.6639 | -1.975 | Night | 202601 | 2026-01-21 | 1.975
2026-01-21 01:58 | 71.8124 | FALSE | FALSE | -0.038799 | -0.054057 | -0.80038 | -1.1023 | 0 |  |  | none | FALSE | 0 | 71.7736 | FALSE | FALSE | 0.121 |  | 72.1932 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.20979 | Normal | 72.6128 | -1.8151 | Night | 202601 | 2026-01-21 | 1.8151
2026-01-21 02:13 | 71.8124 | FALSE | FALSE | -0.053282 | -0.074251 | -0.73026 | -1.0067 | 0 |  |  | none | FALSE | 0 | 71.7591 | FALSE | FALSE | 0.1152 |  | 72.1509 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.19589 | Normal | 72.5427 | -1.728 | Night | 202601 | 2026-01-21 | 1.728
2026-01-21 02:27 | 71.8124 | FALSE | FALSE | -0.094174 | -0.13131 | -0.71481 | -0.98558 | 0 |  |  | none | FALSE | 0 | 71.7182 | FALSE | FALSE | 0.1023 |  | 72.1227 | 0 | 0 | -0.02817 | 0.086706 | 0.32489 | 0.20225 | Normal | 72.5272 | -1.5344 | Night | 202601 | 2026-01-21 | 1.5344
2026-01-21 02:43 | 71.5298 | TRUE | FALSE | 0.085207 | 0.11898 | -1.016 | -1.4005 | -0.2826 | 2026-01-21 06:41 | 2026-01-21 02:43 | lower | TRUE | 1 | 71.615 | FALSE | FALSE | 0.2435 | 2.3662 | 72.0804 | 1 | -0.2826 | -0.0423 | 0.10331 | -2.326 | 0.23271 | Extreme triggered | 72.5458 | -2.3662 | Night | 202601 | 2026-01-21 | 2.3662
2026-01-21 02:58 | 71.5298 | FALSE | FALSE | 0.0038054 | 0.0053198 | -1.0128 | -1.3962 | 0 |  | 2026-01-21 02:43 | lower | TRUE | 1 | 71.5336 | FALSE | FALSE | 0.2772 | 2.1906 | 72.0381 | 2 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.25226 | Extreme/elevated | 72.5426 | -2.0151 | Night | 202601 | 2026-01-21 | 2.0151
2026-01-21 03:13 | 71.5298 | FALSE | FALSE | -0.060661 | -0.084877 | -0.9927 | -1.3688 | 0 |  | 2026-01-21 02:43 | none | FALSE | 1 | 71.4691 | FALSE | FALSE | 0.318 | 2.0503 | 71.9958 | 3 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.26334 | Persistent | 72.5225 | -1.7696 | Night | 202601 | 2026-01-21 | 1.7696
2026-01-21 03:27 | 71.5298 | FALSE | FALSE | -0.11031 | -0.15445 | -0.95775 | -1.3213 | 0 |  | 2026-01-21 02:43 | none | FALSE | 1 | 71.4195 | FALSE | FALSE | 0.3629 | 1.9344 | 71.9535 | 4 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.26701 | Persistent | 72.4875 | -1.5869 | Night | 202601 | 2026-01-21 | 1.5869
2026-01-21 03:42 | 71.5298 | FALSE | FALSE | -0.14575 | -0.20417 | -0.90859 | -1.2543 | 0 |  | 2026-01-21 02:43 | none | FALSE | 1 | 71.3841 | FALSE | FALSE | 0.4108 | 1.837 | 71.9112 | 5 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.26358 | Persistent | 72.4384 | -1.4471 | Night | 202601 | 2026-01-21 | 1.4471
2026-01-21 03:57 | 71.5298 | FALSE | FALSE | -0.16641 | -0.23319 | -0.84465 | -1.1671 | 0 |  | 2026-01-21 02:43 | none | FALSE | 1 | 71.3634 | FALSE | FALSE | 0.4609 | 1.7544 | 71.8689 | 6 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.25277 | Persistent | 72.3745 | -1.3416 | Night | 202601 | 2026-01-21 | 1.3416
2026-01-21 04:12 | 71.5298 | FALSE | TRUE | -0.20455 | -0.28679 | -0.82627 | -1.142 | 0 |  | 2026-01-21 02:43 | none | FALSE | 1 | 71.3252 | FALSE | FALSE | 0.509 | 1.6761 | 71.8407 | 7 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.25771 | Confirmed/Materialized Shift | 72.3561 | -1.2063 | Night | 202601 | 2026-01-21 | 1.2063
2026-01-21 04:27 | 71.5298 | FALSE | TRUE | -0.23606 | -0.33111 | -0.80126 | -1.1078 | 0 |  | 2026-01-21 02:43 | none | FALSE | 1 | 71.2937 | FALSE | FALSE | 0.5012 | 1.6028 | 71.8124 | 8 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.25933 | Confirmed/Materialized Shift | 72.3311 | -1.0897 | Night | 202601 | 2026-01-21 | 1.0897
2026-01-21 04:42 | 71.2472 | TRUE | TRUE | -0.035657 | -0.050072 | -1.0813 | -1.495 | -0.2826 |  | 2026-01-21 02:43 | none | FALSE | 2 | 71.2115 | TRUE | FALSE | 0.582 | 1.6328 | 71.77 | 9 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.27923 | Confirmed/Materialized Shift | 72.3285 | -1.8723 | Night | 202601 | 2026-01-21 | 1.8723
2026-01-21 04:57 | 71.2472 | FALSE | TRUE | -0.10236 | -0.14387 | -1.0632 | -1.4703 | 0 |  | 2026-01-21 02:43 | none | FALSE | 2 | 71.1448 | FALSE | FALSE | 0.5671 | 1.6343 | 71.7276 | 10 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.29139 | Confirmed/Materialized Shift | 72.3104 | -1.6487 | Night | 202601 | 2026-01-21 | 1.6487
2026-01-21 05:12 | 71.2472 | FALSE | TRUE | -0.15547 | -0.21868 | -1.0315 | -1.4271 | 0 |  | 2026-01-21 02:43 | none | FALSE | 1 | 71.0917 | FALSE | FALSE | 0.527 | 1.62 | 71.6852 | 11 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.29675 | Confirmed/Materialized Shift | 72.2787 | -1.4761 | Night | 202601 | 2026-01-21 | 1.4761
2026-01-21 05:27 | 71.2472 | FALSE | TRUE | -0.19573 | -0.27547 | -0.98701 | -1.3664 | 0 |  | 2026-01-21 02:43 | none | FALSE | 1 | 71.0515 | FALSE | FALSE | 0.5178 | 1.5965 | 71.6428 | 12 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.29568 | Confirmed/Materialized Shift | 72.2342 | -1.3381 | Night | 202601 | 2026-01-21 | 1.3381
2026-01-21 05:42 | 71.2472 | FALSE | TRUE | -0.223 | -0.31397 | -0.9295 | -1.2878 | 0 |  | 2026-01-21 02:43 | none | FALSE | 1 | 71.0242 | FALSE | FALSE | 0.5103 | 1.568 | 71.6004 | 13 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.28812 | Confirmed/Materialized Shift | 72.1767 | -1.226 | Night | 202601 | 2026-01-21 | 1.226
2026-01-21 05:57 | 71.2472 | FALSE | TRUE | -0.2362 | -0.33263 | -0.85792 | -1.1898 | 0 |  | 2026-01-21 02:43 | none | FALSE | 1 | 71.011 | FALSE | FALSE | 0.5043 | 1.5372 | 71.5581 | 14 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27353 | Confirmed/Materialized Shift | 72.1051 | -1.1365 | Night | 202601 | 2026-01-21 | 1.1365
2026-01-21 06:12 | 71.2472 | FALSE | TRUE | -0.23289 | -0.32794 | -0.76983 | -1.0689 | 0 |  | 2026-01-21 02:43 | none | FALSE | 1 | 71.0143 | FALSE | FALSE | 0.5 | 1.5061 | 71.5157 | 15 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.25068 | Confirmed/Materialized Shift | 72.017 | -1.071 | Night | 202601 | 2026-01-21 | 1.071
2026-01-21 06:26 | 71.2472 | FALSE | TRUE | -0.20786 | -0.29261 | -0.66002 | -0.91788 | 0 |  | 2026-01-21 02:43 | none | FALSE | 1 | 71.0393 | FALSE | FALSE | 0.498 | 1.4771 | 71.4733 | 16 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.21697 | Confirmed/Materialized Shift | 71.9072 | -1.042 | Night | 202601 | 2026-01-21 | 1.042
2026-01-21 06:41 | 71.2472 | FALSE | FALSE | -0.2163 | -0.30451 | -0.61194 | -0.85158 | 0 |  |  | none | FALSE | 1 | 71.0309 | FALSE | FALSE | 0.0923 |  | 71.445 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.20706 | Persistence ends | 71.8591 | -0.95538 | Night | 202601 | 2026-01-21 | 0.95538
2026-01-21 06:56 | 71.2472 | FALSE | FALSE | -0.21509 | -0.30281 | -0.55421 | -0.77187 | 0 |  |  | none | FALSE | 1 | 71.0321 | FALSE | FALSE | 0.0873 |  | 71.4168 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.19233 | Normal | 71.8014 | -0.88163 | Night | 202601 | 2026-01-21 | 0.88163
2026-01-21 07:11 | 71.2472 | FALSE | FALSE | -0.20176 | -0.28399 | -0.48436 | -0.67524 | 0 |  |  | none | FALSE | 0 | 71.0454 | FALSE | FALSE | 0.0549 |  | 71.3885 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.17153 | Normal | 71.7316 | -0.82375 | Night | 202601 | 2026-01-21 | 0.82375
2026-01-21 07:26 | 70.9646 | TRUE | FALSE | 0.049657 | 0.069925 | -0.71336 | -0.99523 | -0.2826 | 2026-01-21 08:30 | 2026-01-21 07:26 | lower | TRUE | 1 | 71.0143 | FALSE | FALSE | 0.239 | 2.2993 | 71.3461 | 1 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.16593 | Extreme triggered | 71.678 | -2.2993 | Day | 202601 | 2026-01-21 | 2.2993
2026-01-21 07:30 | 70.9646 | FALSE | FALSE | -0.0077242 | -0.010886 | -0.71422 | -0.99642 | 0 |  | 2026-01-21 07:26 | none | FALSE | 1 | 70.9569 | FALSE | FALSE | 0.2733 | 2.1282 | 71.3179 | 2 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18049 | Extreme/elevated | 71.6788 | -1.9572 | Day | 202601 | 2026-01-21 | 1.9572
2026-01-21 07:45 | 70.9646 | FALSE | FALSE | -0.054158 | -0.076375 | -0.70414 | -0.98249 | 0 |  | 2026-01-21 07:26 | none | FALSE | 1 | 70.9104 | FALSE | FALSE | 0.3143 | 1.9903 | 71.2896 | 3 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18957 | Persistent | 71.6687 | -1.7143 | Day | 202601 | 2026-01-21 | 1.7143
2026-01-21 08:00 | 70.9646 | FALSE | FALSE | -0.091185 | -0.12866 | -0.68465 | -0.95555 | 0 |  | 2026-01-21 07:26 | none | FALSE | 1 | 70.8734 | FALSE | FALSE | 0.3591 | 1.8752 | 71.2613 | 4 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.19396 | Persistent | 71.6492 | -1.5299 | Day | 202601 | 2026-01-21 | 1.5299
2026-01-21 08:15 | 70.9646 | FALSE | FALSE | -0.11945 | -0.1686 | -0.65639 | -0.91647 | 0 |  | 2026-01-21 07:26 | none | FALSE | 1 | 70.8452 | FALSE | FALSE | 0.4066 | 1.777 | 71.2331 | 5 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.19396 | Persistent | 71.621 | -1.3842 | Day | 202601 | 2026-01-21 | 1.3842
2026-01-21 08:30 | 71.2472 | TRUE | FALSE | -0.3904 | -0.55097 | -0.33388 | -0.46643 | 0.2826 |  |  | none | FALSE | 2 | 70.8568 | TRUE | FALSE | 0.0675 |  | 71.2189 | 0 | 0.2826 | -0.01413 | 0.11135 | 2.6647 | 0.18107 | Persistence ends | 71.5811 | 0.15607 | Day | 202601 | 2026-01-21 | 0.15607
2026-01-21 08:30 | 71.2472 | FALSE | FALSE | -0.37424 | -0.52805 | -0.28946 | -0.40464 | 0 |  |  | none | FALSE | 2 | 70.873 | FALSE | FALSE | 0.0742 |  | 71.2048 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.16593 | Normal | 71.5367 | 0.25547 | Day | 202601 | 2026-01-21 | 0.25547
2026-01-21 08:45 | 71.5298 | TRUE | FALSE | -0.65684 | -0.92679 | -0.0068632 | -0.009594 | 0.2826 |  |  | none | FALSE | 3 | 70.873 | TRUE | FALSE | 0.2163 |  | 71.2048 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.16593 | Normal | 71.5367 | 1.9586 | Day | 202601 | 2026-01-21 | 1.9586
2026-01-21 09:00 | 71.8124 | FALSE | FALSE | -0.99938 | -1.4113 | 0.18754 | 0.26184 | 0.2826 | 2026-01-21 14:28 | 2026-01-21 09:00 | upper | TRUE | 3 | 70.813 | FALSE | FALSE | 0.3378 | 2.924 | 71.2189 | 1 | 0.2826 | 0.01413 | 0.14424 | 1.8612 | 0.20296 | Extreme triggered | 71.6249 | 2.924 | Day | 202601 | 2026-01-21 | 2.924
2026-01-21 09:15 | 71.8124 | FALSE | FALSE | -1.0504 | -1.4844 | 0.080035 | 0.11157 | 0 |  | 2026-01-21 09:00 | upper | TRUE | 3 | 70.762 | FALSE | FALSE | 0.3553 | 2.627 | 71.2472 | 2 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.24258 | Extreme/elevated | 71.7324 | 2.3299 | Day | 202601 | 2026-01-21 | 2.3299
2026-01-21 09:30 | 71.8124 | FALSE | FALSE | -1.084 | -1.5326 | -0.01012 | -0.014091 | 0 |  | 2026-01-21 09:00 | none | FALSE | 2 | 70.7284 | FALSE | FALSE | 0.3594 | 2.4057 | 71.2755 | 3 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.27353 | Persistent | 71.8225 | 1.963 | Day | 202601 | 2026-01-21 | 1.963
2026-01-21 09:45 | 72.095 | FALSE | FALSE | -1.4351 | -2.031 | 0.11917 | 0.16557 | 0.2826 |  | 2026-01-21 09:00 | upper | TRUE | 2 | 70.6599 | FALSE | TRUE | 0.4432 | 2.3948 | 71.3179 | 4 | 0.2826 | 0.04239 | 0.13829 | 1.737 | 0.32899 | Persistent | 71.9758 | 2.3622 | Day | 202601 | 2026-01-21 | 2.3622
2026-01-21 10:00 | 72.6584 | TRUE | FALSE | -2.1584 | -3.0615 | 0.38159 | 0.52795 | 0.5634 |  | 2026-01-21 09:00 | upper | TRUE | 3 | 70.5 | TRUE | TRUE | 0.562 | 2.4876 | 71.3884 | 5 | 0.5634 | 0.07056 | 0.18023 | 2.7345 | 0.4442 | Persistent | 72.2768 | 2.859 | Day | 202601 | 2026-01-21 | 2.859
2026-01-21 10:15 | 73.2236 | TRUE | FALSE | -2.9418 | -4.1857 | 0.53097 | 0.73044 | 0.5652 |  | 2026-01-21 09:00 | upper | TRUE | 4 | 70.2818 | TRUE | TRUE | 0.6492 | 2.5532 | 71.4872 | 6 | 0.5652 | 0.09882 | 0.21037 | 2.2169 | 0.6027 | Persistent | 72.6926 | 2.881 | Day | 202601 | 2026-01-21 | 2.881
2026-01-21 10:29 | 72.941 | FALSE | TRUE | -2.7313 | -3.8902 | 0.006881 | 0.0094346 | -0.2826 |  | 2026-01-21 09:00 | upper | TRUE | 4 | 70.2097 | FALSE | TRUE | 0.6483 | 2.4756 | 71.5719 | 7 | -0.2826 | 0.08469 | 0.22625 | -1.6234 | 0.6811 | Confirmed/Materialized Shift | 72.9341 | 2.0101 | Day | 202601 | 2026-01-21 | 2.0101
2026-01-21 10:44 | 72.6584 | FALSE | TRUE | -2.4515 | -3.4918 | -0.41968 | -0.57429 | -0.2826 |  | 2026-01-21 09:00 | none | FALSE | 3 | 70.2069 | FALSE | FALSE | 0.5801 | 2.3431 | 71.6425 | 8 | -0.2826 | 0.07056 | 0.24021 | -1.4702 | 0.7178 | Confirmed/Materialized Shift | 73.0781 | 1.4153 | Day | 202601 | 2026-01-21 | 1.4153
2026-01-21 10:59 | 72.6584 | FALSE | TRUE | -2.4368 | -3.4701 | -0.54607 | -0.74595 | 0 |  | 2026-01-21 09:00 | none | FALSE | 3 | 70.2216 | FALSE | FALSE | 0.5702 | 2.2236 | 71.713 | 9 | 0 | 0.07056 | 0.24021 | -0.29374 | 0.74572 | Confirmed/Materialized Shift | 73.2045 | 1.2677 | Day | 202601 | 2026-01-21 | 1.2677
2026-01-21 11:14 | 72.6584 | FALSE | TRUE | -2.4064 | -3.4254 | -0.65682 | -0.89589 | 0 |  | 2026-01-21 09:00 | none | FALSE | 2 | 70.252 | FALSE | FALSE | 0.5333 | 2.1155 | 71.7836 | 10 | 0 | 0.07056 | 0.24021 | -0.29374 | 0.76581 | Confirmed/Materialized Shift | 73.3152 | 1.1423 | Day | 202601 | 2026-01-21 | 1.1423
2026-01-21 11:29 | 72.941 | FALSE | TRUE | -2.6655 | -3.793 | -0.52012 | -0.70802 | 0.2826 |  | 2026-01-21 09:00 | none | FALSE | 2 | 70.2755 | FALSE | FALSE | 0.5469 | 2.0456 | 71.8683 | 11 | 0.2826 | 0.08469 | 0.24412 | 0.8107 | 0.79641 | Confirmed/Materialized Shift | 73.4611 | 1.3469 | Day | 202601 | 2026-01-21 | 1.3469
2026-01-21 11:44 | 72.941 | FALSE | TRUE | -2.6214 | -3.7278 | -0.64537 | -0.87702 | 0 |  | 2026-01-21 09:00 | none | FALSE | 2 | 70.3196 | FALSE | FALSE | 0.5378 | 1.976 | 71.953 | 12 | 0 | 0.08469 | 0.24412 | -0.34692 | 0.81669 | Confirmed/Materialized Shift | 73.5864 | 1.2098 | Day | 202601 | 2026-01-21 | 1.2098
2026-01-21 11:59 | 72.941 | FALSE | TRUE | -2.5099 | -3.5636 | -0.7315 | -0.99291 | 0 |  | 2026-01-21 09:00 | none | FALSE | 2 | 70.4311 | FALSE | FALSE | 0.5303 | 1.9084 | 72.0518 | 13 | 0 | 0.09882 | 0.22948 | -0.43062 | 0.81035 | Confirmed/Materialized Shift | 73.6725 | 1.0973 | Day | 202601 | 2026-01-21 | 1.0973
2026-01-21 12:14 | 73.2236 | FALSE | TRUE | -2.6754 | -3.7923 | -0.55769 | -0.75587 | 0.2826 |  | 2026-01-21 09:00 | none | FALSE | 2 | 70.5482 | FALSE | FALSE | 0.5445 | 1.8656 | 72.1647 | 14 | 0.2826 | 0.11295 | 0.23177 | 0.73198 | 0.80827 | Confirmed/Materialized Shift | 73.7813 | 1.31 | Day | 202601 | 2026-01-21 | 1.31
2026-01-21 12:29 | 73.2236 | FALSE | TRUE | -2.5246 | -3.5709 | -0.6328 | -0.85679 | 0 |  | 2026-01-21 09:00 | none | FALSE | 1 | 70.699 | FALSE | FALSE | 0.5085 | 1.8211 | 72.2777 | 15 | 0 | 0.11295 | 0.23177 | -0.48734 | 0.78935 | Confirmed/Materialized Shift | 73.8564 | 1.1983 | Day | 202601 | 2026-01-21 | 1.1983
2026-01-21 12:44 | 73.5062 | FALSE | TRUE | -2.6438 | -3.7309 | -0.44099 | -0.59635 | 0.2826 |  | 2026-01-21 09:00 | none | FALSE | 0 | 70.8624 | FALSE | FALSE | 0.4952 | 1.7966 | 72.4048 | 16 | 0.2826 | 0.12708 | 0.23313 | 0.66709 | 0.7712 | Confirmed/Materialized Shift | 73.9472 | 1.4282 | Day | 202601 | 2026-01-21 | 1.4282
2026-01-21 12:59 | 73.5062 | FALSE | TRUE | -2.4337 | -3.4243 | -0.48503 | -0.65552 | 0 |  | 2026-01-21 09:00 | none | FALSE | 0 | 71.0725 | FALSE | FALSE | 0.489 | 1.7694 | 72.5319 | 17 | 0 | 0.12708 | 0.23313 | -0.5451 | 0.72968 | Confirmed/Materialized Shift | 73.9912 | 1.3353 | Day | 202601 | 2026-01-21 | 1.3353
2026-01-21 13:14 | 73.7888 | FALSE | TRUE | -2.5606 | -3.5949 | -0.30085 | -0.40606 | 0.2826 |  | 2026-01-21 09:00 | none | FALSE | 0 | 71.2282 | FALSE | FALSE | 0.5053 | 1.7589 | 72.6589 | 18 | 0.2826 | 0.12708 | 0.23313 | 0.66709 | 0.71536 | Confirmed/Materialized Shift | 74.0897 | 1.5794 | Day | 202601 | 2026-01-21 | 1.5794
2026-01-21 13:28 | 73.7888 | FALSE | TRUE | -2.3549 | -3.2965 | -0.3493 | -0.47114 | 0 |  | 2026-01-21 09:00 | none | FALSE | 0 | 71.4339 | FALSE | FALSE | 0.4989 | 1.7444 | 72.786 | 19 | 0 | 0.12708 | 0.23313 | -0.5451 | 0.67604 | Confirmed/Materialized Shift | 74.1381 | 1.4833 | Day | 202601 | 2026-01-21 | 1.4833
2026-01-21 13:43 | 73.7888 | FALSE | TRUE | -2.1759 | -3.0384 | -0.39619 | -0.53406 | 0 |  | 2026-01-21 09:00 | none | FALSE | 0 | 71.6129 | FALSE | FALSE | 0.4923 | 1.7264 | 72.899 | 20 | 0 | 0.11295 | 0.23177 | -0.48734 | 0.64301 | Confirmed/Materialized Shift | 74.185 | 1.3838 | Day | 202601 | 2026-01-21 | 1.3838
2026-01-21 13:59 | 73.7888 | FALSE | TRUE | -2.0283 | -2.8265 | -0.44628 | -0.60117 | 0 |  | 2026-01-21 09:00 | none | FALSE | 0 | 71.7605 | FALSE | FALSE | 0.4852 | 1.705 | 72.9978 | 21 | 0 | 0.09882 | 0.22948 | -0.43062 | 0.61864 | Confirmed/Materialized Shift | 74.2351 | 1.2786 | Day | 202601 | 2026-01-21 | 1.2786
2026-01-21 14:14 | 73.7888 | FALSE | TRUE | -1.8436 | -2.5625 | -0.45919 | -0.61845 | 0 |  | 2026-01-21 09:00 | none | FALSE | 0 | 71.9452 | FALSE | FALSE | 0.4802 | 1.6822 | 73.0966 | 22 | 0 | 0.09882 | 0.22948 | -0.43062 | 0.57569 | Confirmed/Materialized Shift | 74.248 | 1.2024 | Day | 202601 | 2026-01-21 | 1.2024
2026-01-21 14:14 | 74.0714 | FALSE | TRUE | -1.9224 | -2.6645 | -0.19873 | -0.26757 | 0.2826 |  | 2026-01-21 09:00 | none | FALSE | 0 | 72.149 | FALSE | FALSE | 0.5083 | 1.6797 | 73.2096 | 23 | 0.2826 | 0.11295 | 0.23177 | 0.73198 | 0.53028 | Confirmed/Materialized Shift | 74.2701 | 1.6252 | Day | 202601 | 2026-01-21 | 1.6252
2026-01-21 14:17 | 74.0714 | FALSE | TRUE | -1.7522 | -2.4229 | -0.22619 | -0.30443 | 0 |  | 2026-01-21 09:00 | none | FALSE | 0 | 72.3192 | FALSE | FALSE | 0.5028 | 1.674 | 73.3084 | 24 | 0 | 0.09882 | 0.22948 | -0.43062 | 0.4946 | Confirmed/Materialized Shift | 74.2976 | 1.5427 | Day | 202601 | 2026-01-21 | 1.5427
2026-01-21 14:28 | 73.5062 | TRUE | FALSE | -1.099 | -1.5178 | -0.78811 | -1.0608 | -0.5652 |  |  | none | FALSE | 1 | 72.4072 | FALSE | FALSE | 0.0505 |  | 73.3508 | 0 | -0.5652 | 0.04239 | 0.2473 | -2.4569 | 0.47177 | Persistence ends | 74.2943 | 0.32946 | Day | 202601 | 2026-01-21 | 0.32946
2026-01-21 14:43 | 72.941 | TRUE | FALSE | -0.56424 | -0.77958 | -1.3555 | -1.8245 | -0.5652 |  |  | none | FALSE | 2 | 72.3768 | TRUE | FALSE | 0.1121 |  | 73.3366 | 0 | -0.5652 | -0.01413 | 0.25068 | -2.1983 | 0.47994 | Normal | 74.2965 | -0.82436 | Day | 202601 | 2026-01-21 | 0.82436
2026-01-21 14:58 | 72.3758 | FALSE | FALSE | -0.10637 | -0.14718 | -1.9715 | -2.6518 | -0.5652 |  |  | none | FALSE | 2 | 72.2694 | FALSE | FALSE | 0.1768 |  | 73.3084 | 0 | -0.5652 | -0.02826 | 0.27353 | -1.963 | 0.51947 | Normal | 74.3473 | -1.7952 | Day | 202601 | 2026-01-21 | 1.7952
2026-01-21 15:13 | 72.095 | FALSE | FALSE | 0.046315 | 0.064201 | -2.3241 | -3.123 | -0.2808 | 2026-01-21 15:58 | 2026-01-21 15:13 | lower | TRUE | 2 | 72.1413 | FALSE | FALSE | 0.253 | 2.0813 | 73.2802 | 1 | -0.2808 | -0.02817 | 0.27344 | -0.92389 | 0.56945 | Extreme triggered | 74.4191 | -2.0813 | Day | 202601 | 2026-01-21 | 2.0813
2026-01-21 15:28 | 72.095 | FALSE | FALSE | -0.070996 | -0.098572 | -2.3851 | -3.2023 | 0 |  | 2026-01-21 15:13 | none | FALSE | 2 | 72.024 | FALSE | FALSE | 0.2971 | 1.9829 | 73.252 | 2 | 0 | -0.02817 | 0.27344 | 0.10302 | 0.61402 | Extreme/elevated | 74.4801 | -1.8844 | Day | 202601 | 2026-01-21 | 1.8844
2026-01-21 15:43 | 72.3758 | FALSE | FALSE | -0.4007 | -0.55672 | -2.1249 | -2.8522 | 0.2808 |  | 2026-01-21 15:13 | none | FALSE | 2 | 71.9751 | FALSE | FALSE | 0.3196 | 1.777 | 73.2379 | 3 | 0.2808 | -0.01413 | 0.28204 | 1.0457 | 0.6314 | Persistent | 74.5007 | -1.3654 | Day | 202601 | 2026-01-21 | 1.3654
2026-01-21 15:58 | 72.941 | FALSE | FALSE | -0.9659 | -1.342 | -1.5597 | -2.0936 | 0.5652 |  |  | none | FALSE | 2 | 71.9751 | FALSE | FALSE | 0.0885 |  | 73.2379 | 0 | 0.5652 | 0 | 0.30392 | 1.8597 | 0.6314 | Persistence ends | 74.5007 | -0.47024 | Day | 202601 | 2026-01-21 | 0.47024
2026-01-21 16:13 | 72.941 | FALSE | FALSE | -0.9659 | -1.342 | -1.5597 | -2.0936 | 0 |  |  | none | FALSE | 2 | 71.9751 | FALSE | FALSE | 0.0885 |  | 73.2379 | 0 | 0 | 0 | 0.30392 | 0 | 0.6314 | Normal | 74.5007 | -0.47024 | Day | 202601 | 2026-01-21 | 0.47024
2026-01-21 16:27 | 73.2236 | FALSE | FALSE | -1.2267 | -1.7038 | -1.2836 | -1.7227 | 0.2826 |  |  | none | FALSE | 2 | 71.9969 | FALSE | FALSE | 0.0602 |  | 73.252 | 0 | 0.2826 | 0.01413 | 0.31042 | 0.86487 | 0.62756 | Normal | 74.5072 | -0.045318 | Day | 202601 | 2026-01-21 | 0.045318
2026-01-21 16:43 | 72.941 | FALSE | FALSE | -0.9659 | -1.342 | -1.5597 | -2.0936 | -0.2826 |  |  | none | FALSE | 2 | 71.9751 | FALSE | FALSE | 0.0885 |  | 73.2379 | 0 | -0.2826 | -0.01413 | 0.31042 | -0.86487 | 0.6314 | Normal | 74.5007 | -0.47024 | Day | 202601 | 2026-01-21 | 0.47024
2026-01-21 16:58 | 72.6584 | FALSE | FALSE | -0.73793 | -1.026 | -1.8404 | -2.4704 | -0.2826 |  |  | none | FALSE | 1 | 71.9205 | FALSE | FALSE | 0.0856 |  | 73.2096 | 0 | -0.2826 | -0.02826 | 0.31612 | -0.80457 | 0.64459 | Normal | 74.4988 | -0.8552 | Day | 202601 | 2026-01-21 | 0.8552
2026-01-21 17:13 | 72.941 | FALSE | FALSE | -1.0462 | -1.4552 | -1.527 | -2.0505 | 0.2826 |  |  | none | FALSE | 0 | 71.8948 | FALSE | FALSE | 0.0249 |  | 73.1814 | 0 | 0.2826 | -0.02826 | 0.31612 | 0.98336 | 0.64329 | Normal | 74.468 | -0.37369 | Day | 202601 | 2026-01-21 | 0.37369
2026-01-21 17:27 | 72.6584 | FALSE | FALSE | -0.81674 | -1.1369 | -1.7779 | -2.3885 | -0.2826 |  |  | none | FALSE | 0 | 71.8417 | FALSE | FALSE | 0.0494 |  | 73.139 | 0 | -0.2826 | -0.04239 | 0.32107 | -0.74816 | 0.64867 | Normal | 74.4363 | -0.7409 | Day | 202601 | 2026-01-21 | 0.7409
2026-01-21 17:42 | 72.6584 | FALSE | FALSE | -0.85239 | -1.1871 | -1.7006 | -2.287 | 0 |  |  | none | FALSE | 0 | 71.806 | FALSE | FALSE | 0.0443 |  | 73.0825 | 0 | 0 | -0.05652 | 0.31211 | 0.18109 | 0.63824 | Normal | 74.359 | -0.66446 | Day | 202601 | 2026-01-21 | 0.66446
2026-01-21 17:57 | 72.3758 | FALSE | FALSE | -0.63223 | -0.88123 | -1.9043 | -2.5637 | -0.2826 |  |  | none | FALSE | 0 | 71.7436 | FALSE | FALSE | 0.0669 |  | 73.0118 | 0 | -0.2826 | -0.07065 | 0.31579 | -0.67118 | 0.63413 | Normal | 74.2801 | -1.003 | Night | 202601 | 2026-01-21 | 1.003
2026-01-21 18:12 | 72.3758 | FALSE | FALSE | -0.67781 | -0.94537 | -1.8086 | -2.4379 | 0 |  |  | none | FALSE | 0 | 71.698 | FALSE | FALSE | 0.0606 |  | 72.9412 | 0 | 0 | -0.07065 | 0.31579 | 0.22373 | 0.6216 | Normal | 74.1844 | -0.90956 | Night | 202601 | 2026-01-21 | 0.90956
2026-01-21 18:27 | 72.3758 | FALSE | FALSE | -0.7055 | -0.98437 | -1.695 | -2.2883 | 0 |  |  | none | FALSE | 0 | 71.6703 | FALSE | FALSE | 0.055 |  | 72.8705 | 0 | 0 | -0.07065 | 0.31579 | 0.22373 | 0.60012 | Normal | 74.0708 | -0.82439 | Night | 202601 | 2026-01-21 | 0.82439
2026-01-21 18:30 | 72.3758 | FALSE | FALSE | -0.71326 | -0.99531 | -1.5614 | -2.1118 | 0 |  |  | none | FALSE | 0 | 71.6625 | FALSE | FALSE | 0.0497 |  | 72.7999 | 0 | 0 | -0.07065 | 0.31579 | 0.22373 | 0.56867 | Normal | 73.9372 | -0.74574 | Night | 202601 | 2026-01-21 | 0.74574
2026-01-21 18:31 | 72.3758 | FALSE | FALSE | -0.64089 | -0.89342 | -1.3195 | -1.7905 | 0 |  |  | none | FALSE | 0 | 71.7349 | FALSE | FALSE | 0.0462 |  | 72.7151 | 0 | 0 | -0.08478 | 0.3053 | 0.2777 | 0.4901 | Normal | 73.6953 | -0.69231 | Night | 202601 | 2026-01-21 | 0.69231
2026-01-21 18:46 | 72.941 | FALSE | FALSE | -1.0379 | -1.4435 | -0.47309 | -0.64441 | 0.5652 |  |  | none | FALSE | 0 | 71.9031 | FALSE | FALSE | 0.0498 |  | 72.6586 | 0 | 0.5652 | -0.05652 | 0.33797 | 1.8396 | 0.37775 | Normal | 73.4141 | 0.74763 | Night | 202601 | 2026-01-21 | 0.74763
2026-01-21 19:01 | 72.941 | FALSE | FALSE | -0.96868 | -1.3459 | -0.34732 | -0.47391 | 0 |  |  | none | FALSE | 0 | 71.9723 | FALSE | FALSE | 0.063 |  | 72.6303 | 0 | 0 | -0.02826 | 0.31612 | 0.089396 | 0.329 | Normal | 73.2883 | 0.94431 | Night | 202601 | 2026-01-21 | 0.94431
2026-01-21 19:16 | 73.2236 | FALSE | FALSE | -1.2762 | -1.7738 | -0.11792 | -0.16078 | 0.2826 |  |  | none | FALSE | 0 | 71.9474 | FALSE | FALSE | 0.1108 |  | 72.6445 | 0 | 0.2826 | 0.01413 | 0.29657 | 0.90526 | 0.34854 | Normal | 73.3415 | 1.6617 | Night | 202601 | 2026-01-21 | 1.6617
2026-01-21 19:30 | 73.2236 | FALSE | FALSE | -1.2674 | -1.7613 | -0.19383 | -0.26401 | 0 |  |  | none | FALSE | 0 | 71.9562 | FALSE | FALSE | 0.098 |  | 72.6868 | 0 | 0 | 0.04239 | 0.26355 | -0.16084 | 0.3653 | Normal | 73.4174 | 1.4694 | Night | 202601 | 2026-01-21 | 1.4694
2026-01-21 19:45 | 73.5062 | FALSE | FALSE | -1.5106 | -2.0982 | -0.013036 | -0.017731 | 0.2826 |  |  | none | FALSE | 0 | 71.9956 | FALSE | FALSE | 0.1311 |  | 72.7574 | 0 | 0.2826 | 0.07056 | 0.25722 | 0.82435 | 0.38092 | Normal | 73.5192 | 1.9658 | Night | 202601 | 2026-01-21 | 1.9658
2026-01-21 20:00 | 73.2236 | FALSE | FALSE | -1.1311 | -1.569 | -0.3116 | -0.42374 | -0.2826 |  |  | none | FALSE | 0 | 72.0925 | FALSE | FALSE | 0.0757 |  | 72.8138 | 0 | -0.2826 | 0.05643 | 0.2688 | -1.2613 | 0.36068 | Normal | 73.5352 | 1.1361 | Night | 202601 | 2026-01-21 | 1.1361
2026-01-21 20:15 | 73.5062 | FALSE | FALSE | -1.3891 | -1.9262 | -0.11744 | -0.15951 | 0.2826 |  |  | none | FALSE | 0 | 72.1171 | FALSE | FALSE | 0.1125 |  | 72.8704 | 0 | 0.2826 | 0.05652 | 0.26888 | 0.84082 | 0.37665 | Normal | 73.6236 | 1.6882 | Night | 202601 | 2026-01-21 | 1.6882
2026-01-21 20:29 | 73.5062 | FALSE | FALSE | -1.4127 | -1.9595 | -0.19749 | -0.26795 | 0 |  |  | none | FALSE | 0 | 72.0935 | FALSE | FALSE | 0.1006 |  | 72.8986 | 0 | 0 | 0.02826 | 0.24084 | -0.11734 | 0.40254 | Normal | 73.7037 | 1.5094 | Night | 202601 | 2026-01-21 | 1.5094
2026-01-21 20:44 | 73.5062 | FALSE | FALSE | -1.4291 | -1.9828 | -0.27045 | -0.36658 | 0 |  |  | none | FALSE | 0 | 72.0771 | FALSE | FALSE | 0.0909 |  | 72.9269 | 0 | 0 | 0.02826 | 0.24084 | -0.11734 | 0.42489 | Normal | 73.7767 | 1.3635 | Night | 202601 | 2026-01-21 | 1.3635
2026-01-21 20:59 | 73.5062 | FALSE | FALSE | -1.4446 | -2.0047 | -0.31424 | -0.42568 | 0 |  |  | none | FALSE | 0 | 72.0616 | FALSE | FALSE | 0.0857 |  | 72.941 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.43972 | Normal | 73.8204 | 1.2854 | Night | 202601 | 2026-01-21 | 1.2854
2026-01-21 21:14 | 73.5062 | FALSE | FALSE | -1.452 | -2.0151 | -0.3781 | -0.51175 | 0 |  |  | none | FALSE | 0 | 72.0542 | FALSE | FALSE | 0.0782 |  | 72.9693 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.45752 | Normal | 73.8843 | 1.1736 | Night | 202601 | 2026-01-21 | 1.1736
2026-01-21 21:29 | 73.5062 | FALSE | FALSE | -1.4273 | -1.9802 | -0.43823 | -0.59265 | 0 |  |  | none | FALSE | 0 | 72.0789 | FALSE | FALSE | 0.0707 |  | 73.0117 | 0 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.46639 | Normal | 73.9444 | 1.0604 | Night | 202601 | 2026-01-21 | 1.0604
2026-01-21 21:44 | 73.5062 | FALSE | FALSE | -1.424 | -1.9755 | -0.4914 | -0.66407 | 0 |  |  | none | FALSE | 0 | 72.0822 | FALSE | FALSE | 0.0649 |  | 73.0399 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.47884 | Normal | 73.9976 | 0.97379 | Night | 202601 | 2026-01-21 | 0.97379
2026-01-21 21:59 | 73.5062 | FALSE | FALSE | -1.3855 | -1.9211 | -0.53773 | -0.72623 | 0 |  |  | none | FALSE | 0 | 72.1207 | FALSE | FALSE | 0.0588 |  | 73.0823 | 0 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.48081 | Normal | 74.0439 | 0.88163 | Night | 202601 | 2026-01-21 | 0.88163
2026-01-21 22:14 | 73.5062 | FALSE | FALSE | -1.3392 | -1.8557 | -0.57618 | -0.77775 | 0 |  |  | none | FALSE | 0 | 72.167 | FALSE | FALSE | 0.0531 |  | 73.1247 | 0 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.47884 | Normal | 74.0824 | 0.79673 | Night | 202601 | 2026-01-21 | 0.79673
2026-01-21 22:29 | 73.5062 | FALSE | FALSE | -1.2285 | -1.6997 | -0.57849 | -0.78085 | 0 |  |  | none | FALSE | 0 | 72.2777 | FALSE | FALSE | 0.048 |  | 73.1812 | 0 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.45174 | Normal | 74.0847 | 0.71942 | Night | 202601 | 2026-01-21 | 0.71942
2026-01-21 22:44 | 73.5062 | FALSE | FALSE | -1.0982 | -1.5167 | -0.56129 | -0.75781 | 0 |  |  | none | FALSE | 0 | 72.408 | FALSE | FALSE | 0.0431 |  | 73.2377 | 0 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.41488 | Normal | 74.0675 | 0.6471 | Night | 202601 | 2026-01-21 | 0.6471
2026-01-21 22:59 | 73.5062 | FALSE | FALSE | -0.94258 | -1.299 | -0.51868 | -0.70068 | 0 |  |  | none | FALSE | 0 | 72.5636 | FALSE | FALSE | 0.0387 |  | 73.2943 | 0 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.36531 | Normal | 74.0249 | 0.58018 | Night | 202601 | 2026-01-21 | 0.58018
2026-01-21 23:14 | 73.5062 | FALSE | FALSE | -0.74893 | -1.0293 | -0.43807 | -0.59243 | 0 |  |  | none | FALSE | 0 | 72.7573 | FALSE | FALSE | 0.0349 |  | 73.3508 | 0 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.29675 | Normal | 73.9443 | 0.52378 | Night | 202601 | 2026-01-21 | 0.52378
2026-01-21 23:28 | 73.5062 | FALSE | FALSE | -0.47806 | -0.65462 | -0.28024 | -0.3798 | 0 |  |  | none | FALSE | 0 | 73.0281 | FALSE | FALSE | 0.0348 |  | 73.4073 | 0 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.18957 | Normal | 73.7864 | 0.52175 | Night | 202601 | 2026-01-21 | 0.52175
2026-01-21 23:43 | 73.5062 | FALSE | FALSE | -0.38158 | -0.52182 | -0.24028 | -0.32582 | 0 |  |  | none | FALSE | 0 | 73.1246 | FALSE | FALSE | 0.0303 |  | 73.4356 | 0 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.15546 | Normal | 73.7465 | 0.45445 | Night | 202601 | 2026-01-21 | 0.45445
2026-01-21 23:59 | 73.5062 | FALSE | FALSE | -0.24945 | -0.34051 | -0.16467 | -0.22352 | 0 |  |  | none | FALSE | 0 | 73.2568 | FALSE | FALSE | 0.0273 |  | 73.4638 | 0 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.10353 | Normal | 73.6709 | 0.40945 | Night | 202601 | 2026-01-21 | 0.40945
2026-01-22 00:14 | 73.5062 | FALSE | FALSE | -0.20222 | -0.27587 | -0.1457 | -0.19783 | 0 |  |  | none | FALSE | 0 | 73.304 | FALSE | FALSE | 0.0217 |  | 73.4779 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.086982 | Normal | 73.6519 | 0.32489 | Night | 202601 | 2026-01-22 | 0.32489
2026-01-22 00:28 | 73.5062 | FALSE | FALSE | -0.14051 | -0.19152 | -0.11225 | -0.15248 | 0 |  |  | none | FALSE | 0 | 73.3657 | FALSE | FALSE | 0.0149 |  | 73.4921 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.063191 | Normal | 73.6185 | 0.22361 | Night | 202601 | 2026-01-22 | 0.22361
2026-01-22 00:43 | 73.5062 | FALSE | FALSE | -0.14051 | -0.19152 | -0.11225 | -0.15248 | 0 |  |  | none | FALSE | 0 | 73.3657 | FALSE | FALSE | 0.0149 |  | 73.4921 | 0 | 0 | 0 | 0.091688 | 0 | 0.063191 | Normal | 73.6185 | 0.22361 | Night | 202601 | 2026-01-22 | 0.22361
2026-01-22 00:58 | 73.2236 | TRUE | FALSE | 0.14209 | 0.19367 | -0.39485 | -0.53635 | -0.2826 | 2026-01-22 05:27 | 2026-01-22 00:58 | lower | TRUE | 1 | 73.3657 | FALSE | FALSE | 0.3689 | 4.2485 | 73.4921 | 1 | -0.2826 | 0 | 0.091688 | -3.0822 | 0.063191 | Extreme triggered | 73.6185 | -4.2485 | Night | 202601 | 2026-01-22 | 4.2485
2026-01-22 01:13 | 73.2236 | FALSE | FALSE | 0.080375 | 0.10965 | -0.4283 | -0.58153 | 0 |  | 2026-01-22 00:58 | lower | TRUE | 1 | 73.304 | FALSE | FALSE | 0.3378 | 3.5863 | 73.4779 | 2 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.086982 | Extreme/elevated | 73.6519 | -2.924 | Night | 202601 | 2026-01-22 | 2.924
2026-01-22 01:28 | 73.2236 | FALSE | FALSE | 0.03315 | 0.045252 | -0.44727 | -0.60712 | 0 |  | 2026-01-22 00:58 | lower | TRUE | 1 | 73.2568 | FALSE | TRUE | 0.3547 | 3.1643 | 73.4638 | 3 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.10353 | Persistent | 73.6709 | -2.3202 | Night | 202601 | 2026-01-22 | 2.3202
2026-01-22 01:43 | 73.2236 | FALSE | FALSE | -0.0058732 | -0.0080215 | -0.45803 | -0.62164 | 0 |  | 2026-01-22 00:58 | none | FALSE | 1 | 73.2177 | FALSE | FALSE | 0.3871 | 2.8605 | 73.4497 | 4 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.11598 | Persistent | 73.6816 | -1.9494 | Night | 202601 | 2026-01-22 | 1.9494
2026-01-22 01:58 | 73.2236 | FALSE | FALSE | -0.039147 | -0.05349 | -0.46305 | -0.6284 | 0 |  | 2026-01-22 00:58 | none | FALSE | 1 | 73.1845 | FALSE | FALSE | 0.4268 | 2.6261 | 73.4356 | 5 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.12555 | Persistent | 73.6866 | -1.6882 | Night | 202601 | 2026-01-22 | 1.6882
2026-01-22 02:13 | 73.2236 | FALSE | FALSE | -0.067916 | -0.092837 | -0.46356 | -0.62909 | 0 |  | 2026-01-22 00:58 | none | FALSE | 1 | 73.1557 | FALSE | FALSE | 0.4707 | 2.4365 | 73.4214 | 6 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13287 | Persistent | 73.6872 | -1.4888 | Night | 202601 | 2026-01-22 | 1.4888
2026-01-22 02:28 | 73.2236 | FALSE | TRUE | -0.092897 | -0.12703 | -0.46028 | -0.62466 | 0 |  | 2026-01-22 00:58 | none | FALSE | 1 | 73.1307 | FALSE | FALSE | 0.5171 | 2.2782 | 73.4073 | 7 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13829 | Confirmed/Materialized Shift | 73.6839 | -1.3283 | Night | 202601 | 2026-01-22 | 1.3283
2026-01-22 02:43 | 73.2236 | FALSE | TRUE | -0.11452 | -0.15665 | -0.45364 | -0.61572 | 0 |  | 2026-01-22 00:58 | none | FALSE | 1 | 73.1091 | FALSE | FALSE | 0.5082 | 2.1426 | 73.3932 | 8 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14204 | Confirmed/Materialized Shift | 73.6772 | -1.1937 | Night | 202601 | 2026-01-22 | 1.1937
2026-01-22 02:58 | 72.941 | TRUE | TRUE | 0.080837 | 0.1107 | -0.76696 | -1.0405 | -0.2826 |  | 2026-01-22 00:58 | lower | TRUE | 2 | 73.0218 | TRUE | TRUE | 0.6219 | 2.1792 | 73.3649 | 9 | -0.2826 | -0.02826 | 0.086982 | -2.924 | 0.17153 | Confirmed/Materialized Shift | 73.708 | -2.4713 | Night | 202601 | 2026-01-22 | 2.4713
2026-01-22 03:13 | 72.941 | FALSE | TRUE | 0.010989 | 0.015064 | -0.78029 | -1.0584 | 0 |  | 2026-01-22 00:58 | lower | TRUE | 2 | 72.952 | FALSE | TRUE | 0.5943 | 2.167 | 73.3366 | 10 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.19233 | Confirmed/Materialized Shift | 73.7213 | -2.0571 | Night | 202601 | 2026-01-22 | 2.0571
2026-01-22 03:27 | 72.941 | FALSE | TRUE | -0.046739 | -0.064119 | -0.7815 | -1.0601 | 0 |  | 2026-01-22 00:58 | none | FALSE | 1 | 72.8943 | FALSE | FALSE | 0.5469 | 2.1313 | 73.3084 | 11 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.20706 | Confirmed/Materialized Shift | 73.7225 | -1.7743 | Night | 202601 | 2026-01-22 | 1.7743
2026-01-22 03:42 | 72.941 | FALSE | TRUE | -0.094825 | -0.13017 | -0.77306 | -1.0487 | 0 |  | 2026-01-22 00:58 | none | FALSE | 1 | 72.8462 | FALSE | FALSE | 0.5328 | 2.0839 | 73.2801 | 12 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21697 | Confirmed/Materialized Shift | 73.7141 | -1.563 | Night | 202601 | 2026-01-22 | 1.563
2026-01-22 03:57 | 72.941 | FALSE | TRUE | -0.13456 | -0.18481 | -0.75628 | -1.0262 | 0 |  | 2026-01-22 00:58 | none | FALSE | 1 | 72.8064 | FALSE | FALSE | 0.5216 | 2.031 | 73.2519 | 13 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22271 | Confirmed/Materialized Shift | 73.6973 | -1.3958 | Night | 202601 | 2026-01-22 | 1.3958
2026-01-22 04:12 | 72.941 | FALSE | TRUE | -0.16658 | -0.22889 | -0.73178 | -0.99328 | 0 |  | 2026-01-22 00:58 | none | FALSE | 1 | 72.7744 | FALSE | FALSE | 0.5125 | 1.9758 | 73.2236 | 14 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22459 | Confirmed/Materialized Shift | 73.6728 | -1.2583 | Night | 202601 | 2026-01-22 | 1.2583
2026-01-22 04:27 | 72.941 | FALSE | TRUE | -0.19108 | -0.26265 | -0.69976 | -0.95023 | 0 |  | 2026-01-22 00:58 | none | FALSE | 1 | 72.7499 | FALSE | FALSE | 0.5047 | 1.9202 | 73.1953 | 15 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22271 | Confirmed/Materialized Shift | 73.6408 | -1.142 | Night | 202601 | 2026-01-22 | 1.142
2026-01-22 04:42 | 72.941 | FALSE | TRUE | -0.20786 | -0.28579 | -0.66002 | -0.89676 | 0 |  | 2026-01-22 00:58 | none | FALSE | 1 | 72.7331 | FALSE | FALSE | 0.498 | 1.8653 | 73.1671 | 16 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21697 | Confirmed/Materialized Shift | 73.601 | -1.042 | Night | 202601 | 2026-01-22 | 1.042
2026-01-22 04:57 | 72.6584 | TRUE | TRUE | 0.0069363 | 0.0095455 | -0.92564 | -1.2579 | -0.2826 |  | 2026-01-22 00:58 | lower | TRUE | 2 | 72.6653 | TRUE | TRUE | 0.5925 | 1.875 | 73.1247 | 17 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.22968 | Confirmed/Materialized Shift | 73.584 | -2.0302 | Night | 202601 | 2026-01-22 | 2.0302
2026-01-22 05:12 | 72.6584 | FALSE | TRUE | -0.043617 | -0.060066 | -0.89142 | -1.212 | 0 |  | 2026-01-22 00:58 | none | FALSE | 2 | 72.6148 | FALSE | FALSE | 0.578 | 1.8716 | 73.0823 | 18 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.23376 | Confirmed/Materialized Shift | 73.5498 | -1.8134 | Night | 202601 | 2026-01-22 | 1.8134
2026-01-22 05:27 | 72.941 | TRUE | FALSE | -0.31309 | -0.43108 | -0.53917 | -0.73376 | 0.2826 |  |  | none | FALSE | 2 | 72.6279 | TRUE | FALSE | 0.0925 |  | 73.054 | 0 | 0.2826 | -0.02826 | 0.12638 | 2.4597 | 0.21306 | Persistence ends | 73.4802 | -0.53055 | Night | 202601 | 2026-01-22 | 0.53055
2026-01-22 05:42 | 72.6584 | FALSE | FALSE | -0.051631 | -0.071111 | -0.75813 | -1.0326 | -0.2826 |  |  | none | FALSE | 2 | 72.6068 | FALSE | FALSE | 0.1735 |  | 73.0117 | 0 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.20244 | Normal | 73.4165 | -1.745 | Night | 202601 | 2026-01-22 | 1.745
2026-01-22 05:57 | 72.6584 | FALSE | FALSE | -0.096174 | -0.13254 | -0.74615 | -1.0165 | 0 |  |  | none | FALSE | 2 | 72.5622 | FALSE | FALSE | 0.16 |  | 72.9834 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21058 | Normal | 73.4046 | -1.5433 | Night | 202601 | 2026-01-22 | 1.5433
2026-01-22 06:12 | 72.6584 | FALSE | FALSE | -0.13234 | -0.18248 | -0.7258 | -0.98905 | 0 |  |  | none | FALSE | 2 | 72.5261 | FALSE | FALSE | 0.1494 |  | 72.9551 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21454 | Normal | 73.3842 | -1.3831 | Night | 202601 | 2026-01-22 | 1.3831
2026-01-22 06:26 | 72.6584 | FALSE | FALSE | -0.1606 | -0.22153 | -0.69754 | -0.9509 | 0 |  |  | none | FALSE | 2 | 72.4978 | FALSE | FALSE | 0.1406 |  | 72.9269 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21454 | Normal | 73.3559 | -1.2514 | Night | 202601 | 2026-01-22 | 1.2514
2026-01-22 06:41 | 72.6584 | FALSE | FALSE | -0.18095 | -0.24967 | -0.66137 | -0.90204 | 0 |  |  | none | FALSE | 2 | 72.4774 | FALSE | FALSE | 0.1332 |  | 72.8986 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21058 | Normal | 73.3198 | -1.1407 | Night | 202601 | 2026-01-22 | 1.1407
2026-01-22 06:56 | 72.6584 | FALSE | FALSE | -0.19293 | -0.26624 | -0.61683 | -0.8418 | 0 |  |  | none | FALSE | 2 | 72.4655 | FALSE | FALSE | 0.1269 |  | 72.8704 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.20244 | Normal | 73.2752 | -1.047 | Night | 202601 | 2026-01-22 | 1.047
2026-01-22 07:11 | 72.6584 | FALSE | FALSE | -0.19546 | -0.26973 | -0.56284 | -0.76868 | 0 |  |  | none | FALSE | 2 | 72.4629 | FALSE | FALSE | 0.1217 |  | 72.8421 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.18957 | Normal | 73.2212 | -0.96896 | Night | 202601 | 2026-01-22 | 0.96896
2026-01-22 07:26 | 72.3758 | FALSE | FALSE | 0.034903 | 0.048201 | -0.8129 | -1.1107 | -0.2826 | 2026-01-22 07:45 | 2026-01-22 07:26 | lower | TRUE | 1 | 72.4107 | FALSE | FALSE | 0.231 | 2.1794 | 72.7997 | 1 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.1945 | Extreme triggered | 73.1887 | -2.1794 | Day | 202601 | 2026-01-22 | 2.1794
2026-01-22 07:30 | 72.3758 | FALSE | FALSE | 0.0023623 | 0.0032638 | -0.76066 | -1.0401 | 0 |  | 2026-01-22 07:26 | lower | TRUE | 1 | 72.3782 | FALSE | FALSE | 0.277 | 2.096 | 72.7573 | 2 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.18957 | Extreme/elevated | 73.1365 | -2.0125 | Day | 202601 | 2026-01-22 | 2.0125
2026-01-22 07:45 | 72.6584 | TRUE | FALSE | -0.28653 | -0.39591 | -0.45609 | -0.6238 | 0.2826 |  |  | none | FALSE | 1 | 72.3719 | FALSE | FALSE | 0.059 |  | 72.7432 | 0 | 0.2826 | -0.01413 | 0.14424 | 2.0571 | 0.18565 | Persistence ends | 73.1145 | -0.45666 | Day | 202601 | 2026-01-22 | 0.45666
2026-01-22 08:00 | 72.3758 | FALSE | FALSE | -0.054176 | -0.074909 | -0.73242 | -1.0018 | -0.2826 |  |  | none | FALSE | 1 | 72.3216 | FALSE | FALSE | 0.1435 |  | 72.7149 | 0 | -0.2826 | -0.02826 | 0.15614 | -1.6289 | 0.19665 | Normal | 73.1082 | -1.7245 | Day | 202601 | 2026-01-22 | 1.7245
2026-01-22 08:15 | 72.3758 | FALSE | FALSE | -0.095058 | -0.13151 | -0.71678 | -0.98064 | 0 |  |  | none | FALSE | 1 | 72.2807 | FALSE | FALSE | 0.1307 |  | 72.6867 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.20296 | Normal | 73.0926 | -1.5316 | Day | 202601 | 2026-01-22 | 1.5316
2026-01-22 08:30 | 72.6584 | FALSE | FALSE | -0.37379 | -0.5171 | -0.40205 | -0.55029 | 0.2826 |  |  | none | FALSE | 1 | 72.2846 | FALSE | FALSE | 0.0334 |  | 72.6725 | 0 | 0.2826 | -0.01413 | 0.17092 | 1.7361 | 0.19396 | Normal | 73.0604 | -0.072851 | Day | 202601 | 2026-01-22 | 0.072851
2026-01-22 08:30 | 72.6584 | FALSE | FALSE | -0.36675 | -0.50732 | -0.36675 | -0.50222 | 0 |  |  | none | FALSE | 1 | 72.2916 | FALSE | FALSE | 0.0286 |  | 72.6584 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.18338 | Normal | 73.0252 | 0 | Day | 202601 | 2026-01-22 | 0
2026-01-22 08:45 | 72.3758 | FALSE | FALSE | -0.1078 | -0.14916 | -0.61648 | -0.84458 | -0.2826 |  |  | none | FALSE | 1 | 72.268 | FALSE | FALSE | 0.1222 |  | 72.6301 | 0 | -0.2826 | -0.02826 | 0.18107 | -1.4047 | 0.18107 | Normal | 72.9923 | -1.4047 | Day | 202601 | 2026-01-22 | 1.4047
2026-01-22 09:00 | 72.6584 | FALSE | FALSE | -0.37424 | -0.51774 | -0.28946 | -0.39681 | 0.2826 |  |  | none | FALSE | 1 | 72.2842 | FALSE | FALSE | 0.0456 |  | 72.616 | 0 | 0.2826 | -0.01413 | 0.19396 | 1.5299 | 0.16593 | Normal | 72.9479 | 0.25547 | Day | 202601 | 2026-01-22 | 0.25547
2026-01-22 09:15 | 72.3758 | FALSE | FALSE | -0.098978 | -0.13694 | -0.52288 | -0.71727 | -0.2826 |  |  | none | FALSE | 1 | 72.2768 | FALSE | FALSE | 0.1195 |  | 72.5877 | 0 | -0.2826 | -0.02826 | 0.20296 | -1.2532 | 0.15546 | Normal | 72.8987 | -1.3633 | Day | 202601 | 2026-01-22 | 1.3633
2026-01-22 09:30 | 72.3758 | FALSE | FALSE | -0.12505 | -0.17307 | -0.52069 | -0.71428 | 0 |  |  | none | FALSE | 1 | 72.2508 | FALSE | FALSE | 0.1103 |  | 72.5736 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.16143 | Normal | 72.8965 | -1.2254 | Day | 202601 | 2026-01-22 | 1.2254
2026-01-22 09:45 | 72.6584 | FALSE | FALSE | -0.40765 | -0.56421 | -0.23809 | -0.32661 | 0.2826 |  |  | none | FALSE | 1 | 72.2508 | FALSE | FALSE | 0.0636 |  | 72.5736 | 0 | 0.2826 | 0 | 0.20502 | 1.3784 | 0.16143 | Normal | 72.8965 | 0.52517 | Day | 202601 | 2026-01-22 | 0.52517
2026-01-22 10:00 | 72.941 | FALSE | FALSE | -0.69025 | -0.95535 | 0.044515 | 0.061066 | 0.2826 | 2026-01-22 11:55 | 2026-01-22 10:00 | upper | TRUE | 0 | 72.2508 | FALSE | FALSE | 0.2089 | 2.2757 | 72.5736 | 1 | 0.2826 | 0 | 0.20502 | 1.3784 | 0.16143 | Extreme triggered | 72.8965 | 2.2757 | Day | 202601 | 2026-01-22 | 2.2757
2026-01-22 10:15 | 73.5062 | TRUE | FALSE | -1.4177 | -1.9666 | 0.36269 | 0.49586 | 0.5652 |  | 2026-01-22 10:00 | upper | TRUE | 1 | 72.0885 | FALSE | FALSE | 0.3679 | 2.8254 | 72.616 | 2 | 0.5652 | 0.04239 | 0.22968 | 2.2763 | 0.26375 | Extreme/elevated | 73.1435 | 3.3751 | Day | 202601 | 2026-01-22 | 3.3751
2026-01-22 10:29 | 73.5062 | FALSE | FALSE | -1.509 | -2.0959 | 0.18663 | 0.25455 | 0 |  | 2026-01-22 10:00 | upper | TRUE | 1 | 71.9972 | FALSE | TRUE | 0.371 | 2.7385 | 72.6584 | 3 | 0 | 0.04239 | 0.22968 | -0.18456 | 0.33058 | Persistent | 73.3196 | 2.5646 | Day | 202601 | 2026-01-22 | 2.5646
2026-01-22 10:44 | 73.5062 | FALSE | FALSE | -1.5676 | -2.179 | 0.043244 | 0.058866 | 0 |  | 2026-01-22 10:00 | upper | TRUE | 1 | 71.9386 | FALSE | TRUE | 0.398 | 2.5822 | 72.7008 | 4 | 0 | 0.04239 | 0.22968 | -0.18456 | 0.38108 | Persistent | 73.463 | 2.1135 | Day | 202601 | 2026-01-22 | 2.1135
2026-01-22 10:59 | 73.5062 | FALSE | FALSE | -1.6053 | -2.2327 | -0.079309 | -0.10778 | 0 |  | 2026-01-22 10:00 | none | FALSE | 1 | 71.9009 | FALSE | FALSE | 0.4351 | 2.4281 | 72.7432 | 5 | 0 | 0.04239 | 0.22968 | -0.18456 | 0.42116 | Persistent | 73.5855 | 1.8117 | Day | 202601 | 2026-01-22 | 1.8117
2026-01-22 11:15 | 73.5062 | FALSE | FALSE | -1.6278 | -2.2647 | -0.18657 | -0.25317 | 0 |  | 2026-01-22 10:00 | none | FALSE | 1 | 71.8784 | FALSE | FALSE | 0.4773 | 2.2882 | 72.7856 | 6 | 0 | 0.04239 | 0.22968 | -0.18456 | 0.4536 | Persistent | 73.6928 | 1.5887 | Day | 202601 | 2026-01-22 | 1.5887
2026-01-22 11:29 | 73.7888 | FALSE | TRUE | -1.9557 | -2.7225 | -0.06227 | -0.084318 | 0.2826 |  | 2026-01-22 10:00 | none | FALSE | 1 | 71.8331 | FALSE | FALSE | 0.5537 | 2.2294 | 72.8421 | 7 | 0.2826 | 0.05652 | 0.23555 | 0.9598 | 0.50449 | Confirmed/Materialized Shift | 73.8511 | 1.8766 | Day | 202601 | 2026-01-22 | 1.8766
2026-01-22 11:37 | 74.0714 | FALSE | TRUE | -2.3024 | -3.208 | 0.014952 | 0.02019 | 0.2826 |  | 2026-01-22 10:00 | upper | TRUE | 1 | 71.769 | FALSE | TRUE | 0.5636 | 2.204 | 72.9127 | 8 | 0.2826 | 0.07065 | 0.24041 | 0.88163 | 0.57185 | Confirmed/Materialized Shift | 74.0564 | 2.0261 | Day | 202601 | 2026-01-22 | 2.0261
2026-01-22 11:40 | 74.0714 | FALSE | TRUE | -2.2985 | -3.2025 | -0.15076 | -0.20312 | 0 |  | 2026-01-22 10:00 | none | FALSE | 1 | 71.7729 | FALSE | FALSE | 0.5455 | 2.154 | 72.9975 | 9 | 0 | 0.08478 | 0.22645 | -0.37438 | 0.61232 | Confirmed/Materialized Shift | 74.2222 | 1.7538 | Day | 202601 | 2026-01-22 | 1.7538
2026-01-22 11:55 | 72.941 | TRUE | FALSE | -1.105 | -1.5383 | -1.2746 | -1.7174 | -1.1304 |  |  | none | FALSE | 2 | 71.836 | TRUE | FALSE | 0.0666 |  | 73.0258 | 0 | -1.1304 | 0.02826 | 0.35392 | -3.2738 | 0.59491 | Persistence ends | 74.2156 | -0.14251 | Day | 202601 | 2026-01-22 | 0.14251
2026-01-22 12:10 | 72.941 | FALSE | FALSE | -1.0792 | -1.5018 | -1.277 | -1.7206 | 0 |  |  | none | FALSE | 2 | 71.8618 | FALSE | FALSE | 0.0683 |  | 73.0399 | 0 | 0 | 0.01413 | 0.34883 | -0.040506 | 0.58905 | Normal | 74.218 | -0.16791 | Day | 202601 | 2026-01-22 | 0.16791
2026-01-22 12:25 | 72.941 | FALSE | FALSE | -1.0103 | -1.4045 | -1.2646 | -1.7042 | 0 |  |  | none | FALSE | 1 | 71.9307 | FALSE | FALSE | 0.0435 |  | 73.0682 | 0 | 0 | 0.02826 | 0.34184 | -0.082671 | 0.56872 | Normal | 74.2056 | -0.22361 | Day | 202601 | 2026-01-22 | 0.22361
2026-01-22 12:29 | 72.941 | FALSE | FALSE | -0.93677 | -1.301 | -1.2476 | -1.6817 | 0 |  |  | none | FALSE | 1 | 72.0042 | FALSE | FALSE | 0.0475 |  | 73.0964 | 0 | 0 | 0.02826 | 0.34184 | -0.082671 | 0.5461 | Normal | 74.1886 | -0.28462 | Day | 202601 | 2026-01-22 | 0.28462
2026-01-22 12:44 | 73.2236 | FALSE | FALSE | -1.1725 | -1.6273 | -0.97466 | -1.3136 | 0.2826 |  |  | none | FALSE | 1 | 72.0511 | FALSE | FALSE | 0.0409 |  | 73.1247 | 0 | 0.2826 | 0.02826 | 0.34184 | 0.74404 | 0.53678 | Normal | 74.1983 | 0.18426 | Day | 202601 | 2026-01-22 | 0.18426
2026-01-22 12:59 | 72.941 | FALSE | FALSE | -0.85718 | -1.1891 | -1.2528 | -1.6886 | -0.2826 |  |  | none | FALSE | 1 | 72.0838 | FALSE | FALSE | 0.0536 |  | 73.1388 | 0 | -0.2826 | 0.01413 | 0.34883 | -0.85063 | 0.5275 | Normal | 74.1938 | -0.37501 | Day | 202601 | 2026-01-22 | 0.37501
2026-01-22 13:14 | 72.6584 | FALSE | FALSE | -0.52438 | -0.72695 | -1.5135 | -2.0405 | -0.2826 |  |  | none | FALSE | 1 | 72.134 | FALSE | FALSE | 0.0933 |  | 73.153 | 0 | -0.2826 | 0.01413 | 0.34883 | -0.85063 | 0.50946 | Normal | 74.1719 | -0.97073 | Day | 202601 | 2026-01-22 | 0.97073
2026-01-22 13:28 | 72.941 | FALSE | FALSE | -0.77159 | -1.0691 | -1.2237 | -1.65 | 0.2826 |  |  | none | FALSE | 1 | 72.1694 | FALSE | FALSE | 0.0588 |  | 73.1671 | 0 | 0.2826 | 0.01413 | 0.34883 | 0.76962 | 0.49883 | Normal | 74.1647 | -0.45322 | Day | 202601 | 2026-01-22 | 0.45322
2026-01-22 13:43 | 73.2236 | FALSE | FALSE | -0.93967 | -1.3 | -0.91141 | -1.2294 | 0.2826 |  |  | none | FALSE | 1 | 72.2839 | FALSE | FALSE | 0.0306 |  | 73.2095 | 0 | 0.2826 | 0.04239 | 0.34642 | 0.69341 | 0.46277 | Normal | 74.135 | 0.030533 | Day | 202601 | 2026-01-22 | 0.030533
2026-01-22 13:59 | 72.941 | FALSE | FALSE | -0.55305 | -0.76401 | -1.1465 | -1.5475 | -0.2826 |  |  | none | FALSE | 1 | 72.3879 | FALSE | FALSE | 0.0751 |  | 73.2377 | 0 | -0.2826 | 0.02826 | 0.35392 | -0.87834 | 0.42489 | Normal | 74.0875 | -0.69837 | Day | 202601 | 2026-01-22 | 0.69837
2026-01-22 14:14 | 72.941 | FALSE | FALSE | -0.50717 | -0.70018 | -1.1289 | -1.5241 | 0 |  |  | none | FALSE | 0 | 72.4338 | FALSE | FALSE | 0.0507 |  | 73.2519 | 0 | 0 | 0.01413 | 0.34883 | -0.040506 | 0.40901 | Normal | 74.0699 | -0.76003 | Day | 202601 | 2026-01-22 | 0.76003
2026-01-22 14:28 | 72.941 | FALSE | FALSE | -0.50717 | -0.70018 | -1.1289 | -1.5241 | 0 |  |  | none | FALSE | 0 | 72.4338 | FALSE | FALSE | 0.0507 |  | 73.2519 | 0 | 0 | 0 | 0.34306 | 0 | 0.40901 | Normal | 74.0699 | -0.76003 | Day | 202601 | 2026-01-22 | 0.76003
2026-01-22 14:43 | 72.941 | FALSE | FALSE | -0.53748 | -0.74234 | -1.1027 | -1.4892 | 0 |  |  | none | FALSE | 0 | 72.4035 | FALSE | FALSE | 0.0459 |  | 73.2236 | 0 | 0 | -0.02826 | 0.31629 | 0.089349 | 0.41004 | Normal | 74.0437 | -0.6892 | Day | 202601 | 2026-01-22 | 0.6892
2026-01-22 14:58 | 72.941 | FALSE | FALSE | -0.56369 | -0.77882 | -1.0724 | -1.4489 | 0 |  |  | none | FALSE | 0 | 72.3773 | FALSE | FALSE | 0.0415 |  | 73.1953 | 0 | 0 | -0.02826 | 0.31629 | 0.089349 | 0.40901 | Normal | 74.0134 | -0.62184 | Day | 202601 | 2026-01-22 | 0.62184
2026-01-22 15:13 | 72.941 | FALSE | FALSE | -0.58576 | -0.80956 | -1.0379 | -1.403 | 0 |  |  | none | FALSE | 0 | 72.3552 | FALSE | FALSE | 0.0371 |  | 73.1671 | 0 | 0 | -0.02826 | 0.31629 | 0.089349 | 0.40592 | Normal | 73.9789 | -0.55696 | Day | 202601 | 2026-01-22 | 0.55696
2026-01-22 15:28 | 72.941 | FALSE | FALSE | -0.60359 | -0.83442 | -0.99923 | -1.3514 | 0 |  |  | none | FALSE | 0 | 72.3374 | FALSE | FALSE | 0.0329 |  | 73.1388 | 0 | 0 | -0.02826 | 0.31629 | 0.089349 | 0.40071 | Normal | 73.9402 | -0.49368 | Day | 202601 | 2026-01-22 | 0.49368
2026-01-22 15:43 | 72.941 | FALSE | FALSE | -0.61703 | -0.85315 | -0.95615 | -1.2939 | 0 |  |  | none | FALSE | 0 | 72.324 | FALSE | FALSE | 0.0287 |  | 73.1106 | 0 | 0 | -0.02826 | 0.31629 | 0.089349 | 0.3933 | Normal | 73.8972 | -0.43113 | Day | 202601 | 2026-01-22 | 0.43113
2026-01-22 15:58 | 72.941 | FALSE | FALSE | -0.5942 | -0.82132 | -0.84854 | -1.1499 | 0 |  |  | none | FALSE | 0 | 72.3468 | FALSE | FALSE | 0.0235 |  | 73.0682 | 0 | 0 | -0.04239 | 0.30787 | 0.13769 | 0.36068 | Normal | 73.7895 | -0.35258 | Day | 202601 | 2026-01-22 | 0.35258
2026-01-22 16:13 | 72.941 | FALSE | FALSE | -0.47564 | -0.65637 | -0.61694 | -0.83872 | 0 |  |  | none | FALSE | 0 | 72.4654 | FALSE | FALSE | 0.0172 |  | 73.0117 | 0 | 0 | -0.05652 | 0.29851 | 0.18934 | 0.27315 | Normal | 73.5579 | -0.25865 | Day | 202601 | 2026-01-22 | 0.25865
2026-01-22 16:27 | 72.6584 | FALSE | FALSE | 0.023268 | 0.032014 | -0.54193 | -0.74034 | -0.2826 | 2026-01-22 17:57 | 2026-01-22 16:27 | lower | TRUE | 0 | 72.6817 | FALSE | FALSE | 0.2024 | 2.1794 | 72.941 | 1 | -0.2826 | -0.07065 | 0.30236 | -0.70098 | 0.12967 | Extreme triggered | 73.2003 | -2.1794 | Day | 202601 | 2026-01-22 | 2.1794
2026-01-22 16:43 | 72.3758 | FALSE | FALSE | 0.1748 | 0.24094 | -0.89908 | -1.227 | -0.2826 |  | 2026-01-22 16:27 | lower | TRUE | 0 | 72.5506 | FALSE | FALSE | 0.312 | 2.5724 | 72.9127 | 2 | -0.2826 | -0.02826 | 0.18107 | -1.4047 | 0.18107 | Extreme/elevated | 73.2749 | -2.9654 | Day | 202601 | 2026-01-22 | 2.9654
2026-01-22 16:58 | 72.3758 | FALSE | FALSE | 0.074735 | 0.10315 | -0.94262 | -1.2857 | 0 |  | 2026-01-22 16:27 | lower | TRUE | 0 | 72.4505 | FALSE | TRUE | 0.3277 | 2.4964 | 72.8845 | 3 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.21697 | Persistent | 73.3184 | -2.3444 | Day | 202601 | 2026-01-22 | 2.3444
2026-01-22 17:13 | 72.095 | FALSE | FALSE | 0.18922 | 0.26177 | -1.3051 | -1.7781 | -0.2808 |  | 2026-01-22 16:27 | lower | TRUE | 0 | 72.2842 | FALSE | TRUE | 0.4071 | 2.5419 | 72.8422 | 4 | -0.2808 | -0.0423 | 0.18945 | -1.2589 | 0.27898 | Persistent | 73.4001 | -2.6783 | Day | 202601 | 2026-01-22 | 2.6783
2026-01-22 17:27 | 72.095 | FALSE | FALSE | 0.057377 | 0.079521 | -1.3524 | -1.8413 | 0 |  | 2026-01-22 16:27 | lower | TRUE | 0 | 72.1524 | FALSE | TRUE | 0.4309 | 2.469 | 72.7999 | 5 | 0 | -0.0423 | 0.18945 | 0.22327 | 0.32375 | Persistent | 73.4474 | -2.1772 | Day | 202601 | 2026-01-22 | 2.1772
2026-01-22 17:42 | 72.095 | FALSE | FALSE | -0.03905 | -0.054194 | -1.336 | -1.8193 | 0 |  | 2026-01-22 16:27 | none | FALSE | 0 | 72.0559 | FALSE | FALSE | 0.4686 | 2.3719 | 72.7434 | 6 | 0 | -0.05643 | 0.17384 | 0.3246 | 0.34375 | Persistent | 73.431 | -1.8864 | Day | 202601 | 2026-01-22 | 1.8864
2026-01-22 17:57 | 72.3758 | FALSE | FALSE | -0.36028 | -0.50028 | -1.0391 | -1.4153 | 0.2808 |  |  | none | FALSE | 0 | 72.0155 | FALSE | FALSE | 0.0647 |  | 72.7152 | 0 | 0.2808 | -0.02826 | 0.18077 | 1.7097 | 0.34983 | Persistence ends | 73.4149 | -0.97015 | Night | 202601 | 2026-01-22 | 0.97015
2026-01-22 18:12 | 72.6584 | FALSE | FALSE | -0.64288 | -0.89269 | -0.75646 | -1.0304 | 0.2826 |  |  | none | FALSE | 0 | 72.0155 | FALSE | FALSE | 0.0108 |  | 72.7152 | 0 | 0.2826 | 0 | 0.18308 | 1.5436 | 0.34983 | Normal | 73.4149 | -0.16233 | Night | 202601 | 2026-01-22 | 0.16233
2026-01-22 18:27 | 72.6584 | FALSE | FALSE | -0.64918 | -0.90152 | -0.7345 | -1.0008 | 0 |  |  | none | FALSE | 0 | 72.0092 | FALSE | FALSE | 0.0082 |  | 72.7011 | 0 | 0 | -0.01413 | 0.17061 | 0.082823 | 0.34592 | Normal | 73.3929 | -0.12332 | Night | 202601 | 2026-01-22 | 0.12332
2026-01-22 18:30 | 72.6584 | FALSE | FALSE | -0.63226 | -0.87783 | -0.66106 | -0.90162 | 0 |  |  | none | FALSE | 0 | 72.0261 | FALSE | FALSE | 0.003 |  | 72.6728 | 0 | 0 | -0.02826 | 0.1558 | 0.18139 | 0.32333 | Normal | 73.3195 | -0.044536 | Night | 202601 | 2026-01-22 | 0.044536
2026-01-22 18:31 | 72.6584 | FALSE | FALSE | -0.63395 | -0.88019 | -0.63449 | -0.86569 | 0 |  |  | none | FALSE | 0 | 72.0245 | FALSE | FALSE | 0.0001 |  | 72.6587 | 0 | 0 | -0.01413 | 0.14387 | 0.098211 | 0.31711 | Normal | 73.2929 | -0.00085144 | Night | 202601 | 2026-01-22 | 0.00085144
2026-01-22 18:46 | 73.2236 | TRUE | FALSE | -1.223 | -1.6985 | -0.12136 | -0.16547 | 0.5652 |  |  | none | FALSE | 1 | 72.0006 | FALSE | FALSE | 0.1378 |  | 72.6728 | 0 | 0.5652 | 0.01413 | 0.19368 | 2.8452 | 0.33608 | Normal | 73.345 | 1.6389 | Night | 202601 | 2026-01-22 | 1.6389
2026-01-22 19:01 | 73.2236 | FALSE | FALSE | -1.2436 | -1.7276 | -0.17021 | -0.23192 | 0 |  |  | none | FALSE | 1 | 71.98 | FALSE | FALSE | 0.1298 |  | 72.6869 | 0 | 0 | 0.01413 | 0.19368 | -0.072955 | 0.35344 | Normal | 73.3938 | 1.5184 | Night | 202601 | 2026-01-22 | 1.5184
2026-01-22 19:16 | 73.2236 | FALSE | FALSE | -1.2614 | -1.7528 | -0.2163 | -0.29453 | 0 |  |  | none | FALSE | 1 | 71.9622 | FALSE | FALSE | 0.1229 |  | 72.7011 | 0 | 0 | 0.01413 | 0.19368 | -0.072955 | 0.36942 | Normal | 73.4399 | 1.4145 | Night | 202601 | 2026-01-22 | 1.4145
2026-01-22 19:30 | 73.2236 | FALSE | FALSE | -1.2768 | -1.7746 | -0.25997 | -0.35378 | 0 |  |  | none | FALSE | 1 | 71.9468 | FALSE | FALSE | 0.1168 |  | 72.7152 | 0 | 0 | 0.01413 | 0.19368 | -0.072955 | 0.38419 | Normal | 73.4836 | 1.3233 | Night | 202601 | 2026-01-22 | 1.3233
2026-01-22 19:45 | 73.2236 | FALSE | FALSE | -1.2901 | -1.7934 | -0.30149 | -0.41005 | 0 |  |  | none | FALSE | 1 | 71.9335 | FALSE | FALSE | 0.1114 |  | 72.7293 | 0 | 0 | 0.01413 | 0.19368 | -0.072955 | 0.39789 | Normal | 73.5251 | 1.2423 | Night | 202601 | 2026-01-22 | 1.2423
2026-01-22 20:00 | 73.2236 | FALSE | FALSE | -1.3014 | -1.8094 | -0.34108 | -0.46364 | 0 |  |  | none | FALSE | 1 | 71.9222 | FALSE | FALSE | 0.1065 |  | 72.7434 | 0 | 0 | 0.01413 | 0.19368 | -0.072955 | 0.41061 | Normal | 73.5647 | 1.1693 | Night | 202601 | 2026-01-22 | 1.1693
2026-01-22 20:15 | 73.2236 | FALSE | FALSE | -1.3109 | -1.823 | -0.3789 | -0.5148 | 0 |  |  | none | FALSE | 1 | 71.9127 | FALSE | FALSE | 0.1021 |  | 72.7576 | 0 | 0 | 0.01413 | 0.19368 | -0.072955 | 0.42246 | Normal | 73.6025 | 1.1031 | Night | 202601 | 2026-01-22 | 1.1031
2026-01-22 20:29 | 73.2236 | FALSE | FALSE | -1.3189 | -1.8342 | -0.41511 | -0.56371 | 0 |  |  | none | FALSE | 1 | 71.9047 | FALSE | FALSE | 0.0981 |  | 72.7717 | 0 | 0 | 0.01413 | 0.19368 | -0.072955 | 0.4335 | Normal | 73.6387 | 1.0424 | Night | 202601 | 2026-01-22 | 1.0424
2026-01-22 20:44 | 73.2236 | FALSE | FALSE | -1.3253 | -1.8434 | -0.44983 | -0.61057 | 0 |  |  | none | FALSE | 1 | 71.8983 | FALSE | FALSE | 0.0943 |  | 72.7858 | 0 | 0 | 0.01413 | 0.19368 | -0.072955 | 0.44379 | Normal | 73.6734 | 0.98641 | Night | 202601 | 2026-01-22 | 0.98641
2026-01-22 20:59 | 73.5062 | FALSE | FALSE | -1.6193 | -2.2525 | -0.26334 | -0.35698 | 0.2826 |  |  | none | FALSE | 1 | 71.8869 | FALSE | FALSE | 0.1246 |  | 72.8282 | 0 | 0.2826 | 0.04239 | 0.18929 | 1.269 | 0.47066 | Normal | 73.7695 | 1.4405 | Night | 202601 | 2026-01-22 | 1.4405
2026-01-22 21:14 | 73.5062 | FALSE | FALSE | -1.5839 | -2.2022 | -0.34099 | -0.46175 | 0 |  |  | none | FALSE | 0 | 71.9223 | FALSE | FALSE | 0.0861 |  | 72.8847 | 0 | 0 | 0.05652 | 0.17366 | -0.32547 | 0.48122 | Normal | 73.8472 | 1.2914 | Night | 202601 | 2026-01-22 | 1.2914
2026-01-22 21:29 | 73.5062 | FALSE | FALSE | -1.5343 | -2.1318 | -0.40441 | -0.54716 | 0 |  |  | none | FALSE | 0 | 71.9719 | FALSE | FALSE | 0.0777 |  | 72.9413 | 0 | 0 | 0.05652 | 0.17366 | -0.32547 | 0.48467 | Normal | 73.9106 | 1.1656 | Night | 202601 | 2026-01-22 | 1.1656
2026-01-22 21:44 | 73.5062 | FALSE | FALSE | -1.4082 | -1.9532 | -0.41945 | -0.56739 | 0 |  |  | none | FALSE | 0 | 72.098 | FALSE | FALSE | 0.0721 |  | 73.0118 | 0 | 0 | 0.07056 | 0.15534 | -0.45424 | 0.45691 | Normal | 73.9256 | 1.082 | Night | 202601 | 2026-01-22 | 1.082
2026-01-22 21:59 | 73.5062 | FALSE | FALSE | -1.2536 | -1.7351 | -0.406 | -0.54931 | 0 |  |  | none | FALSE | 0 | 72.2526 | FALSE | FALSE | 0.0681 |  | 73.0824 | 0 | 0 | 0.07056 | 0.15534 | -0.45424 | 0.41491 | Normal | 73.9122 | 1.0215 | Night | 202601 | 2026-01-22 | 1.0215
2026-01-22 22:14 | 73.5062 | FALSE | FALSE | -1.0605 | -1.4638 | -0.35399 | -0.47927 | 0 |  |  | none | FALSE | 0 | 72.4457 | FALSE | FALSE | 0.0666 |  | 73.153 | 0 | 0 | 0.07056 | 0.15534 | -0.45424 | 0.35362 | Normal | 73.8602 | 0.99895 | Night | 202601 | 2026-01-22 | 0.99895
2026-01-22 22:29 | 73.5062 | FALSE | FALSE | -0.91791 | -1.2645 | -0.32445 | -0.43945 | 0 |  |  | none | FALSE | 0 | 72.5883 | FALSE | FALSE | 0.0637 |  | 73.2095 | 0 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.31059 | Normal | 73.8306 | 0.95538 | Night | 202601 | 2026-01-22 | 0.95538
2026-01-22 22:44 | 73.5062 | FALSE | FALSE | -0.83132 | -1.1439 | -0.32264 | -0.43701 | 0 |  |  | none | FALSE | 0 | 72.6749 | FALSE | FALSE | 0.0588 |  | 73.2519 | 0 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.28849 | Normal | 73.8288 | 0.88163 | Night | 202601 | 2026-01-22 | 0.88163
2026-01-22 22:59 | 73.5062 | FALSE | FALSE | -0.72655 | -0.99828 | -0.30265 | -0.41004 | 0 |  |  | none | FALSE | 0 | 72.7797 | FALSE | FALSE | 0.0549 |  | 73.2943 | 0 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.2573 | Normal | 73.8088 | 0.82375 | Night | 202601 | 2026-01-22 | 0.82375
2026-01-22 23:14 | 73.2236 | FALSE | FALSE | -0.32225 | -0.44204 | -0.52007 | -0.70525 | -0.2826 |  |  | none | FALSE | 0 | 72.9013 | FALSE | FALSE | 0.0313 |  | 73.3225 | 0 | -0.2826 | 0.02826 | 0.15614 | -1.9909 | 0.21058 | Normal | 73.7437 | -0.4697 | Night | 202601 | 2026-01-22 | 0.4697
2026-01-22 23:29 | 73.5062 | FALSE | FALSE | -0.43124 | -0.59014 | -0.14864 | -0.20181 | 0.2826 |  |  | none | FALSE | 0 | 73.075 | FALSE | FALSE | 0.065 |  | 73.3649 | 0 | 0.2826 | 0.04239 | 0.16593 | 1.4477 | 0.14497 | Normal | 73.6548 | 0.97468 | Night | 202601 | 2026-01-22 | 0.97468
2026-01-22 23:44 | 73.2236 | TRUE | FALSE | -0.14864 | -0.20341 | -0.43124 | -0.58549 | -0.2826 |  |  | none | FALSE | 1 | 73.075 | FALSE | FALSE | 0.0936 |  | 73.3649 | 0 | -0.2826 | 0 | 0.12967 | -2.1794 | 0.14497 | Normal | 73.6548 | -0.97468 | Night | 202601 | 2026-01-22 | 0.97468
2026-01-22 23:59 | 73.2236 | FALSE | FALSE | -0.14864 | -0.20341 | -0.43124 | -0.58549 | 0 |  |  | none | FALSE | 1 | 73.075 | FALSE | FALSE | 0.0936 |  | 73.3649 | 0 | 0 | 0 | 0.12967 | 0 | 0.14497 | Normal | 73.6548 | -0.97468 | Night | 202601 | 2026-01-22 | 0.97468
2026-01-23 00:14 | 73.2236 | FALSE | FALSE | -0.14864 | -0.20341 | -0.43124 | -0.58549 | 0 |  |  | none | FALSE | 1 | 73.075 | FALSE | FALSE | 0.0936 |  | 73.3649 | 0 | 0 | 0 | 0.12967 | 0 | 0.14497 | Normal | 73.6548 | -0.97468 | Night | 202601 | 2026-01-23 | 0.97468
2026-01-23 00:28 | 73.2236 | FALSE | FALSE | -0.14864 | -0.20341 | -0.43124 | -0.58549 | 0 |  |  | none | FALSE | 1 | 73.075 | FALSE | FALSE | 0.0936 |  | 73.3649 | 0 | 0 | 0 | 0.12967 | 0 | 0.14497 | Normal | 73.6548 | -0.97468 | Night | 202601 | 2026-01-23 | 0.97468
2026-01-23 00:43 | 73.2236 | FALSE | FALSE | -0.14864 | -0.20341 | -0.43124 | -0.58549 | 0 |  |  | none | FALSE | 1 | 73.075 | FALSE | FALSE | 0.0936 |  | 73.3649 | 0 | 0 | 0 | 0.12967 | 0 | 0.14497 | Normal | 73.6548 | -0.97468 | Night | 202601 | 2026-01-23 | 0.97468
2026-01-23 00:58 | 73.2236 | FALSE | FALSE | -0.14864 | -0.20341 | -0.43124 | -0.58549 | 0 |  |  | none | FALSE | 1 | 73.075 | FALSE | FALSE | 0.0936 |  | 73.3649 | 0 | 0 | 0 | 0.12967 | 0 | 0.14497 | Normal | 73.6548 | -0.97468 | Night | 202601 | 2026-01-23 | 0.97468
2026-01-23 01:13 | 73.2236 | FALSE | FALSE | -0.14864 | -0.20341 | -0.43124 | -0.58549 | 0 |  |  | none | FALSE | 1 | 73.075 | FALSE | FALSE | 0.0936 |  | 73.3649 | 0 | 0 | 0 | 0.12967 | 0 | 0.14497 | Normal | 73.6548 | -0.97468 | Night | 202601 | 2026-01-23 | 0.97468
2026-01-23 01:28 | 73.2236 | FALSE | FALSE | -0.14864 | -0.20341 | -0.43124 | -0.58549 | 0 |  |  | none | FALSE | 1 | 73.075 | FALSE | FALSE | 0.0936 |  | 73.3649 | 0 | 0 | 0 | 0.12967 | 0 | 0.14497 | Normal | 73.6548 | -0.97468 | Night | 202601 | 2026-01-23 | 0.97468
2026-01-23 01:43 | 73.2236 | FALSE | FALSE | -0.14864 | -0.20341 | -0.43124 | -0.58549 | 0 |  |  | none | FALSE | 1 | 73.075 | FALSE | FALSE | 0.0936 |  | 73.3649 | 0 | 0 | 0 | 0.12967 | 0 | 0.14497 | Normal | 73.6548 | -0.97468 | Night | 202601 | 2026-01-23 | 0.97468
2026-01-23 01:58 | 73.2236 | FALSE | FALSE | -0.16132 | -0.2208 | -0.41566 | -0.56445 | 0 |  |  | none | FALSE | 1 | 73.0623 | FALSE | FALSE | 0.0873 |  | 73.3508 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14424 | Normal | 73.6393 | -0.88163 | Night | 202601 | 2026-01-23 | 0.88163
2026-01-23 02:13 | 73.2236 | FALSE | FALSE | -0.17104 | -0.23414 | -0.39712 | -0.53942 | 0 |  |  | none | FALSE | 0 | 73.0526 | FALSE | FALSE | 0.0531 |  | 73.3366 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14204 | Normal | 73.6207 | -0.79582 | Night | 202601 | 2026-01-23 | 0.79582
2026-01-23 02:28 | 73.2236 | FALSE | FALSE | -0.17768 | -0.24324 | -0.3755 | -0.51019 | 0 |  |  | none | FALSE | 0 | 73.0459 | FALSE | FALSE | 0.0477 |  | 73.3225 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13829 | Normal | 73.5991 | -0.71522 | Night | 202601 | 2026-01-23 | 0.71522
2026-01-23 02:43 | 73.2236 | FALSE | FALSE | -0.18096 | -0.24774 | -0.35052 | -0.47641 | 0 |  |  | none | FALSE | 0 | 73.0426 | FALSE | FALSE | 0.0425 |  | 73.3084 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13287 | Normal | 73.5741 | -0.63808 | Night | 202601 | 2026-01-23 | 0.63808
2026-01-23 02:58 | 73.2236 | FALSE | FALSE | -0.18045 | -0.24704 | -0.32175 | -0.43748 | 0 |  |  | none | FALSE | 0 | 73.0432 | FALSE | FALSE | 0.0375 |  | 73.2943 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.12555 | Normal | 73.5453 | -0.56273 | Night | 202601 | 2026-01-23 | 0.56273
2026-01-23 03:13 | 73.2236 | FALSE | FALSE | -0.17543 | -0.24016 | -0.28847 | -0.39242 | 0 |  |  | none | FALSE | 0 | 73.0482 | FALSE | FALSE | 0.0325 |  | 73.2801 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.11598 | Normal | 73.5121 | -0.48734 | Night | 202601 | 2026-01-23 | 0.48734
2026-01-23 03:27 | 73.2236 | FALSE | FALSE | -0.16467 | -0.22539 | -0.24945 | -0.33951 | 0 |  |  | none | FALSE | 0 | 73.0589 | FALSE | FALSE | 0.0273 |  | 73.266 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.10353 | Normal | 73.473 | -0.40945 | Night | 202601 | 2026-01-23 | 0.40945
2026-01-23 03:42 | 73.2236 | FALSE | FALSE | -0.1457 | -0.19938 | -0.20222 | -0.27541 | 0 |  |  | none | FALSE | 0 | 73.0779 | FALSE | FALSE | 0.0217 |  | 73.2519 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.086982 | Normal | 73.4258 | -0.32489 | Night | 202601 | 2026-01-23 | 0.32489
2026-01-23 03:57 | 73.2236 | FALSE | FALSE | -0.11225 | -0.15354 | -0.14051 | -0.19153 | 0 |  |  | none | FALSE | 0 | 73.1113 | FALSE | FALSE | 0.0149 |  | 73.2377 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.063191 | Normal | 73.3641 | -0.22361 | Night | 202601 | 2026-01-23 | 0.22361
2026-01-23 04:12 | 73.2236 | FALSE | FALSE | -0.11225 | -0.15354 | -0.14051 | -0.19153 | 0 |  |  | none | FALSE | 0 | 73.1113 | FALSE | FALSE | 0.0149 |  | 73.2377 | 0 | 0 | 0 | 0.091688 | 0 | 0.063191 | Normal | 73.3641 | -0.22361 | Night | 202601 | 2026-01-23 | 0.22361
2026-01-23 04:27 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-23
2026-01-23 04:42 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-23
2026-01-23 04:57 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-23
2026-01-23 05:12 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-23
2026-01-23 05:27 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-23
2026-01-23 05:42 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-23
2026-01-23 05:57 | 73.2236 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 73.2236 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0 | 0 |  | 0 | Normal | 73.2236 |  | Night | 202601 | 2026-01-23
2026-01-23 06:12 | 72.941 | TRUE | FALSE | 0.14209 | 0.19442 | -0.39485 | -0.53842 | -0.2826 | 2026-01-23 06:26 | 2026-01-23 06:12 | lower | TRUE | 1 | 73.0831 | FALSE | FALSE | 0.3689 | 4.2485 | 73.2095 | 1 | -0.2826 | -0.01413 | 0.063191 | -4.2485 | 0.063191 | Extreme triggered | 73.3359 | -4.2485 | Night | 202601 | 2026-01-23 | 4.2485
2026-01-23 06:26 | 73.2236 | TRUE | FALSE | -0.14051 | -0.19226 | -0.11225 | -0.15307 | 0.2826 |  |  | none | FALSE | 2 | 73.0831 | TRUE | FALSE | 0.072 |  | 73.2095 | 0 | 0.2826 | 0 | 0.091688 | 3.0822 | 0.063191 | Persistence ends | 73.3359 | 0.22361 | Night | 202601 | 2026-01-23 | 0.22361
2026-01-23 06:41 | 72.941 | TRUE | FALSE | 0.080375 | 0.11007 | -0.4283 | -0.58377 | -0.2826 | 2026-01-23 08:30 | 2026-01-23 06:41 | lower | TRUE | 3 | 73.0214 | TRUE | FALSE | 0.3378 | 2.924 | 73.1953 | 1 | -0.2826 | -0.01413 | 0.11135 | -2.411 | 0.086982 | Extreme triggered | 73.3693 | -2.924 | Night | 202601 | 2026-01-23 | 2.924
2026-01-23 06:56 | 72.941 | FALSE | FALSE | 0.03315 | 0.045428 | -0.44727 | -0.60946 | 0 |  | 2026-01-23 06:41 | lower | TRUE | 3 | 72.9742 | FALSE | FALSE | 0.3547 | 2.6221 | 73.1812 | 2 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.10353 | Extreme/elevated | 73.3883 | -2.3202 | Night | 202601 | 2026-01-23 | 2.3202
2026-01-23 07:12 | 72.941 | FALSE | FALSE | -0.0058732 | -0.0080526 | -0.45803 | -0.62403 | 0 |  | 2026-01-23 06:41 | none | FALSE | 3 | 72.9351 | FALSE | FALSE | 0.3871 | 2.3979 | 73.1671 | 3 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.11598 | Persistent | 73.399 | -1.9494 | Night | 202601 | 2026-01-23 | 1.9494
2026-01-23 07:26 | 72.941 | FALSE | FALSE | -0.039147 | -0.053698 | -0.46305 | -0.63082 | 0 |  | 2026-01-23 06:41 | none | FALSE | 3 | 72.9019 | FALSE | FALSE | 0.4268 | 2.2204 | 73.153 | 4 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.12555 | Persistent | 73.404 | -1.6882 | Day | 202601 | 2026-01-23 | 1.6882
2026-01-23 07:30 | 72.941 | FALSE | FALSE | -0.067916 | -0.093197 | -0.46356 | -0.63151 | 0 |  | 2026-01-23 06:41 | none | FALSE | 3 | 72.8731 | FALSE | FALSE | 0.4707 | 2.0741 | 73.1388 | 5 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13287 | Persistent | 73.4046 | -1.4888 | Day | 202601 | 2026-01-23 | 1.4888
2026-01-23 07:45 | 72.941 | FALSE | FALSE | -0.092897 | -0.12752 | -0.46028 | -0.62707 | 0 |  | 2026-01-23 06:41 | none | FALSE | 3 | 72.8481 | FALSE | FALSE | 0.5171 | 1.9498 | 73.1247 | 6 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13829 | Persistent | 73.4013 | -1.3283 | Day | 202601 | 2026-01-23 | 1.3283
2026-01-23 08:00 | 72.941 | FALSE | TRUE | -0.11452 | -0.15726 | -0.45364 | -0.61809 | 0 |  | 2026-01-23 06:41 | none | FALSE | 3 | 72.8265 | FALSE | FALSE | 0.5653 | 1.8418 | 73.1106 | 7 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14204 | Confirmed/Materialized Shift | 73.3946 | -1.1937 | Day | 202601 | 2026-01-23 | 1.1937
2026-01-23 08:16 | 72.941 | FALSE | TRUE | -0.13306 | -0.18275 | -0.44392 | -0.60492 | 0 |  | 2026-01-23 06:41 | none | FALSE | 3 | 72.8079 | FALSE | FALSE | 0.5576 | 1.7463 | 73.0964 | 8 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14424 | Confirmed/Materialized Shift | 73.3849 | -1.0775 | Day | 202601 | 2026-01-23 | 1.0775
2026-01-23 08:30 | 72.941 | FALSE | FALSE | -0.14864 | -0.2042 | -0.43124 | -0.58774 | 0 |  |  | none | FALSE | 2 | 72.7924 | FALSE | FALSE | 0.1221 |  | 73.0823 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14497 | Persistence ends | 73.3722 | -0.97468 | Day | 202601 | 2026-01-23 | 0.97468
2026-01-23 08:30 | 72.941 | FALSE | FALSE | -0.16132 | -0.22165 | -0.41566 | -0.56663 | 0 |  |  | none | FALSE | 1 | 72.7797 | FALSE | FALSE | 0.0873 |  | 73.0682 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14424 | Normal | 73.3567 | -0.88163 | Day | 202601 | 2026-01-23 | 0.88163
2026-01-23 08:45 | 72.941 | FALSE | FALSE | -0.17104 | -0.23505 | -0.39712 | -0.5415 | 0 |  |  | none | FALSE | 0 | 72.77 | FALSE | FALSE | 0.0531 |  | 73.054 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14204 | Normal | 73.3381 | -0.79582 | Day | 202601 | 2026-01-23 | 0.79582
2026-01-23 09:00 | 72.941 | FALSE | FALSE | -0.17768 | -0.24418 | -0.3755 | -0.51216 | 0 |  |  | none | FALSE | 0 | 72.7633 | FALSE | FALSE | 0.0477 |  | 73.0399 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13829 | Normal | 73.3165 | -0.71522 | Day | 202601 | 2026-01-23 | 0.71522
2026-01-23 09:15 | 72.941 | FALSE | FALSE | -0.18096 | -0.2487 | -0.35052 | -0.47825 | 0 |  |  | none | FALSE | 0 | 72.76 | FALSE | FALSE | 0.0425 |  | 73.0258 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13287 | Normal | 73.2915 | -0.63808 | Day | 202601 | 2026-01-23 | 0.63808
2026-01-23 09:30 | 73.2236 | TRUE | FALSE | -0.46356 | -0.6371 | -0.067916 | -0.092665 | 0.2826 |  |  | none | FALSE | 1 | 72.76 | FALSE | FALSE | 0.1278 |  | 73.0258 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.13287 | Normal | 73.2915 | 1.4888 | Day | 202601 | 2026-01-23 | 1.4888
2026-01-23 09:45 | 73.2236 | FALSE | FALSE | -0.46356 | -0.6371 | -0.067916 | -0.092665 | 0 |  |  | none | FALSE | 1 | 72.76 | FALSE | FALSE | 0.1278 |  | 73.0258 | 0 | 0 | 0 | 0.12967 | 0 | 0.13287 | Normal | 73.2915 | 1.4888 | Day | 202601 | 2026-01-23 | 1.4888
2026-01-23 10:00 | 73.5062 | FALSE | FALSE | -0.79814 | -1.0977 | 0.13444 | 0.18323 | 0.2826 | 2026-01-23 11:12 | 2026-01-23 10:00 | upper | TRUE | 1 | 72.7081 | FALSE | FALSE | 0.2731 | 2.8102 | 73.0399 | 1 | 0.2826 | 0.01413 | 0.14424 | 1.8612 | 0.16593 | Extreme triggered | 73.3718 | 2.8102 | Day | 202601 | 2026-01-23 | 2.8102
2026-01-23 10:15 | 73.7888 | FALSE | FALSE | -1.1872 | -1.6353 | 0.25401 | 0.34543 | 0.2826 |  | 2026-01-23 10:00 | upper | TRUE | 1 | 72.6016 | FALSE | FALSE | 0.3488 | 2.9495 | 73.0682 | 2 | 0.2826 | 0.02826 | 0.15614 | 1.6289 | 0.23331 | Extreme/elevated | 73.5348 | 3.0887 | Day | 202601 | 2026-01-23 | 3.0887
2026-01-23 10:29 | 73.5062 | FALSE | FALSE | -0.92609 | -1.276 | -0.078293 | -0.1064 | -0.2826 |  | 2026-01-23 10:00 | none | FALSE | 1 | 72.5801 | FALSE | FALSE | 0.3125 | 2.5291 | 73.0823 | 3 | -0.2826 | 0.01413 | 0.17092 | -1.7361 | 0.2511 | Persistent | 73.5845 | 1.6882 | Day | 202601 | 2026-01-23 | 1.6882
2026-01-23 10:44 | 73.7888 | FALSE | FALSE | -1.2519 | -1.7259 | 0.076308 | 0.10352 | 0.2826 |  | 2026-01-23 10:00 | upper | TRUE | 1 | 72.5369 | FALSE | TRUE | 0.4078 | 2.4617 | 73.1247 | 4 | 0.2826 | 0.04239 | 0.16593 | 1.4477 | 0.2939 | Persistent | 73.7125 | 2.2596 | Day | 202601 | 2026-01-23 | 2.2596
2026-01-23 10:54 | 74.0714 | FALSE | FALSE | -1.6286 | -2.2481 | 0.18005 | 0.24366 | 0.2826 |  | 2026-01-23 10:00 | upper | TRUE | 1 | 72.4428 | FALSE | TRUE | 0.4808 | 2.4688 | 73.1671 | 5 | 0.2826 | 0.04239 | 0.16593 | 1.4477 | 0.36214 | Persistent | 73.8914 | 2.4972 | Day | 202601 | 2026-01-23 | 2.4972
2026-01-23 10:57 | 74.0714 | FALSE | FALSE | -1.6679 | -2.3036 | 0.027722 | 0.03744 | 0 |  | 2026-01-23 10:00 | upper | TRUE | 1 | 72.4035 | FALSE | TRUE | 0.5093 | 2.4019 | 73.2236 | 6 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.41004 | Persistent | 74.0437 | 2.0676 | Day | 202601 | 2026-01-23 | 2.0676
2026-01-23 11:12 | 73.2236 | TRUE | FALSE | -0.79511 | -1.0978 | -0.82337 | -1.112 | -0.8478 |  |  | none | FALSE | 2 | 72.4285 | TRUE | FALSE | 0.0595 |  | 73.2377 | 0 | -0.8478 | 0.01413 | 0.25068 | -3.4384 | 0.40462 | Persistence ends | 74.047 | -0.034922 | Day | 202601 | 2026-01-23 | 0.034922
2026-01-23 11:27 | 73.2236 | FALSE | FALSE | -0.76895 | -1.0613 | -0.82547 | -1.1148 | 0 |  |  | none | FALSE | 2 | 72.4547 | FALSE | FALSE | 0.0619 |  | 73.2519 | 0 | 0 | 0.01413 | 0.25068 | -0.056367 | 0.3986 | Normal | 74.0491 | -0.070897 | Day | 202601 | 2026-01-23 | 0.070897
2026-01-23 11:29 | 72.941 | FALSE | FALSE | -0.48635 | -0.67124 | -1.1081 | -1.4964 | -0.2826 |  |  | none | FALSE | 1 | 72.4547 | FALSE | FALSE | 0.0806 |  | 73.2519 | 0 | -0.2826 | 0 | 0.25933 | -1.0897 | 0.3986 | Normal | 74.0491 | -0.77987 | Day | 202601 | 2026-01-23 | 0.77987
2026-01-23 11:44 | 73.2236 | FALSE | FALSE | -0.74153 | -1.023 | -0.82631 | -1.1159 | 0.2826 |  |  | none | FALSE | 1 | 72.4821 | FALSE | FALSE | 0.0358 |  | 73.266 | 0 | 0.2826 | 0.01413 | 0.26692 | 1.0058 | 0.39196 | Normal | 74.0499 | -0.10815 | Day | 202601 | 2026-01-23 | 0.10815
2026-01-23 11:59 | 73.5062 | FALSE | FALSE | -0.98724 | -1.3614 | -0.56334 | -0.76055 | 0.2826 |  |  | none | FALSE | 1 | 72.519 | FALSE | FALSE | 0.065 |  | 73.2943 | 0 | 0.2826 | 0.02826 | 0.27353 | 0.92984 | 0.38764 | Normal | 74.0695 | 0.54676 | Day | 202601 | 2026-01-23 | 0.54676
2026-01-23 12:14 | 73.5062 | FALSE | FALSE | -0.94586 | -1.3035 | -0.57848 | -0.78083 | 0 |  |  | none | FALSE | 1 | 72.5603 | FALSE | FALSE | 0.0607 |  | 73.3225 | 0 | 0 | 0.02826 | 0.27353 | -0.10332 | 0.38108 | Normal | 74.0847 | 0.48202 | Day | 202601 | 2026-01-23 | 0.48202
2026-01-23 12:29 | 73.5062 | FALSE | FALSE | -0.89974 | -1.2392 | -0.58888 | -0.79476 | 0 |  |  | none | FALSE | 1 | 72.6065 | FALSE | FALSE | 0.0564 |  | 73.3508 | 0 | 0 | 0.02826 | 0.27353 | -0.10332 | 0.37215 | Normal | 74.0951 | 0.41765 | Day | 202601 | 2026-01-23 | 0.41765
2026-01-23 12:44 | 73.2236 | FALSE | FALSE | -0.58065 | -0.79932 | -0.86325 | -1.1652 | -0.2826 |  |  | none | FALSE | 1 | 72.643 | FALSE | FALSE | 0.0547 |  | 73.3649 | 0 | -0.2826 | 0.01413 | 0.28223 | -1.0514 | 0.36097 | Normal | 74.0868 | -0.39144 | Day | 202601 | 2026-01-23 | 0.39144
2026-01-23 12:59 | 73.2236 | FALSE | FALSE | -0.54224 | -0.74605 | -0.8531 | -1.1516 | 0 |  |  | none | FALSE | 1 | 72.6814 | FALSE | FALSE | 0.0583 |  | 73.379 | 0 | 0 | 0.01413 | 0.28223 | -0.050066 | 0.34883 | Normal | 74.0767 | -0.44557 | Day | 202601 | 2026-01-23 | 0.44557
2026-01-23 13:14 | 73.5062 | FALSE | FALSE | -0.76703 | -1.0545 | -0.56921 | -0.76843 | 0.2826 |  |  | none | FALSE | 1 | 72.7392 | FALSE | FALSE | 0.0483 |  | 73.4073 | 0 | 0.2826 | 0.02826 | 0.28849 | 0.88163 | 0.33406 | Normal | 74.0754 | 0.29608 | Day | 202601 | 2026-01-23 | 0.29608
2026-01-23 13:28 | 73.5062 | FALSE | FALSE | -0.70256 | -0.96501 | -0.56126 | -0.75777 | 0 |  |  | none | FALSE | 0 | 72.8036 | FALSE | FALSE | 0.0149 |  | 73.4356 | 0 | 0 | 0.02826 | 0.28849 | -0.097959 | 0.31596 | Normal | 74.0675 | 0.22361 | Day | 202601 | 2026-01-23 | 0.22361
2026-01-23 13:43 | 73.2236 | FALSE | FALSE | -0.37095 | -0.50917 | -0.82311 | -1.1116 | -0.2826 |  |  | none | FALSE | 0 | 72.8527 | FALSE | FALSE | 0.0505 |  | 73.4497 | 0 | -0.2826 | 0.01413 | 0.29675 | -0.99994 | 0.29851 | Normal | 74.0467 | -0.75735 | Day | 202601 | 2026-01-23 | 0.75735
2026-01-23 13:59 | 73.2236 | FALSE | FALSE | -0.37095 | -0.50917 | -0.82311 | -1.1116 | 0 |  |  | none | FALSE | 0 | 72.8527 | FALSE | FALSE | 0.0505 |  | 73.4497 | 0 | 0 | 0 | 0.28994 | 0 | 0.29851 | Normal | 74.0467 | -0.75735 | Day | 202601 | 2026-01-23 | 0.75735
2026-01-23 14:14 | 73.5062 | FALSE | FALSE | -0.63019 | -0.86475 | -0.54541 | -0.73653 | 0.2826 |  |  | none | FALSE | 0 | 72.876 | FALSE | FALSE | 0.0096 |  | 73.4638 | 0 | 0.2826 | 0.01413 | 0.29675 | 0.90471 | 0.2939 | Normal | 74.0516 | 0.14423 | Day | 202601 | 2026-01-23 | 0.14423
2026-01-23 14:28 | 73.2236 | FALSE | FALSE | -0.37095 | -0.50917 | -0.82311 | -1.1116 | -0.2826 |  |  | none | FALSE | 0 | 72.8527 | FALSE | FALSE | 0.0505 |  | 73.4497 | 0 | -0.2826 | -0.01413 | 0.29675 | -0.90471 | 0.29851 | Normal | 74.0467 | -0.75735 | Day | 202601 | 2026-01-23 | 0.75735
2026-01-23 14:43 | 73.5062 | FALSE | FALSE | -0.6469 | -0.88787 | -0.5056 | -0.68313 | 0.2826 |  |  | none | FALSE | 0 | 72.8593 | FALSE | FALSE | 0.0163 |  | 73.4356 | 0 | 0.2826 | -0.01413 | 0.29675 | 0.99994 | 0.28812 | Normal | 74.0118 | 0.24521 | Day | 202601 | 2026-01-23 | 0.24521
2026-01-23 14:58 | 73.2236 | FALSE | FALSE | -0.38496 | -0.5285 | -0.7806 | -1.0548 | -0.2826 |  |  | none | FALSE | 0 | 72.8386 | FALSE | FALSE | 0.0453 |  | 73.4214 | 0 | -0.2826 | -0.01413 | 0.29675 | -0.90471 | 0.29139 | Normal | 74.0042 | -0.67889 | Day | 202601 | 2026-01-23 | 0.67889
2026-01-23 15:13 | 73.2236 | FALSE | FALSE | -0.39266 | -0.53914 | -0.73178 | -0.98949 | 0 |  |  | none | FALSE | 0 | 72.8309 | FALSE | FALSE | 0.0402 |  | 73.3932 | 0 | 0 | -0.02826 | 0.28849 | 0.097959 | 0.28111 | Normal | 73.9554 | -0.60318 | Day | 202601 | 2026-01-23 | 0.60318
2026-01-23 15:28 | 73.2236 | FALSE | FALSE | -0.33945 | -0.46573 | -0.59379 | -0.8044 | 0 |  |  | none | FALSE | 0 | 72.8842 | FALSE | FALSE | 0.0363 |  | 73.3508 | 0 | 0 | -0.04239 | 0.27923 | 0.15181 | 0.23331 | Normal | 73.8174 | -0.54507 | Day | 202601 | 2026-01-23 | 0.54507
2026-01-23 15:43 | 73.2236 | FALSE | FALSE | -0.23809 | -0.32621 | -0.40765 | -0.55363 | 0 |  |  | none | FALSE | 0 | 72.9855 | FALSE | FALSE | 0.035 |  | 73.3084 | 0 | 0 | -0.04239 | 0.27923 | 0.15181 | 0.16143 | Normal | 73.6312 | -0.52517 | Day | 202601 | 2026-01-23 | 0.52517
2026-01-23 15:58 | 72.941 | FALSE | FALSE | -0.0077242 | -0.010591 | -0.71422 | -0.96969 | -0.2826 |  |  | none | FALSE | 0 | 72.9333 | FALSE | FALSE | 0.1305 |  | 73.2943 | 0 | -0.2826 | -0.01413 | 0.21454 | -1.2514 | 0.18049 | Normal | 73.6552 | -1.9572 | Day | 202601 | 2026-01-23 | 1.9572
2026-01-23 16:13 | 73.2236 | FALSE | FALSE | -0.29032 | -0.39807 | -0.43162 | -0.58601 | 0.2826 |  |  | none | FALSE | 0 | 72.9333 | FALSE | FALSE | 0.0261 |  | 73.2943 | 0 | 0.2826 | 0 | 0.22459 | 1.2583 | 0.18049 | Normal | 73.6552 | -0.39144 | Day | 202601 | 2026-01-23 | 0.39144
2026-01-23 16:27 | 73.2236 | FALSE | FALSE | -0.23809 | -0.32621 | -0.40765 | -0.55363 | 0 |  |  | none | FALSE | 0 | 72.9855 | FALSE | FALSE | 0.035 |  | 73.3084 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.16143 | Normal | 73.6312 | -0.52517 | Day | 202601 | 2026-01-23 | 0.52517
2026-01-23 16:43 | 72.941 | FALSE | FALSE | -0.0077242 | -0.010591 | -0.71422 | -0.96969 | -0.2826 |  |  | none | FALSE | 0 | 72.9333 | FALSE | FALSE | 0.1305 |  | 73.2943 | 0 | -0.2826 | -0.01413 | 0.21454 | -1.2514 | 0.18049 | Normal | 73.6552 | -1.9572 | Day | 202601 | 2026-01-23 | 1.9572
2026-01-23 16:58 | 72.941 | FALSE | FALSE | -0.054158 | -0.074304 | -0.70414 | -0.95612 | 0 |  |  | none | FALSE | 0 | 72.8868 | FALSE | FALSE | 0.1143 |  | 73.266 | 0 | 0 | -0.02826 | 0.20296 | 0.13924 | 0.18957 | Normal | 73.6451 | -1.7143 | Day | 202601 | 2026-01-23 | 1.7143
2026-01-23 17:13 | 72.941 | FALSE | FALSE | -0.091185 | -0.12517 | -0.68465 | -0.9299 | 0 |  |  | none | FALSE | 0 | 72.8498 | FALSE | FALSE | 0.102 |  | 73.2377 | 0 | 0 | -0.02826 | 0.20296 | 0.13924 | 0.19396 | Normal | 73.6256 | -1.5299 | Day | 202601 | 2026-01-23 | 1.5299
2026-01-23 17:27 | 72.6584 | FALSE | FALSE | 0.091523 | 0.12581 | -0.98236 | -1.334 | -0.2826 | 2026-01-23 18:27 | 2026-01-23 17:27 | lower | TRUE | 0 | 72.7499 | FALSE | FALSE | 0.2179 | 2.411 | 73.1953 | 1 | -0.2826 | -0.04239 | 0.21058 | -1.1407 | 0.22271 | Extreme triggered | 73.6408 | -2.411 | Day | 202601 | 2026-01-23 | 2.411
2026-01-23 17:42 | 72.3758 | FALSE | FALSE | 0.2009 | 0.27681 | -1.3534 | -1.8356 | -0.2826 |  | 2026-01-23 17:27 | lower | TRUE | 0 | 72.5767 | FALSE | FALSE | 0.2941 | 2.5541 | 73.153 | 2 | -0.2826 | -0.04239 | 0.21058 | -1.1407 | 0.28812 | Extreme/elevated | 73.7292 | -2.6973 | Day | 202601 | 2026-01-23 | 2.6973
2026-01-23 17:57 | 72.3758 | FALSE | FALSE | 0.063497 | 0.087655 | -1.406 | -1.9056 | 0 |  | 2026-01-23 17:27 | lower | TRUE | 0 | 72.4393 | FALSE | TRUE | 0.3174 | 2.4325 | 73.1106 | 3 | 0 | -0.04239 | 0.21058 | 0.2013 | 0.33563 | Persistent | 73.7818 | -2.1892 | Night | 202601 | 2026-01-23 | 2.1892
2026-01-23 18:12 | 72.6584 | FALSE | FALSE | -0.26337 | -0.36379 | -1.0829 | -1.4685 | 0.2826 |  | 2026-01-23 17:27 | none | FALSE | 0 | 72.395 | FALSE | FALSE | 0.3097 | 2.1287 | 73.0682 | 4 | 0.2826 | -0.04239 | 0.21058 | 1.5433 | 0.33657 | Persistent | 73.7413 | -1.2175 | Night | 202601 | 2026-01-23 | 1.2175
2026-01-23 18:27 | 72.941 | FALSE | FALSE | -0.54356 | -0.7508 | -0.74138 | -1.0062 | 0.2826 |  |  | none | FALSE | 0 | 72.3974 | FALSE | FALSE | 0.0205 |  | 73.0399 | 0 | 0.2826 | -0.02826 | 0.22271 | 1.3958 | 0.32123 | Persistence ends | 73.6824 | -0.30791 | Night | 202601 | 2026-01-23 | 0.30791
2026-01-23 18:30 | 72.941 | FALSE | FALSE | -0.55309 | -0.76407 | -0.72265 | -0.98101 | 0 |  |  | none | FALSE | 0 | 72.3879 | FALSE | FALSE | 0.0177 |  | 73.0258 | 0 | 0 | -0.01413 | 0.21454 | 0.065863 | 0.31894 | Normal | 73.6637 | -0.26582 | Night | 202601 | 2026-01-23 | 0.26582
2026-01-23 18:31 | 72.941 | FALSE | FALSE | -0.56126 | -0.77544 | -0.70256 | -0.954 | 0 |  |  | none | FALSE | 0 | 72.3797 | FALSE | FALSE | 0.0149 |  | 73.0117 | 0 | 0 | -0.01413 | 0.21454 | 0.065863 | 0.31596 | Normal | 73.6436 | -0.22361 | Night | 202601 | 2026-01-23 | 0.22361
2026-01-23 18:46 | 73.5062 | TRUE | FALSE | -1.1265 | -1.5563 | -0.13736 | -0.18652 | 0.5652 |  |  | none | FALSE | 1 | 72.3797 | FALSE | FALSE | 0.1329 |  | 73.0117 | 0 | 0.5652 | 0 | 0.24258 | 2.3299 | 0.31596 | Normal | 73.6436 | 1.5652 | Night | 202601 | 2026-01-23 | 1.5652
2026-01-23 19:01 | 73.7888 | FALSE | FALSE | -1.4656 | -2.0264 | 0.032201 | 0.043658 | 0.2826 | 2026-01-23 20:59 | 2026-01-23 19:01 | upper | TRUE | 1 | 72.3232 | FALSE | FALSE | 0.225 | 2.0899 | 73.0399 | 1 | 0.2826 | 0.02826 | 0.24084 | 1.056 | 0.35834 | Extreme triggered | 73.7566 | 2.0899 | Night | 202601 | 2026-01-23 | 2.0899
2026-01-23 19:16 | 73.7888 | FALSE | FALSE | -1.4997 | -2.0746 | -0.030158 | -0.040854 | 0 |  | 2026-01-23 19:01 | none | FALSE | 1 | 72.2891 | FALSE | FALSE | 0.2709 | 2.0055 | 73.054 | 2 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.38246 | Extreme/elevated | 73.819 | 1.9211 | Night | 202601 | 2026-01-23 | 1.9211
2026-01-23 19:30 | 73.7888 | FALSE | FALSE | -1.5368 | -2.127 | -0.12377 | -0.16745 | 0 |  | 2026-01-23 19:01 | none | FALSE | 1 | 72.252 | FALSE | FALSE | 0.3135 | 1.9043 | 73.0823 | 3 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.41513 | Persistent | 73.9126 | 1.7019 | Night | 202601 | 2026-01-23 | 1.7019
2026-01-23 19:45 | 73.7888 | FALSE | FALSE | -1.5653 | -2.1673 | -0.20881 | -0.28219 | 0 |  | 2026-01-23 19:01 | none | FALSE | 1 | 72.2235 | FALSE | FALSE | 0.3591 | 1.8105 | 73.1106 | 4 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.44353 | Persistent | 73.9976 | 1.5292 | Night | 202601 | 2026-01-23 | 1.5292
2026-01-23 20:00 | 73.7888 | FALSE | FALSE | -1.5868 | -2.1977 | -0.28685 | -0.38724 | 0 |  | 2026-01-23 19:01 | none | FALSE | 1 | 72.202 | FALSE | FALSE | 0.4068 | 1.7259 | 73.1388 | 5 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.46841 | Persistent | 74.0756 | 1.3876 | Night | 202601 | 2026-01-23 | 1.3876
2026-01-23 20:15 | 73.7888 | FALSE | FALSE | -1.6024 | -2.2198 | -0.35895 | -0.4841 | 0 |  | 2026-01-23 19:01 | none | FALSE | 1 | 72.1864 | FALSE | FALSE | 0.456 | 1.6496 | 73.1671 | 6 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.49034 | Persistent | 74.1478 | 1.2679 | Night | 202601 | 2026-01-23 | 1.2679
2026-01-23 20:29 | 73.7888 | FALSE | TRUE | -1.5916 | -2.2046 | -0.43298 | -0.58336 | 0 |  | 2026-01-23 19:01 | none | FALSE | 1 | 72.1972 | FALSE | FALSE | 0.5049 | 1.5775 | 73.2095 | 7 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.50615 | Confirmed/Materialized Shift | 74.2218 | 1.1446 | Night | 202601 | 2026-01-23 | 1.1446
2026-01-23 20:44 | 73.7888 | FALSE | TRUE | -1.5961 | -2.2108 | -0.49393 | -0.66493 | 0 |  | 2026-01-23 19:01 | none | FALSE | 1 | 72.1927 | FALSE | FALSE | 0.4989 | 1.5121 | 73.2377 | 8 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.5225 | Confirmed/Materialized Shift | 74.2827 | 1.0547 | Night | 202601 | 2026-01-23 | 1.0547
2026-01-23 20:59 | 73.7888 | FALSE | FALSE | -1.5964 | -2.2113 | -0.55076 | -0.74087 | 0 |  |  | none | FALSE | 1 | 72.1924 | FALSE | FALSE | 0.0935 |  | 73.266 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.53678 | Persistence ends | 74.3396 | 0.97397 | Night | 202601 | 2026-01-23 | 0.97397
2026-01-23 21:14 | 73.7888 | FALSE | FALSE | -1.5668 | -2.1695 | -0.60599 | -0.81456 | 0 |  |  | none | FALSE | 0 | 72.222 | FALSE | FALSE | 0.059 |  | 73.3084 | 0 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.54321 | Normal | 74.3948 | 0.88442 | Night | 202601 | 2026-01-23 | 0.88442
2026-01-23 21:29 | 74.0714 | FALSE | FALSE | -1.8294 | -2.5324 | -0.41644 | -0.55907 | 0.2826 |  |  | none | FALSE | 0 | 72.242 | FALSE | FALSE | 0.0839 |  | 73.3649 | 0 | 0.2826 | 0.05652 | 0.19665 | 1.1497 | 0.56147 | Normal | 74.4878 | 1.2583 | Night | 202601 | 2026-01-23 | 1.2583
2026-01-23 21:44 | 74.0714 | FALSE | FALSE | -1.7966 | -2.4858 | -0.49666 | -0.66606 | 0 |  |  | none | FALSE | 0 | 72.2748 | FALSE | FALSE | 0.0756 |  | 73.4214 | 0 | 0 | 0.05652 | 0.19665 | -0.28742 | 0.57332 | Normal | 74.5681 | 1.1337 | Night | 202601 | 2026-01-23 | 1.1337
2026-01-23 21:59 | 74.0714 | FALSE | FALSE | -1.7019 | -2.3517 | -0.54323 | -0.72805 | 0 |  |  | none | FALSE | 0 | 72.3695 | FALSE | FALSE | 0.0688 |  | 73.4921 | 0 | 0 | 0.07065 | 0.18049 | -0.39144 | 0.56128 | Normal | 74.6146 | 1.0322 | Night | 202601 | 2026-01-23 | 1.0322
2026-01-23 22:14 | 74.0714 | FALSE | FALSE | -1.5135 | -2.0859 | -0.52438 | -0.70296 | 0 |  |  | none | FALSE | 0 | 72.5579 | FALSE | FALSE | 0.0647 |  | 73.5768 | 0 | 0 | 0.08478 | 0.16143 | -0.52517 | 0.50946 | Normal | 74.5958 | 0.97073 | Night | 202601 | 2026-01-23 | 0.97073
2026-01-23 22:29 | 74.0714 | FALSE | FALSE | -1.2791 | -1.7572 | -0.45957 | -0.61662 | 0 |  |  | none | FALSE | 0 | 72.7923 | FALSE | FALSE | 0.0628 |  | 73.6616 | 0 | 0 | 0.08478 | 0.16143 | -0.52517 | 0.43467 | Normal | 74.531 | 0.94271 | Night | 202601 | 2026-01-23 | 0.94271
2026-01-23 22:44 | 74.0714 | FALSE | FALSE | -1.0862 | -1.4883 | -0.40801 | -0.54781 | 0 |  |  | none | FALSE | 0 | 72.9852 | FALSE | FALSE | 0.0605 |  | 73.7323 | 0 | 0 | 0.07065 | 0.15546 | -0.45445 | 0.37356 | Normal | 74.4794 | 0.9078 | Night | 202601 | 2026-01-23 | 0.9078
2026-01-23 22:59 | 74.0714 | FALSE | FALSE | -0.94377 | -1.2906 | -0.37857 | -0.50849 | 0 |  |  | none | FALSE | 0 | 73.1276 | FALSE | FALSE | 0.057 |  | 73.7888 | 0 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.33058 | Normal | 74.45 | 0.85485 | Night | 202601 | 2026-01-23 | 0.85485
2026-01-23 23:14 | 74.0714 | FALSE | FALSE | -0.76384 | -1.042 | -0.31168 | -0.41902 | 0 |  |  | none | FALSE | 0 | 73.3076 | FALSE | FALSE | 0.0561 |  | 73.8453 | 0 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.26888 | Normal | 74.3831 | 0.84082 | Night | 202601 | 2026-01-23 | 0.84082
2026-01-23 23:28 | 74.0714 | FALSE | FALSE | -0.50769 | -0.69013 | -0.16857 | -0.22706 | 0 |  |  | none | FALSE | 0 | 73.5637 | FALSE | FALSE | 0.0669 |  | 73.9018 | 0 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.16906 | Normal | 74.24 | 1.0029 | Night | 202601 | 2026-01-23 | 1.0029
2026-01-23 23:43 | 74.0714 | FALSE | FALSE | -0.43124 | -0.58561 | -0.14864 | -0.20027 | 0 |  |  | none | FALSE | 0 | 73.6402 | FALSE | FALSE | 0.065 |  | 73.9301 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.14497 | Normal | 74.22 | 0.97468 | Night | 202601 | 2026-01-23 | 0.97468
2026-01-23 23:58 | 74.0714 | FALSE | FALSE | -0.41566 | -0.56433 | -0.16132 | -0.21731 | 0 |  |  | none | FALSE | 0 | 73.6557 | FALSE | FALSE | 0.0588 |  | 73.9442 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.14424 | Normal | 74.2327 | 0.88163 | Night | 202601 | 2026-01-23 | 0.88163
2026-01-24 00:14 | 74.0714 | FALSE | FALSE | -0.39712 | -0.53903 | -0.17104 | -0.23039 | 0 |  |  | none | FALSE | 0 | 73.6743 | FALSE | FALSE | 0.0531 |  | 73.9584 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.14204 | Normal | 74.2424 | 0.79582 | Night | 202601 | 2026-01-24 | 0.79582
2026-01-24 00:28 | 73.7888 | TRUE | FALSE | -0.11452 | -0.15545 | -0.45364 | -0.61103 | -0.2826 |  |  | none | FALSE | 1 | 73.6743 | FALSE | FALSE | 0.1082 |  | 73.9584 | 0 | -0.2826 | 0 | 0.091688 | -3.0822 | 0.14204 | Normal | 74.2424 | -1.1937 | Night | 202601 | 2026-01-24 | 1.1937
2026-01-24 00:43 | 74.0714 | TRUE | FALSE | -0.3755 | -0.50952 | -0.17768 | -0.2393 | 0.2826 |  |  | none | FALSE | 2 | 73.6959 | TRUE | FALSE | 0.1048 |  | 73.9725 | 0 | 0.2826 | 0.01413 | 0.11135 | 2.411 | 0.13829 | Normal | 74.2491 | 0.71522 | Night | 202601 | 2026-01-24 | 0.71522
2026-01-24 00:58 | 73.7888 | TRUE | FALSE | -0.092897 | -0.12605 | -0.46028 | -0.61991 | -0.2826 |  |  | none | FALSE | 3 | 73.6959 | TRUE | FALSE | 0.1743 |  | 73.9725 | 0 | -0.2826 | 0 | 0.12967 | -2.1794 | 0.13829 | Normal | 74.2491 | -1.3283 | Night | 202601 | 2026-01-24 | 1.3283
2026-01-24 01:13 | 73.7888 | FALSE | FALSE | -0.092897 | -0.12605 | -0.46028 | -0.61991 | 0 |  |  | none | FALSE | 3 | 73.6959 | FALSE | FALSE | 0.1743 |  | 73.9725 | 0 | 0 | 0 | 0.12967 | 0 | 0.13829 | Normal | 74.2491 | -1.3283 | Night | 202601 | 2026-01-24 | 1.3283
2026-01-24 01:28 | 73.7888 | FALSE | FALSE | -0.092897 | -0.12605 | -0.46028 | -0.61991 | 0 |  |  | none | FALSE | 3 | 73.6959 | FALSE | FALSE | 0.1743 |  | 73.9725 | 0 | 0 | 0 | 0.12967 | 0 | 0.13829 | Normal | 74.2491 | -1.3283 | Night | 202601 | 2026-01-24 | 1.3283
2026-01-24 01:43 | 73.7888 | FALSE | FALSE | -0.092897 | -0.12605 | -0.46028 | -0.61991 | 0 |  |  | none | FALSE | 3 | 73.6959 | FALSE | FALSE | 0.1743 |  | 73.9725 | 0 | 0 | 0 | 0.12967 | 0 | 0.13829 | Normal | 74.2491 | -1.3283 | Night | 202601 | 2026-01-24 | 1.3283
2026-01-24 01:58 | 73.7888 | FALSE | FALSE | -0.092897 | -0.12605 | -0.46028 | -0.61991 | 0 |  |  | none | FALSE | 3 | 73.6959 | FALSE | FALSE | 0.1743 |  | 73.9725 | 0 | 0 | 0 | 0.12967 | 0 | 0.13829 | Normal | 74.2491 | -1.3283 | Night | 202601 | 2026-01-24 | 1.3283
2026-01-24 02:13 | 73.7888 | FALSE | FALSE | -0.092897 | -0.12605 | -0.46028 | -0.61991 | 0 |  |  | none | FALSE | 3 | 73.6959 | FALSE | FALSE | 0.1743 |  | 73.9725 | 0 | 0 | 0 | 0.12967 | 0 | 0.13829 | Normal | 74.2491 | -1.3283 | Night | 202601 | 2026-01-24 | 1.3283
2026-01-24 02:27 | 73.5062 | TRUE | FALSE | 0.096194 | 0.13069 | -0.77987 | -1.0498 | -0.2826 | 2026-01-24 04:27 | 2026-01-24 02:27 | lower | TRUE | 4 | 73.6024 | TRUE | FALSE | 0.3423 | 2.5628 | 73.9442 | 1 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.17092 | Extreme triggered | 74.2861 | -2.5628 | Night | 202601 | 2026-01-24 | 2.5628
2026-01-24 02:42 | 73.5062 | FALSE | FALSE | 0.021855 | 0.029723 | -0.79769 | -1.0735 | 0 |  | 2026-01-24 02:27 | lower | TRUE | 4 | 73.5281 | FALSE | FALSE | 0.3694 | 2.3377 | 73.916 | 2 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.19396 | Extreme/elevated | 74.3039 | -2.1127 | Night | 202601 | 2026-01-24 | 2.1127
2026-01-24 02:58 | 73.5062 | FALSE | FALSE | -0.039654 | -0.053976 | -0.80267 | -1.0802 | 0 |  | 2026-01-24 02:27 | none | FALSE | 3 | 73.4665 | FALSE | FALSE | 0.3779 | 2.1624 | 73.8877 | 3 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21058 | Persistent | 74.3089 | -1.8117 | Night | 202601 | 2026-01-24 | 1.8117
2026-01-24 03:13 | 73.5062 | FALSE | FALSE | -0.091222 | -0.12426 | -0.79772 | -1.0736 | 0 |  | 2026-01-24 02:27 | none | FALSE | 2 | 73.415 | FALSE | FALSE | 0.3917 | 2.0192 | 73.8594 | 4 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.22224 | Persistent | 74.3039 | -1.5895 | Night | 202601 | 2026-01-24 | 1.5895
2026-01-24 03:27 | 73.5062 | FALSE | FALSE | -0.13436 | -0.18313 | -0.78434 | -1.0558 | 0 |  | 2026-01-24 02:27 | none | FALSE | 1 | 73.3718 | FALSE | FALSE | 0.4086 | 1.8983 | 73.8312 | 5 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.22968 | Persistent | 74.2905 | -1.415 | Night | 202601 | 2026-01-24 | 1.415
2026-01-24 03:42 | 73.5062 | FALSE | FALSE | -0.16989 | -0.23165 | -0.76335 | -1.0278 | 0 |  | 2026-01-24 02:27 | none | FALSE | 1 | 73.3363 | FALSE | FALSE | 0.4562 | 1.7939 | 73.8029 | 6 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.23331 | Persistent | 74.2695 | -1.2718 | Night | 202601 | 2026-01-24 | 1.2718
2026-01-24 03:57 | 73.5062 | FALSE | TRUE | -0.19815 | -0.27029 | -0.73509 | -0.99013 | 0 |  | 2026-01-24 02:27 | none | FALSE | 1 | 73.3081 | FALSE | FALSE | 0.5053 | 1.702 | 73.7747 | 7 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.23331 | Confirmed/Materialized Shift | 74.2413 | -1.1507 | Night | 202601 | 2026-01-24 | 1.1507
2026-01-24 04:12 | 73.5062 | FALSE | TRUE | -0.21914 | -0.29902 | -0.69956 | -0.94273 | 0 |  | 2026-01-24 02:27 | none | FALSE | 1 | 73.2871 | FALSE | FALSE | 0.4983 | 1.62 | 73.7464 | 8 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.22968 | Confirmed/Materialized Shift | 74.2058 | -1.0459 | Night | 202601 | 2026-01-24 | 1.0459
2026-01-24 04:27 | 73.5062 | FALSE | FALSE | -0.23252 | -0.31733 | -0.65642 | -0.88511 | 0 |  |  | none | FALSE | 1 | 73.2737 | FALSE | FALSE | 0.0922 |  | 73.7181 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.22224 | Persistence ends | 74.1626 | -0.95372 | Night | 202601 | 2026-01-24 | 0.95372
2026-01-24 04:42 | 73.2236 | FALSE | FALSE | -0.011746 | -0.016044 | -0.91607 | -1.2356 | -0.2826 |  |  | none | FALSE | 1 | 73.2119 | FALSE | FALSE | 0.1585 |  | 73.6758 | 0 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.23195 | Normal | 74.1397 | -1.9494 | Night | 202601 | 2026-01-24 | 1.9494
2026-01-24 04:57 | 73.2236 | FALSE | FALSE | -0.056847 | -0.077695 | -0.87639 | -1.1827 | 0 |  |  | none | FALSE | 0 | 73.1668 | FALSE | FALSE | 0.1171 |  | 73.6334 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.23331 | Normal | 74.1 | -1.7563 | Night | 202601 | 2026-01-24 | 1.7563
2026-01-24 05:12 | 73.2236 | FALSE | FALSE | -0.085523 | -0.11693 | -0.82028 | -1.1078 | 0 |  |  | none | FALSE | 0 | 73.1381 | FALSE | FALSE | 0.1082 |  | 73.591 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.22645 | Normal | 74.0439 | -1.6223 | Night | 202601 | 2026-01-24 | 1.6223
2026-01-24 05:27 | 73.2236 | FALSE | FALSE | -0.13198 | -0.18057 | -0.81022 | -1.0944 | 0 |  |  | none | FALSE | 0 | 73.0916 | FALSE | FALSE | 0.096 |  | 73.5627 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.23555 | Normal | 74.0338 | -1.4397 | Night | 202601 | 2026-01-24 | 1.4397
2026-01-24 05:42 | 73.2236 | FALSE | FALSE | -0.13234 | -0.18107 | -0.7258 | -0.98149 | 0 |  |  | none | FALSE | 0 | 73.0913 | FALSE | FALSE | 0.0922 |  | 73.5203 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.21454 | Normal | 73.9494 | -1.3831 | Night | 202601 | 2026-01-24 | 1.3831
2026-01-24 05:57 | 73.2236 | FALSE | FALSE | -0.1606 | -0.21982 | -0.69754 | -0.94363 | 0 |  |  | none | FALSE | 0 | 73.063 | FALSE | FALSE | 0.0834 |  | 73.4921 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21454 | Normal | 73.9211 | -1.2514 | Night | 202601 | 2026-01-24 | 1.2514
2026-01-24 06:12 | 73.2236 | FALSE | FALSE | -0.18095 | -0.24774 | -0.66137 | -0.89514 | 0 |  |  | none | FALSE | 0 | 73.0426 | FALSE | FALSE | 0.076 |  | 73.4638 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21058 | Normal | 73.885 | -1.1407 | Night | 202601 | 2026-01-24 | 1.1407
2026-01-24 06:26 | 73.2236 | FALSE | FALSE | -0.19293 | -0.26418 | -0.61683 | -0.83536 | 0 |  |  | none | FALSE | 0 | 73.0307 | FALSE | FALSE | 0.0698 |  | 73.4356 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.20244 | Normal | 73.8404 | -1.047 | Night | 202601 | 2026-01-24 | 1.047
2026-01-24 06:41 | 72.941 | TRUE | FALSE | 0.026035 | 0.03568 | -0.87829 | -1.1898 | -0.2826 | 2026-01-24 08:15 | 2026-01-24 06:41 | lower | TRUE | 1 | 72.967 | FALSE | FALSE | 0.2272 | 2.1222 | 73.3932 | 1 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.21306 | Extreme triggered | 73.8193 | -2.1222 | Night | 202601 | 2026-01-24 | 2.1222
2026-01-24 06:56 | 72.941 | FALSE | FALSE | -0.019304 | -0.026473 | -0.83884 | -1.137 | 0 |  | 2026-01-24 06:41 | none | FALSE | 1 | 72.9217 | FALSE | FALSE | 0.2702 | 2.0161 | 73.3508 | 2 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.21454 | Extreme/elevated | 73.7798 | -1.91 | Night | 202601 | 2026-01-24 | 1.91
2026-01-24 07:11 | 72.941 | FALSE | FALSE | -0.046739 | -0.064119 | -0.7815 | -1.0601 | 0 |  | 2026-01-24 06:41 | none | FALSE | 1 | 72.8943 | FALSE | FALSE | 0.3183 | 1.9355 | 73.3084 | 3 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.20706 | Persistent | 73.7225 | -1.7743 | Night | 202601 | 2026-01-24 | 1.7743
2026-01-24 07:26 | 72.941 | FALSE | FALSE | -0.094825 | -0.13017 | -0.77306 | -1.0487 | 0 |  | 2026-01-24 06:41 | none | FALSE | 1 | 72.8462 | FALSE | FALSE | 0.3613 | 1.8424 | 73.2801 | 4 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21697 | Persistent | 73.7141 | -1.563 | Day | 202601 | 2026-01-24 | 1.563
2026-01-24 07:30 | 72.941 | FALSE | FALSE | -0.13456 | -0.18481 | -0.75628 | -1.0262 | 0 |  | 2026-01-24 06:41 | none | FALSE | 1 | 72.8064 | FALSE | FALSE | 0.4073 | 1.7531 | 73.2519 | 5 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22271 | Persistent | 73.6973 | -1.3958 | Day | 202601 | 2026-01-24 | 1.3958
2026-01-24 07:45 | 72.941 | FALSE | FALSE | -0.16658 | -0.22889 | -0.73178 | -0.99328 | 0 |  | 2026-01-24 06:41 | none | FALSE | 1 | 72.7744 | FALSE | FALSE | 0.4553 | 1.6706 | 73.2236 | 6 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22459 | Persistent | 73.6728 | -1.2583 | Day | 202601 | 2026-01-24 | 1.2583
2026-01-24 08:00 | 72.941 | FALSE | TRUE | -0.19108 | -0.26265 | -0.69976 | -0.95023 | 0 |  | 2026-01-24 06:41 | none | FALSE | 1 | 72.7499 | FALSE | FALSE | 0.5047 | 1.5951 | 73.1953 | 7 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22271 | Confirmed/Materialized Shift | 73.6408 | -1.142 | Day | 202601 | 2026-01-24 | 1.142
2026-01-24 08:15 | 73.2236 | TRUE | FALSE | -0.46355 | -0.6371 | -0.37877 | -0.51462 | 0.2826 |  |  | none | FALSE | 2 | 72.76 | TRUE | FALSE | 0.0706 |  | 73.1812 | 0 | 0.2826 | -0.01413 | 0.11135 | 2.6647 | 0.21058 | Persistence ends | 73.6024 | 0.2013 | Day | 202601 | 2026-01-24 | 0.2013
2026-01-24 08:30 | 73.2236 | FALSE | FALSE | -0.44982 | -0.6181 | -0.33678 | -0.45782 | 0 |  |  | none | FALSE | 2 | 72.7738 | FALSE | FALSE | 0.0763 |  | 73.1671 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.19665 | Normal | 73.5604 | 0.28742 | Day | 202601 | 2026-01-24 | 0.28742
2026-01-24 08:45 | 73.5062 | TRUE | FALSE | -0.73242 | -1.0064 | -0.054176 | -0.073648 | 0.2826 |  |  | none | FALSE | 3 | 72.7738 | TRUE | FALSE | 0.2007 |  | 73.1671 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.19665 | Normal | 73.5604 | 1.7245 | Day | 202601 | 2026-01-24 | 1.7245
2026-01-24 08:45 | 73.5062 | FALSE | FALSE | -0.73242 | -1.0064 | -0.054176 | -0.073648 | 0 |  |  | none | FALSE | 2 | 72.7738 | FALSE | FALSE | 0.1721 |  | 73.1671 | 0 | 0 | 0 | 0.12967 | 0 | 0.19665 | Normal | 73.5604 | 1.7245 | Day | 202601 | 2026-01-24 | 1.7245
2026-01-24 09:00 | 73.7888 | FALSE | FALSE | -1.0669 | -1.4672 | 0.14824 | 0.2013 | 0.2826 | 2026-01-24 09:23 | 2026-01-24 09:00 | upper | TRUE | 2 | 72.7219 | FALSE | FALSE | 0.2906 | 2.6454 | 73.1812 | 1 | 0.2826 | 0.01413 | 0.14424 | 1.8612 | 0.22968 | Extreme triggered | 73.6406 | 2.6454 | Day | 202601 | 2026-01-24 | 2.6454
2026-01-24 09:05 | 74.0714 | FALSE | FALSE | -1.456 | -2.0051 | 0.23961 | 0.32454 | 0.2826 |  | 2026-01-24 09:00 | upper | TRUE | 2 | 72.6154 | FALSE | FALSE | 0.3573 | 2.7167 | 73.2236 | 2 | 0.2826 | 0.04239 | 0.13829 | 1.737 | 0.30409 | Extreme/elevated | 73.8318 | 2.788 | Day | 202601 | 2026-01-24 | 2.788
2026-01-24 09:08 | 74.0714 | FALSE | FALSE | -1.5221 | -2.098 | 0.088721 | 0.11992 | 0 |  | 2026-01-24 09:00 | upper | TRUE | 2 | 72.5493 | FALSE | TRUE | 0.3784 | 2.5603 | 73.266 | 3 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.35834 | Persistent | 73.9827 | 2.2476 | Day | 202601 | 2026-01-24 | 2.2476
2026-01-24 09:23 | 73.5062 | TRUE | FALSE | -0.95035 | -1.3098 | -0.49819 | -0.67319 | -0.5652 |  |  | none | FALSE | 3 | 72.5558 | TRUE | FALSE | 0.1273 |  | 73.2801 | 0 | -0.5652 | 0.01413 | 0.19396 | -2.9869 | 0.36214 | Persistence ends | 74.0044 | 0.62429 | Day | 202601 | 2026-01-24 | 0.62429
2026-01-24 09:39 | 73.2236 | FALSE | FALSE | -0.66775 | -0.92033 | -0.78079 | -1.0551 | -0.2826 |  |  | none | FALSE | 3 | 72.5558 | FALSE | FALSE | 0.0961 |  | 73.2801 | 0 | -0.2826 | 0 | 0.20502 | -1.3784 | 0.36214 | Normal | 74.0044 | -0.15607 | Day | 202601 | 2026-01-24 | 0.15607
2026-01-24 09:44 | 73.2236 | FALSE | FALSE | -0.66775 | -0.92033 | -0.78079 | -1.0551 | 0 |  |  | none | FALSE | 3 | 72.5558 | FALSE | FALSE | 0.0961 |  | 73.2801 | 0 | 0 | 0 | 0.20502 | 0 | 0.36214 | Normal | 74.0044 | -0.15607 | Day | 202601 | 2026-01-24 | 0.15607
2026-01-24 09:59 | 72.941 | FALSE | FALSE | -0.41479 | -0.57191 | -1.0648 | -1.4388 | -0.2826 |  |  | none | FALSE | 2 | 72.5262 | FALSE | FALSE | 0.1157 |  | 73.266 | 0 | -0.2826 | -0.01413 | 0.21454 | -1.2514 | 0.36989 | Normal | 74.0058 | -0.87862 | Day | 202601 | 2026-01-24 | 0.87862
2026-01-24 10:14 | 72.6584 | FALSE | FALSE | -0.20886 | -0.28829 | -1.3675 | -1.8474 | -0.2826 |  |  | none | FALSE | 2 | 72.4495 | FALSE | FALSE | 0.1551 |  | 73.2377 | 0 | -0.2826 | -0.02826 | 0.22271 | -1.142 | 0.3941 | Normal | 74.0259 | -1.47 | Day | 202601 | 2026-01-24 | 1.47
2026-01-24 10:30 | 72.3758 | FALSE | FALSE | -0.057982 | -0.080177 | -1.6971 | -2.2911 | -0.2826 |  |  | none | FALSE | 1 | 72.3178 | FALSE | FALSE | 0.1531 |  | 73.1953 | 0 | -0.2826 | -0.04239 | 0.22968 | -1.0459 | 0.43876 | Normal | 74.0729 | -1.8679 | Day | 202601 | 2026-01-24 | 1.8679
2026-01-24 10:44 | 72.3758 | FALSE | FALSE | -0.15448 | -0.2139 | -1.737 | -2.3438 | 0 |  |  | none | FALSE | 1 | 72.2213 | FALSE | FALSE | 0.1401 |  | 73.1671 | 0 | 0 | -0.02826 | 0.22271 | 0.12689 | 0.47288 | Normal | 74.1128 | -1.6733 | Day | 202601 | 2026-01-24 | 1.6733
2026-01-24 10:59 | 72.6584 | FALSE | FALSE | -0.47361 | -0.65611 | -1.4627 | -1.9734 | 0.2826 |  |  | none | FALSE | 1 | 72.1848 | FALSE | FALSE | 0.0967 |  | 73.153 | 0 | 0.2826 | -0.01413 | 0.23331 | 1.2718 | 0.48408 | Normal | 74.1211 | -1.0216 | Day | 202601 | 2026-01-24 | 1.0216
2026-01-24 11:14 | 72.6584 | FALSE | FALSE | -0.50879 | -0.70518 | -1.4696 | -1.9826 | 0 |  |  | none | FALSE | 1 | 72.1496 | FALSE | FALSE | 0.0933 |  | 73.1388 | 0 | 0 | -0.01413 | 0.23331 | 0.060564 | 0.4946 | Normal | 74.128 | -0.97132 | Day | 202601 | 2026-01-24 | 0.97132
2026-01-24 11:29 | 72.941 | FALSE | FALSE | -0.79139 | -1.0969 | -1.187 | -1.6013 | 0.2826 |  |  | none | FALSE | 1 | 72.1496 | FALSE | FALSE | 0.0552 |  | 73.1388 | 0 | 0.2826 | 0 | 0.24258 | 1.165 | 0.4946 | Normal | 74.128 | -0.39996 | Day | 202601 | 2026-01-24 | 0.39996
2026-01-24 11:44 | 72.941 | FALSE | FALSE | -0.79139 | -1.0969 | -1.187 | -1.6013 | 0 |  |  | none | FALSE | 0 | 72.1496 | FALSE | FALSE | 0.0267 |  | 73.1388 | 0 | 0 | 0 | 0.24258 | 0 | 0.4946 | Normal | 74.128 | -0.39996 | Day | 202601 | 2026-01-24 | 0.39996
2026-01-24 11:59 | 72.941 | FALSE | FALSE | -0.79139 | -1.0969 | -1.187 | -1.6013 | 0 |  |  | none | FALSE | 0 | 72.1496 | FALSE | FALSE | 0.0267 |  | 73.1388 | 0 | 0 | 0 | 0.24258 | 0 | 0.4946 | Normal | 74.128 | -0.39996 | Day | 202601 | 2026-01-24 | 0.39996
2026-01-24 12:14 | 72.941 | FALSE | FALSE | -0.79139 | -1.0969 | -1.187 | -1.6013 | 0 |  |  | none | FALSE | 0 | 72.1496 | FALSE | FALSE | 0.0267 |  | 73.1388 | 0 | 0 | 0 | 0.24258 | 0 | 0.4946 | Normal | 74.128 | -0.39996 | Day | 202601 | 2026-01-24 | 0.39996
2026-01-24 12:29 | 73.2236 | FALSE | FALSE | -1.074 | -1.4886 | -0.90443 | -1.2201 | 0.2826 |  |  | none | FALSE | 0 | 72.1496 | FALSE | FALSE | 0.0114 |  | 73.1388 | 0 | 0.2826 | 0 | 0.24258 | 1.165 | 0.4946 | Normal | 74.128 | 0.17141 | Day | 202601 | 2026-01-24 | 0.17141
2026-01-24 12:43 | 73.2236 | FALSE | FALSE | -1.074 | -1.4886 | -0.90443 | -1.2201 | 0 |  |  | none | FALSE | 0 | 72.1496 | FALSE | FALSE | 0.0114 |  | 73.1388 | 0 | 0 | 0 | 0.24258 | 0 | 0.4946 | Normal | 74.128 | 0.17141 | Day | 202601 | 2026-01-24 | 0.17141
2026-01-24 12:58 | 72.941 | FALSE | FALSE | -0.80768 | -1.1197 | -1.1468 | -1.5479 | -0.2826 |  |  | none | FALSE | 0 | 72.1333 | FALSE | FALSE | 0.0231 |  | 73.1106 | 0 | -0.2826 | -0.02826 | 0.24084 | -1.056 | 0.48862 | Normal | 74.0878 | -0.34702 | Day | 202601 | 2026-01-24 | 0.34702
2026-01-24 13:14 | 72.941 | FALSE | FALSE | -0.82033 | -1.1374 | -1.1029 | -1.4896 | 0 |  |  | none | FALSE | 0 | 72.1207 | FALSE | FALSE | 0.0196 |  | 73.0823 | 0 | 0 | -0.02826 | 0.24084 | 0.11734 | 0.48081 | Normal | 74.0439 | -0.29388 | Day | 202601 | 2026-01-24 | 0.29388
2026-01-24 13:29 | 72.941 | FALSE | FALSE | -0.80457 | -1.1153 | -1.0024 | -1.3556 | 0 |  |  | none | FALSE | 0 | 72.1364 | FALSE | FALSE | 0.0146 |  | 73.0399 | 0 | 0 | -0.04239 | 0.22968 | 0.18456 | 0.45174 | Normal | 73.9434 | -0.21895 | Day | 202601 | 2026-01-24 | 0.21895
2026-01-24 13:43 | 72.941 | FALSE | FALSE | -0.71978 | -0.99663 | -0.80456 | -1.091 | 0 |  |  | none | FALSE | 0 | 72.2212 | FALSE | FALSE | 0.0074 |  | 72.9834 | 0 | 0 | -0.05652 | 0.21697 | 0.26049 | 0.38108 | Normal | 73.7456 | -0.11124 | Day | 202601 | 2026-01-24 | 0.11124
2026-01-24 13:58 | 72.941 | FALSE | FALSE | -0.57859 | -0.79957 | -0.55033 | -0.74883 | 0 |  |  | none | FALSE | 0 | 72.3624 | FALSE | FALSE | 0.0033 |  | 72.9269 | 0 | 0 | -0.05652 | 0.21697 | 0.26049 | 0.28223 | Normal | 73.4913 | 0.050066 | Day | 202601 | 2026-01-24 | 0.050066
2026-01-24 14:13 | 73.2236 | FALSE | FALSE | -0.82627 | -1.1413 | -0.20455 | -0.27857 | 0.2826 |  |  | none | FALSE | 0 | 72.3973 | FALSE | FALSE | 0.0804 |  | 72.9127 | 0 | 0.2826 | -0.01413 | 0.19396 | 1.5299 | 0.25771 | Normal | 73.4282 | 1.2063 | Day | 202601 | 2026-01-24 | 1.2063
2026-01-24 14:28 | 73.2236 | FALSE | FALSE | -0.82627 | -1.1413 | -0.20455 | -0.27857 | 0 |  |  | none | FALSE | 0 | 72.3973 | FALSE | FALSE | 0.0804 |  | 72.9127 | 0 | 0 | 0 | 0.18338 | 0 | 0.25771 | Normal | 73.4282 | 1.2063 | Day | 202601 | 2026-01-24 | 1.2063
2026-01-24 14:43 | 73.2236 | FALSE | FALSE | -0.82627 | -1.1413 | -0.20455 | -0.27857 | 0 |  |  | none | FALSE | 0 | 72.3973 | FALSE | FALSE | 0.0804 |  | 72.9127 | 0 | 0 | 0 | 0.18338 | 0 | 0.25771 | Normal | 73.4282 | 1.2063 | Day | 202601 | 2026-01-24 | 1.2063
2026-01-24 14:58 | 73.2236 | FALSE | FALSE | -0.83057 | -1.1473 | -0.23711 | -0.32277 | 0 |  |  | none | FALSE | 0 | 72.393 | FALSE | FALSE | 0.0741 |  | 72.9269 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.26692 | Normal | 73.4607 | 1.1117 | Day | 202601 | 2026-01-24 | 1.1117
2026-01-24 15:13 | 73.2236 | FALSE | FALSE | -0.80231 | -1.1078 | -0.26537 | -0.3611 | 0 |  |  | none | FALSE | 0 | 72.4213 | FALSE | FALSE | 0.0671 |  | 72.9551 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.26692 | Normal | 73.489 | 1.0058 | Day | 202601 | 2026-01-24 | 1.0058
2026-01-24 15:28 | 72.941 | FALSE | FALSE | -0.41696 | -0.57493 | -0.50174 | -0.68318 | -0.2826 |  |  | none | FALSE | 0 | 72.524 | FALSE | FALSE | 0.0123 |  | 72.9834 | 0 | -0.2826 | 0.02826 | 0.15614 | -1.9909 | 0.22968 | Normal | 73.4427 | -0.18456 | Day | 202601 | 2026-01-24 | 0.18456
2026-01-24 15:43 | 72.941 | FALSE | FALSE | -0.29032 | -0.39962 | -0.43162 | -0.58826 | 0 |  |  | none | FALSE | 0 | 72.6507 | FALSE | FALSE | 0.0261 |  | 73.0117 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.18049 | Normal | 73.3726 | -0.39144 | Day | 202601 | 2026-01-24 | 0.39144
2026-01-24 15:58 | 73.2236 | FALSE | FALSE | -0.51554 | -0.70906 | -0.14816 | -0.20193 | 0.2826 |  |  | none | FALSE | 0 | 72.7081 | FALSE | FALSE | 0.0738 |  | 73.0399 | 0 | 0.2826 | 0.02826 | 0.15614 | 1.6289 | 0.16593 | Normal | 73.3718 | 1.1071 | Day | 202601 | 2026-01-24 | 1.1071
2026-01-24 16:13 | 73.2236 | FALSE | FALSE | -0.44392 | -0.60995 | -0.13306 | -0.18139 | 0 |  |  | none | FALSE | 0 | 72.7797 | FALSE | FALSE | 0.0718 |  | 73.0682 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.14424 | Normal | 73.3567 | 1.0775 | Day | 202601 | 2026-01-24 | 1.0775
2026-01-24 16:28 | 73.2236 | FALSE | FALSE | -0.43124 | -0.59243 | -0.14864 | -0.20259 | 0 |  |  | none | FALSE | 0 | 72.7924 | FALSE | FALSE | 0.065 |  | 73.0823 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.14497 | Normal | 73.3722 | 0.97468 | Day | 202601 | 2026-01-24 | 0.97468
2026-01-24 16:42 | 73.2236 | FALSE | FALSE | -0.41566 | -0.5709 | -0.16132 | -0.21982 | 0 |  |  | none | FALSE | 0 | 72.8079 | FALSE | FALSE | 0.0588 |  | 73.0964 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.14424 | Normal | 73.3849 | 0.88163 | Day | 202601 | 2026-01-24 | 0.88163
2026-01-24 16:57 | 72.941 | FALSE | FALSE | -0.13306 | -0.18275 | -0.44392 | -0.60492 | -0.2826 |  |  | none | FALSE | 0 | 72.8079 | FALSE | FALSE | 0.0718 |  | 73.0964 | 0 | -0.2826 | 0 | 0.15881 | -1.7795 | 0.14424 | Normal | 73.3849 | -1.0775 | Day | 202601 | 2026-01-24 | 1.0775
2026-01-24 17:12 | 72.941 | FALSE | FALSE | -0.13306 | -0.18275 | -0.44392 | -0.60492 | 0 |  |  | none | FALSE | 0 | 72.8079 | FALSE | FALSE | 0.0718 |  | 73.0964 | 0 | 0 | 0 | 0.15881 | 0 | 0.14424 | Normal | 73.3849 | -1.0775 | Day | 202601 | 2026-01-24 | 1.0775
2026-01-24 17:27 | 72.6584 | FALSE | FALSE | 0.067934 | 0.093411 | -0.75161 | -1.0238 | -0.2826 | 2026-01-24 17:46 | 2026-01-24 17:27 | lower | TRUE | 0 | 72.7263 | FALSE | FALSE | 0.217 | 2.3975 | 73.0682 | 1 | -0.2826 | -0.02826 | 0.15614 | -1.6289 | 0.17092 | Extreme triggered | 73.41 | -2.3975 | Day | 202601 | 2026-01-24 | 2.3975
2026-01-24 17:30 | 72.6584 | FALSE | FALSE | 0.0023623 | 0.0032512 | -0.76066 | -1.036 | 0 |  | 2026-01-24 17:27 | lower | TRUE | 0 | 72.6608 | FALSE | FALSE | 0.2484 | 2.205 | 73.0399 | 2 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.18957 | Extreme/elevated | 73.4191 | -2.0125 | Day | 202601 | 2026-01-24 | 2.0125
2026-01-24 17:31 | 72.6584 | FALSE | FALSE | -0.046739 | -0.064369 | -0.7815 | -1.0641 | 0 |  | 2026-01-24 17:27 | none | FALSE | 0 | 72.6117 | FALSE | FALSE | 0.2897 | 2.0614 | 73.0258 | 3 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.20706 | Persistent | 73.4399 | -1.7743 | Day | 202601 | 2026-01-24 | 1.7743
2026-01-24 17:46 | 73.2236 | TRUE | FALSE | -0.60485 | -0.83292 | -0.23747 | -0.32327 | 0.5652 |  |  | none | FALSE | 1 | 72.6187 | FALSE | FALSE | 0.0867 |  | 73.0399 | 0 | 0.5652 | 0.01413 | 0.19396 | 2.8412 | 0.21058 | Persistence ends | 73.4611 | 0.8723 | Day | 202601 | 2026-01-24 | 0.8723
2026-01-24 18:01 | 73.7888 | TRUE | FALSE | -1.2411 | -1.7108 | 0.17187 | 0.23347 | 0.5652 | 2026-01-24 21:29 | 2026-01-24 18:01 | upper | TRUE | 2 | 72.5477 | TRUE | FALSE | 0.2905 | 2.643 | 73.0823 | 1 | 0.5652 | 0.04239 | 0.22968 | 2.2763 | 0.26731 | Extreme triggered | 73.6169 | 2.643 | Night | 202601 | 2026-01-24 | 2.643
2026-01-24 18:16 | 74.0714 | FALSE | FALSE | -1.6212 | -2.2376 | 0.24401 | 0.33051 | 0.2826 |  | 2026-01-24 18:01 | upper | TRUE | 2 | 72.4502 | FALSE | FALSE | 0.352 | 2.6759 | 73.1388 | 2 | 0.2826 | 0.05652 | 0.23555 | 0.9598 | 0.34429 | Extreme/elevated | 73.8274 | 2.7087 | Night | 202601 | 2026-01-24 | 2.7087
2026-01-24 18:30 | 74.0714 | FALSE | FALSE | -1.6733 | -2.3112 | 0.078853 | 0.10657 | 0 |  | 2026-01-24 18:01 | upper | TRUE | 2 | 72.3981 | FALSE | TRUE | 0.3751 | 2.5165 | 73.1953 | 3 | 0 | 0.05652 | 0.23555 | -0.23995 | 0.3986 | Persistent | 73.9925 | 2.1978 | Night | 202601 | 2026-01-24 | 2.1978
2026-01-24 18:45 | 74.0714 | FALSE | FALSE | -1.7221 | -2.3803 | -0.054801 | -0.073929 | 0 |  | 2026-01-24 18:01 | none | FALSE | 2 | 72.3493 | FALSE | FALSE | 0.4108 | 2.3565 | 73.2377 | 4 | 0 | 0.04239 | 0.22968 | -0.18456 | 0.44424 | Persistent | 74.1262 | 1.8766 | Night | 202601 | 2026-01-24 | 1.8766
2026-01-24 19:00 | 74.3522 | FALSE | FALSE | -2.0766 | -2.8731 | 0.039505 | 0.053161 | 0.2808 |  | 2026-01-24 18:01 | upper | TRUE | 2 | 72.2756 | FALSE | TRUE | 0.4814 | 2.3007 | 73.2942 | 5 | 0.2808 | 0.05643 | 0.23546 | 0.9529 | 0.50927 | Persistent | 74.3127 | 2.0776 | Night | 202601 | 2026-01-24 | 2.0776
2026-01-24 19:15 | 74.6348 | FALSE | FALSE | -2.4507 | -3.395 | 0.089494 | 0.12005 | 0.2826 |  | 2026-01-24 18:01 | upper | TRUE | 2 | 72.1841 | FALSE | TRUE | 0.5434 | 2.2759 | 73.3647 | 6 | 0.2826 | 0.07056 | 0.24032 | 0.88231 | 0.59029 | Persistent | 74.5453 | 2.1516 | Night | 202601 | 2026-01-24 | 2.1516
2026-01-24 19:29 | 74.6348 | FALSE | TRUE | -2.5065 | -3.4751 | -0.10747 | -0.14379 | 0 |  | 2026-01-24 18:01 | none | FALSE | 2 | 72.1283 | FALSE | FALSE | 0.5795 | 2.213 | 73.4353 | 7 | 0 | 0.07056 | 0.24032 | -0.2936 | 0.6535 | Confirmed/Materialized Shift | 74.7423 | 1.8355 | Night | 202601 | 2026-01-24 | 1.8355
2026-01-24 19:44 | 74.6348 | FALSE | TRUE | -2.5364 | -3.5179 | -0.27843 | -0.37167 | 0 |  | 2026-01-24 18:01 | none | FALSE | 2 | 72.0984 | FALSE | FALSE | 0.5641 | 2.1369 | 73.5058 | 8 | 0 | 0.07056 | 0.24032 | -0.2936 | 0.7037 | Confirmed/Materialized Shift | 74.9132 | 1.6043 | Night | 202601 | 2026-01-24 | 1.6043
2026-01-24 19:59 | 74.6348 | FALSE | TRUE | -2.5111 | -3.4817 | -0.4226 | -0.56304 | 0 |  | 2026-01-24 18:01 | none | FALSE | 2 | 72.1237 | FALSE | FALSE | 0.5521 | 2.0577 | 73.5905 | 9 | 0 | 0.08469 | 0.22637 | -0.37412 | 0.73344 | Confirmed/Materialized Shift | 75.0574 | 1.4238 | Night | 202601 | 2026-01-24 | 1.4238
2026-01-24 20:14 | 74.9174 | FALSE | TRUE | -2.7748 | -3.8463 | -0.3187 | -0.42359 | 0.2826 |  | 2026-01-24 18:01 | none | FALSE | 1 | 72.1426 | FALSE | FALSE | 0.5344 | 2.0107 | 73.6894 | 10 | 0.2826 | 0.09882 | 0.2296 | 0.80043 | 0.77337 | Confirmed/Materialized Shift | 75.2361 | 1.5879 | Night | 202601 | 2026-01-24 | 1.5879
2026-01-24 20:29 | 74.9174 | FALSE | TRUE | -2.7663 | -3.8341 | -0.47962 | -0.63612 | 0 |  | 2026-01-24 18:01 | none | FALSE | 0 | 72.1511 | FALSE | FALSE | 0.4939 | 1.956 | 73.774 | 11 | 0 | 0.08469 | 0.22637 | -0.37412 | 0.81149 | Confirmed/Materialized Shift | 75.397 | 1.409 | Night | 202601 | 2026-01-24 | 1.409
2026-01-24 20:44 | 74.9174 | FALSE | TRUE | -2.7365 | -3.7912 | -0.61921 | -0.81975 | 0 |  | 2026-01-24 18:01 | none | FALSE | 0 | 72.1809 | FALSE | FALSE | 0.4841 | 1.8982 | 73.8587 | 12 | 0 | 0.08469 | 0.22637 | -0.37412 | 0.83894 | Confirmed/Materialized Shift | 75.5366 | 1.2619 | Night | 202601 | 2026-01-24 | 1.2619
2026-01-24 20:59 | 74.9174 | FALSE | TRUE | -2.6875 | -3.7207 | -0.73953 | -0.97748 | 0 |  | 2026-01-24 18:01 | none | FALSE | 0 | 72.2299 | FALSE | FALSE | 0.4758 | 1.8396 | 73.9434 | 13 | 0 | 0.08469 | 0.22637 | -0.37412 | 0.85675 | Confirmed/Materialized Shift | 75.6569 | 1.1368 | Night | 202601 | 2026-01-24 | 1.1368
2026-01-24 21:14 | 74.9174 | FALSE | TRUE | -2.6203 | -3.6244 | -0.84176 | -1.1111 | 0 |  | 2026-01-24 18:01 | none | FALSE | 0 | 72.2971 | FALSE | FALSE | 0.4685 | 1.7816 | 74.0281 | 14 | 0 | 0.08469 | 0.22637 | -0.37412 | 0.86553 | Confirmed/Materialized Shift | 75.7592 | 1.0275 | Night | 202601 | 2026-01-24 | 1.0275
2026-01-24 21:29 | 74.9174 | FALSE | FALSE | -2.4855 | -3.4315 | -0.90456 | -1.193 | 0 |  |  | none | FALSE | 0 | 72.4319 | FALSE | FALSE | 0.0622 |  | 74.1269 | 0 | 0 | 0.09882 | 0.2105 | -0.46945 | 0.84751 | Persistence ends | 75.822 | 0.93269 | Night | 202601 | 2026-01-24 | 0.93269
2026-01-24 21:44 | 74.9174 | FALSE | FALSE | -2.3249 | -3.2026 | -0.94158 | -1.2412 | 0 |  |  | none | FALSE | 0 | 72.5925 | FALSE | FALSE | 0.0565 |  | 74.2258 | 0 | 0 | 0.09882 | 0.2105 | -0.46945 | 0.81662 | Normal | 75.859 | 0.84697 | Night | 202601 | 2026-01-24 | 0.84697
2026-01-24 21:59 | 74.9174 | FALSE | FALSE | -2.061 | -2.8289 | -0.90362 | -1.1918 | 0 |  |  | none | FALSE | 0 | 72.8564 | FALSE | FALSE | 0.0521 |  | 74.3387 | 0 | 0 | 0.11295 | 0.19224 | -0.58754 | 0.74116 | Normal | 75.821 | 0.7808 | Night | 202601 | 2026-01-24 | 0.7808
2026-01-24 22:14 | 74.9174 | FALSE | FALSE | -1.7384 | -2.3756 | -0.80691 | -1.0656 | 0 |  |  | none | FALSE | 0 | 73.179 | FALSE | FALSE | 0.0488 |  | 74.4517 | 0 | 0 | 0.11295 | 0.19224 | -0.58754 | 0.63633 | Normal | 75.7243 | 0.73193 | Night | 202601 | 2026-01-24 | 0.73193
2026-01-24 22:28 | 74.9174 | FALSE | FALSE | -1.3196 | -1.7929 | -0.61395 | -0.81284 | 0 |  |  | none | FALSE | 0 | 73.5978 | FALSE | FALSE | 0.0487 |  | 74.5646 | 0 | 0 | 0.11295 | 0.19224 | -0.58754 | 0.48338 | Normal | 75.5314 | 0.72987 | Night | 202601 | 2026-01-24 | 0.72987
2026-01-24 22:43 | 74.9174 | FALSE | FALSE | -1.0111 | -1.3681 | -0.47488 | -0.62987 | 0 |  |  | none | FALSE | 0 | 73.9063 | FALSE | FALSE | 0.0481 |  | 74.6493 | 0 | 0 | 0.08469 | 0.16132 | -0.52499 | 0.37149 | Normal | 75.3923 | 0.72171 | Night | 202601 | 2026-01-24 | 0.72171
2026-01-24 22:59 | 74.9174 | FALSE | FALSE | -0.84245 | -1.1373 | -0.41909 | -0.55629 | 0 |  |  | none | FALSE | 0 | 74.075 | FALSE | FALSE | 0.0447 |  | 74.7057 | 0 | 0 | 0.05643 | 0.11579 | -0.48734 | 0.31538 | Normal | 75.3365 | 0.67118 | Night | 202601 | 2026-01-24 | 0.67118
2026-01-24 23:14 | 74.9174 | FALSE | FALSE | -0.73068 | -0.98492 | -0.39192 | -0.52042 | 0 |  |  | none | FALSE | 0 | 74.1867 | FALSE | FALSE | 0.0402 |  | 74.748 | 0 | 0 | 0.0423 | 0.10331 | -0.40945 | 0.28065 | Normal | 75.3093 | 0.60352 | Night | 202601 | 2026-01-24 | 0.60352
2026-01-24 23:28 | 74.9174 | FALSE | FALSE | -0.59311 | -0.79801 | -0.33895 | -0.4504 | 0 |  |  | none | FALSE | 0 | 74.3243 | FALSE | FALSE | 0.0364 |  | 74.7903 | 0 | 0 | 0.0423 | 0.10331 | -0.40945 | 0.23302 | Normal | 75.2564 | 0.54537 | Night | 202601 | 2026-01-24 | 0.54537
2026-01-24 23:43 | 74.9174 | FALSE | FALSE | -0.40765 | -0.5471 | -0.23809 | -0.31679 | 0 |  |  | none | FALSE | 0 | 74.5098 | FALSE | FALSE | 0.035 |  | 74.8326 | 0 | 0 | 0.0423 | 0.10331 | -0.40945 | 0.16143 | Normal | 75.1555 | 0.52517 | Night | 202601 | 2026-01-24 | 0.52517
2026-01-24 23:58 | 74.9174 | FALSE | FALSE | -0.28847 | -0.38654 | -0.17543 | -0.23362 | 0 |  |  | none | FALSE | 0 | 74.6289 | FALSE | FALSE | 0.0325 |  | 74.8609 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.11598 | Normal | 75.0928 | 0.48734 | Night | 202601 | 2026-01-24 | 0.48734
2026-01-25 00:13 | 74.9174 | FALSE | FALSE | -0.24945 | -0.33408 | -0.16467 | -0.21932 | 0 |  |  | none | FALSE | 0 | 74.668 | FALSE | FALSE | 0.0273 |  | 74.875 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.10353 | Normal | 75.0821 | 0.40945 | Night | 202601 | 2026-01-25 | 0.40945
2026-01-25 00:28 | 74.9174 | FALSE | FALSE | -0.20222 | -0.27066 | -0.1457 | -0.19411 | 0 |  |  | none | FALSE | 0 | 74.7152 | FALSE | FALSE | 0.0217 |  | 74.8891 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.086982 | Normal | 75.0631 | 0.32489 | Night | 202601 | 2026-01-25 | 0.32489
2026-01-25 00:43 | 74.9174 | FALSE | FALSE | -0.14051 | -0.18791 | -0.11225 | -0.14961 | 0 |  |  | none | FALSE | 0 | 74.7769 | FALSE | FALSE | 0.0149 |  | 74.9033 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.063191 | Normal | 75.0297 | 0.22361 | Night | 202601 | 2026-01-25 | 0.22361
2026-01-25 00:58 | 74.9174 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.9174 | FALSE | FALSE | 0 |  | 74.9174 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0 | Normal | 74.9174 |  | Night | 202601 | 2026-01-25
2026-01-25 01:13 | 74.9174 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.9174 | FALSE | FALSE | 0 |  | 74.9174 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.9174 |  | Night | 202601 | 2026-01-25
2026-01-25 01:27 | 74.9174 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.9174 | FALSE | FALSE | 0 |  | 74.9174 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.9174 |  | Night | 202601 | 2026-01-25
2026-01-25 01:43 | 74.9174 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.9174 | FALSE | FALSE | 0 |  | 74.9174 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.9174 |  | Night | 202601 | 2026-01-25
2026-01-25 01:58 | 74.9174 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.9174 | FALSE | FALSE | 0 |  | 74.9174 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.9174 |  | Night | 202601 | 2026-01-25
2026-01-25 02:13 | 74.9174 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.9174 | FALSE | FALSE | 0 |  | 74.9174 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.9174 |  | Night | 202601 | 2026-01-25
2026-01-25 02:27 | 74.6348 | TRUE | FALSE | 0.14209 | 0.19002 | -0.39485 | -0.52626 | -0.2826 | 2026-01-25 02:42 | 2026-01-25 02:27 | lower | TRUE | 1 | 74.7769 | FALSE | FALSE | 0.3689 | 4.2485 | 74.9033 | 1 | -0.2826 | -0.01413 | 0.063191 | -4.2485 | 0.063191 | Extreme triggered | 75.0297 | -4.2485 | Night | 202601 | 2026-01-25 | 4.2485
2026-01-25 02:42 | 74.9174 | TRUE | FALSE | -0.14051 | -0.18791 | -0.11225 | -0.14961 | 0.2826 |  |  | none | FALSE | 2 | 74.7769 | TRUE | FALSE | 0.072 |  | 74.9033 | 0 | 0.2826 | 0 | 0.091688 | 3.0822 | 0.063191 | Persistence ends | 75.0297 | 0.22361 | Night | 202601 | 2026-01-25 | 0.22361
2026-01-25 02:57 | 74.6348 | TRUE | FALSE | 0.080375 | 0.10758 | -0.4283 | -0.57059 | -0.2826 | 2026-01-25 07:56 | 2026-01-25 02:57 | lower | TRUE | 3 | 74.7152 | TRUE | FALSE | 0.3378 | 2.924 | 74.8891 | 1 | -0.2826 | -0.01413 | 0.11135 | -2.411 | 0.086982 | Extreme triggered | 75.0631 | -2.924 | Night | 202601 | 2026-01-25 | 2.924
2026-01-25 03:12 | 74.6348 | FALSE | FALSE | 0.03315 | 0.044397 | -0.44727 | -0.59571 | 0 |  | 2026-01-25 02:57 | lower | TRUE | 3 | 74.668 | FALSE | FALSE | 0.3547 | 2.6221 | 74.875 | 2 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.10353 | Extreme/elevated | 75.0821 | -2.3202 | Night | 202601 | 2026-01-25 | 2.3202
2026-01-25 03:27 | 74.6348 | FALSE | FALSE | -0.0058732 | -0.0078699 | -0.45803 | -0.60996 | 0 |  | 2026-01-25 02:57 | none | FALSE | 3 | 74.6289 | FALSE | FALSE | 0.3871 | 2.3979 | 74.8609 | 3 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.11598 | Persistent | 75.0928 | -1.9494 | Night | 202601 | 2026-01-25 | 1.9494
2026-01-25 03:42 | 74.6348 | FALSE | FALSE | -0.039147 | -0.052479 | -0.46305 | -0.61659 | 0 |  | 2026-01-25 02:57 | none | FALSE | 3 | 74.5957 | FALSE | FALSE | 0.4268 | 2.2204 | 74.8468 | 4 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.12555 | Persistent | 75.0978 | -1.6882 | Night | 202601 | 2026-01-25 | 1.6882
2026-01-25 03:57 | 74.6348 | FALSE | FALSE | -0.067916 | -0.09108 | -0.46356 | -0.61726 | 0 |  | 2026-01-25 02:57 | none | FALSE | 3 | 74.5669 | FALSE | FALSE | 0.4707 | 2.0741 | 74.8326 | 5 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13287 | Persistent | 75.0984 | -1.4888 | Night | 202601 | 2026-01-25 | 1.4888
2026-01-25 04:12 | 74.3522 | TRUE | FALSE | 0.11403 | 0.15313 | -0.79029 | -1.0517 | -0.2826 |  | 2026-01-25 02:57 | lower | TRUE | 4 | 74.4662 | TRUE | TRUE | 0.6354 | 2.1742 | 74.8044 | 6 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.16906 | Persistent | 75.1425 | -2.6745 | Night | 202601 | 2026-01-25 | 2.6745
2026-01-25 04:27 | 74.3522 | FALSE | TRUE | 0.034903 | 0.04692 | -0.8129 | -1.0815 | 0 |  | 2026-01-25 02:57 | lower | TRUE | 4 | 74.3871 | FALSE | TRUE | 0.6596 | 2.1749 | 74.7761 | 7 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.1945 | Confirmed/Materialized Shift | 75.1651 | -2.1794 | Night | 202601 | 2026-01-25 | 2.1794
2026-01-25 04:42 | 74.3522 | FALSE | TRUE | -0.030485 | -0.041018 | -0.82177 | -1.0932 | 0 |  | 2026-01-25 02:57 | none | FALSE | 4 | 74.3217 | FALSE | FALSE | 0.6381 | 2.1352 | 74.7478 | 8 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21306 | Confirmed/Materialized Shift | 75.174 | -1.8569 | Night | 202601 | 2026-01-25 | 1.8569
2026-01-25 04:57 | 74.3522 | FALSE | TRUE | -0.085523 | -0.11516 | -0.82028 | -1.0912 | 0 |  | 2026-01-25 02:57 | none | FALSE | 3 | 74.2667 | FALSE | FALSE | 0.5939 | 2.0782 | 74.7196 | 9 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.22645 | Confirmed/Materialized Shift | 75.1725 | -1.6223 | Night | 202601 | 2026-01-25 | 1.6223
2026-01-25 05:12 | 74.0714 | FALSE | TRUE | 0.078814 | 0.10629 | -1.1329 | -1.5065 | -0.2808 |  | 2026-01-25 02:57 | lower | TRUE | 2 | 74.1502 | FALSE | TRUE | 0.6104 | 2.1003 | 74.6773 | 10 | -0.2808 | -0.0423 | 0.13813 | -1.7266 | 0.26353 | Confirmed/Materialized Shift | 75.2043 | -2.2991 | Night | 202601 | 2026-01-25 | 2.2991
2026-01-25 05:26 | 74.0714 | FALSE | TRUE | -0.015565 | -0.021018 | -1.1427 | -1.5193 | 0 |  | 2026-01-25 02:57 | none | FALSE | 1 | 74.0558 | FALSE | FALSE | 0.5583 | 2.0863 | 74.635 | 11 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.28957 | Confirmed/Materialized Shift | 75.2141 | -1.9462 | Night | 202601 | 2026-01-25 | 1.9462
2026-01-25 05:41 | 74.0714 | FALSE | TRUE | -0.093497 | -0.12639 | -1.1361 | -1.5106 | 0 |  | 2026-01-25 02:57 | none | FALSE | 1 | 73.9779 | FALSE | FALSE | 0.5416 | 2.0537 | 74.5927 | 12 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.30739 | Confirmed/Materialized Shift | 75.2075 | -1.6958 | Night | 202601 | 2026-01-25 | 1.6958
2026-01-25 05:56 | 74.0714 | FALSE | TRUE | -0.15775 | -0.21343 | -1.1157 | -1.4839 | 0 |  | 2026-01-25 02:57 | none | FALSE | 1 | 73.9136 | FALSE | FALSE | 0.5289 | 2.0115 | 74.5504 | 13 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.31837 | Confirmed/Materialized Shift | 75.1871 | -1.5045 | Night | 202601 | 2026-01-25 | 1.5045
2026-01-25 06:11 | 74.0714 | FALSE | TRUE | -0.20972 | -0.28394 | -1.0831 | -1.4411 | 0 |  | 2026-01-25 02:57 | none | FALSE | 1 | 73.8617 | FALSE | FALSE | 0.5186 | 1.9643 | 74.5081 | 14 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.3232 | Confirmed/Materialized Shift | 75.1545 | -1.3511 | Night | 202601 | 2026-01-25 | 1.3511
2026-01-25 06:26 | 74.0714 | FALSE | TRUE | -0.24996 | -0.3386 | -1.0387 | -1.3829 | 0 |  | 2026-01-25 02:57 | none | FALSE | 1 | 73.8214 | FALSE | FALSE | 0.5102 | 1.915 | 74.4658 | 15 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.32217 | Confirmed/Materialized Shift | 75.1101 | -1.2241 | Night | 202601 | 2026-01-25 | 1.2241
2026-01-25 06:41 | 74.0714 | FALSE | TRUE | -0.27835 | -0.3772 | -0.98251 | -1.3091 | 0 |  | 2026-01-25 02:57 | none | FALSE | 0 | 73.793 | FALSE | FALSE | 0.4745 | 1.8651 | 74.4235 | 16 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.31522 | Confirmed/Materialized Shift | 75.0539 | -1.117 | Night | 202601 | 2026-01-25 | 1.117
2026-01-25 06:56 | 73.7888 | FALSE | TRUE | -0.067877 | -0.092072 | -1.2244 | -1.6322 | -0.2826 |  | 2026-01-25 02:57 | none | FALSE | 0 | 73.7209 | FALSE | FALSE | 0.5193 | 1.8607 | 74.3671 | 17 | -0.2826 | -0.05643 | 0.1477 | -1.5313 | 0.32306 | Confirmed/Materialized Shift | 75.0132 | -1.7899 | Night | 202601 | 2026-01-25 | 1.7899
2026-01-25 07:11 | 73.7888 | FALSE | TRUE | -0.11904 | -0.16159 | -1.1627 | -1.5512 | 0 |  | 2026-01-25 02:57 | none | FALSE | 0 | 73.6698 | FALSE | FALSE | 0.5086 | 1.8478 | 74.3106 | 18 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.32043 | Confirmed/Materialized Shift | 74.9515 | -1.6285 | Night | 202601 | 2026-01-25 | 1.6285
2026-01-25 07:26 | 73.7888 | FALSE | TRUE | -0.18257 | -0.24804 | -1.1416 | -1.5236 | 0 |  | 2026-01-25 02:57 | none | FALSE | 0 | 73.6062 | FALSE | FALSE | 0.4966 | 1.8268 | 74.2683 | 19 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.33105 | Confirmed/Materialized Shift | 74.9304 | -1.4485 | Day | 202601 | 2026-01-25 | 1.4485
2026-01-25 07:41 | 73.7888 | FALSE | TRUE | -0.19713 | -0.26787 | -1.0433 | -1.3942 | 0 |  | 2026-01-25 02:57 | none | FALSE | 0 | 73.5917 | FALSE | FALSE | 0.491 | 1.8036 | 74.2119 | 20 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.31011 | Confirmed/Materialized Shift | 74.8321 | -1.3643 | Day | 202601 | 2026-01-25 | 1.3643
2026-01-25 07:56 | 74.0714 | TRUE | FALSE | -0.47745 | -0.64877 | -0.70209 | -0.93896 | 0.2826 |  |  | none | FALSE | 1 | 73.5939 | FALSE | FALSE | 0.054 |  | 74.1837 | 0 | 0.2826 | -0.02817 | 0.12619 | 2.4627 | 0.29489 | Persistence ends | 74.7735 | -0.38089 | Day | 202601 | 2026-01-25 | 0.38089
2026-01-25 08:11 | 74.0714 | FALSE | FALSE | -0.46749 | -0.63515 | -0.63579 | -0.85105 | 0 |  |  | none | FALSE | 1 | 73.6039 | FALSE | FALSE | 0.0489 |  | 74.1556 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.27582 | Normal | 74.7072 | -0.30509 | Day | 202601 | 2026-01-25 | 0.30509
2026-01-25 08:25 | 74.3522 | TRUE | FALSE | -0.72387 | -0.98314 | -0.30231 | -0.40494 | 0.2808 |  |  | none | FALSE | 2 | 73.6283 | TRUE | FALSE | 0.1119 |  | 74.1414 | 0 | 0.2808 | -0.01413 | 0.14387 | 2.0499 | 0.25654 | Normal | 74.6545 | 0.82161 | Day | 202601 | 2026-01-25 | 0.82161
2026-01-25 08:30 | 74.3522 | FALSE | FALSE | -0.69451 | -0.94289 | -0.24469 | -0.32802 | 0 |  |  | none | FALSE | 2 | 73.6577 | FALSE | FALSE | 0.121 |  | 74.1273 | 0 | 0 | -0.01413 | 0.14387 | 0.098211 | 0.2348 | Normal | 74.5969 | 0.95788 | Day | 202601 | 2026-01-25 | 0.95788
2026-01-25 08:45 | 74.6348 | FALSE | FALSE | -0.97711 | -1.3266 | 0.03791 | 0.05082 | 0.2826 | 2026-01-25 10:00 | 2026-01-25 08:45 | upper | TRUE | 2 | 73.6577 | FALSE | FALSE | 0.2584 | 2.1615 | 74.1273 | 1 | 0.2826 | 0 | 0.15847 | 1.7833 | 0.2348 | Extreme triggered | 74.5969 | 2.1615 | Day | 202601 | 2026-01-25 | 2.1615
2026-01-25 09:01 | 74.9174 | FALSE | FALSE | -1.3432 | -1.8256 | 0.18053 | 0.24155 | 0.2826 |  | 2026-01-25 08:45 | upper | TRUE | 2 | 73.5742 | FALSE | FALSE | 0.3462 | 2.3913 | 74.1556 | 2 | 0.2826 | 0.02826 | 0.1558 | 1.6325 | 0.29066 | Extreme/elevated | 74.7369 | 2.6211 | Day | 202601 | 2026-01-25 | 2.6211
2026-01-25 09:16 | 74.9174 | FALSE | FALSE | -1.4034 | -1.909 | 0.063794 | 0.085225 | 0 |  | 2026-01-25 08:45 | upper | TRUE | 2 | 73.514 | FALSE | TRUE | 0.3746 | 2.3243 | 74.1838 | 3 | 0 | 0.02826 | 0.1558 | -0.18139 | 0.3349 | Persistent | 74.8536 | 2.1905 | Day | 202601 | 2026-01-25 | 2.1905
2026-01-25 09:30 | 75.2 | FALSE | FALSE | -1.7816 | -2.4266 | 0.16603 | 0.22128 | 0.2826 |  | 2026-01-25 08:45 | upper | TRUE | 2 | 73.4184 | FALSE | TRUE | 0.4465 | 2.346 | 74.2262 | 4 | 0.2826 | 0.04239 | 0.1656 | 1.4505 | 0.40388 | Persistent | 75.034 | 2.4111 | Day | 202601 | 2026-01-25 | 2.4111
2026-01-25 09:30 | 75.2 | FALSE | FALSE | -1.8486 | -2.5202 | 0.014229 | 0.018925 | 0 |  | 2026-01-25 08:45 | upper | TRUE | 2 | 73.3514 | FALSE | TRUE | 0.4783 | 2.283 | 74.2686 | 5 | 0 | 0.04239 | 0.1656 | -0.25597 | 0.45859 | Persistent | 75.1858 | 2.031 | Day | 202601 | 2026-01-25 | 2.031
2026-01-25 09:33 | 75.4826 | FALSE | FALSE | -2.2029 | -3.0061 | 0.08404 | 0.11146 | 0.2826 |  | 2026-01-25 08:45 | upper | TRUE | 2 | 73.2797 | FALSE | TRUE | 0.5439 | 2.2623 | 74.3392 | 6 | 0.2826 | 0.07056 | 0.15534 | 1.365 | 0.5297 | Persistent | 75.3986 | 2.1587 | Day | 202601 | 2026-01-25 | 2.1587
2026-01-25 09:48 | 75.2 | FALSE | TRUE | -1.9224 | -2.6234 | -0.31355 | -0.41523 | -0.2826 |  | 2026-01-25 08:45 | none | FALSE | 1 | 73.2776 | FALSE | FALSE | 0.5245 | 2.1447 | 74.3956 | 7 | -0.2826 | 0.05643 | 0.17384 | -1.9502 | 0.55899 | Confirmed/Materialized Shift | 75.5136 | 1.4391 | Day | 202601 | 2026-01-25 | 1.4391
2026-01-25 10:00 | 74.0714 | TRUE | FALSE | -0.79379 | -1.0833 | -1.4422 | -1.9098 | -1.1286 |  |  | none | FALSE | 2 | 73.2776 | TRUE | FALSE | 0.0958 |  | 74.3956 | 0 | -1.1286 | 0 | 0.31719 | -3.5581 | 0.55899 | Persistence ends | 75.5136 | -0.57994 | Day | 202601 | 2026-01-25 | 0.57994
2026-01-25 10:15 | 73.5062 | FALSE | FALSE | -0.31824 | -0.43483 | -2.0405 | -2.701 | -0.5652 |  |  | none | FALSE | 1 | 73.188 | FALSE | FALSE | 0.1259 |  | 74.3673 | 0 | -0.5652 | -0.02826 | 0.34144 | -1.5726 | 0.58968 | Normal | 75.5467 | -1.4603 | Day | 202601 | 2026-01-25 | 1.4603
2026-01-25 10:30 | 73.2236 | FALSE | FALSE | -0.17941 | -0.24561 | -2.3821 | -3.1506 | -0.2826 |  |  | none | FALSE | 1 | 73.0442 | FALSE | FALSE | 0.1432 |  | 74.3249 | 0 | -0.2826 | -0.04239 | 0.34603 | -0.69419 | 0.64037 | Normal | 75.6057 | -1.7198 | Day | 202601 | 2026-01-25 | 1.7198
2026-01-25 10:45 | 73.2236 | FALSE | FALSE | -0.3102 | -0.42544 | -2.4281 | -3.2096 | 0 |  |  | none | FALSE | 1 | 72.9134 | FALSE | FALSE | 0.1317 |  | 74.2825 | 0 | 0 | -0.04239 | 0.34603 | 0.1225 | 0.68457 | Normal | 75.6517 | -1.5469 | Day | 202601 | 2026-01-25 | 1.5469
2026-01-25 11:00 | 73.2236 | FALSE | FALSE | -0.4304 | -0.59126 | -2.4635 | -3.2548 | 0 |  |  | none | FALSE | 1 | 72.7932 | FALSE | FALSE | 0.1222 |  | 74.2401 | 0 | 0 | -0.04239 | 0.34603 | 0.1225 | 0.72348 | Normal | 75.6871 | -1.4051 | Day | 202601 | 2026-01-25 | 1.4051
2026-01-25 11:15 | 73.2236 | FALSE | FALSE | -0.51669 | -0.71065 | -2.4933 | -3.2929 | 0 |  |  | none | FALSE | 1 | 72.7069 | FALSE | FALSE | 0.1161 |  | 74.2119 | 0 | 0 | -0.02826 | 0.34144 | 0.082766 | 0.75249 | Normal | 75.7169 | -1.3134 | Day | 202601 | 2026-01-25 | 1.3134
2026-01-25 11:29 | 73.2236 | FALSE | FALSE | -0.59867 | -0.82433 | -2.5187 | -3.3254 | 0 |  |  | none | FALSE | 1 | 72.6249 | FALSE | FALSE | 0.1107 |  | 74.1836 | 0 | 0 | -0.02826 | 0.34144 | 0.082766 | 0.77935 | Normal | 75.7423 | -1.2318 | Day | 202601 | 2026-01-25 | 1.2318
2026-01-25 11:44 | 73.2236 | FALSE | FALSE | -0.67677 | -0.93287 | -2.5403 | -3.3529 | 0 |  |  | none | FALSE | 1 | 72.5468 | FALSE | FALSE | 0.1058 |  | 74.1554 | 0 | 0 | -0.02826 | 0.34144 | 0.082766 | 0.80427 | Normal | 75.7639 | -1.1585 | Day | 202601 | 2026-01-25 | 1.1585
2026-01-25 11:59 | 73.2236 | FALSE | FALSE | -0.75134 | -1.0367 | -2.5584 | -3.3759 | 0 |  |  | none | FALSE | 1 | 72.4723 | FALSE | FALSE | 0.1014 |  | 74.1271 | 0 | 0 | -0.02826 | 0.34144 | 0.082766 | 0.82742 | Normal | 75.782 | -1.092 | Day | 202601 | 2026-01-25 | 1.092
2026-01-25 12:14 | 73.2236 | FALSE | FALSE | -0.84245 | -1.1639 | -2.5647 | -3.384 | 0 |  |  | none | FALSE | 1 | 72.3811 | FALSE | FALSE | 0.096 |  | 74.0847 | 0 | 0 | -0.04239 | 0.33366 | 0.12704 | 0.85179 | Normal | 75.7883 | -1.011 | Day | 202601 | 2026-01-25 | 1.011
2026-01-25 12:29 | 73.2236 | FALSE | FALSE | -0.92789 | -1.2835 | -2.5653 | -3.3849 | 0 |  |  | none | FALSE | 0 | 72.2957 | FALSE | FALSE | 0.0625 |  | 74.0423 | 0 | 0 | -0.04239 | 0.33366 | 0.12704 | 0.87331 | Normal | 75.7889 | -0.9375 | Day | 202601 | 2026-01-25 | 0.9375
2026-01-25 12:44 | 73.2236 | FALSE | FALSE | -1.0148 | -1.4054 | -2.5394 | -3.3518 | 0 |  |  | none | FALSE | 0 | 72.2088 | FALSE | FALSE | 0.0572 |  | 73.9859 | 0 | 0 | -0.05643 | 0.32515 | 0.17355 | 0.88856 | Normal | 75.763 | -0.8579 | Day | 202601 | 2026-01-25 | 0.8579
2026-01-25 12:59 | 73.2236 | FALSE | FALSE | -1.0938 | -1.5164 | -2.5056 | -3.3086 | 0 |  |  | none | FALSE | 0 | 72.1298 | FALSE | FALSE | 0.0523 |  | 73.9295 | 0 | 0 | -0.05643 | 0.32515 | 0.17355 | 0.89984 | Normal | 75.7292 | -0.78444 | Day | 202601 | 2026-01-25 | 0.78444
2026-01-25 13:14 | 72.941 | FALSE | FALSE | -0.91545 | -1.271 | -2.723 | -3.5988 | -0.2826 |  |  | none | FALSE | 0 | 72.0255 | FALSE | FALSE | 0.0662 |  | 73.8448 | 0 | -0.2826 | -0.08469 | 0.31863 | -0.62114 | 0.90962 | Normal | 75.664 | -0.99358 | Day | 202601 | 2026-01-25 | 0.99358
2026-01-25 13:29 | 72.941 | FALSE | FALSE | -0.9834 | -1.3666 | -2.5933 | -3.4333 | 0 |  |  | none | FALSE | 0 | 71.9576 | FALSE | FALSE | 0.06 |  | 73.746 | 0 | 0 | -0.09882 | 0.30755 | 0.32131 | 0.89418 | Normal | 75.5343 | -0.90022 | Day | 202601 | 2026-01-25 | 0.90022
2026-01-25 13:44 | 72.941 | FALSE | FALSE | -1.0273 | -1.4284 | -2.4395 | -3.2363 | 0 |  |  | none | FALSE | 0 | 71.9137 | FALSE | FALSE | 0.0543 |  | 73.6471 | 0 | 0 | -0.09882 | 0.30755 | 0.32131 | 0.8667 | Normal | 75.3805 | -0.81475 | Day | 202601 | 2026-01-25 | 0.81475
2026-01-25 13:59 | 72.941 | FALSE | FALSE | -1.0031 | -1.3944 | -2.1895 | -2.9143 | 0 |  |  | none | FALSE | 0 | 71.9379 | FALSE | FALSE | 0.0495 |  | 73.5342 | 0 | 0 | -0.11295 | 0.29536 | 0.38242 | 0.79816 | Normal | 75.1305 | -0.7432 | Day | 202601 | 2026-01-25 | 0.7432
2026-01-25 14:14 | 72.941 | FALSE | FALSE | -0.92845 | -1.2893 | -1.8889 | -2.5243 | 0 |  |  | none | FALSE | 0 | 72.0125 | FALSE | FALSE | 0.0455 |  | 73.4212 | 0 | 0 | -0.11295 | 0.29536 | 0.38242 | 0.70435 | Normal | 74.8299 | -0.68182 | Day | 202601 | 2026-01-25 | 0.68182
2026-01-25 14:28 | 72.941 | FALSE | FALSE | -0.68144 | -0.94304 | -1.3878 | -1.8671 | 0 |  |  | none | FALSE | 0 | 72.2596 | FALSE | FALSE | 0.0455 |  | 73.2942 | 0 | 0 | -0.12708 | 0.28189 | 0.45081 | 0.5173 | Normal | 74.3288 | -0.6827 | Day | 202601 | 2026-01-25 | 0.6827
2026-01-25 14:43 | 73.2236 | FALSE | FALSE | -0.54367 | -0.74803 | -0.48715 | -0.6609 | 0.2826 |  |  | none | FALSE | 0 | 72.6799 | FALSE | FALSE | 0.0073 |  | 73.1953 | 0 | 0.2826 | -0.09882 | 0.29357 | 1.2993 | 0.25771 | Normal | 73.7108 | 0.10966 | Day | 202601 | 2026-01-25 | 0.10966
2026-01-25 14:58 | 73.5062 | FALSE | FALSE | -0.68705 | -0.9435 | -0.0088098 | -0.011984 | 0.2826 |  |  | none | FALSE | 0 | 72.8192 | FALSE | FALSE | 0.13 |  | 73.1671 | 0 | 0.2826 | -0.02826 | 0.18107 | 1.7168 | 0.17396 | Normal | 73.515 | 1.9494 | Day | 202601 | 2026-01-25 | 1.9494
2026-01-25 15:14 | 73.7888 | FALSE | FALSE | -1.0288 | -1.4139 | 0.18643 | 0.25329 | 0.2826 | 2026-01-25 16:58 | 2026-01-25 15:14 | upper | TRUE | 0 | 72.76 | FALSE | FALSE | 0.2495 | 2.8853 | 73.1812 | 1 | 0.2826 | 0.01413 | 0.14424 | 1.8612 | 0.21058 | Extreme triggered | 73.6024 | 2.8853 | Day | 202601 | 2026-01-25 | 2.8853
2026-01-25 15:28 | 73.7888 | FALSE | FALSE | -1.0807 | -1.4863 | 0.077974 | 0.10578 | 0 |  | 2026-01-25 15:14 | upper | TRUE | 0 | 72.7081 | FALSE | FALSE | 0.2684 | 2.5982 | 73.2095 | 2 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.25068 | Extreme/elevated | 73.7108 | 2.3111 | Day | 202601 | 2026-01-25 | 2.3111
2026-01-25 15:43 | 74.0714 | FALSE | FALSE | -1.4521 | -1.9996 | 0.18696 | 0.25305 | 0.2826 |  | 2026-01-25 15:14 | upper | TRUE | 0 | 72.6193 | FALSE | TRUE | 0.3442 | 2.5958 | 73.2519 | 3 | 0.2826 | 0.04239 | 0.13829 | 1.737 | 0.31629 | Persistent | 73.8844 | 2.5911 | Day | 202601 | 2026-01-25 | 2.5911
2026-01-25 15:58 | 73.7888 | FALSE | FALSE | -1.1849 | -1.6321 | -0.16757 | -0.22658 | -0.2826 |  | 2026-01-25 15:14 | none | FALSE | 0 | 72.6039 | FALSE | FALSE | 0.3289 | 2.323 | 73.2801 | 4 | -0.2826 | 0.02826 | 0.15614 | -1.9909 | 0.33813 | Persistent | 73.9564 | 1.5044 | Day | 202601 | 2026-01-25 | 1.5044
2026-01-25 16:13 | 74.0714 | FALSE | FALSE | -1.5111 | -2.0825 | -0.013276 | -0.01792 | 0.2826 |  | 2026-01-25 15:14 | none | FALSE | 0 | 72.5603 | FALSE | FALSE | 0.4167 | 2.2514 | 73.3225 | 5 | 0.2826 | 0.04239 | 0.16593 | 1.4477 | 0.38108 | Persistent | 74.0847 | 1.9652 | Day | 202601 | 2026-01-25 | 1.9652
2026-01-25 16:28 | 73.7888 | FALSE | FALSE | -1.2262 | -1.6899 | -0.35016 | -0.47231 | -0.2826 |  | 2026-01-25 15:14 | none | FALSE | 0 | 72.5626 | FALSE | FALSE | 0.417 | 2.0614 | 73.3508 | 6 | -0.2826 | 0.02826 | 0.18107 | -1.7168 | 0.3941 | Persistent | 74.139 | 1.1115 | Day | 202601 | 2026-01-25 | 1.1115
2026-01-25 16:43 | 73.7888 | FALSE | TRUE | -1.219 | -1.6798 | -0.39947 | -0.53846 | 0 |  | 2026-01-25 15:14 | none | FALSE | 0 | 72.5698 | FALSE | FALSE | 0.4675 | 1.9116 | 73.379 | 7 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.40462 | Confirmed/Materialized Shift | 74.1883 | 1.0127 | Day | 202601 | 2026-01-25 | 1.0127
2026-01-25 16:58 | 73.7888 | FALSE | FALSE | -1.2072 | -1.6632 | -0.44419 | -0.59837 | 0 |  |  | none | FALSE | 0 | 72.5816 | FALSE | FALSE | 0.0616 |  | 73.4073 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.41285 | Persistence ends | 74.233 | 0.92409 | Day | 202601 | 2026-01-25 | 0.92409
2026-01-25 17:13 | 73.7888 | FALSE | FALSE | -1.1911 | -1.6407 | -0.48458 | -0.65242 | 0 |  |  | none | FALSE | 0 | 72.5977 | FALSE | FALSE | 0.0562 |  | 73.4356 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.41891 | Normal | 74.2734 | 0.84325 | Day | 202601 | 2026-01-25 | 0.84325
2026-01-25 17:27 | 73.5062 | FALSE | FALSE | -0.88881 | -1.224 | -0.77577 | -1.0444 | -0.2826 |  |  | none | FALSE | 0 | 72.6174 | FALSE | FALSE | 0.0091 |  | 73.4497 | 0 | -0.2826 | 0.01413 | 0.19396 | -1.5299 | 0.41614 | Normal | 74.282 | 0.13582 | Day | 202601 | 2026-01-25 | 0.13582
2026-01-25 17:30 | 73.5062 | FALSE | FALSE | -0.86809 | -1.1951 | -0.78331 | -1.0544 | 0 |  |  | none | FALSE | 0 | 72.6381 | FALSE | FALSE | 0.0068 |  | 73.4638 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.41285 | Normal | 74.2895 | 0.10268 | Day | 202601 | 2026-01-25 | 0.10268
2026-01-25 17:31 | 73.5062 | FALSE | FALSE | -0.84629 | -1.1647 | -0.78977 | -1.063 | 0 |  |  | none | FALSE | 0 | 72.6599 | FALSE | FALSE | 0.0046 |  | 73.4779 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.40901 | Normal | 74.296 | 0.069093 | Day | 202601 | 2026-01-25 | 0.069093
2026-01-25 17:46 | 74.0714 | TRUE | FALSE | -1.355 | -1.8634 | -0.28109 | -0.37804 | 0.5652 |  |  | none | FALSE | 1 | 72.7164 | FALSE | FALSE | 0.1161 |  | 73.5345 | 0 | 0.5652 | 0.05652 | 0.21697 | 2.3444 | 0.40901 | Normal | 74.3525 | 1.3128 | Day | 202601 | 2026-01-25 | 1.3128
2026-01-25 18:01 | 74.0714 | FALSE | FALSE | -1.2818 | -1.761 | -0.32099 | -0.43149 | 0 |  |  | none | FALSE | 1 | 72.7896 | FALSE | FALSE | 0.1085 |  | 73.591 | 0 | 0 | 0.05652 | 0.21697 | -0.26049 | 0.40071 | Normal | 74.3924 | 1.1989 | Night | 202601 | 2026-01-25 | 1.1989
2026-01-25 18:16 | 74.6348 | FALSE | FALSE | -1.8266 | -2.5088 | 0.09166 | 0.12296 | 0.5634 | 2026-01-25 21:59 | 2026-01-25 18:16 | upper | TRUE | 1 | 72.8082 | FALSE | FALSE | 0.2331 | 2.2113 | 73.6757 | 1 | 0.5634 | 0.08469 | 0.24412 | 1.9609 | 0.43374 | Extreme triggered | 74.5431 | 2.2113 | Night | 202601 | 2026-01-25 | 2.2113
2026-01-25 18:30 | 74.9174 | FALSE | FALSE | -2.1033 | -2.8886 | 0.18251 | 0.24421 | 0.2826 |  | 2026-01-25 18:16 | upper | TRUE | 1 | 72.8141 | FALSE | FALSE | 0.3015 | 2.2957 | 73.7745 | 2 | 0.2826 | 0.09882 | 0.24712 | 0.74368 | 0.4802 | Extreme/elevated | 74.7349 | 2.3801 | Night | 202601 | 2026-01-25 | 2.3801
2026-01-25 18:45 | 74.9174 | FALSE | FALSE | -2.0491 | -2.812 | 0.039105 | 0.052225 | 0 |  | 2026-01-25 18:16 | upper | TRUE | 1 | 72.8683 | FALSE | TRUE | 0.3385 | 2.2231 | 73.8733 | 3 | 0 | 0.09882 | 0.24712 | -0.39988 | 0.50249 | Persistent | 74.8783 | 2.0778 | Night | 202601 | 2026-01-25 | 2.0778
2026-01-25 19:00 | 74.9174 | FALSE | FALSE | -1.9529 | -2.6766 | -0.062394 | -0.083214 | 0 |  | 2026-01-25 18:16 | none | FALSE | 1 | 72.9645 | FALSE | FALSE | 0.3822 | 2.1363 | 73.9721 | 4 | 0 | 0.09882 | 0.24712 | -0.39988 | 0.50383 | Persistent | 74.9798 | 1.8762 | Night | 202601 | 2026-01-25 | 1.8762
2026-01-25 19:15 | 74.9174 | FALSE | FALSE | -1.8879 | -2.5851 | -0.16672 | -0.22204 | 0 |  | 2026-01-25 18:16 | none | FALSE | 1 | 73.0295 | FALSE | FALSE | 0.426 | 2.0442 | 74.0568 | 5 | 0 | 0.08469 | 0.24412 | -0.34692 | 0.51365 | Persistent | 75.0841 | 1.6754 | Night | 202601 | 2026-01-25 | 1.6754
2026-01-25 19:29 | 75.2 | FALSE | FALSE | -2.1704 | -2.972 | -0.053465 | -0.071046 | 0.2826 |  | 2026-01-25 18:16 | none | FALSE | 1 | 73.0296 | FALSE | FALSE | 0.4984 | 2.0208 | 74.1415 | 6 | 0.2826 | 0.08469 | 0.24412 | 0.8107 | 0.55598 | Persistent | 75.2535 | 1.9038 | Night | 202601 | 2026-01-25 | 1.9038
2026-01-25 19:44 | 75.2 | FALSE | TRUE | -2.1817 | -2.9879 | -0.20587 | -0.27302 | 0 |  | 2026-01-25 18:16 | none | FALSE | 1 | 73.0183 | FALSE | FALSE | 0.5389 | 1.9685 | 74.2121 | 7 | 0 | 0.07056 | 0.24021 | -0.29374 | 0.5969 | Confirmed/Materialized Shift | 75.4059 | 1.6551 | Night | 202601 | 2026-01-25 | 1.6551
2026-01-25 19:59 | 75.2 | FALSE | TRUE | -2.1711 | -2.973 | -0.33641 | -0.44536 | 0 |  | 2026-01-25 18:16 | none | FALSE | 1 | 73.0289 | FALSE | FALSE | 0.5261 | 1.9054 | 74.2826 | 8 | 0 | 0.07056 | 0.24021 | -0.29374 | 0.62689 | Confirmed/Materialized Shift | 75.5364 | 1.4634 | Night | 202601 | 2026-01-25 | 1.4634
2026-01-25 20:15 | 75.2 | FALSE | TRUE | -2.1748 | -2.9782 | -0.45296 | -0.59873 | 0 |  | 2026-01-25 18:16 | none | FALSE | 0 | 73.0252 | FALSE | FALSE | 0.4874 | 1.8393 | 74.3391 | 9 | 0 | 0.05643 | 0.23535 | -0.23978 | 0.65695 | Confirmed/Materialized Shift | 75.653 | 1.3105 | Night | 202601 | 2026-01-25 | 1.3105
2026-01-25 20:29 | 75.2 | FALSE | TRUE | -2.1312 | -2.9166 | -0.55039 | -0.72659 | 0 |  | 2026-01-25 18:16 | none | FALSE | 0 | 73.0688 | FALSE | FALSE | 0.4786 | 1.7733 | 74.4096 | 10 | 0 | 0.07056 | 0.22203 | -0.3178 | 0.67039 | Confirmed/Materialized Shift | 75.7504 | 1.179 | Night | 202601 | 2026-01-25 | 1.179
2026-01-25 20:44 | 75.2 | FALSE | TRUE | -2.1093 | -2.8859 | -0.64144 | -0.84576 | 0 |  | 2026-01-25 18:16 | none | FALSE | 0 | 73.0907 | FALSE | FALSE | 0.4712 | 1.7091 | 74.466 | 11 | 0 | 0.05643 | 0.21675 | -0.26035 | 0.68769 | Confirmed/Materialized Shift | 75.8414 | 1.0673 | Night | 202601 | 2026-01-25 | 1.0673
2026-01-25 20:59 | 75.4826 | FALSE | TRUE | -2.3399 | -3.199 | -0.47615 | -0.62685 | 0.2826 |  | 2026-01-25 18:16 | none | FALSE | 0 | 73.1427 | FALSE | FALSE | 0.4882 | 1.677 | 74.5507 | 12 | 0.2826 | 0.08469 | 0.20684 | 0.95683 | 0.704 | Confirmed/Materialized Shift | 75.9587 | 1.3237 | Night | 202601 | 2026-01-25 | 1.3237
2026-01-25 21:29 | 75.4826 | FALSE | TRUE | -2.2659 | -3.0948 | -0.57159 | -0.75155 | 0 |  | 2026-01-25 18:16 | none | FALSE | 0 | 73.2167 | FALSE | FALSE | 0.4796 | 1.6398 | 74.6354 | 13 | 0 | 0.08469 | 0.20684 | -0.40945 | 0.70938 | Confirmed/Materialized Shift | 76.0542 | 1.1942 | Night | 202601 | 2026-01-25 | 1.1942
2026-01-25 21:44 | 75.4826 | FALSE | TRUE | -2.1706 | -2.9608 | -0.64566 | -0.84813 | 0 |  | 2026-01-25 18:16 | none | FALSE | 0 | 73.312 | FALSE | FALSE | 0.4722 | 1.6001 | 74.7201 | 14 | 0 | 0.08469 | 0.20684 | -0.40945 | 0.70407 | Confirmed/Materialized Shift | 76.1283 | 1.083 | Night | 202601 | 2026-01-25 | 1.083
2026-01-25 21:59 | 75.4826 | FALSE | FALSE | -2.0535 | -2.7965 | -0.69788 | -0.91609 | 0 |  |  | none | FALSE | 0 | 73.4291 | FALSE | FALSE | 0.0657 |  | 74.8048 | 0 | 0 | 0.08469 | 0.20684 | -0.40945 | 0.68783 | Persistence ends | 76.1805 | 0.9854 | Night | 202601 | 2026-01-25 | 0.9854
2026-01-25 22:14 | 75.4826 | FALSE | FALSE | -1.8411 | -2.5001 | -0.68318 | -0.89697 | 0 |  |  | none | FALSE | 0 | 73.6415 | FALSE | FALSE | 0.0612 |  | 74.9036 | 0 | 0 | 0.09882 | 0.18934 | -0.52192 | 0.63108 | Normal | 76.1658 | 0.91743 | Night | 202601 | 2026-01-25 | 0.91743
2026-01-25 22:28 | 75.4826 | FALSE | FALSE | -1.5808 | -2.139 | -0.62047 | -0.8153 | 0 |  |  | none | FALSE | 0 | 73.9018 | FALSE | FALSE | 0.0582 |  | 75.0024 | 0 | 0 | 0.09882 | 0.18934 | -0.52192 | 0.55031 | Normal | 76.1031 | 0.87251 | Night | 202601 | 2026-01-25 | 0.87251
2026-01-25 22:44 | 75.2 | FALSE | FALSE | -0.96025 | -1.2934 | -0.73453 | -0.96732 | -0.2826 |  |  | none | FALSE | 0 | 74.2398 | FALSE | FALSE | 0.0178 |  | 75.0871 | 0 | -0.2826 | 0.08469 | 0.20684 | -1.7757 | 0.42369 | Normal | 75.9345 | 0.26637 | Night | 202601 | 2026-01-25 | 0.26637
2026-01-25 22:59 | 75.4826 | FALSE | FALSE | -1.041 | -1.3984 | -0.39121 | -0.51561 | 0.2826 |  |  | none | FALSE | 0 | 74.4416 | FALSE | FALSE | 0.0605 |  | 75.1577 | 0 | 0.2826 | 0.07056 | 0.18023 | 1.1765 | 0.35806 | Normal | 75.8738 | 0.9074 | Night | 202601 | 2026-01-25 | 0.9074
2026-01-25 23:14 | 75.2 | FALSE | FALSE | -0.48723 | -0.65213 | -0.51549 | -0.68082 | -0.2826 |  |  | none | FALSE | 0 | 74.7128 | FALSE | FALSE | 0.0038 |  | 75.2141 | 0 | -0.2826 | 0.05643 | 0.1964 | -1.7262 | 0.25068 | Normal | 75.7155 | -0.056367 | Night | 202601 | 2026-01-25 | 0.056367
2026-01-25 23:28 | 75.2 | FALSE | FALSE | -0.37877 | -0.50624 | -0.46355 | -0.61265 | 0 |  |  | none | FALSE | 0 | 74.8212 | FALSE | FALSE | 0.0134 |  | 75.2424 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.21058 | Normal | 75.6636 | -0.2013 | Night | 202601 | 2026-01-25 | 0.2013
2026-01-25 23:43 | 75.4826 | FALSE | FALSE | -0.61683 | -0.82392 | -0.19293 | -0.25495 | 0.2826 |  |  | none | FALSE | 0 | 74.8658 | FALSE | FALSE | 0.0698 |  | 75.2707 | 0 | 0.2826 | 0.02826 | 0.15614 | 1.6289 | 0.20244 | Normal | 75.6755 | 1.047 | Night | 202601 | 2026-01-25 | 1.047
2026-01-25 23:58 | 75.2 | FALSE | FALSE | -0.28653 | -0.38248 | -0.45609 | -0.60284 | -0.2826 |  |  | none | FALSE | 0 | 74.9135 | FALSE | FALSE | 0.0304 |  | 75.2848 | 0 | -0.2826 | 0.01413 | 0.17092 | -1.7361 | 0.18565 | Normal | 75.6561 | -0.45666 | Night | 202601 | 2026-01-25 | 0.45666
2026-01-26 00:13 | 75.2 | FALSE | FALSE | -0.23294 | -0.31073 | -0.43076 | -0.56956 | 0 |  |  | none | FALSE | 0 | 74.9671 | FALSE | FALSE | 0.0397 |  | 75.2989 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.16593 | Normal | 75.6308 | -0.59611 | Night | 202601 | 2026-01-26 | 0.59611
2026-01-26 00:28 | 75.2 | FALSE | FALSE | -0.17104 | -0.22797 | -0.39712 | -0.52532 | 0 |  |  | none | FALSE | 0 | 75.029 | FALSE | FALSE | 0.0531 |  | 75.313 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.14204 | Normal | 75.5971 | -0.79582 | Night | 202601 | 2026-01-26 | 0.79582
2026-01-26 00:43 | 75.2 | FALSE | FALSE | -0.17104 | -0.22797 | -0.39712 | -0.52532 | 0 |  |  | none | FALSE | 0 | 75.029 | FALSE | FALSE | 0.0531 |  | 75.313 | 0 | 0 | 0 | 0.15881 | 0 | 0.14204 | Normal | 75.5971 | -0.79582 | Night | 202601 | 2026-01-26 | 0.79582
2026-01-26 00:58 | 75.2 | FALSE | FALSE | -0.17104 | -0.22797 | -0.39712 | -0.52532 | 0 |  |  | none | FALSE | 0 | 75.029 | FALSE | FALSE | 0.0531 |  | 75.313 | 0 | 0 | 0 | 0.15881 | 0 | 0.14204 | Normal | 75.5971 | -0.79582 | Night | 202601 | 2026-01-26 | 0.79582
2026-01-26 01:13 | 75.2 | FALSE | FALSE | -0.17104 | -0.22797 | -0.39712 | -0.52532 | 0 |  |  | none | FALSE | 0 | 75.029 | FALSE | FALSE | 0.0531 |  | 75.313 | 0 | 0 | 0 | 0.15881 | 0 | 0.14204 | Normal | 75.5971 | -0.79582 | Night | 202601 | 2026-01-26 | 0.79582
2026-01-26 01:28 | 75.2 | FALSE | FALSE | -0.17104 | -0.22797 | -0.39712 | -0.52532 | 0 |  |  | none | FALSE | 0 | 75.029 | FALSE | FALSE | 0.0531 |  | 75.313 | 0 | 0 | 0 | 0.15881 | 0 | 0.14204 | Normal | 75.5971 | -0.79582 | Night | 202601 | 2026-01-26 | 0.79582
2026-01-26 01:43 | 75.2 | FALSE | FALSE | -0.17104 | -0.22797 | -0.39712 | -0.52532 | 0 |  |  | none | FALSE | 0 | 75.029 | FALSE | FALSE | 0.0531 |  | 75.313 | 0 | 0 | 0 | 0.15881 | 0 | 0.14204 | Normal | 75.5971 | -0.79582 | Night | 202601 | 2026-01-26 | 0.79582
2026-01-26 01:58 | 74.9174 | FALSE | FALSE | 0.049657 | 0.066238 | -0.71336 | -0.94322 | -0.2826 | 2026-01-26 04:12 | 2026-01-26 01:58 | lower | TRUE | 0 | 74.9671 | FALSE | FALSE | 0.2104 | 2.2993 | 75.2989 | 1 | -0.2826 | -0.01413 | 0.17092 | -1.5708 | 0.16593 | Extreme triggered | 75.6308 | -2.2993 | Night | 202601 | 2026-01-26 | 2.2993
2026-01-26 02:13 | 74.9174 | FALSE | FALSE | -0.0077242 | -0.010311 | -0.71422 | -0.94435 | 0 |  | 2026-01-26 01:58 | none | FALSE | 0 | 74.9097 | FALSE | FALSE | 0.2448 | 2.1282 | 75.2707 | 2 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.18049 | Extreme/elevated | 75.6316 | -1.9572 | Night | 202601 | 2026-01-26 | 1.9572
2026-01-26 02:27 | 74.9174 | FALSE | FALSE | -0.054158 | -0.072342 | -0.70414 | -0.93113 | 0 |  | 2026-01-26 01:58 | none | FALSE | 0 | 74.8632 | FALSE | FALSE | 0.2857 | 1.9903 | 75.2424 | 3 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.18957 | Persistent | 75.6215 | -1.7143 | Night | 202601 | 2026-01-26 | 1.7143
2026-01-26 02:42 | 74.9174 | FALSE | FALSE | -0.091185 | -0.12186 | -0.68465 | -0.90559 | 0 |  | 2026-01-26 01:58 | none | FALSE | 0 | 74.8262 | FALSE | FALSE | 0.3306 | 1.8752 | 75.2141 | 4 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.19396 | Persistent | 75.602 | -1.5299 | Night | 202601 | 2026-01-26 | 1.5299
2026-01-26 02:57 | 74.9174 | FALSE | FALSE | -0.11945 | -0.15969 | -0.65639 | -0.86854 | 0 |  | 2026-01-26 01:58 | none | FALSE | 0 | 74.798 | FALSE | FALSE | 0.378 | 1.777 | 75.1859 | 5 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.19396 | Persistent | 75.5738 | -1.3842 | Night | 202601 | 2026-01-26 | 1.3842
2026-01-26 03:12 | 74.9174 | FALSE | FALSE | -0.13894 | -0.1858 | -0.61936 | -0.81994 | 0 |  | 2026-01-26 01:58 | none | FALSE | 0 | 74.7785 | FALSE | FALSE | 0.4273 | 1.692 | 75.1576 | 6 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.18957 | Persistent | 75.5368 | -1.2671 | Night | 202601 | 2026-01-26 | 1.2671
2026-01-26 03:27 | 74.9174 | FALSE | TRUE | -0.14902 | -0.19931 | -0.57292 | -0.75894 | 0 |  | 2026-01-26 01:58 | none | FALSE | 0 | 74.7684 | FALSE | FALSE | 0.4783 | 1.618 | 75.1294 | 7 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.18049 | Confirmed/Materialized Shift | 75.4903 | -1.1743 | Night | 202601 | 2026-01-26 | 1.1743
2026-01-26 03:42 | 74.9174 | FALSE | TRUE | -0.17349 | -0.23211 | -0.56913 | -0.75394 | 0 |  | 2026-01-26 01:58 | none | FALSE | 0 | 74.7439 | FALSE | FALSE | 0.471 | 1.549 | 75.1152 | 8 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.18565 | Confirmed/Materialized Shift | 75.4865 | -1.0655 | Night | 202601 | 2026-01-26 | 1.0655
2026-01-26 03:57 | 74.9174 | FALSE | TRUE | -0.16857 | -0.22551 | -0.50769 | -0.6731 | 0 |  | 2026-01-26 01:58 | none | FALSE | 0 | 74.7488 | FALSE | FALSE | 0.4669 | 1.4883 | 75.087 | 9 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.16906 | Confirmed/Materialized Shift | 75.4251 | -1.0029 | Night | 202601 | 2026-01-26 | 1.0029
2026-01-26 04:12 | 74.9174 | FALSE | FALSE | -0.18641 | -0.24944 | -0.49727 | -0.65938 | 0 |  |  | none | FALSE | 0 | 74.731 | FALSE | FALSE | 0.0606 |  | 75.0728 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.17092 | Persistence ends | 75.4147 | -0.90938 | Night | 202601 | 2026-01-26 | 0.90938
2026-01-26 04:27 | 74.9174 | FALSE | FALSE | -0.20176 | -0.27004 | -0.48436 | -0.64238 | 0 |  |  | none | FALSE | 0 | 74.7156 | FALSE | FALSE | 0.0549 |  | 75.0587 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.17153 | Normal | 75.4018 | -0.82375 | Night | 202601 | 2026-01-26 | 0.82375
2026-01-26 04:42 | 74.9174 | FALSE | FALSE | -0.17104 | -0.22883 | -0.39712 | -0.52729 | 0 |  |  | none | FALSE | 0 | 74.7464 | FALSE | FALSE | 0.0531 |  | 75.0304 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.14204 | Normal | 75.3145 | -0.79582 | Night | 202601 | 2026-01-26 | 0.79582
2026-01-26 04:57 | 74.9174 | FALSE | FALSE | -0.17768 | -0.23773 | -0.3755 | -0.49871 | 0 |  |  | none | FALSE | 0 | 74.7397 | FALSE | FALSE | 0.0477 |  | 75.0163 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13829 | Normal | 75.2929 | -0.71522 | Night | 202601 | 2026-01-26 | 0.71522
2026-01-26 05:12 | 74.9174 | FALSE | FALSE | -0.18096 | -0.24213 | -0.35052 | -0.46569 | 0 |  |  | none | FALSE | 0 | 74.7364 | FALSE | FALSE | 0.0425 |  | 75.0022 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13287 | Normal | 75.2679 | -0.63808 | Night | 202601 | 2026-01-26 | 0.63808
2026-01-26 05:26 | 74.9174 | FALSE | FALSE | -0.18045 | -0.24144 | -0.32175 | -0.42763 | 0 |  |  | none | FALSE | 0 | 74.737 | FALSE | FALSE | 0.0375 |  | 74.9881 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.12555 | Normal | 75.2391 | -0.56273 | Night | 202601 | 2026-01-26 | 0.56273
2026-01-26 05:41 | 74.9174 | FALSE | FALSE | -0.17543 | -0.23472 | -0.28847 | -0.38358 | 0 |  |  | none | FALSE | 0 | 74.742 | FALSE | FALSE | 0.0325 |  | 74.9739 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.11598 | Normal | 75.2059 | -0.48734 | Night | 202601 | 2026-01-26 | 0.48734
2026-01-26 05:56 | 74.9174 | FALSE | FALSE | -0.16467 | -0.22029 | -0.24945 | -0.33186 | 0 |  |  | none | FALSE | 0 | 74.7527 | FALSE | FALSE | 0.0273 |  | 74.9598 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.10353 | Normal | 75.1668 | -0.40945 | Night | 202601 | 2026-01-26 | 0.40945
2026-01-26 06:11 | 74.9174 | FALSE | FALSE | -0.1457 | -0.19487 | -0.20222 | -0.2692 | 0 |  |  | none | FALSE | 0 | 74.7717 | FALSE | FALSE | 0.0217 |  | 74.9457 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.086982 | Normal | 75.1196 | -0.32489 | Night | 202601 | 2026-01-26 | 0.32489
2026-01-26 06:26 | 74.9174 | FALSE | FALSE | -0.11225 | -0.15006 | -0.14051 | -0.18721 | 0 |  |  | none | FALSE | 0 | 74.8051 | FALSE | FALSE | 0.0149 |  | 74.9315 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.063191 | Normal | 75.0579 | -0.22361 | Night | 202601 | 2026-01-26 | 0.22361
2026-01-26 06:41 | 74.9174 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.9174 | FALSE | FALSE | 0 |  | 74.9174 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0 | Normal | 74.9174 |  | Night | 202601 | 2026-01-26
2026-01-26 06:56 | 74.9174 | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  |  | none | FALSE | 0 | 74.9174 | FALSE | FALSE | 0 |  | 74.9174 | 0 | 0 | 0 | 0 |  | 0 | Normal | 74.9174 |  | Night | 202601 | 2026-01-26
2026-01-26 07:11 | 74.6348 | TRUE | FALSE | 0.14209 | 0.19002 | -0.39485 | -0.52626 | -0.2826 | 2026-01-26 07:26 | 2026-01-26 07:11 | lower | TRUE | 1 | 74.7769 | FALSE | FALSE | 0.3689 | 4.2485 | 74.9033 | 1 | -0.2826 | -0.01413 | 0.063191 | -4.2485 | 0.063191 | Extreme triggered | 75.0297 | -4.2485 | Day | 202601 | 2026-01-26 | 4.2485
2026-01-26 07:26 | 74.9174 | TRUE | FALSE | -0.14051 | -0.18791 | -0.11225 | -0.14961 | 0.2826 |  |  | none | FALSE | 2 | 74.7769 | TRUE | FALSE | 0.072 |  | 74.9033 | 0 | 0.2826 | 0 | 0.091688 | 3.0822 | 0.063191 | Persistence ends | 75.0297 | 0.22361 | Day | 202601 | 2026-01-26 | 0.22361
2026-01-26 07:30 | 74.6348 | TRUE | FALSE | 0.080375 | 0.10758 | -0.4283 | -0.57059 | -0.2826 | 2026-01-26 08:16 | 2026-01-26 07:30 | lower | TRUE | 3 | 74.7152 | TRUE | FALSE | 0.3378 | 2.924 | 74.8891 | 1 | -0.2826 | -0.01413 | 0.11135 | -2.411 | 0.086982 | Extreme triggered | 75.0631 | -2.924 | Day | 202601 | 2026-01-26 | 2.924
2026-01-26 07:45 | 74.6348 | FALSE | FALSE | 0.03315 | 0.044397 | -0.44727 | -0.59571 | 0 |  | 2026-01-26 07:30 | lower | TRUE | 3 | 74.668 | FALSE | FALSE | 0.3547 | 2.6221 | 74.875 | 2 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.10353 | Extreme/elevated | 75.0821 | -2.3202 | Day | 202601 | 2026-01-26 | 2.3202
2026-01-26 08:00 | 74.6348 | FALSE | FALSE | -0.0058732 | -0.0078699 | -0.45803 | -0.60996 | 0 |  | 2026-01-26 07:30 | none | FALSE | 3 | 74.6289 | FALSE | FALSE | 0.3871 | 2.3979 | 74.8609 | 3 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.11598 | Persistent | 75.0928 | -1.9494 | Day | 202601 | 2026-01-26 | 1.9494
2026-01-26 08:16 | 74.9174 | TRUE | FALSE | -0.28847 | -0.38654 | -0.17543 | -0.23362 | 0.2826 |  |  | none | FALSE | 4 | 74.6289 | TRUE | FALSE | 0.1468 |  | 74.8609 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.11598 | Persistence ends | 75.0928 | 0.48734 | Day | 202601 | 2026-01-26 | 0.48734
2026-01-26 08:30 | 74.6348 | FALSE | FALSE | -0.039147 | -0.052479 | -0.46305 | -0.61659 | -0.2826 |  |  | none | FALSE | 4 | 74.5957 | FALSE | FALSE | 0.2268 |  | 74.8468 | 0 | -0.2826 | -0.01413 | 0.14424 | -1.8612 | 0.12555 | Normal | 75.0978 | -1.6882 | Day | 202601 | 2026-01-26 | 1.6882
2026-01-26 08:30 | 74.6348 | FALSE | FALSE | -0.067916 | -0.09108 | -0.46356 | -0.61726 | 0 |  |  | none | FALSE | 4 | 74.5669 | FALSE | FALSE | 0.2135 |  | 74.8326 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.13287 | Normal | 75.0984 | -1.4888 | Day | 202601 | 2026-01-26 | 1.4888
2026-01-26 08:33 | 74.6348 | FALSE | FALSE | -0.092897 | -0.12462 | -0.46028 | -0.61293 | 0 |  |  | none | FALSE | 4 | 74.5419 | FALSE | FALSE | 0.2028 |  | 74.8185 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.13829 | Normal | 75.0951 | -1.3283 | Day | 202601 | 2026-01-26 | 1.3283
2026-01-26 08:48 | 74.0714 | TRUE | FALSE | 0.27536 | 0.37037 | -1.1342 | -1.5082 | -0.5634 | 2026-01-26 10:29 | 2026-01-26 08:48 | lower | TRUE | 5 | 74.3468 | TRUE | FALSE | 0.4188 | 3.2824 | 74.7762 | 1 | -0.5634 | -0.0423 | 0.18931 | -2.7526 | 0.21472 | Extreme triggered | 75.2056 | -3.2824 | Day | 202601 | 2026-01-26 | 3.2824
2026-01-26 09:03 | 73.2236 | TRUE | FALSE | 0.65704 | 0.88933 | -2.2788 | -3.0181 | -0.8478 |  | 2026-01-26 08:48 | lower | TRUE | 5 | 73.8806 | TRUE | FALSE | 0.4985 | 3.4515 | 74.6915 | 2 | -0.8478 | -0.08469 | 0.26077 | -2.9263 | 0.40543 | Extreme/elevated | 75.5024 | -3.6206 | Day | 202601 | 2026-01-26 | 3.6206
2026-01-26 09:18 | 72.095 | TRUE | FALSE | 1.0475 | 1.4321 | -3.8633 | -5.0861 | -1.1286 |  | 2026-01-26 08:48 | lower | TRUE | 5 | 73.1425 | TRUE | TRUE | 0.5468 | 3.4637 | 74.5504 | 3 | -1.1286 | -0.14112 | 0.34875 | -2.8315 | 0.70396 | Persistent | 75.9583 | -3.488 | Day | 202601 | 2026-01-26 | 3.488
2026-01-26 09:28 | 71.8124 | FALSE | FALSE | 0.73054 | 1.007 | -4.4349 | -5.8165 | -0.2826 |  | 2026-01-26 08:48 | lower | TRUE | 4 | 72.5429 | FALSE | TRUE | 0.5288 | 3.295 | 74.3951 | 4 | -0.2826 | -0.15525 | 0.34846 | -0.36547 | 0.92609 | Persistent | 76.2473 | -2.7888 | Day | 202601 | 2026-01-26 | 2.7888
2026-01-26 09:30 | 72.095 | FALSE | FALSE | 0.060645 | 0.084047 | -4.2574 | -5.576 | 0.2826 |  | 2026-01-26 08:48 | lower | TRUE | 4 | 72.1556 | FALSE | TRUE | 0.5372 | 3.0475 | 74.254 | 5 | 0.2826 | -0.14112 | 0.3606 | 1.175 | 1.0492 | Persistent | 76.3524 | -2.0578 | Day | 202601 | 2026-01-26 | 2.0578
2026-01-26 09:45 | 72.3758 | FALSE | FALSE | -0.48162 | -0.6699 | -3.9839 | -5.2173 | 0.2808 |  | 2026-01-26 08:48 | none | FALSE | 4 | 71.8942 | FALSE | FALSE | 0.5617 | 2.801 | 74.1269 | 6 | 0.2808 | -0.12708 | 0.37168 | 1.0974 | 1.1164 | Persistent | 76.3597 | -1.5686 | Day | 202601 | 2026-01-26 | 1.5686
2026-01-26 10:00 | 72.3758 | FALSE | TRUE | -0.70644 | -0.98569 | -3.9545 | -5.1808 | 0 |  | 2026-01-26 08:48 | none | FALSE | 3 | 71.6694 | FALSE | FALSE | 0.5786 | 2.6 | 73.9998 | 7 | 0 | -0.12708 | 0.37168 | 0.3419 | 1.1652 | Confirmed/Materialized Shift | 76.3303 | -1.3937 | Day | 202601 | 2026-01-26 | 1.3937
2026-01-26 10:15 | 72.6584 | FALSE | TRUE | -1.1335 | -1.5848 | -3.5905 | -4.7089 | 0.2826 |  | 2026-01-26 08:48 | none | FALSE | 3 | 71.5249 | FALSE | FALSE | 0.5551 | 2.405 | 73.8869 | 8 | 0.2826 | -0.11295 | 0.382 | 1.0355 | 1.181 | Confirmed/Materialized Shift | 76.2489 | -1.0402 | Day | 202601 | 2026-01-26 | 1.0402
2026-01-26 10:29 | 72.6584 | FALSE | FALSE | -1.255 | -1.7576 | -3.4861 | -4.5783 | 0 |  |  | none | FALSE | 3 | 71.4034 | FALSE | FALSE | 0.1485 |  | 73.7739 | 0 | 0 | -0.11295 | 0.382 | 0.29568 | 1.1853 | Persistence ends | 76.1445 | -0.94117 | Day | 202601 | 2026-01-26 | 0.94117
2026-01-26 10:44 | 72.941 | FALSE | FALSE | -1.6002 | -2.2431 | -3.0685 | -4.037 | 0.2826 |  |  | none | FALSE | 3 | 71.3408 | FALSE | FALSE | 0.1276 |  | 73.6751 | 0 | 0.2826 | -0.09882 | 0.3915 | 0.97424 | 1.1672 | Normal | 76.0095 | -0.62898 | Day | 202601 | 2026-01-26 | 0.62898
2026-01-26 10:59 | 72.941 | FALSE | FALSE | -1.6443 | -2.3063 | -2.9149 | -3.8427 | 0 |  |  | none | FALSE | 2 | 71.2967 | FALSE | FALSE | 0.0943 |  | 73.5763 | 0 | 0 | -0.09882 | 0.3915 | 0.25241 | 1.1398 | Normal | 75.8559 | -0.55738 | Day | 202601 | 2026-01-26 | 0.55738
2026-01-26 11:15 | 73.2236 | FALSE | FALSE | -1.9463 | -2.7306 | -2.5106 | -3.315 | 0.2826 |  |  | none | FALSE | 1 | 71.2773 | FALSE | FALSE | 0.0455 |  | 73.5058 | 0 | 0.2826 | -0.07056 | 0.39789 | 0.88759 | 1.1142 | Normal | 75.7342 | -0.25322 | Day | 202601 | 2026-01-26 | 0.25322
2026-01-26 11:29 | 73.2236 | FALSE | FALSE | -1.9316 | -2.7095 | -2.3266 | -3.0795 | 0 |  |  | none | FALSE | 0 | 71.292 | FALSE | FALSE | 0.0124 |  | 73.4211 | 0 | 0 | -0.08469 | 0.38962 | 0.21737 | 1.0645 | Normal | 75.5502 | -0.18549 | Day | 202601 | 2026-01-26 | 0.18549
2026-01-26 11:44 | 73.2236 | FALSE | FALSE | -1.925 | -2.6999 | -2.1788 | -2.8895 | 0 |  |  | none | FALSE | 0 | 71.2986 | FALSE | FALSE | 0.0082 |  | 73.3505 | 0 | 0 | -0.07056 | 0.38718 | 0.18224 | 1.0259 | Normal | 75.4024 | -0.12369 | Day | 202601 | 2026-01-26 | 0.12369
2026-01-26 11:59 | 73.5062 | FALSE | FALSE | -2.1754 | -3.0498 | -1.7512 | -2.3269 | 0.2826 |  |  | none | FALSE | 0 | 71.3308 | FALSE | FALSE | 0.0144 |  | 73.2941 | 0 | 0.2826 | -0.05643 | 0.39497 | 0.85837 | 0.98166 | Normal | 75.2574 | 0.21609 | Day | 202601 | 2026-01-26 | 0.21609
2026-01-26 12:14 | 73.5062 | FALSE | FALSE | -2.132 | -2.987 | -1.5948 | -2.1236 | 0 |  |  | none | FALSE | 0 | 71.3742 | FALSE | FALSE | 0.0192 |  | 73.2376 | 0 | 0 | -0.05643 | 0.39497 | 0.14287 | 0.9317 | Normal | 75.101 | 0.28825 | Day | 202601 | 2026-01-26 | 0.28825
2026-01-26 12:29 | 73.5062 | FALSE | FALSE | -2.0339 | -2.8458 | -1.3557 | -1.8109 | 0 |  |  | none | FALSE | 0 | 71.4723 | FALSE | FALSE | 0.0267 |  | 73.1671 | 0 | 0 | -0.07056 | 0.38718 | 0.18224 | 0.84741 | Normal | 74.8619 | 0.40018 | Day | 202601 | 2026-01-26 | 0.40018
2026-01-26 12:44 | 73.2236 | FALSE | FALSE | -1.6758 | -2.3423 | -1.4217 | -1.9046 | -0.2826 |  |  | none | FALSE | 0 | 71.5478 | FALSE | FALSE | 0.0109 |  | 73.0965 | 0 | -0.2826 | -0.07056 | 0.38718 | -0.54765 | 0.77437 | Normal | 74.6453 | 0.16411 | Day | 202601 | 2026-01-26 | 0.16411
2026-01-26 12:59 | 72.941 | FALSE | FALSE | -1.2986 | -1.8126 | -1.4403 | -1.9363 | -0.2826 |  |  | none | FALSE | 0 | 71.6424 | FALSE | FALSE | 0.0069 |  | 73.0118 | 0 | -0.2826 | -0.08469 | 0.38962 | -0.50796 | 0.68472 | Normal | 74.3813 | -0.10344 | Day | 202601 | 2026-01-26 | 0.10344
2026-01-26 13:14 | 72.941 | FALSE | FALSE | -1.1504 | -1.6024 | -1.1227 | -1.5158 | 0 |  |  | none | FALSE | 0 | 71.7906 | FALSE | FALSE | 0.0016 |  | 72.9271 | 0 | 0 | -0.08469 | 0.38962 | 0.21737 | 0.56826 | Normal | 74.0637 | 0.02439 | Day | 202601 | 2026-01-26 | 0.02439
2026-01-26 13:28 | 72.941 | FALSE | FALSE | -1.0717 | -1.4912 | -0.93092 | -1.2602 | 0 |  |  | none | FALSE | 0 | 71.8693 | FALSE | FALSE | 0.0094 |  | 72.8706 | 0 | 0 | -0.05652 | 0.37321 | 0.15144 | 0.50065 | Normal | 73.8719 | 0.14058 | Day | 202601 | 2026-01-26 | 0.14058
2026-01-26 13:43 | 72.941 | FALSE | FALSE | -1.0727 | -1.4926 | -0.90371 | -1.2238 | 0 |  |  | none | FALSE | 0 | 71.8683 | FALSE | FALSE | 0.0114 |  | 72.8565 | 0 | 0 | -0.01413 | 0.32343 | 0.043688 | 0.49411 | Normal | 73.8447 | 0.17103 | Day | 202601 | 2026-01-26 | 0.17103
2026-01-26 13:59 | 72.941 | FALSE | FALSE | -0.96334 | -1.3384 | -0.87892 | -1.1906 | 0 |  |  | none | FALSE | 0 | 71.9777 | FALSE | FALSE | 0.0061 |  | 72.8988 | 0 | 0 | 0.0423 | 0.18945 | -0.22327 | 0.46056 | Normal | 73.8199 | 0.091649 | Day | 202601 | 2026-01-26 | 0.091649
2026-01-26 14:14 | 72.941 | FALSE | FALSE | -0.75192 | -1.0416 | -0.78036 | -1.0585 | 0 |  |  | none | FALSE | 0 | 72.1891 | FALSE | FALSE | 0.0025 |  | 72.9552 | 0 | 0 | 0.05643 | 0.17384 | -0.3246 | 0.38307 | Normal | 73.7214 | -0.037121 | Day | 202601 | 2026-01-26 | 0.037121
2026-01-26 14:28 | 73.2236 | FALSE | FALSE | -0.86993 | -1.2023 | -0.44603 | -0.60545 | 0.2826 |  |  | none | FALSE | 0 | 72.3537 | FALSE | FALSE | 0.0429 |  | 73.0117 | 0 | 0.2826 | 0.05643 | 0.17384 | 1.301 | 0.32899 | Normal | 73.6696 | 0.64424 | Day | 202601 | 2026-01-26 | 0.64424
2026-01-26 14:43 | 73.2236 | FALSE | FALSE | -0.76093 | -1.0501 | -0.42181 | -0.57275 | 0 |  |  | none | FALSE | 0 | 72.4627 | FALSE | FALSE | 0.0382 |  | 73.054 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.29568 | Normal | 73.6454 | 0.57345 | Day | 202601 | 2026-01-26 | 0.57345
2026-01-26 14:58 | 73.2236 | FALSE | FALSE | -0.62853 | -0.8658 | -0.37419 | -0.50842 | 0 |  |  | none | FALSE | 0 | 72.5951 | FALSE | FALSE | 0.0338 |  | 73.0964 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.25068 | Normal | 73.5978 | 0.5073 | Day | 202601 | 2026-01-26 | 0.5073
2026-01-26 15:13 | 73.2236 | FALSE | FALSE | -0.55826 | -0.76827 | -0.36044 | -0.48984 | 0 |  |  | none | FALSE | 0 | 72.6653 | FALSE | FALSE | 0.0287 |  | 73.1247 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.22968 | Normal | 73.584 | 0.43065 | Day | 202601 | 2026-01-26 | 0.43065
2026-01-26 15:28 | 73.2236 | FALSE | FALSE | -0.47553 | -0.65367 | -0.33423 | -0.45438 | 0 |  |  | none | FALSE | 0 | 72.7481 | FALSE | FALSE | 0.0233 |  | 73.153 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.20244 | Normal | 73.5578 | 0.34899 | Day | 202601 | 2026-01-26 | 0.34899
2026-01-26 15:43 | 73.2236 | FALSE | FALSE | -0.44982 | -0.6181 | -0.33678 | -0.45782 | 0 |  |  | none | FALSE | 0 | 72.7738 | FALSE | FALSE | 0.0192 |  | 73.1671 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.19665 | Normal | 73.5604 | 0.28742 | Day | 202601 | 2026-01-26 | 0.28742
2026-01-26 15:58 | 73.2236 | FALSE | FALSE | -0.42154 | -0.57902 | -0.33676 | -0.4578 | 0 |  |  | none | FALSE | 0 | 72.8021 | FALSE | FALSE | 0.0149 |  | 73.1812 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.18957 | Normal | 73.5604 | 0.22361 | Day | 202601 | 2026-01-26 | 0.22361
2026-01-26 16:13 | 73.5062 | FALSE | FALSE | -0.71678 | -0.98473 | -0.095058 | -0.12915 | 0.2826 |  |  | none | FALSE | 0 | 72.7894 | FALSE | FALSE | 0.1021 |  | 73.1953 | 0 | 0.2826 | 0.01413 | 0.14424 | 1.8612 | 0.20296 | Normal | 73.6013 | 1.5316 | Day | 202601 | 2026-01-26 | 1.5316
2026-01-26 16:28 | 73.2236 | FALSE | FALSE | -0.43418 | -0.59649 | -0.37766 | -0.51311 | -0.2826 |  |  | none | FALSE | 0 | 72.7894 | FALSE | FALSE | 0.0093 |  | 73.1953 | 0 | -0.2826 | 0 | 0.15881 | -1.7795 | 0.20296 | Normal | 73.6013 | 0.13924 | Day | 202601 | 2026-01-26 | 0.13924
2026-01-26 16:43 | 73.2236 | FALSE | FALSE | -0.43418 | -0.59649 | -0.37766 | -0.51311 | 0 |  |  | none | FALSE | 0 | 72.7894 | FALSE | FALSE | 0.0093 |  | 73.1953 | 0 | 0 | 0 | 0.15881 | 0 | 0.20296 | Normal | 73.6013 | 0.13924 | Day | 202601 | 2026-01-26 | 0.13924
2026-01-26 16:58 | 73.2236 | FALSE | FALSE | -0.42154 | -0.57902 | -0.33676 | -0.4578 | 0 |  |  | none | FALSE | 0 | 72.8021 | FALSE | FALSE | 0.0149 |  | 73.1812 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.18957 | Normal | 73.5604 | 0.22361 | Day | 202601 | 2026-01-26 | 0.22361
2026-01-26 17:13 | 73.2236 | FALSE | FALSE | -0.40445 | -0.55542 | -0.29141 | -0.39639 | 0 |  |  | none | FALSE | 0 | 72.8192 | FALSE | FALSE | 0.0217 |  | 73.1671 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.17396 | Normal | 73.515 | 0.32489 | Day | 202601 | 2026-01-26 | 0.32489
2026-01-26 17:27 | 73.2236 | FALSE | FALSE | -0.38158 | -0.52384 | -0.24028 | -0.32707 | 0 |  |  | none | FALSE | 0 | 72.842 | FALSE | FALSE | 0.0303 |  | 73.153 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.15546 | Normal | 73.4639 | 0.45445 | Day | 202601 | 2026-01-26 | 0.45445
2026-01-26 17:42 | 73.2236 | FALSE | FALSE | -0.38158 | -0.52384 | -0.24028 | -0.32707 | 0 |  |  | none | FALSE | 0 | 72.842 | FALSE | FALSE | 0.0303 |  | 73.153 | 0 | 0 | 0 | 0.12967 | 0 | 0.15546 | Normal | 73.4639 | 0.45445 | Day | 202601 | 2026-01-26 | 0.45445
2026-01-26 17:57 | 72.941 | TRUE | FALSE | -0.098978 | -0.13588 | -0.52288 | -0.71175 | -0.2826 |  |  | none | FALSE | 1 | 72.842 | FALSE | FALSE | 0.1195 |  | 73.153 | 0 | -0.2826 | 0 | 0.12967 | -2.1794 | 0.15546 | Normal | 73.4639 | -1.3633 | Day | 202601 | 2026-01-26 | 1.3633
2026-01-26 18:12 | 72.941 | FALSE | FALSE | -0.098978 | -0.13588 | -0.52288 | -0.71175 | 0 |  |  | none | FALSE | 1 | 72.842 | FALSE | FALSE | 0.1195 |  | 73.153 | 0 | 0 | 0 | 0.12967 | 0 | 0.15546 | Normal | 73.4639 | -1.3633 | Night | 202601 | 2026-01-26 | 1.3633
2026-01-26 18:27 | 72.941 | FALSE | FALSE | -0.098978 | -0.13588 | -0.52288 | -0.71175 | 0 |  |  | none | FALSE | 1 | 72.842 | FALSE | FALSE | 0.1195 |  | 73.153 | 0 | 0 | 0 | 0.12967 | 0 | 0.15546 | Normal | 73.4639 | -1.3633 | Night | 202601 | 2026-01-26 | 1.3633
2026-01-26 18:31 | 72.941 | FALSE | FALSE | -0.098978 | -0.13588 | -0.52288 | -0.71175 | 0 |  |  | none | FALSE | 1 | 72.842 | FALSE | FALSE | 0.1195 |  | 73.153 | 0 | 0 | 0 | 0.12967 | 0 | 0.15546 | Normal | 73.4639 | -1.3633 | Night | 202601 | 2026-01-26 | 1.3633
2026-01-26 18:46 | 72.941 | FALSE | FALSE | -0.098978 | -0.13588 | -0.52288 | -0.71175 | 0 |  |  | none | FALSE | 1 | 72.842 | FALSE | FALSE | 0.1195 |  | 73.153 | 0 | 0 | 0 | 0.12967 | 0 | 0.15546 | Normal | 73.4639 | -1.3633 | Night | 202601 | 2026-01-26 | 1.3633
2026-01-26 19:01 | 73.5062 | TRUE | FALSE | -0.65684 | -0.90165 | -0.0068632 | -0.009336 | 0.5652 |  |  | none | FALSE | 2 | 72.8494 | TRUE | FALSE | 0.1877 |  | 73.1812 | 0 | 0.5652 | 0.02826 | 0.18107 | 2.9654 | 0.16593 | Normal | 73.5131 | 1.9586 | Night | 202601 | 2026-01-26 | 1.9586
2026-01-26 19:16 | 73.7888 | FALSE | FALSE | -1.0084 | -1.3855 | 0.15026 | 0.20405 | 0.2826 | 2026-01-26 20:44 | 2026-01-26 19:16 | upper | TRUE | 2 | 72.7804 | FALSE | FALSE | 0.2943 | 2.7004 | 73.2095 | 1 | 0.2826 | 0.02826 | 0.18107 | 1.4047 | 0.21454 | Extreme triggered | 73.6385 | 2.7004 | Night | 202601 | 2026-01-26 | 2.7004
2026-01-26 19:30 | 74.0714 | FALSE | FALSE | -1.3965 | -1.9216 | 0.24256 | 0.32855 | 0.2826 |  | 2026-01-26 19:16 | upper | TRUE | 2 | 72.6749 | FALSE | FALSE | 0.3608 | 2.7706 | 73.2519 | 2 | 0.2826 | 0.04239 | 0.18957 | 1.2671 | 0.28849 | Extreme/elevated | 73.8288 | 2.8408 | Night | 202601 | 2026-01-26 | 2.8408
2026-01-26 19:45 | 74.0714 | FALSE | FALSE | -1.4602 | -2.011 | 0.094093 | 0.12719 | 0 |  | 2026-01-26 19:16 | upper | TRUE | 2 | 72.6112 | FALSE | TRUE | 0.3803 | 2.6056 | 73.2943 | 3 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.34153 | Persistent | 73.9773 | 2.2755 | Night | 202601 | 2026-01-26 | 2.2755
2026-01-26 20:00 | 74.0714 | FALSE | FALSE | -1.4997 | -2.0665 | -0.030158 | -0.040698 | 0 |  | 2026-01-26 19:16 | none | FALSE | 2 | 72.5717 | FALSE | FALSE | 0.4138 | 2.4345 | 73.3366 | 4 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.38246 | Persistent | 74.1016 | 1.9211 | Night | 202601 | 2026-01-26 | 1.9211
2026-01-26 20:15 | 74.0714 | FALSE | FALSE | -1.5221 | -2.0981 | -0.13739 | -0.18514 | 0 |  | 2026-01-26 19:16 | none | FALSE | 1 | 72.5493 | FALSE | FALSE | 0.4255 | 2.2813 | 73.379 | 5 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.41488 | Persistent | 74.2088 | 1.6688 | Night | 202601 | 2026-01-26 | 1.6688
2026-01-26 20:29 | 74.0714 | FALSE | FALSE | -1.5313 | -2.111 | -0.23137 | -0.31138 | 0 |  | 2026-01-26 19:16 | none | FALSE | 1 | 72.5401 | FALSE | FALSE | 0.4698 | 2.1469 | 73.4214 | 6 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.44067 | Persistent | 74.3028 | 1.475 | Night | 202601 | 2026-01-26 | 1.475
2026-01-26 20:44 | 73.7888 | FALSE | FALSE | -1.23 | -1.6951 | -0.55171 | -0.74214 | -0.2826 |  |  | none | FALSE | 1 | 72.5588 | FALSE | FALSE | 0.0793 |  | 73.4497 | 0 | -0.2826 | 0.02826 | 0.20296 | -1.5316 | 0.44542 | Persistence ends | 74.3405 | 0.76135 | Night | 202601 | 2026-01-26 | 0.76135
2026-01-26 20:59 | 73.7888 | FALSE | FALSE | -1.2285 | -1.693 | -0.57849 | -0.77789 | 0 |  |  | none | FALSE | 1 | 72.5603 | FALSE | FALSE | 0.0765 |  | 73.4638 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.45174 | Normal | 74.3673 | 0.71942 | Night | 202601 | 2026-01-26 | 0.71942
2026-01-26 21:14 | 73.7888 | FALSE | FALSE | -1.2039 | -1.6586 | -0.61047 | -0.82053 | 0 |  |  | none | FALSE | 1 | 72.5849 | FALSE | FALSE | 0.0722 |  | 73.4921 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.4536 | Normal | 74.3993 | 0.65417 | Night | 202601 | 2026-01-26 | 0.65417
2026-01-26 21:29 | 73.7888 | FALSE | FALSE | -1.1757 | -1.6191 | -0.63873 | -0.85819 | 0 |  |  | none | FALSE | 0 | 72.6131 | FALSE | FALSE | 0.0395 |  | 73.5203 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.4536 | Normal | 74.4275 | 0.59187 | Night | 202601 | 2026-01-26 | 0.59187
2026-01-26 21:44 | 73.7888 | FALSE | FALSE | -1.1437 | -1.5744 | -0.66327 | -0.89087 | 0 |  |  | none | FALSE | 0 | 72.6451 | FALSE | FALSE | 0.0354 |  | 73.5486 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.45174 | Normal | 74.4521 | 0.53174 | Night | 202601 | 2026-01-26 | 0.53174
2026-01-26 21:59 | 73.7888 | FALSE | FALSE | -1.108 | -1.5244 | -0.68406 | -0.91853 | 0 |  |  | none | FALSE | 0 | 72.6808 | FALSE | FALSE | 0.0315 |  | 73.5768 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.448 | Normal | 74.4729 | 0.4731 | Night | 202601 | 2026-01-26 | 0.4731
2026-01-26 22:14 | 73.5062 | FALSE | FALSE | -0.79657 | -1.0955 | -0.96613 | -1.2973 | -0.2826 |  |  | none | FALSE | 0 | 72.7096 | FALSE | FALSE | 0.0128 |  | 73.591 | 0 | -0.2826 | 0.01413 | 0.19396 | -1.5299 | 0.44067 | Normal | 74.4723 | -0.19239 | Night | 202601 | 2026-01-26 | 0.19239
2026-01-26 22:29 | 73.5062 | FALSE | FALSE | -0.76655 | -1.0538 | -0.96437 | -1.295 | 0 |  |  | none | FALSE | 0 | 72.7396 | FALSE | FALSE | 0.0152 |  | 73.6051 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.43273 | Normal | 74.4706 | -0.22857 | Night | 202601 | 2026-01-26 | 0.22857
2026-01-26 22:44 | 73.2236 | FALSE | FALSE | -0.4326 | -0.5943 | -1.2239 | -1.6439 | -0.2826 |  |  | none | FALSE | 0 | 72.791 | FALSE | FALSE | 0.0637 |  | 73.6192 | 0 | -0.2826 | 0.01413 | 0.19396 | -1.5299 | 0.41412 | Normal | 74.4475 | -0.95538 | Night | 202601 | 2026-01-26 | 0.95538
2026-01-26 22:59 | 73.2236 | FALSE | FALSE | -0.37842 | -0.51949 | -1.198 | -1.6097 | 0 |  |  | none | FALSE | 0 | 72.8452 | FALSE | FALSE | 0.0693 |  | 73.6334 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.3941 | Normal | 74.4216 | -1.0398 | Night | 202601 | 2026-01-26 | 1.0398
2026-01-26 23:14 | 73.2236 | FALSE | FALSE | -0.32097 | -0.44028 | -1.1688 | -1.5711 | 0 |  |  | none | FALSE | 0 | 72.9026 | FALSE | FALSE | 0.0759 |  | 73.6475 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.37244 | Normal | 74.3924 | -1.1382 | Night | 202601 | 2026-01-26 | 1.1382
2026-01-26 23:28 | 73.2236 | FALSE | FALSE | -0.25964 | -0.35585 | -1.1357 | -1.5273 | 0 |  |  | none | FALSE | 0 | 72.964 | FALSE | FALSE | 0.0837 |  | 73.6616 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.34883 | Normal | 74.3593 | -1.2557 | Night | 202601 | 2026-01-26 | 1.2557
2026-01-26 23:43 | 73.2236 | FALSE | FALSE | -0.19357 | -0.26506 | -1.0979 | -1.4772 | 0 |  |  | none | FALSE | 0 | 73.03 | FALSE | FALSE | 0.0934 |  | 73.6758 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.32287 | Normal | 74.3215 | -1.4005 | Night | 202601 | 2026-01-26 | 1.4005
2026-01-26 23:58 | 72.941 | FALSE | FALSE | -0.015448 | -0.021184 | -1.4284 | -1.9207 | -0.2826 |  |  | none | FALSE | 0 | 72.9256 | FALSE | FALSE | 0.1305 |  | 73.6475 | 0 | -0.2826 | -0.02826 | 0.15614 | -1.6289 | 0.36097 | Normal | 74.3694 | -1.9572 | Night | 202601 | 2026-01-26 | 1.9572
2026-01-27 00:14 | 72.941 | FALSE | FALSE | -0.11981 | -0.16452 | -1.448 | -1.9466 | 0 |  |  | none | FALSE | 0 | 72.8212 | FALSE | FALSE | 0.113 |  | 73.6051 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.39196 | Normal | 74.389 | -1.6943 | Night | 202601 | 2026-01-27 | 1.6943
2026-01-27 00:28 | 72.941 | FALSE | FALSE | -0.19749 | -0.27148 | -1.4127 | -1.8999 | 0 |  |  | none | FALSE | 0 | 72.7435 | FALSE | FALSE | 0.1006 |  | 73.5486 | 0 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.40254 | Normal | 74.3537 | -1.5094 | Night | 202601 | 2026-01-27 | 1.5094
2026-01-27 00:43 | 72.6584 | FALSE | FALSE | -0.038608 | -0.053165 | -1.6777 | -2.2569 | -0.2826 |  |  | none | FALSE | 0 | 72.6198 | FALSE | FALSE | 0.1273 |  | 73.4779 | 0 | -0.2826 | -0.07065 | 0.12555 | -1.6882 | 0.42907 | Normal | 74.3361 | -1.91 | Night | 202601 | 2026-01-27 | 1.91
2026-01-27 00:58 | 72.3758 | FALSE | FALSE | 0.075162 | 0.10374 | -1.9596 | -2.6361 | -0.2826 | 2026-01-27 08:30 | 2026-01-27 00:58 | lower | TRUE | 0 | 72.451 | FALSE | FALSE | 0.2011 | 2.1595 | 73.3932 | 1 | -0.2826 | -0.08478 | 0.13287 | -1.4888 | 0.4711 | Extreme triggered | 74.3354 | -2.1595 | Night | 202601 | 2026-01-27 | 2.1595
2026-01-27 01:13 | 72.3758 | FALSE | FALSE | -0.056626 | -0.0783 | -1.9218 | -2.5866 | 0 |  | 2026-01-27 00:58 | none | FALSE | 0 | 72.3192 | FALSE | FALSE | 0.24 | 2.0225 | 73.3084 | 2 | 0 | -0.08478 | 0.13287 | 0.63808 | 0.4946 | Extreme/elevated | 74.2976 | -1.8855 | Night | 202601 | 2026-01-27 | 1.8855
2026-01-27 01:28 | 72.3758 | FALSE | FALSE | -0.15659 | -0.21682 | -1.8522 | -2.4953 | 0 |  | 2026-01-27 00:58 | none | FALSE | 0 | 72.2192 | FALSE | FALSE | 0.284 | 1.9111 | 73.2236 | 3 | 0 | -0.08478 | 0.13287 | 0.63808 | 0.50219 | Persistent | 74.228 | -1.6882 | Night | 202601 | 2026-01-27 | 1.6882
2026-01-27 01:43 | 72.095 | FALSE | FALSE | -0.042136 | -0.058479 | -2.13 | -2.8696 | -0.2808 |  | 2026-01-27 00:58 | none | FALSE | 0 | 72.0529 | FALSE | FALSE | 0.3567 | 1.9139 | 73.1389 | 4 | -0.2808 | -0.08469 | 0.13273 | -1.4775 | 0.54302 | Persistent | 74.225 | -1.9224 | Night | 202601 | 2026-01-27 | 1.9224
2026-01-27 01:58 | 72.095 | FALSE | FALSE | -0.17647 | -0.24538 | -2.0949 | -2.8237 | 0 |  | 2026-01-27 00:58 | none | FALSE | 0 | 71.9185 | FALSE | FALSE | 0.3983 | 1.869 | 73.0542 | 5 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.56785 | Persistent | 74.1899 | -1.6892 | Night | 202601 | 2026-01-27 | 1.6892
2026-01-27 02:13 | 71.8124 | FALSE | FALSE | -0.065196 | -0.090869 | -2.3512 | -3.1703 | -0.2826 |  | 2026-01-27 00:58 | none | FALSE | 0 | 71.7472 | FALSE | FALSE | 0.469 | 1.8728 | 72.9554 | 6 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.6041 | Persistent | 74.1636 | -1.8921 | Night | 202601 | 2026-01-27 | 1.8921
2026-01-27 02:27 | 71.8124 | FALSE | TRUE | -0.19978 | -0.27897 | -2.2881 | -3.0879 | 0 |  | 2026-01-27 00:58 | none | FALSE | 0 | 71.6126 | FALSE | FALSE | 0.5119 | 1.8451 | 72.8566 | 7 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.62198 | Confirmed/Materialized Shift | 74.1005 | -1.6788 | Night | 202601 | 2026-01-27 | 1.6788
2026-01-27 02:43 | 71.5298 | FALSE | TRUE | -0.082845 | -0.11595 | -2.5105 | -3.3907 | -0.2826 |  | 2026-01-27 00:58 | none | FALSE | 0 | 71.447 | FALSE | FALSE | 0.5248 | 1.8485 | 72.7436 | 8 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.64834 | Confirmed/Materialized Shift | 74.0403 | -1.8722 | Night | 202601 | 2026-01-27 | 1.8722
2026-01-27 02:58 | 71.5298 | FALSE | TRUE | -0.20597 | -0.28878 | -2.4077 | -3.2564 | 0 |  | 2026-01-27 00:58 | none | FALSE | 0 | 71.3238 | FALSE | FALSE | 0.5123 | 1.8303 | 72.6307 | 9 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.65343 | Confirmed/Materialized Shift | 73.9375 | -1.6848 | Night | 202601 | 2026-01-27 | 1.6848
2026-01-27 03:13 | 71.2472 | FALSE | TRUE | -0.10632 | -0.14945 | -2.6474 | -3.5826 | -0.2826 |  | 2026-01-27 00:58 | none | FALSE | 0 | 71.1409 | FALSE | FALSE | 0.523 | 1.8318 | 72.5177 | 10 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.68843 | Confirmed/Materialized Shift | 73.8946 | -1.8456 | Night | 202601 | 2026-01-27 | 1.8456
2026-01-27 03:27 | 70.9646 | FALSE | TRUE | -0.033353 | -0.047022 | -2.8855 | -3.9072 | -0.2826 |  | 2026-01-27 00:58 | none | FALSE | 0 | 70.9312 | FALSE | FALSE | 0.5303 | 1.843 | 72.3906 | 11 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.7297 | Confirmed/Materialized Shift | 73.8501 | -1.9543 | Night | 202601 | 2026-01-27 | 1.9543
2026-01-27 03:42 | 70.9646 | FALSE | TRUE | -0.22255 | -0.31459 | -2.8487 | -3.8594 | 0 |  | 2026-01-27 00:58 | none | FALSE | 0 | 70.7421 | FALSE | FALSE | 0.514 | 1.8319 | 72.2777 | 12 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.76782 | Confirmed/Materialized Shift | 73.8133 | -1.7102 | Night | 202601 | 2026-01-27 | 1.7102
2026-01-27 03:57 | 70.682 | FALSE | TRUE | -0.15554 | -0.22054 | -3.0928 | -4.1922 | -0.2826 |  | 2026-01-27 00:58 | none | FALSE | 0 | 70.5265 | FALSE | FALSE | 0.5206 | 1.8301 | 72.1506 | 13 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.81208 | Confirmed/Materialized Shift | 73.7748 | -1.8085 | Night | 202601 | 2026-01-27 | 1.8085
2026-01-27 04:12 | 70.682 | FALSE | TRUE | -0.32627 | -0.46375 | -3.0094 | -4.0837 | 0 |  | 2026-01-27 00:58 | none | FALSE | 0 | 70.3557 | FALSE | FALSE | 0.5072 | 1.8143 | 72.0235 | 14 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.83391 | Confirmed/Materialized Shift | 73.6914 | -1.6087 | Night | 202601 | 2026-01-27 | 1.6087
2026-01-27 04:27 | 70.3994 | FALSE | TRUE | -0.23456 | -0.3343 | -3.2004 | -4.3484 | -0.2826 |  | 2026-01-27 00:58 | none | FALSE | 0 | 70.1648 | FALSE | FALSE | 0.5151 | 1.8085 | 71.8823 | 15 | -0.2826 | -0.14121 | 0.14488 | -0.97592 | 0.85875 | Confirmed/Materialized Shift | 73.5998 | -1.7269 | Night | 202601 | 2026-01-27 | 1.7269
2026-01-27 04:42 | 70.3994 | FALSE | TRUE | -0.37585 | -0.53675 | -3.0593 | -4.1646 | 0 |  | 2026-01-27 00:58 | none | FALSE | 0 | 70.0235 | FALSE | FALSE | 0.5042 | 1.7931 | 71.7411 | 16 | 0 | -0.14121 | 0.14488 | 0.97468 | 0.85879 | Confirmed/Materialized Shift | 73.4587 | -1.5623 | Night | 202601 | 2026-01-27 | 1.5623
2026-01-27 04:57 | 70.1168 | FALSE | TRUE | -0.2828 | -0.40497 | -3.249 | -4.4285 | -0.2826 |  | 2026-01-27 00:58 | none | FALSE | 0 | 69.834 | FALSE | FALSE | 0.512 | 1.7864 | 71.5999 | 17 | -0.2826 | -0.14121 | 0.14488 | -0.97592 | 0.88296 | Confirmed/Materialized Shift | 73.3658 | -1.6797 | Night | 202601 | 2026-01-27 | 1.6797
2026-01-27 05:12 | 70.1168 | FALSE | TRUE | -0.42415 | -0.6086 | -3.108 | -4.2444 | 0 |  | 2026-01-27 00:58 | none | FALSE | 0 | 69.6926 | FALSE | FALSE | 0.5013 | 1.7716 | 71.4587 | 18 | 0 | -0.14121 | 0.14488 | 0.97468 | 0.88303 | Confirmed/Materialized Shift | 73.2248 | -1.5197 | Night | 202601 | 2026-01-27 | 1.5197
2026-01-27 05:27 | 70.1168 | FALSE | TRUE | -0.5173 | -0.74326 | -2.9187 | -3.9963 | 0 |  | 2026-01-27 00:58 | none | FALSE | 0 | 69.5995 | FALSE | FALSE | 0.4932 | 1.7519 | 71.3175 | 19 | 0 | -0.14121 | 0.14488 | 0.97468 | 0.859 | Confirmed/Materialized Shift | 73.0355 | -1.3978 | Night | 202601 | 2026-01-27 | 1.3978
2026-01-27 05:42 | 69.836 | FALSE | TRUE | -0.37753 | -0.54353 | -3.0583 | -4.1955 | -0.2808 |  | 2026-01-27 00:58 | none | FALSE | 0 | 69.4585 | FALSE | FALSE | 0.504 | 1.7423 | 71.1764 | 20 | -0.2808 | -0.14112 | 0.14479 | -0.96473 | 0.85895 | Confirmed/Materialized Shift | 72.8943 | -1.5605 | Night | 202601 | 2026-01-27 | 1.5605
2026-01-27 05:57 | 69.836 | FALSE | TRUE | -0.50669 | -0.73084 | -2.9334 | -4.0312 | 0 |  | 2026-01-27 00:58 | none | FALSE | 0 | 69.3293 | FALSE | FALSE | 0.4941 | 1.7266 | 71.0494 | 21 | 0 | -0.12699 | 0.14404 | 0.88163 | 0.86003 | Confirmed/Materialized Shift | 72.7694 | -1.4109 | Night | 202601 | 2026-01-27 | 1.4109
2026-01-27 06:12 | 69.5534 | FALSE | TRUE | -0.37011 | -0.53498 | -3.0798 | -4.2403 | -0.2826 |  | 2026-01-27 00:58 | none | FALSE | 0 | 69.1833 | FALSE | FALSE | 0.5047 | 1.7195 | 70.9083 | 22 | -0.2826 | -0.14112 | 0.14479 | -0.97716 | 0.86249 | Confirmed/Materialized Shift | 72.6332 | -1.5709 | Night | 202601 | 2026-01-27 | 1.5709
2026-01-27 06:26 | 69.5534 | FALSE | TRUE | -0.46695 | -0.6759 | -2.8944 | -3.9952 | 0 |  | 2026-01-27 00:58 | none | FALSE | 0 | 69.0864 | FALSE | FALSE | 0.4963 | 1.7075 | 70.7671 | 23 | 0 | -0.14112 | 0.14479 | 0.97467 | 0.84035 | Confirmed/Materialized Shift | 72.4478 | -1.4443 | Night | 202601 | 2026-01-27 | 1.4443
2026-01-27 06:41 | 69.2708 | FALSE | TRUE | -0.33038 | -0.47922 | -3.0406 | -4.2049 | -0.2826 |  | 2026-01-27 00:58 | none | FALSE | 0 | 68.9404 | FALSE | FALSE | 0.5072 | 1.7034 | 70.6259 | 24 | -0.2826 | -0.14121 | 0.14488 | -0.97592 | 0.84275 | Confirmed/Materialized Shift | 72.3114 | -1.608 | Night | 202601 | 2026-01-27 | 1.608
2026-01-27 06:56 | 69.2708 | FALSE | TRUE | -0.42597 | -0.61874 | -2.8538 | -3.9568 | 0 |  | 2026-01-27 00:58 | none | FALSE | 0 | 68.8448 | FALSE | FALSE | 0.4987 | 1.6945 | 70.4847 | 25 | 0 | -0.14121 | 0.14488 | 0.97468 | 0.81994 | Confirmed/Materialized Shift | 72.1246 | -1.4805 | Night | 202601 | 2026-01-27 | 1.4805
2026-01-27 07:11 | 69.2708 | FALSE | TRUE | -0.51328 | -0.7465 | -2.687 | -3.7341 | 0 |  | 2026-01-27 00:58 | none | FALSE | 0 | 68.7575 | FALSE | FALSE | 0.4906 | 1.6815 | 70.3576 | 26 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.80006 | Confirmed/Materialized Shift | 71.9578 | -1.3585 | Day | 202601 | 2026-01-27 | 1.3585
2026-01-27 07:26 | 68.9882 | FALSE | TRUE | -0.32923 | -0.47952 | -2.7857 | -3.8812 | -0.2826 |  | 2026-01-27 00:58 | none | FALSE | 0 | 68.659 | FALSE | FALSE | 0.5051 | 1.6777 | 70.2164 | 27 | -0.2826 | -0.14121 | 0.14488 | -0.97592 | 0.77873 | Confirmed/Materialized Shift | 71.7739 | -1.5772 | Day | 202601 | 2026-01-27 | 1.5772
2026-01-27 07:30 | 68.9882 | FALSE | TRUE | -0.41942 | -0.61168 | -2.6217 | -3.6611 | 0 |  | 2026-01-27 00:58 | none | FALSE | 0 | 68.5688 | FALSE | FALSE | 0.4966 | 1.6695 | 70.0893 | 28 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.76028 | Confirmed/Materialized Shift | 71.6099 | -1.4483 | Day | 202601 | 2026-01-27 | 1.4483
2026-01-27 07:45 | 68.7056 | FALSE | TRUE | -0.23883 | -0.34883 | -2.7239 | -3.8134 | -0.2826 |  | 2026-01-27 00:58 | none | FALSE | 0 | 68.4668 | FALSE | FALSE | 0.5118 | 1.6698 | 69.9481 | 29 | -0.2826 | -0.14121 | 0.14488 | -0.97592 | 0.74069 | Confirmed/Materialized Shift | 71.4295 | -1.6776 | Day | 202601 | 2026-01-27 | 1.6776
2026-01-27 08:00 | 68.7056 | FALSE | TRUE | -0.33237 | -0.48612 | -2.5633 | -3.5967 | 0 |  | 2026-01-27 00:58 | none | FALSE | 0 | 68.3732 | FALSE | FALSE | 0.5027 | 1.6655 | 69.8211 | 30 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.72392 | Confirmed/Materialized Shift | 71.2689 | -1.5409 | Day | 202601 | 2026-01-27 | 1.5409
2026-01-27 08:16 | 68.9882 | TRUE | TRUE | -0.6537 | -0.95662 | -2.1218 | -2.9838 | 0.2826 |  | 2026-01-27 00:58 | none | FALSE | 1 | 68.3345 | FALSE | FALSE | 0.4991 | 1.6459 | 69.7222 | 31 | 0.2826 | -0.09882 | 0.16582 | 2.3002 | 0.69387 | Confirmed/Materialized Shift | 71.11 | -1.0579 | Day | 202601 | 2026-01-27 | 1.0579
2026-01-27 08:30 | 69.2708 | FALSE | FALSE | -0.90353 | -1.3216 | -1.637 | -2.3087 | 0.2826 |  |  | none | FALSE | 1 | 68.3673 | FALSE | FALSE | 0.0671 |  | 69.6376 | 0 | 0.2826 | -0.08469 | 0.18555 | 1.9794 | 0.63514 | Persistence ends | 70.9078 | -0.57743 | Day | 202601 | 2026-01-27 | 0.57743
2026-01-27 08:30 | 69.2708 | FALSE | FALSE | -0.88334 | -1.2917 | -1.4757 | -2.0859 | 0 |  |  | none | FALSE | 1 | 68.3875 | FALSE | FALSE | 0.0621 |  | 69.567 | 0 | 0 | -0.07056 | 0.18038 | 0.39118 | 0.58977 | Normal | 70.7465 | -0.50222 | Day | 202601 | 2026-01-27 | 0.50222
2026-01-27 08:45 | 69.2708 | FALSE | FALSE | -0.836 | -1.2216 | -1.2873 | -1.8244 | 0 |  |  | none | FALSE | 1 | 68.4348 | FALSE | FALSE | 0.0569 |  | 69.4964 | 0 | 0 | -0.07056 | 0.18038 | 0.39118 | 0.53082 | Normal | 70.5581 | -0.42506 | Day | 202601 | 2026-01-27 | 0.42506
2026-01-27 09:00 | 69.5534 | FALSE | FALSE | -1.0732 | -1.5672 | -0.87467 | -1.2419 | 0.2826 |  |  | none | FALSE | 1 | 68.4802 | FALSE | FALSE | 0.0422 |  | 69.4541 | 0 | 0.2826 | -0.0423 | 0.18945 | 1.7149 | 0.48697 | Normal | 70.4281 | 0.20385 | Day | 202601 | 2026-01-27 | 0.20385
2026-01-27 09:15 | 69.836 | FALSE | FALSE | -1.2976 | -1.8933 | -0.47755 | -0.67917 | 0.2826 |  |  | none | FALSE | 1 | 68.5384 | FALSE | FALSE | 0.0902 |  | 69.426 | 0 | 0.2826 | -0.02817 | 0.20284 | 1.5321 | 0.44379 | Normal | 70.3135 | 0.92394 | Day | 202601 | 2026-01-27 | 0.92394
2026-01-27 09:30 | 70.1168 | FALSE | FALSE | -1.5784 | -2.303 | -0.19675 | -0.27981 | 0.2808 |  |  | none | FALSE | 1 | 68.5384 | FALSE | FALSE | 0.1323 |  | 69.426 | 0 | 0.2808 | 0 | 0.20476 | 1.3714 | 0.44379 | Normal | 70.3135 | 1.5567 | Day | 202601 | 2026-01-27 | 1.5567
2026-01-27 09:45 | 70.3994 | FALSE | FALSE | -1.9006 | -2.7746 | 0.018043 | 0.025636 | 0.2826 | 2026-01-27 15:47 | 2026-01-27 09:45 | upper | TRUE | 1 | 68.4988 | FALSE | FALSE | 0.2216 | 2.0383 | 69.4401 | 1 | 0.2826 | 0.01413 | 0.21429 | 1.2528 | 0.47063 | Extreme triggered | 70.3814 | 2.0383 | Day | 202601 | 2026-01-27 | 2.0383
2026-01-27 10:00 | 70.682 | FALSE | FALSE | -2.2677 | -3.3146 | 0.15965 | 0.22638 | 0.2826 |  | 2026-01-27 09:45 | upper | TRUE | 1 | 68.4143 | FALSE | FALSE | 0.2964 | 2.1706 | 69.4684 | 2 | 0.2826 | 0.02826 | 0.22247 | 1.1433 | 0.527 | Extreme/elevated | 70.5224 | 2.3029 | Day | 202601 | 2026-01-27 | 2.3029
2026-01-27 10:15 | 70.9646 | FALSE | FALSE | -2.6809 | -3.9262 | 0.1987 | 0.28079 | 0.2826 |  | 2026-01-27 09:45 | upper | TRUE | 1 | 68.2837 | FALSE | TRUE | 0.3547 | 2.2205 | 69.5248 | 3 | 0.2826 | 0.05643 | 0.21687 | 1.0429 | 0.62056 | Persistent | 70.7659 | 2.3202 | Day | 202601 | 2026-01-27 | 2.3202
2026-01-27 10:29 | 71.2472 | FALSE | FALSE | -3.1091 | -4.563 | 0.19461 | 0.27389 | 0.2826 |  | 2026-01-27 09:45 | upper | TRUE | 0 | 68.1381 | FALSE | TRUE | 0.3797 | 2.2321 | 69.5953 | 4 | 0.2826 | 0.07056 | 0.22215 | 0.95451 | 0.72863 | Persistent | 71.0526 | 2.2671 | Day | 202601 | 2026-01-27 | 2.2671
2026-01-27 10:44 | 71.5298 | FALSE | FALSE | -3.5297 | -5.1908 | 0.14156 | 0.19829 | 0.2826 |  | 2026-01-27 09:45 | upper | TRUE | 0 | 68.0001 | FALSE | TRUE | 0.4302 | 2.2191 | 69.6942 | 5 | 0.2826 | 0.09882 | 0.2105 | 0.87306 | 0.84704 | Persistent | 71.3882 | 2.1671 | Day | 202601 | 2026-01-27 | 2.1671
2026-01-27 10:59 | 71.8124 | FALSE | FALSE | -3.9435 | -5.8105 | 0.067081 | 0.093499 | 0.2826 |  | 2026-01-27 09:45 | upper | TRUE | 0 | 67.8689 | FALSE | TRUE | 0.4808 | 2.1942 | 69.8071 | 6 | 0.2826 | 0.11295 | 0.21299 | 0.79653 | 0.9691 | Persistent | 71.7453 | 2.0692 | Day | 202601 | 2026-01-27 | 2.0692
2026-01-27 11:15 | 71.8124 | FALSE | TRUE | -3.9936 | -5.8886 | -0.23713 | -0.32912 | 0 |  | 2026-01-27 09:45 | none | FALSE | 0 | 67.8188 | FALSE | FALSE | 0.5184 | 2.1344 | 69.9342 | 7 | 0 | 0.12708 | 0.19388 | -0.65545 | 1.0577 | Confirmed/Materialized Shift | 72.0495 | 1.7758 | Day | 202601 | 2026-01-27 | 1.7758
2026-01-27 11:29 | 72.095 | FALSE | TRUE | -4.3176 | -6.3703 | -0.27845 | -0.38474 | 0.2826 |  | 2026-01-27 09:45 | none | FALSE | 0 | 67.7774 | FALSE | FALSE | 0.5172 | 2.0873 | 70.0754 | 8 | 0.2826 | 0.14121 | 0.19443 | 0.7272 | 1.149 | Confirmed/Materialized Shift | 72.3734 | 1.7577 | Day | 202601 | 2026-01-27 | 1.7577
2026-01-27 11:44 | 72.3758 | FALSE | TRUE | -4.6265 | -6.8289 | -0.33625 | -0.46243 | 0.2808 |  | 2026-01-27 09:45 | none | FALSE | 0 | 67.7493 | FALSE | FALSE | 0.5153 | 2.0475 | 70.2306 | 9 | 0.2808 | 0.15525 | 0.19383 | 0.64772 | 1.2407 | Confirmed/Materialized Shift | 72.712 | 1.729 | Day | 202601 | 2026-01-27 | 1.729
2026-01-27 11:59 | 72.3758 | FALSE | TRUE | -4.5604 | -6.7247 | -0.60886 | -0.83423 | 0 |  | 2026-01-27 09:45 | none | FALSE | 0 | 67.8154 | FALSE | FALSE | 0.5019 | 1.9956 | 70.4 | 10 | 0 | 0.16938 | 0.16894 | -1.0026 | 1.2923 | Confirmed/Materialized Shift | 72.9847 | 1.5289 | Day | 202601 | 2026-01-27 | 1.5289
2026-01-27 12:14 | 72.6584 | FALSE | TRUE | -4.7568 | -7.0054 | -0.60705 | -0.82856 | 0.2826 |  | 2026-01-27 09:45 | none | FALSE | 0 | 67.9016 | FALSE | FALSE | 0.5032 | 1.9549 | 70.5835 | 11 | 0.2826 | 0.18351 | 0.16581 | 0.5976 | 1.341 | Confirmed/Materialized Shift | 73.2654 | 1.5473 | Day | 202601 | 2026-01-27 | 1.5473
2026-01-27 12:29 | 72.941 | FALSE | TRUE | -4.8717 | -7.157 | -0.58036 | -0.78938 | 0.2826 |  | 2026-01-27 09:45 | none | FALSE | 0 | 68.0693 | FALSE | FALSE | 0.5049 | 1.9231 | 70.7953 | 12 | 0.2826 | 0.21177 | 0.12544 | 0.56464 | 1.363 | Confirmed/Materialized Shift | 73.5214 | 1.5742 | Day | 202601 | 2026-01-27 | 1.5742
2026-01-27 12:44 | 72.941 | FALSE | TRUE | -4.6344 | -6.7847 | -0.76653 | -1.04 | 0 |  | 2026-01-27 09:45 | none | FALSE | 0 | 68.3066 | FALSE | FALSE | 0.4955 | 1.8854 | 71.0071 | 13 | 0 | 0.21177 | 0.12544 | -1.6882 | 1.3502 | Confirmed/Materialized Shift | 73.7075 | 1.4323 | Day | 202601 | 2026-01-27 | 1.4323
2026-01-27 12:59 | 72.941 | FALSE | TRUE | -4.3928 | -6.4084 | -0.92027 | -1.2459 | 0 |  | 2026-01-27 09:45 | none | FALSE | 0 | 68.5482 | FALSE | FALSE | 0.4871 | 1.8441 | 71.2047 | 14 | 0 | 0.19764 | 0.13275 | -1.4888 | 1.3283 | Confirmed/Materialized Shift | 73.8613 | 1.3072 | Day | 202601 | 2026-01-27 | 1.3072
2026-01-27 13:14 | 73.2236 | FALSE | TRUE | -4.4601 | -6.4861 | -0.81761 | -1.1043 | 0.2826 |  | 2026-01-27 09:45 | none | FALSE | 0 | 68.7635 | FALSE | FALSE | 0.492 | 1.8132 | 71.4024 | 15 | 0.2826 | 0.19764 | 0.13275 | 0.64001 | 1.3194 | Confirmed/Materialized Shift | 74.0412 | 1.3803 | Day | 202601 | 2026-01-27 | 1.3803
2026-01-27 13:28 | 73.2236 | FALSE | TRUE | -4.1811 | -6.0558 | -0.9339 | -1.2593 | 0 |  | 2026-01-27 09:45 | none | FALSE | 0 | 69.0425 | FALSE | FALSE | 0.4846 | 1.7792 | 71.6 | 16 | 0 | 0.19764 | 0.13275 | -1.4888 | 1.2787 | Confirmed/Materialized Shift | 74.1575 | 1.2697 | Day | 202601 | 2026-01-27 | 1.2697
2026-01-27 13:44 | 73.2236 | FALSE | TRUE | -3.832 | -5.5223 | -0.98011 | -1.3208 | 0 |  | 2026-01-27 09:45 | none | FALSE | 0 | 69.3916 | FALSE | FALSE | 0.479 | 1.7443 | 71.7976 | 17 | 0 | 0.19764 | 0.13275 | -1.4888 | 1.203 | Confirmed/Materialized Shift | 74.2037 | 1.1853 | Day | 202601 | 2026-01-27 | 1.1853
2026-01-27 13:59 | 73.2236 | FALSE | TRUE | -3.4819 | -4.9926 | -0.99699 | -1.3433 | 0 |  | 2026-01-27 09:45 | none | FALSE | 0 | 69.7417 | FALSE | FALSE | 0.474 | 1.709 | 71.9811 | 18 | 0 | 0.18351 | 0.13816 | -1.3283 | 1.1197 | Confirmed/Materialized Shift | 74.2206 | 1.1096 | Day | 202601 | 2026-01-27 | 1.1096
2026-01-27 14:14 | 73.5062 | FALSE | TRUE | -3.4378 | -4.9063 | -0.75469 | -1.0163 | 0.2826 |  | 2026-01-27 09:45 | none | FALSE | 0 | 70.0684 | FALSE | FALSE | 0.4853 | 1.6864 | 72.1647 | 19 | 0.2826 | 0.18351 | 0.13816 | 0.71722 | 1.0481 | Confirmed/Materialized Shift | 74.2609 | 1.28 | Day | 202601 | 2026-01-27 | 1.28
2026-01-27 14:28 | 73.5062 | FALSE | TRUE | -3.1135 | -4.4231 | -0.76938 | -1.0358 | 0 |  | 2026-01-27 09:45 | none | FALSE | 0 | 70.3927 | FALSE | FALSE | 0.4805 | 1.6625 | 72.3341 | 20 | 0 | 0.16947 | 0.14197 | -1.1937 | 0.97073 | Confirmed/Materialized Shift | 74.2756 | 1.2074 | Day | 202601 | 2026-01-27 | 1.2074
2026-01-27 14:43 | 73.7888 | FALSE | TRUE | -3.1034 | -4.3904 | -0.53298 | -0.71712 | 0.2826 |  | 2026-01-27 09:45 | none | FALSE | 0 | 70.6854 | FALSE | FALSE | 0.4942 | 1.6506 | 72.5036 | 21 | 0.2826 | 0.16947 | 0.14197 | 0.79688 | 0.90909 | Confirmed/Materialized Shift | 74.3218 | 1.4137 | Day | 202601 | 2026-01-27 | 1.4137
2026-01-27 14:58 | 73.5062 | TRUE | TRUE | -2.5151 | -3.5429 | -0.79235 | -1.0664 | -0.2826 |  | 2026-01-27 09:45 | none | FALSE | 1 | 70.9911 | FALSE | FALSE | 0.498 | 1.623 | 72.6448 | 22 | -0.2826 | 0.14121 | 0.17145 | -2.4719 | 0.82687 | Confirmed/Materialized Shift | 74.2985 | 1.0417 | Day | 202601 | 2026-01-27 | 1.0417
2026-01-27 15:13 | 73.7888 | FALSE | TRUE | -2.5299 | -3.5503 | -0.52433 | -0.70557 | 0.2826 |  | 2026-01-27 09:45 | none | FALSE | 1 | 71.2589 | FALSE | FALSE | 0.5161 | 1.6095 | 72.786 | 23 | 0.2826 | 0.14121 | 0.17145 | 0.82465 | 0.76356 | Confirmed/Materialized Shift | 74.3131 | 1.3133 | Day | 202601 | 2026-01-27 | 1.3133
2026-01-27 15:28 | 73.7888 | FALSE | TRUE | -2.2818 | -3.1911 | -0.53045 | -0.71374 | 0 |  | 2026-01-27 09:45 | none | FALSE | 1 | 71.507 | FALSE | FALSE | 0.5116 | 1.5943 | 72.9131 | 24 | 0 | 0.12708 | 0.17083 | -0.74389 | 0.70307 | Confirmed/Materialized Shift | 74.3192 | 1.2455 | Day | 202601 | 2026-01-27 | 1.2455
2026-01-27 15:29 | 74.0714 | FALSE | TRUE | -2.3687 | -3.3035 | -0.30627 | -0.41177 | 0.2826 |  | 2026-01-27 09:45 | none | FALSE | 1 | 71.7027 | FALSE | FALSE | 0.5314 | 1.5922 | 73.0402 | 25 | 0.2826 | 0.12708 | 0.17083 | 0.91037 | 0.66874 | Confirmed/Materialized Shift | 74.3777 | 1.542 | Day | 202601 | 2026-01-27 | 1.542
2026-01-27 15:32 | 74.0714 | FALSE | TRUE | -2.1995 | -3.0604 | -0.36301 | -0.48769 | 0 |  | 2026-01-27 09:45 | none | FALSE | 1 | 71.8719 | FALSE | FALSE | 0.5241 | 1.5861 | 73.1531 | 26 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.64064 | Confirmed/Materialized Shift | 74.4344 | 1.4334 | Day | 202601 | 2026-01-27 | 1.4334
2026-01-27 15:47 | 72.941 | TRUE | FALSE | -0.85363 | -1.1842 | -1.3907 | -1.871 | -1.1304 |  |  | none | FALSE | 2 | 72.0874 | TRUE | FALSE | 0.0891 |  | 73.2096 | 0 | -1.1304 | 0.05643 | 0.32539 | -3.6474 | 0.56109 | Persistence ends | 74.3317 | -0.47864 | Day | 202601 | 2026-01-27 | 0.47864
2026-01-27 16:02 | 72.3758 | FALSE | FALSE | -0.22145 | -0.30691 | -1.9171 | -2.5804 | -0.5652 |  |  | none | FALSE | 2 | 72.1543 | FALSE | FALSE | 0.1629 |  | 73.2236 | 0 | -0.5652 | 0.01404 | 0.34876 | -1.6608 | 0.53463 | Normal | 74.2929 | -1.5858 | Day | 202601 | 2026-01-27 | 1.5858
2026-01-27 16:17 | 71.8124 | FALSE | FALSE | 0.19648 | 0.27286 | -2.5696 | -3.4546 | -0.5634 | 2026-01-27 16:43 | 2026-01-27 16:17 | lower | TRUE | 2 | 72.0089 | FALSE | FALSE | 0.2697 | 2.3312 | 73.1954 | 1 | -0.5634 | -0.02817 | 0.36546 | -1.4645 | 0.59327 | Extreme triggered | 74.382 | -2.3312 | Day | 202601 | 2026-01-27 | 2.3312
2026-01-27 16:18 | 71.8124 | FALSE | FALSE | 0.064195 | 0.089313 | -2.6455 | -3.553 | 0 |  | 2026-01-27 16:17 | lower | TRUE | 2 | 71.8766 | FALSE | FALSE | 0.3114 | 2.2153 | 73.1673 | 2 | 0 | -0.02817 | 0.36546 | 0.07708 | 0.64533 | Extreme/elevated | 74.4579 | -2.0995 | Day | 202601 | 2026-01-27 | 2.0995
2026-01-27 16:28 | 72.3758 | FALSE | FALSE | -0.54265 | -0.75543 | -2.0973 | -2.8162 | 0.5634 |  | 2026-01-27 16:17 | none | FALSE | 2 | 71.8332 | FALSE | FALSE | 0.3071 | 1.8695 | 73.1531 | 3 | 0.5634 | -0.01413 | 0.383 | 1.5079 | 0.65999 | Persistent | 74.4731 | -1.1778 | Day | 202601 | 2026-01-27 | 1.1778
2026-01-27 16:43 | 72.941 | FALSE | FALSE | -1.1078 | -1.5422 | -1.5321 | -2.0573 | 0.5652 |  |  | none | FALSE | 1 | 71.8332 | FALSE | FALSE | 0.05 |  | 73.1531 | 0 | 0.5652 | 0 | 0.39939 | 1.4152 | 0.65999 | Persistence ends | 74.4731 | -0.32141 | Day | 202601 | 2026-01-27 | 0.32141
2026-01-27 16:58 | 72.941 | FALSE | FALSE | -1.1078 | -1.5422 | -1.5321 | -2.0573 | 0 |  |  | none | FALSE | 1 | 71.8332 | FALSE | FALSE | 0.05 |  | 73.1531 | 0 | 0 | 0 | 0.39939 | 0 | 0.65999 | Normal | 74.4731 | -0.32141 | Day | 202601 | 2026-01-27 | 0.32141
2026-01-27 17:13 | 72.941 | FALSE | FALSE | -1.1078 | -1.5422 | -1.5321 | -2.0573 | 0 |  |  | none | FALSE | 1 | 71.8332 | FALSE | FALSE | 0.05 |  | 73.1531 | 0 | 0 | 0 | 0.39939 | 0 | 0.65999 | Normal | 74.4731 | -0.32141 | Day | 202601 | 2026-01-27 | 0.32141
2026-01-27 17:27 | 73.2236 | FALSE | FALSE | -1.3904 | -1.9357 | -1.2495 | -1.6778 | 0.2826 |  |  | none | FALSE | 1 | 71.8332 | FALSE | FALSE | 0.0357 |  | 73.1531 | 0 | 0.2826 | 0 | 0.39939 | 0.70758 | 0.65999 | Normal | 74.4731 | 0.10677 | Day | 202601 | 2026-01-27 | 0.10677
2026-01-27 17:42 | 72.941 | FALSE | FALSE | -1.1248 | -1.5663 | -1.5208 | -2.0425 | -0.2826 |  |  | none | FALSE | 1 | 71.8162 | FALSE | FALSE | 0.0485 |  | 73.139 | 0 | -0.2826 | -0.01413 | 0.40436 | -0.66394 | 0.66142 | Normal | 74.4618 | -0.29935 | Day | 202601 | 2026-01-27 | 0.29935
2026-01-27 17:57 | 72.941 | FALSE | FALSE | -1.1412 | -1.5894 | -1.5089 | -2.0268 | 0 |  |  | none | FALSE | 0 | 71.7998 | FALSE | FALSE | 0.0185 |  | 73.1249 | 0 | 0 | -0.01413 | 0.40436 | 0.034944 | 0.66254 | Normal | 74.4499 | -0.27752 | Day | 202601 | 2026-01-27 | 0.27752
2026-01-27 18:12 | 72.941 | FALSE | FALSE | -1.1569 | -1.6117 | -1.4964 | -2.0103 | 0 |  |  | none | FALSE | 0 | 71.7841 | FALSE | FALSE | 0.0171 |  | 73.1107 | 0 | 0 | -0.01413 | 0.40436 | 0.034944 | 0.66334 | Normal | 74.4374 | -0.25589 | Night | 202601 | 2026-01-27 | 0.25589
2026-01-27 18:27 | 72.941 | FALSE | FALSE | -1.1738 | -1.6355 | -1.4567 | -1.958 | 0 |  |  | none | FALSE | 0 | 71.7672 | FALSE | FALSE | 0.0143 |  | 73.0825 | 0 | 0 | -0.02826 | 0.39834 | 0.070945 | 0.65762 | Normal | 74.3977 | -0.21514 | Night | 202601 | 2026-01-27 | 0.21514
2026-01-27 18:30 | 72.941 | FALSE | FALSE | -1.1879 | -1.6555 | -1.4143 | -1.9021 | 0 |  |  | none | FALSE | 0 | 71.7531 | FALSE | FALSE | 0.0116 |  | 73.0542 | 0 | 0 | -0.02826 | 0.39834 | 0.070945 | 0.65056 | Normal | 74.3553 | -0.17404 | Night | 202601 | 2026-01-27 | 0.17404
2026-01-27 18:31 | 72.941 | FALSE | FALSE | -1.1839 | -1.6499 | -1.3256 | -1.7849 | 0 |  |  | none | FALSE | 0 | 71.7571 | FALSE | FALSE | 0.0075 |  | 73.0118 | 0 | 0 | -0.04239 | 0.39168 | 0.10822 | 0.62738 | Normal | 74.2666 | -0.1129 | Night | 202601 | 2026-01-27 | 0.1129
2026-01-27 18:46 | 72.941 | FALSE | FALSE | -1.1906 | -1.6593 | -1.2757 | -1.7189 | 0 |  |  | none | FALSE | 0 | 71.7504 | FALSE | FALSE | 0.0046 |  | 72.9836 | 0 | 0 | -0.02826 | 0.38764 | 0.072903 | 0.61658 | Normal | 74.2167 | -0.069043 | Night | 202601 | 2026-01-27 | 0.069043
2026-01-27 19:01 | 72.6584 | FALSE | FALSE | -0.91159 | -1.2706 | -1.4489 | -1.9551 | -0.2826 |  |  | none | FALSE | 0 | 71.7468 | FALSE | FALSE | 0.0303 |  | 72.927 | 0 | -0.2826 | -0.05652 | 0.38437 | -0.58818 | 0.59012 | Normal | 74.1073 | -0.45525 | Night | 202601 | 2026-01-27 | 0.45525
2026-01-27 19:16 | 72.6584 | FALSE | FALSE | -0.90069 | -1.2552 | -1.325 | -1.7909 | 0 |  |  | none | FALSE | 0 | 71.7577 | FALSE | FALSE | 0.0254 |  | 72.8705 | 0 | 0 | -0.05652 | 0.38437 | 0.14704 | 0.55641 | Normal | 73.9834 | -0.38125 | Night | 202601 | 2026-01-27 | 0.38125
2026-01-27 19:30 | 72.3758 | FALSE | FALSE | -0.56782 | -0.79075 | -1.3877 | -1.8813 | -0.2826 |  |  | none | FALSE | 0 | 71.808 | FALSE | FALSE | 0.0559 |  | 72.7857 | 0 | -0.2826 | -0.08478 | 0.37887 | -0.52214 | 0.48889 | Normal | 73.7635 | -0.83854 | Night | 202601 | 2026-01-27 | 0.83854
2026-01-27 19:45 | 72.3758 | FALSE | FALSE | -0.45788 | -0.63668 | -1.1082 | -1.5081 | 0 |  |  | none | FALSE | 0 | 71.9179 | FALSE | FALSE | 0.0554 |  | 72.701 | 0 | 0 | -0.08478 | 0.37887 | 0.22377 | 0.39153 | Normal | 73.484 | -0.83052 | Night | 202601 | 2026-01-27 | 0.83052
2026-01-27 20:00 | 72.3758 | FALSE | FALSE | -0.49045 | -0.68227 | -1.0843 | -1.476 | 0 |  |  | none | FALSE | 0 | 71.8853 | FALSE | FALSE | 0.0503 |  | 72.6727 | 0 | 0 | -0.02826 | 0.28812 | 0.098085 | 0.39368 | Normal | 73.4601 | -0.75419 | Night | 202601 | 2026-01-27 | 0.75419
2026-01-27 20:15 | 72.095 | FALSE | FALSE | -0.25536 | -0.35546 | -1.3827 | -1.8818 | -0.2808 |  |  | none | FALSE | 0 | 71.8396 | FALSE | FALSE | 0.0918 |  | 72.6587 | 0 | -0.2808 | -0.01404 | 0.26642 | -1.0013 | 0.40952 | Normal | 73.4777 | -1.3764 | Night | 202601 | 2026-01-27 | 1.3764
2026-01-27 20:29 | 71.8124 | FALSE | FALSE | 0.027236 | 0.037912 | -1.6653 | -2.2664 | -0.2826 | 2026-01-28 10:06 | 2026-01-27 20:29 | lower | TRUE | 0 | 71.8396 | FALSE | FALSE | 0.1949 | 2.0665 | 72.6587 | 1 | -0.2826 | 0 | 0.24225 | -1.1666 | 0.40952 | Extreme triggered | 73.4777 | -2.0665 | Night | 202601 | 2026-01-27 | 2.0665
2026-01-27 20:44 | 71.8124 | FALSE | FALSE | 0.027236 | 0.037912 | -1.6653 | -2.2664 | 0 |  | 2026-01-27 20:29 | lower | TRUE | 0 | 71.8396 | FALSE | FALSE | 0.2521 | 2.0665 | 72.6587 | 2 | 0 | 0 | 0.24225 | 0 | 0.40952 | Extreme/elevated | 73.4777 | -2.0665 | Night | 202601 | 2026-01-27 | 2.0665
2026-01-27 20:59 | 71.5298 | FALSE | FALSE | 0.13016 | 0.18163 | -2.043 | -2.7768 | -0.2826 |  | 2026-01-27 20:29 | lower | TRUE | 0 | 71.66 | FALSE | TRUE | 0.3229 | 2.1351 | 72.6164 | 3 | -0.2826 | -0.0423 | 0.21047 | -1.1417 | 0.47821 | Persistent | 73.5728 | -2.2722 | Night | 202601 | 2026-01-27 | 2.2722
2026-01-27 21:14 | 71.5298 | FALSE | FALSE | -0.04235 | -0.059242 | -2.0744 | -2.8183 | 0 |  | 2026-01-27 20:29 | none | FALSE | 0 | 71.4874 | FALSE | FALSE | 0.3566 | 2.0813 | 72.5458 | 4 | 0 | -0.07056 | 0.15534 | 0.45424 | 0.52918 | Persistent | 73.6042 | -1.92 | Night | 202601 | 2026-01-27 | 1.92
2026-01-27 21:29 | 71.2472 | FALSE | FALSE | 0.025611 | 0.035934 | -2.4022 | -3.2617 | -0.2826 |  | 2026-01-27 20:29 | lower | TRUE | 0 | 71.2728 | FALSE | TRUE | 0.4219 | 2.0737 | 72.4611 | 5 | -0.2826 | -0.08469 | 0.16132 | -1.2268 | 0.59415 | Persistent | 73.6494 | -2.0431 | Night | 202601 | 2026-01-27 | 2.0431
2026-01-27 21:44 | 70.9646 | FALSE | FALSE | 0.058309 | 0.082099 | -2.7371 | -3.7137 | -0.2826 |  | 2026-01-27 20:29 | lower | TRUE | 0 | 71.0229 | FALSE | TRUE | 0.482 | 2.0759 | 72.3623 | 6 | -0.2826 | -0.09882 | 0.16582 | -1.1083 | 0.6697 | Persistent | 73.7017 | -2.0871 | Night | 202601 | 2026-01-27 | 2.0871
2026-01-27 21:59 | 70.9646 | FALSE | TRUE | -0.12782 | -0.18044 | -2.6973 | -3.6618 | 0 |  | 2026-01-27 20:29 | none | FALSE | 0 | 70.8368 | FALSE | FALSE | 0.5213 | 2.0392 | 72.2494 | 7 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.70628 | Confirmed/Materialized Shift | 73.6619 | -1.819 | Night | 202601 | 2026-01-27 | 1.819
2026-01-27 22:14 | 70.682 | FALSE | TRUE | -0.08121 | -0.11503 | -2.99 | -4.0585 | -0.2826 |  | 2026-01-27 20:29 | none | FALSE | 0 | 70.6008 | FALSE | FALSE | 0.5263 | 2.0211 | 72.1364 | 8 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.76781 | Confirmed/Materialized Shift | 73.672 | -1.8942 | Night | 202601 | 2026-01-27 | 1.8942
2026-01-27 22:29 | 70.682 | FALSE | TRUE | -0.27516 | -0.39081 | -2.9581 | -4.0169 | 0 |  | 2026-01-27 20:29 | none | FALSE | 0 | 70.4068 | FALSE | FALSE | 0.5106 | 1.9809 | 72.0234 | 9 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.8083 | Confirmed/Materialized Shift | 73.6401 | -1.6596 | Night | 202601 | 2026-01-27 | 1.6596
2026-01-27 22:44 | 70.682 | FALSE | TRUE | -0.43321 | -0.61669 | -2.8902 | -3.9284 | 0 |  | 2026-01-27 20:29 | none | FALSE | 0 | 70.2488 | FALSE | FALSE | 0.4986 | 1.9307 | 71.9105 | 10 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.83086 | Confirmed/Materialized Shift | 73.5722 | -1.4786 | Night | 202601 | 2026-01-27 | 1.4786
2026-01-27 22:59 | 70.3994 | FALSE | TRUE | -0.33367 | -0.47622 | -3.1017 | -4.2199 | -0.2826 |  | 2026-01-27 20:29 | none | FALSE | 0 | 70.0657 | FALSE | FALSE | 0.5074 | 1.9017 | 71.7834 | 11 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.85884 | Confirmed/Materialized Shift | 73.5011 | -1.6115 | Night | 202601 | 2026-01-27 | 1.6115
2026-01-27 23:14 | 70.3994 | FALSE | TRUE | -0.47616 | -0.68097 | -2.99 | -4.0742 | 0 |  | 2026-01-27 20:29 | none | FALSE | 0 | 69.9232 | FALSE | FALSE | 0.4967 | 1.8641 | 71.6563 | 12 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.86655 | Confirmed/Materialized Shift | 73.3894 | -1.4505 | Night | 202601 | 2026-01-27 | 1.4505
2026-01-27 23:28 | 70.1168 | FALSE | TRUE | -0.35416 | -0.50766 | -3.1508 | -4.3004 | -0.2826 |  | 2026-01-27 20:29 | none | FALSE | 0 | 69.7626 | FALSE | FALSE | 0.5064 | 1.8434 | 71.5151 | 13 | -0.2826 | -0.14121 | 0.14488 | -0.97592 | 0.87624 | Confirmed/Materialized Shift | 73.2676 | -1.5958 | Night | 202601 | 2026-01-27 | 1.5958
2026-01-27 23:43 | 70.1168 | FALSE | TRUE | -0.4665 | -0.66978 | -2.9807 | -4.0778 | 0 |  | 2026-01-27 20:29 | none | FALSE | 0 | 69.6503 | FALSE | FALSE | 0.4972 | 1.816 | 71.3739 | 14 | 0 | -0.14121 | 0.14488 | 0.97468 | 0.86181 | Confirmed/Materialized Shift | 73.0975 | -1.4587 | Night | 202601 | 2026-01-27 | 1.4587
2026-01-27 23:58 | 70.1168 | FALSE | TRUE | -0.56944 | -0.81878 | -2.8295 | -3.8789 | 0 |  | 2026-01-27 20:29 | none | FALSE | 0 | 69.5474 | FALSE | FALSE | 0.4887 | 1.7835 | 71.2468 | 15 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.84974 | Confirmed/Materialized Shift | 72.9463 | -1.3299 | Night | 202601 | 2026-01-27 | 1.3299
2026-01-28 00:14 | 69.836 | FALSE | TRUE | -0.40478 | -0.583 | -2.9442 | -4.0454 | -0.2808 |  | 2026-01-27 20:29 | none | FALSE | 0 | 69.4312 | FALSE | FALSE | 0.5011 | 1.7669 | 71.1057 | 16 | -0.2808 | -0.14112 | 0.14479 | -0.96473 | 0.83725 | Confirmed/Materialized Shift | 72.7802 | -1.5165 | Night | 202601 | 2026-01-28 | 1.5165
2026-01-28 00:28 | 69.836 | FALSE | TRUE | -0.51131 | -0.73756 | -2.7968 | -3.8506 | 0 |  | 2026-01-27 20:29 | none | FALSE | 0 | 69.3247 | FALSE | FALSE | 0.4921 | 1.7442 | 70.9787 | 17 | 0 | -0.12699 | 0.14404 | 0.88163 | 0.82702 | Confirmed/Materialized Shift | 72.6328 | -1.3817 | Night | 202601 | 2026-01-28 | 1.3817
2026-01-28 00:43 | 69.5534 | FALSE | TRUE | -0.34944 | -0.50494 | -2.9179 | -4.0262 | -0.2826 |  | 2026-01-27 20:29 | none | FALSE | 0 | 69.204 | FALSE | FALSE | 0.5048 | 1.7346 | 70.8376 | 18 | -0.2826 | -0.14112 | 0.14479 | -0.97716 | 0.81682 | Confirmed/Materialized Shift | 72.4713 | -1.5722 | Night | 202601 | 2026-01-28 | 1.5722
2026-01-28 00:58 | 69.5534 | FALSE | TRUE | -0.41705 | -0.60323 | -2.7032 | -3.7412 | 0 |  | 2026-01-27 20:29 | none | FALSE | 0 | 69.1364 | FALSE | FALSE | 0.4977 | 1.7205 | 70.6965 | 19 | 0 | -0.14112 | 0.14479 | 0.97467 | 0.78007 | Confirmed/Materialized Shift | 72.2566 | -1.4654 | Night | 202601 | 2026-01-28 | 1.4654
2026-01-28 01:13 | 69.2708 | FALSE | TRUE | -0.25378 | -0.3677 | -2.8227 | -3.9154 | -0.2826 |  | 2026-01-27 20:29 | none | FALSE | 0 | 69.017 | FALSE | FALSE | 0.5113 | 1.718 | 70.5553 | 20 | -0.2826 | -0.14121 | 0.14488 | -0.97592 | 0.76913 | Confirmed/Materialized Shift | 72.0935 | -1.67 | Night | 202601 | 2026-01-28 | 1.67
2026-01-28 01:28 | 69.2708 | FALSE | TRUE | -0.36342 | -0.5274 | -2.6782 | -3.7224 | 0 |  | 2026-01-27 20:29 | none | FALSE | 0 | 68.9074 | FALSE | FALSE | 0.5015 | 1.7086 | 70.4282 | 21 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.76041 | Confirmed/Materialized Shift | 71.949 | -1.5221 | Night | 202601 | 2026-01-28 | 1.5221
2026-01-28 01:43 | 69.2708 | FALSE | TRUE | -0.42691 | -0.62012 | -2.4876 | -3.4666 | 0 |  | 2026-01-27 20:29 | none | FALSE | 0 | 68.8439 | FALSE | FALSE | 0.4943 | 1.6952 | 70.3011 | 22 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.72862 | Confirmed/Materialized Shift | 71.7584 | -1.4141 | Night | 202601 | 2026-01-28 | 1.4141
2026-01-28 01:58 | 69.2708 | FALSE | TRUE | -0.48815 | -0.70969 | -2.3229 | -3.2445 | 0 |  | 2026-01-27 20:29 | none | FALSE | 0 | 68.7827 | FALSE | FALSE | 0.487 | 1.6783 | 70.1882 | 23 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.70276 | Confirmed/Materialized Shift | 71.5937 | -1.3054 | Night | 202601 | 2026-01-28 | 1.3054
2026-01-28 02:13 | 68.9882 | FALSE | TRUE | -0.28051 | -0.40826 | -2.4263 | -3.3975 | -0.2826 |  | 2026-01-27 20:29 | none | FALSE | 0 | 68.7077 | FALSE | FALSE | 0.5057 | 1.6744 | 70.0611 | 24 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.6767 | Confirmed/Materialized Shift | 71.4145 | -1.5855 | Night | 202601 | 2026-01-28 | 1.5855
2026-01-28 02:27 | 68.9882 | FALSE | TRUE | -0.35312 | -0.51448 | -2.273 | -3.1897 | 0 |  | 2026-01-27 20:29 | none | FALSE | 0 | 68.6351 | FALSE | FALSE | 0.4975 | 1.6659 | 69.9481 | 25 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.65653 | Confirmed/Materialized Shift | 71.2612 | -1.4621 | Night | 202601 | 2026-01-28 | 1.4621
2026-01-28 02:43 | 68.7056 | FALSE | TRUE | -0.2038 | -0.29751 | -2.463 | -3.4608 | -0.2826 |  | 2026-01-27 20:29 | none | FALSE | 0 | 68.5018 | FALSE | FALSE | 0.513 | 1.667 | 69.8352 | 26 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.66669 | Confirmed/Materialized Shift | 71.1686 | -1.6943 | Night | 202601 | 2026-01-28 | 1.6943
2026-01-28 02:58 | 68.7056 | FALSE | TRUE | -0.29648 | -0.4334 | -2.3298 | -3.2797 | 0 |  | 2026-01-27 20:29 | none | FALSE | 0 | 68.4091 | FALSE | FALSE | 0.5032 | 1.6626 | 69.7222 | 27 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.65656 | Confirmed/Materialized Shift | 71.0354 | -1.5484 | Night | 202601 | 2026-01-28 | 1.5484
2026-01-28 03:13 | 68.423 | FALSE | TRUE | -0.16723 | -0.24501 | -2.5398 | -3.5791 | -0.2826 |  | 2026-01-27 20:29 | none | FALSE | 0 | 68.2558 | FALSE | FALSE | 0.5169 | 1.6659 | 69.6093 | 28 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.67676 | Confirmed/Materialized Shift | 70.9628 | -1.7529 | Night | 202601 | 2026-01-28 | 1.7529
2026-01-28 03:27 | 68.423 | FALSE | TRUE | -0.28029 | -0.41133 | -2.427 | -3.4255 | 0 |  | 2026-01-27 20:29 | none | FALSE | 0 | 68.1427 | FALSE | FALSE | 0.5057 | 1.6631 | 69.4963 | 29 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.67682 | Confirmed/Materialized Shift | 70.85 | -1.5859 | Night | 202601 | 2026-01-28 | 1.5859
2026-01-28 03:42 | 68.423 | FALSE | TRUE | -0.35307 | -0.51869 | -2.2739 | -3.2163 | 0 |  | 2026-01-27 20:29 | none | FALSE | 0 | 68.0699 | FALSE | FALSE | 0.4975 | 1.6564 | 69.3834 | 30 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.65673 | Confirmed/Materialized Shift | 70.6969 | -1.4624 | Night | 202601 | 2026-01-28 | 1.4624
2026-01-28 03:57 | 68.1404 | FALSE | TRUE | -0.20391 | -0.30015 | -2.464 | -3.4899 | -0.2826 |  | 2026-01-27 20:29 | none | FALSE | 0 | 67.9365 | FALSE | FALSE | 0.513 | 1.6576 | 69.2704 | 31 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.66697 | Confirmed/Materialized Shift | 70.6044 | -1.6943 | Night | 202601 | 2026-01-28 | 1.6943
2026-01-28 04:12 | 68.1404 | FALSE | TRUE | -0.29677 | -0.43743 | -2.3309 | -3.3076 | 0 |  | 2026-01-27 20:29 | none | FALSE | 0 | 67.8436 | FALSE | FALSE | 0.5032 | 1.6542 | 69.1575 | 32 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.65693 | Confirmed/Materialized Shift | 70.4713 | -1.5483 | Night | 202601 | 2026-01-28 | 1.5483
2026-01-28 04:27 | 67.8596 | FALSE | TRUE | -0.16903 | -0.24971 | -2.5391 | -3.6067 | -0.2808 |  | 2026-01-27 20:29 | none | FALSE | 0 | 67.6906 | FALSE | FALSE | 0.5167 | 1.6571 | 69.0446 | 33 | -0.2808 | -0.11286 | 0.14182 | -1.1842 | 0.67703 | Confirmed/Materialized Shift | 70.3987 | -1.7503 | Night | 202601 | 2026-01-28 | 1.7503
2026-01-28 09:51 | 67.577 | FALSE | TRUE | -0.065428 | -0.096914 | -2.7467 | -3.9058 | -0.2826 |  | 2026-01-27 20:29 | none | FALSE | 0 | 67.5116 | FALSE | FALSE | 0.5271 | 1.6645 | 68.9176 | 34 | -0.2826 | -0.12699 | 0.14404 | -1.0803 | 0.70303 | Confirmed/Materialized Shift | 70.3237 | -1.9069 | Day | 202601 | 2026-01-28 | 1.9069
2026-01-28 10:06 | 68.423 | TRUE | FALSE | -0.8922 | -1.3212 | -1.7121 | -2.4412 | 0.846 |  |  | none | FALSE | 1 | 67.5308 | FALSE | FALSE | 0.0705 |  | 68.8329 | 0 | 0.846 | -0.08469 | 0.26047 | 3.5732 | 0.65108 | Persistence ends | 70.1351 | -0.62965 | Day | 202601 | 2026-01-28 | 0.62965
2026-01-28 10:06 | 68.423 | FALSE | FALSE | -0.88469 | -1.3099 | -1.5633 | -2.2337 | 0 |  |  | none | FALSE | 1 | 67.5383 | FALSE | FALSE | 0.0655 |  | 68.7623 | 0 | 0 | -0.07065 | 0.25688 | 0.27503 | 0.612 | Normal | 69.9863 | -0.55442 | Day | 202601 | 2026-01-28 | 0.55442
2026-01-28 10:36 | 69.2708 | TRUE | FALSE | -1.6798 | -2.4852 | -0.60627 | -0.86763 | 0.8478 |  |  | none | FALSE | 2 | 67.591 | TRUE | FALSE | 0.1198 |  | 68.734 | 0 | 0.8478 | -0.02826 | 0.32899 | 2.6629 | 0.57152 | Normal | 69.8771 | 0.93918 | Day | 202601 | 2026-01-28 | 0.93918
2026-01-28 10:51 | 69.836 | FALSE | FALSE | -2.2795 | -3.3742 | -0.10381 | -0.14842 | 0.5652 |  |  | none | FALSE | 2 | 67.5565 | FALSE | FALSE | 0.1789 |  | 68.7482 | 0 | 0.5652 | 0.01413 | 0.34853 | 1.5811 | 0.59582 | Normal | 69.9398 | 1.8258 | Day | 202601 | 2026-01-28 | 1.8258
2026-01-28 11:06 | 70.1168 | FALSE | FALSE | -2.6345 | -3.904 | 0.046437 | 0.066272 | 0.2808 | 2026-01-28 16:49 | 2026-01-28 11:06 | upper | TRUE | 2 | 67.4823 | FALSE | FALSE | 0.2524 | 2.0718 | 68.7763 | 1 | 0.2808 | 0.02817 | 0.35355 | 0.71456 | 0.64701 | Extreme triggered | 70.0704 | 2.0718 | Day | 202601 | 2026-01-28 | 2.0718
2026-01-28 11:21 | 70.3994 | FALSE | FALSE | -3.0378 | -4.5096 | 0.095504 | 0.13584 | 0.2826 |  | 2026-01-28 11:06 | upper | TRUE | 2 | 67.3616 | FALSE | FALSE | 0.3134 | 2.1008 | 68.8328 | 2 | 0.2826 | 0.05643 | 0.34997 | 0.64625 | 0.73556 | Extreme/elevated | 70.3039 | 2.1298 | Day | 202601 | 2026-01-28 | 2.1298
2026-01-28 11:36 | 70.682 | FALSE | FALSE | -3.4588 | -5.1452 | 0.098557 | 0.13963 | 0.2826 |  | 2026-01-28 11:06 | upper | TRUE | 2 | 67.2232 | FALSE | TRUE | 0.3697 | 2.1063 | 68.9033 | 3 | 0.2826 | 0.07056 | 0.35326 | 0.60023 | 0.84006 | Persistent | 70.5834 | 2.1173 | Day | 202601 | 2026-01-28 | 2.1173
2026-01-28 11:51 | 70.9646 | FALSE | FALSE | -3.8893 | -5.7985 | 0.063822 | 0.090015 | 0.2826 |  | 2026-01-28 11:06 | upper | TRUE | 2 | 67.0753 | FALSE | TRUE | 0.4235 | 2.0964 | 68.988 | 4 | 0.2826 | 0.08469 | 0.35593 | 0.55603 | 0.95638 | Persistent | 70.9008 | 2.0667 | Day | 202601 | 2026-01-28 | 2.0667
2026-01-28 12:06 | 71.2472 | FALSE | FALSE | -4.3226 | -6.4589 | -0.0018603 | -0.002611 | 0.2826 |  | 2026-01-28 11:06 | none | FALSE | 2 | 66.9246 | FALSE | FALSE | 0.4761 | 2.0768 | 69.0868 | 5 | 0.2826 | 0.09882 | 0.358 | 0.51336 | 1.0811 | Persistent | 71.2491 | 1.9983 | Day | 202601 | 2026-01-28 | 1.9983
2026-01-28 12:21 | 71.2472 | FALSE | FALSE | -4.4143 | -6.6049 | -0.31944 | -0.44636 | 0 |  | 2026-01-28 11:06 | none | FALSE | 2 | 66.8329 | FALSE | FALSE | 0.5153 | 2.019 | 69.1998 | 6 | 0 | 0.11295 | 0.34758 | -0.32496 | 1.1834 | Persistent | 71.5666 | 1.7301 | Day | 202601 | 2026-01-28 | 1.7301
2026-01-28 12:36 | 71.5298 | FALSE | TRUE | -4.7851 | -7.1692 | -0.37922 | -0.52736 | 0.2826 |  | 2026-01-28 11:06 | none | FALSE | 1 | 66.7447 | FALSE | FALSE | 0.5423 | 1.9743 | 69.3269 | 7 | 0.2826 | 0.12708 | 0.34849 | 0.44627 | 1.2911 | Confirmed/Materialized Shift | 71.909 | 1.7063 | Day | 202601 | 2026-01-28 | 1.7063
2026-01-28 12:51 | 71.8124 | FALSE | TRUE | -5.1204 | -7.6777 | -0.46002 | -0.6365 | 0.2826 |  | 2026-01-28 11:06 | none | FALSE | 1 | 66.692 | FALSE | FALSE | 0.5399 | 1.9363 | 69.4822 | 8 | 0.2826 | 0.15534 | 0.33622 | 0.37851 | 1.3951 | Confirmed/Materialized Shift | 72.2724 | 1.6703 | Day | 202601 | 2026-01-28 | 1.6703
2026-01-28 13:05 | 71.8124 | FALSE | TRUE | -5.1244 | -7.6841 | -0.77469 | -1.0673 | 0 |  | 2026-01-28 11:06 | none | FALSE | 0 | 66.688 | FALSE | FALSE | 0.4983 | 1.885 | 69.6376 | 9 | 0 | 0.15534 | 0.33622 | -0.46202 | 1.4748 | Confirmed/Materialized Shift | 72.5871 | 1.4747 | Day | 202601 | 2026-01-28 | 1.4747
2026-01-28 13:20 | 72.095 | FALSE | TRUE | -5.3591 | -8.0303 | -0.81139 | -1.1129 | 0.2826 |  | 2026-01-28 11:06 | none | FALSE | 0 | 66.7359 | FALSE | FALSE | 0.4983 | 1.8439 | 69.8212 | 10 | 0.2826 | 0.1836 | 0.32087 | 0.30853 | 1.5426 | Confirmed/Materialized Shift | 72.9064 | 1.474 | Day | 202601 | 2026-01-28 | 1.474
2026-01-28 13:35 | 72.095 | FALSE | TRUE | -5.261 | -7.8718 | -1.0805 | -1.4766 | 0 |  | 2026-01-28 11:06 | none | FALSE | 0 | 66.834 | FALSE | FALSE | 0.4879 | 1.7962 | 70.0048 | 11 | 0 | 0.1836 | 0.32087 | -0.57219 | 1.5854 | Confirmed/Materialized Shift | 73.1755 | 1.3185 | Day | 202601 | 2026-01-28 | 1.3185
2026-01-28 13:50 | 72.3758 | FALSE | TRUE | -5.4209 | -8.0963 | -1.0741 | -1.4623 | 0.2808 |  | 2026-01-28 11:06 | none | FALSE | 0 | 66.9549 | FALSE | FALSE | 0.4892 | 1.758 | 70.2024 | 12 | 0.2808 | 0.19764 | 0.31855 | 0.26106 | 1.6237 | Confirmed/Materialized Shift | 73.4499 | 1.3385 | Day | 202601 | 2026-01-28 | 1.3385
2026-01-28 14:05 | 72.3758 | FALSE | TRUE | -5.1953 | -7.7334 | -1.272 | -1.7272 | 0 |  | 2026-01-28 11:06 | none | FALSE | 0 | 67.1805 | FALSE | FALSE | 0.4809 | 1.7161 | 70.4142 | 13 | 0 | 0.21177 | 0.30196 | -0.70131 | 1.6168 | Confirmed/Materialized Shift | 73.6478 | 1.2133 | Day | 202601 | 2026-01-28 | 1.2133
2026-01-28 14:20 | 72.6584 | FALSE | TRUE | -5.2142 | -7.7312 | -1.1775 | -1.5948 | 0.2826 |  | 2026-01-28 11:06 | none | FALSE | 0 | 67.4442 | FALSE | FALSE | 0.4842 | 1.6838 | 70.6401 | 14 | 0.2826 | 0.2259 | 0.29812 | 0.19019 | 1.5979 | Confirmed/Materialized Shift | 73.8359 | 1.2631 | Day | 202601 | 2026-01-28 | 1.2631
2026-01-28 14:35 | 72.6584 | FALSE | TRUE | -4.8118 | -7.0921 | -1.255 | -1.6979 | 0 |  | 2026-01-28 11:06 | none | FALSE | 0 | 67.8466 | FALSE | FALSE | 0.4782 | 1.6497 | 70.88 | 15 | 0 | 0.23994 | 0.279 | -0.86 | 1.5167 | Confirmed/Materialized Shift | 73.9134 | 1.1726 | Day | 202601 | 2026-01-28 | 1.1726
2026-01-28 14:50 | 72.941 | FALSE | TRUE | -4.5307 | -6.6228 | -0.94506 | -1.2791 | 0.2826 |  | 2026-01-28 11:06 | none | FALSE | 0 | 68.4103 | FALSE | FALSE | 0.4873 | 1.6284 | 71.1482 | 16 | 0.2826 | 0.2682 | 0.25045 | 0.057497 | 1.3689 | Confirmed/Materialized Shift | 73.8861 | 1.3096 | Day | 202601 | 2026-01-28 | 1.3096
2026-01-28 15:05 | 72.941 | FALSE | TRUE | -4.0956 | -5.9489 | -0.96177 | -1.3014 | 0 |  | 2026-01-28 11:06 | none | FALSE | 0 | 68.8454 | FALSE | FALSE | 0.4826 | 1.6055 | 71.3741 | 17 | 0 | 0.2259 | 0.21692 | -1.0414 | 1.2643 | Confirmed/Materialized Shift | 73.9028 | 1.2393 | Day | 202601 | 2026-01-28 | 1.2393
2026-01-28 15:20 | 73.2236 | FALSE | TRUE | -3.8541 | -5.5559 | -0.63513 | -0.85993 | 0.2826 |  | 2026-01-28 11:06 | none | FALSE | 0 | 69.3695 | FALSE | FALSE | 0.4956 | 1.596 | 71.6141 | 18 | 0.2826 | 0.24003 | 0.21054 | 0.20219 | 1.1223 | Confirmed/Materialized Shift | 73.8587 | 1.4341 | Day | 202601 | 2026-01-28 | 1.4341
2026-01-28 15:35 | 73.2236 | FALSE | TRUE | -3.4765 | -4.9845 | -0.65289 | -0.88376 | 0 |  | 2026-01-28 11:06 | none | FALSE | 0 | 69.7471 | FALSE | FALSE | 0.4912 | 1.584 | 71.8118 | 19 | 0 | 0.19764 | 0.16133 | -1.225 | 1.0324 | Confirmed/Materialized Shift | 73.8765 | 1.3676 | Day | 202601 | 2026-01-28 | 1.3676
2026-01-28 15:50 | 73.2236 | FALSE | TRUE | -3.1764 | -4.5346 | -0.69148 | -0.9355 | 0 |  | 2026-01-28 11:06 | none | FALSE | 0 | 70.0472 | FALSE | FALSE | 0.4857 | 1.569 | 71.9811 | 20 | 0 | 0.16938 | 0.14189 | -1.1937 | 0.96696 | Confirmed/Materialized Shift | 73.9151 | 1.2849 | Day | 202601 | 2026-01-28 | 1.2849
2026-01-28 16:04 | 73.2236 | FALSE | TRUE | -2.8848 | -4.1013 | -0.71059 | -0.96111 | 0 |  | 2026-01-28 11:06 | none | FALSE | 0 | 70.3388 | FALSE | FALSE | 0.4806 | 1.5519 | 72.1365 | 21 | 0 | 0.15534 | 0.14416 | -1.0775 | 0.89885 | Confirmed/Materialized Shift | 73.9342 | 1.2094 | Day | 202601 | 2026-01-28 | 1.2094
2026-01-28 16:19 | 73.2236 | FALSE | TRUE | -2.6076 | -3.6927 | -0.71581 | -0.96811 | 0 |  | 2026-01-28 11:06 | none | FALSE | 0 | 70.616 | FALSE | FALSE | 0.4759 | 1.5331 | 72.2777 | 22 | 0 | 0.14121 | 0.14488 | -0.97468 | 0.83086 | Confirmed/Materialized Shift | 73.9394 | 1.1385 | Day | 202601 | 2026-01-28 | 1.1385
2026-01-28 16:34 | 73.2236 | FALSE | TRUE | -2.3504 | -3.3163 | -0.71272 | -0.96396 | 0 |  | 2026-01-28 11:06 | none | FALSE | 0 | 70.8732 | FALSE | FALSE | 0.4713 | 1.513 | 72.4048 | 23 | 0 | 0.12708 | 0.14414 | -0.88163 | 0.76577 | Confirmed/Materialized Shift | 73.9363 | 1.0693 | Day | 202601 | 2026-01-28 | 1.0693
2026-01-28 16:49 | 73.2236 | FALSE | FALSE | -2.1188 | -2.9798 | -0.70706 | -0.95639 | 0 |  |  | none | FALSE | 0 | 71.1048 | FALSE | FALSE | 0.0666 |  | 72.5177 | 0 | 0 | 0.11295 | 0.14193 | -0.79582 | 0.70647 | Persistence ends | 73.9307 | 0.99915 | Day | 202601 | 2026-01-28 | 0.99915
2026-01-28 17:04 | 73.2236 | FALSE | FALSE | -1.9187 | -2.6908 | -0.70456 | -0.95303 | 0 |  |  | none | FALSE | 0 | 71.3049 | FALSE | FALSE | 0.0617 |  | 72.6166 | 0 | 0 | 0.09882 | 0.13817 | -0.71522 | 0.65581 | Normal | 73.9282 | 0.92566 | Day | 202601 | 2026-01-28 | 0.92566
2026-01-28 17:19 | 73.2236 | FALSE | FALSE | -1.6753 | -2.3415 | -0.65883 | -0.89172 | 0 |  |  | none | FALSE | 0 | 71.5483 | FALSE | FALSE | 0.0581 |  | 72.7154 | 0 | 0 | 0.09882 | 0.13817 | -0.71522 | 0.58353 | Normal | 73.8824 | 0.87096 | Day | 202601 | 2026-01-28 | 0.87096
2026-01-28 17:34 | 73.2236 | FALSE | FALSE | -1.4677 | -2.0454 | -0.62063 | -0.84046 | 0 |  |  | none | FALSE | 0 | 71.7559 | FALSE | FALSE | 0.0541 |  | 72.8001 | 0 | 0 | 0.08469 | 0.13273 | -0.63807 | 0.52208 | Normal | 73.8442 | 0.81125 | Day | 202601 | 2026-01-28 | 0.81125
2026-01-28 17:49 | 73.2236 | FALSE | FALSE | -1.3026 | -1.8111 | -0.59662 | -0.8082 | 0 |  |  | none | FALSE | 0 | 71.921 | FALSE | FALSE | 0.0496 |  | 72.8706 | 0 | 0 | 0.07056 | 0.12539 | -0.56273 | 0.4748 | Normal | 73.8202 | 0.74343 | Day | 202601 | 2026-01-28 | 0.74343
2026-01-28 18:04 | 73.2236 | FALSE | FALSE | -1.1017 | -1.5276 | -0.53688 | -0.72786 | 0 |  |  | none | FALSE | 0 | 72.1219 | FALSE | FALSE | 0.046 |  | 72.9412 | 0 | 0 | 0.07056 | 0.12539 | -0.56273 | 0.40965 | Normal | 73.7605 | 0.68942 | Night | 202601 | 2026-01-28 | 0.68942
2026-01-28 18:19 | 73.2236 | FALSE | FALSE | -0.94979 | -1.3142 | -0.49781 | -0.67526 | 0 |  |  | none | FALSE | 0 | 72.2738 | FALSE | FALSE | 0.0416 |  | 72.9976 | 0 | 0 | 0.05643 | 0.11579 | -0.48734 | 0.3619 | Normal | 73.7214 | 0.62445 | Night | 202601 | 2026-01-28 | 0.62445
2026-01-28 18:30 | 73.2236 | FALSE | FALSE | -0.76093 | -1.0501 | -0.42181 | -0.57275 | 0 |  |  | none | FALSE | 0 | 72.4627 | FALSE | FALSE | 0.0382 |  | 73.054 | 0 | 0 | 0.05643 | 0.11579 | -0.48734 | 0.29568 | Normal | 73.6454 | 0.57345 | Night | 202601 | 2026-01-28 | 0.57345
2026-01-28 18:31 | 73.2236 | FALSE | FALSE | -0.62853 | -0.8658 | -0.37419 | -0.50842 | 0 |  |  | none | FALSE | 0 | 72.5951 | FALSE | FALSE | 0.0338 |  | 73.0964 | 0 | 0 | 0.04239 | 0.10353 | -0.40945 | 0.25068 | Normal | 73.5978 | 0.5073 | Night | 202601 | 2026-01-28 | 0.5073
2026-01-28 18:46 | 73.2236 | FALSE | FALSE | -0.45609 | -0.62677 | -0.28653 | -0.38978 | 0 |  |  | none | FALSE | 0 | 72.7675 | FALSE | FALSE | 0.0304 |  | 73.1388 | 0 | 0 | 0.04239 | 0.10353 | -0.40945 | 0.18565 | Normal | 73.5101 | 0.45666 | Night | 202601 | 2026-01-28 | 0.45666
2026-01-28 19:01 | 72.941 | TRUE | FALSE | -0.098978 | -0.13588 | -0.52288 | -0.71175 | -0.2826 |  |  | none | FALSE | 1 | 72.842 | FALSE | FALSE | 0.1195 |  | 73.153 | 0 | -0.2826 | 0.01413 | 0.11135 | -2.6647 | 0.15546 | Normal | 73.4639 | -1.3633 | Night | 202601 | 2026-01-28 | 1.3633
2026-01-28 19:16 | 72.941 | FALSE | FALSE | -0.0058732 | -0.0080526 | -0.45803 | -0.62403 | 0 |  |  | none | FALSE | 1 | 72.9351 | FALSE | FALSE | 0.1585 |  | 73.1671 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.11598 | Normal | 73.399 | -1.9494 | Night | 202601 | 2026-01-28 | 1.9494
2026-01-28 19:30 | 72.6584 | TRUE | FALSE | 0.18362 | 0.25208 | -0.80548 | -1.0964 | -0.2826 | 2026-01-29 10:14 | 2026-01-28 19:30 | lower | TRUE | 2 | 72.842 | TRUE | FALSE | 0.3264 | 3.1811 | 73.153 | 1 | -0.2826 | -0.01413 | 0.11135 | -2.411 | 0.15546 | Extreme triggered | 73.4639 | -3.1811 | Night | 202601 | 2026-01-28 | 3.1811
2026-01-28 19:45 | 72.3758 | TRUE | FALSE | 0.28954 | 0.39845 | -1.2082 | -1.642 | -0.2826 |  | 2026-01-28 19:30 | lower | TRUE | 3 | 72.6653 | TRUE | FALSE | 0.4174 | 3.2209 | 73.1247 | 2 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.22968 | Extreme/elevated | 73.584 | -3.2606 | Night | 202601 | 2026-01-28 | 3.2606
2026-01-28 20:00 | 72.095 | FALSE | FALSE | 0.32615 | 0.45035 | -1.6204 | -2.1981 | -0.2808 |  | 2026-01-28 19:30 | lower | TRUE | 3 | 72.4211 | FALSE | TRUE | 0.4577 | 3.1499 | 73.0683 | 3 | -0.2808 | -0.05643 | 0.11579 | -1.9377 | 0.32356 | Persistent | 73.7154 | -3.008 | Night | 202601 | 2026-01-28 | 3.008
2026-01-28 20:15 | 71.8124 | FALSE | FALSE | 0.33398 | 0.46292 | -2.0366 | -2.7578 | -0.2826 |  | 2026-01-28 19:30 | lower | TRUE | 3 | 72.1464 | FALSE | TRUE | 0.4999 | 3.0586 | 72.9977 | 4 | -0.2826 | -0.07056 | 0.12539 | -1.6911 | 0.42566 | Persistent | 73.849 | -2.7846 | Night | 202601 | 2026-01-28 | 2.7846
2026-01-28 20:29 | 71.8124 | FALSE | FALSE | 0.12035 | 0.16731 | -2.1091 | -2.8532 | 0 |  | 2026-01-28 19:30 | lower | TRUE | 3 | 71.9327 | FALSE | TRUE | 0.5209 | 2.8953 | 72.9271 | 5 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.4972 | Persistent | 73.9215 | -2.2421 | Night | 202601 | 2026-01-28 | 2.2421
2026-01-28 20:44 | 71.8124 | FALSE | FALSE | -0.056256 | -0.0784 | -2.1446 | -2.8998 | 0 |  | 2026-01-28 19:30 | none | FALSE | 3 | 71.7561 | FALSE | FALSE | 0.5551 | 2.729 | 72.8566 | 6 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.55022 | Persistent | 73.957 | -1.8978 | Night | 202601 | 2026-01-28 | 1.8978
2026-01-28 20:59 | 71.5298 | FALSE | TRUE | 0.0079907 | 0.01117 | -2.4762 | -3.3459 | -0.2826 |  | 2026-01-28 19:30 | lower | TRUE | 3 | 71.5378 | FALSE | TRUE | 0.6199 | 2.6267 | 72.7719 | 7 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.61705 | Confirmed/Materialized Shift | 74.006 | -2.0129 | Night | 202601 | 2026-01-28 | 2.0129
2026-01-28 21:14 | 71.5298 | FALSE | TRUE | -0.17476 | -0.24491 | -2.4896 | -3.3634 | 0 |  | 2026-01-28 19:30 | none | FALSE | 3 | 71.355 | FALSE | FALSE | 0.6016 | 2.5156 | 72.6872 | 8 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.66608 | Confirmed/Materialized Shift | 74.0194 | -1.7376 | Night | 202601 | 2026-01-28 | 1.7376
2026-01-28 21:29 | 71.2472 | FALSE | TRUE | -0.11123 | -0.15636 | -2.7936 | -3.773 | -0.2826 |  | 2026-01-28 19:30 | none | FALSE | 2 | 71.136 | FALSE | FALSE | 0.5803 | 2.4413 | 72.5884 | 9 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.72621 | Confirmed/Materialized Shift | 74.0408 | -1.8468 | Night | 202601 | 2026-01-28 | 1.8468
2026-01-28 21:44 | 70.9646 | FALSE | TRUE | -0.078485 | -0.11072 | -3.1001 | -4.1857 | -0.2826 |  | 2026-01-28 19:30 | none | FALSE | 2 | 70.8861 | FALSE | FALSE | 0.5839 | 2.3873 | 72.4754 | 10 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.79466 | Confirmed/Materialized Shift | 74.0647 | -1.9012 | Night | 202601 | 2026-01-28 | 1.9012
2026-01-28 21:59 | 70.682 | FALSE | TRUE | -0.070663 | -0.10007 | -3.4034 | -4.5938 | -0.2826 |  | 2026-01-28 19:30 | none | FALSE | 1 | 70.6113 | FALSE | FALSE | 0.5565 | 2.3447 | 72.3483 | 11 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.86851 | Confirmed/Materialized Shift | 74.0854 | -1.9186 | Night | 202601 | 2026-01-28 | 1.9186
2026-01-28 22:14 | 70.682 | FALSE | TRUE | -0.29717 | -0.42221 | -3.3757 | -4.5582 | 0 |  | 2026-01-28 19:30 | none | FALSE | 0 | 70.3848 | FALSE | FALSE | 0.5118 | 2.289 | 72.2213 | 12 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.91822 | Confirmed/Materialized Shift | 74.0577 | -1.6764 | Night | 202601 | 2026-01-28 | 1.6764
2026-01-28 22:29 | 70.3994 | FALSE | TRUE | -0.26249 | -0.37425 | -3.6238 | -4.8955 | -0.2826 |  | 2026-01-28 19:30 | none | FALSE | 0 | 70.1369 | FALSE | FALSE | 0.5153 | 2.246 | 72.0801 | 13 | -0.2826 | -0.14121 | 0.14488 | -0.97592 | 0.97157 | Confirmed/Materialized Shift | 74.0232 | -1.7298 | Night | 202601 | 2026-01-28 | 1.7298
2026-01-28 22:44 | 70.3994 | FALSE | TRUE | -0.46335 | -0.66254 | -3.5423 | -4.7906 | 0 |  | 2026-01-28 19:30 | none | FALSE | 0 | 69.936 | FALSE | FALSE | 0.5025 | 2.1954 | 71.9389 | 14 | 0 | -0.14121 | 0.14488 | 0.97468 | 1.0014 | Confirmed/Materialized Shift | 73.9417 | -1.5373 | Night | 202601 | 2026-01-28 | 1.5373
2026-01-28 22:59 | 70.1168 | FALSE | TRUE | -0.39752 | -0.57017 | -3.7309 | -5.0522 | -0.2826 |  | 2026-01-28 19:30 | none | FALSE | 0 | 69.7193 | FALSE | FALSE | 0.5077 | 2.1567 | 71.7835 | 15 | -0.2826 | -0.15534 | 0.14416 | -0.88276 | 1.0321 | Confirmed/Materialized Shift | 73.8477 | -1.6148 | Night | 202601 | 2026-01-28 | 1.6148
2026-01-28 23:14 | 69.836 | FALSE | TRUE | -0.34369 | -0.49458 | -3.9 | -5.2891 | -0.2808 |  | 2026-01-28 19:30 | none | FALSE | 0 | 69.4923 | FALSE | FALSE | 0.5117 | 2.1266 | 71.6141 | 16 | -0.2808 | -0.16938 | 0.14189 | -0.78525 | 1.0609 | Confirmed/Materialized Shift | 73.736 | -1.676 | Night | 202601 | 2026-01-28 | 1.676
2026-01-28 23:28 | 69.5534 | FALSE | TRUE | -0.29281 | -0.42276 | -4.0472 | -5.4989 | -0.2826 |  | 2026-01-28 19:30 | none | FALSE | 0 | 69.2606 | FALSE | FALSE | 0.5153 | 2.1033 | 71.4306 | 17 | -0.2826 | -0.18351 | 0.13816 | -0.71722 | 1.085 | Confirmed/Materialized Shift | 73.6006 | -1.7301 | Night | 202601 | 2026-01-28 | 1.7301
2026-01-28 23:43 | 69.5534 | FALSE | TRUE | -0.45857 | -0.66368 | -3.846 | -5.2398 | 0 |  | 2026-01-28 19:30 | none | FALSE | 0 | 69.0948 | FALSE | FALSE | 0.5049 | 2.0739 | 71.2471 | 18 | 0 | -0.18351 | 0.13816 | 1.3283 | 1.0761 | Confirmed/Materialized Shift | 73.3994 | -1.5739 | Night | 202601 | 2026-01-28 | 1.5739
2026-01-28 23:59 | 69.2708 | FALSE | TRUE | -0.37716 | -0.54746 | -3.9628 | -5.4111 | -0.2826 |  | 2026-01-28 19:30 | none | FALSE | 0 | 68.8936 | FALSE | FALSE | 0.5102 | 2.0517 | 71.0636 | 19 | -0.2826 | -0.18351 | 0.13816 | -0.71722 | 1.085 | Confirmed/Materialized Shift | 73.2336 | -1.6524 | Night | 202601 | 2026-01-28 | 1.6524
2026-01-29 00:14 | 69.2708 | FALSE | TRUE | -0.5124 | -0.74522 | -3.731 | -5.1108 | 0 |  | 2026-01-28 19:30 | none | FALSE | 0 | 68.7584 | FALSE | FALSE | 0.5011 | 2.025 | 70.8801 | 20 | 0 | -0.18351 | 0.13816 | 1.3283 | 1.0608 | Confirmed/Materialized Shift | 73.0018 | -1.517 | Night | 202601 | 2026-01-29 | 1.517
2026-01-29 00:28 | 68.9882 | FALSE | TRUE | -0.40054 | -0.58398 | -3.8173 | -5.2431 | -0.2826 |  | 2026-01-28 19:30 | none | FALSE | 0 | 68.5877 | FALSE | FALSE | 0.508 | 2.0057 | 70.6966 | 21 | -0.2826 | -0.18351 | 0.13816 | -0.71722 | 1.0545 | Confirmed/Materialized Shift | 72.8055 | -1.6201 | Night | 202601 | 2026-01-29 | 1.6201
2026-01-29 00:43 | 68.9882 | FALSE | TRUE | -0.54608 | -0.79787 | -3.6241 | -4.991 | 0 |  | 2026-01-28 19:30 | none | FALSE | 0 | 68.4421 | FALSE | FALSE | 0.4984 | 1.9816 | 70.5272 | 22 | 0 | -0.16938 | 0.14189 | 1.1937 | 1.0425 | Confirmed/Materialized Shift | 72.6123 | -1.4762 | Night | 202601 | 2026-01-29 | 1.4762
2026-01-29 00:58 | 68.7056 | FALSE | TRUE | -0.44733 | -0.65534 | -3.7516 | -5.1777 | -0.2826 |  | 2026-01-28 19:30 | none | FALSE | 0 | 68.2583 | FALSE | FALSE | 0.5049 | 1.9639 | 70.3577 | 23 | -0.2826 | -0.16947 | 0.14197 | -0.79688 | 1.0497 | Confirmed/Materialized Shift | 72.4572 | -1.5739 | Night | 202601 | 2026-01-29 | 1.5739
2026-01-29 01:13 | 68.7056 | FALSE | TRUE | -0.60922 | -0.89464 | -3.6028 | -4.9825 | 0 |  | 2026-01-28 19:30 | none | FALSE | 0 | 68.0964 | FALSE | FALSE | 0.4948 | 1.9413 | 70.2024 | 24 | 0 | -0.15534 | 0.14416 | 1.0775 | 1.053 | Confirmed/Materialized Shift | 72.3084 | -1.4214 | Night | 202601 | 2026-01-29 | 1.4214
2026-01-29 01:28 | 68.7056 | FALSE | TRUE | -0.72243 | -1.0627 | -3.4053 | -4.7224 | 0 |  | 2026-01-28 19:30 | none | FALSE | 0 | 67.9832 | FALSE | FALSE | 0.4867 | 1.9156 | 70.047 | 25 | 0 | -0.15534 | 0.14416 | 1.0775 | 1.0319 | Confirmed/Materialized Shift | 72.1109 | -1.2999 | Night | 202601 | 2026-01-29 | 1.2999
2026-01-29 01:43 | 68.423 | FALSE | TRUE | -0.55486 | -0.81756 | -3.464 | -4.8187 | -0.2826 |  | 2026-01-28 19:30 | none | FALSE | 0 | 67.8681 | FALSE | FALSE | 0.4965 | 1.8976 | 69.8776 | 26 | -0.2826 | -0.16947 | 0.14197 | -0.79688 | 1.0047 | Confirmed/Materialized Shift | 71.887 | -1.4477 | Night | 202601 | 2026-01-29 | 1.4477
2026-01-29 01:58 | 68.423 | FALSE | TRUE | -0.65191 | -0.96193 | -3.2504 | -4.535 | 0 |  | 2026-01-28 19:30 | none | FALSE | 0 | 67.7711 | FALSE | FALSE | 0.4888 | 1.8767 | 69.7222 | 27 | 0 | -0.15534 | 0.14416 | 1.0775 | 0.97557 | Confirmed/Materialized Shift | 71.6734 | -1.3318 | Night | 202601 | 2026-01-29 | 1.3318
2026-01-29 02:13 | 68.423 | FALSE | TRUE | -0.69265 | -1.0227 | -2.9804 | -4.1741 | 0 |  | 2026-01-28 19:30 | none | FALSE | 0 | 67.7304 | FALSE | FALSE | 0.483 | 1.8541 | 69.5669 | 28 | 0 | -0.15534 | 0.14416 | 1.0775 | 0.91827 | Confirmed/Materialized Shift | 71.4034 | -1.2457 | Night | 202601 | 2026-01-29 | 1.2457
2026-01-29 02:28 | 68.1404 | FALSE | TRUE | -0.49103 | -0.72584 | -3.0333 | -4.2619 | -0.2826 |  | 2026-01-28 19:30 | none | FALSE | 0 | 67.6494 | FALSE | FALSE | 0.4962 | 1.84 | 69.4116 | 29 | -0.2826 | -0.15534 | 0.14416 | -0.88276 | 0.88109 | Confirmed/Materialized Shift | 71.1737 | -1.4427 | Night | 202601 | 2026-01-29 | 1.4427
2026-01-29 02:43 | 68.1404 | FALSE | TRUE | -0.55935 | -0.82768 | -2.8193 | -3.973 | 0 |  | 2026-01-28 19:30 | none | FALSE | 0 | 67.581 | FALSE | FALSE | 0.4892 | 1.8232 | 69.2703 | 30 | 0 | -0.14121 | 0.14488 | 0.97468 | 0.84465 | Confirmed/Materialized Shift | 70.9597 | -1.3378 | Night | 202601 | 2026-01-29 | 1.3378
2026-01-29 09:43 | 66.4466 | TRUE | TRUE | 0.63106 | 0.94079 | -4.5929 | -6.4653 | -1.6938 |  | 2026-01-28 19:30 | lower | TRUE | 1 | 67.0777 | FALSE | TRUE | 0.6044 | 1.8495 | 69.0586 | 31 | -1.6938 | -0.21177 | 0.37625 | -3.9389 | 0.99046 | Confirmed/Materialized Shift | 71.0395 | -2.6371 | Day | 202601 | 2026-01-29 | 2.6371
2026-01-29 09:43 | 66.4466 | FALSE | TRUE | 0.25156 | 0.37717 | -4.5489 | -6.4072 | 0 |  | 2026-01-28 19:30 | lower | TRUE | 1 | 66.6982 | FALSE | TRUE | 0.5775 | 1.8615 | 68.8468 | 32 | 0 | -0.21177 | 0.37625 | 0.56284 | 1.0743 | Confirmed/Materialized Shift | 70.9955 | -2.2342 | Day | 202601 | 2026-01-29 | 2.2342
2026-01-29 09:58 | 67.577 | TRUE | TRUE | -0.96052 | -1.4419 | -3.2179 | -4.5454 | 1.1304 |  | 2026-01-28 19:30 | none | FALSE | 2 | 66.6165 | TRUE | FALSE | 0.5292 | 1.8378 | 68.7057 | 33 | 1.1304 | -0.14112 | 0.48048 | 2.6464 | 1.0446 | Confirmed/Materialized Shift | 70.7949 | -1.0805 | Day | 202601 | 2026-01-29 | 1.0805
2026-01-29 10:14 | 68.1404 | FALSE | FALSE | -1.4904 | -2.2362 | -2.3951 | -3.3956 | 0.5634 |  |  | none | FALSE | 2 | 66.65 | FALSE | FALSE | 0.0882 |  | 68.5927 | 0 | 0.5634 | -0.11295 | 0.50508 | 1.3391 | 0.97139 | Persistence ends | 70.5355 | -0.46566 | Day | 202601 | 2026-01-29 | 0.46566
2026-01-29 10:29 | 68.7056 | FALSE | FALSE | -1.9909 | -2.9843 | -1.6241 | -2.3093 | 0.5652 |  |  | none | FALSE | 2 | 66.7147 | FALSE | FALSE | 0.0707 |  | 68.5222 | 0 | 0.5652 | -0.07056 | 0.52526 | 1.2104 | 0.90376 | Normal | 70.3297 | 0.20295 | Day | 202601 | 2026-01-29 | 0.20295
2026-01-29 10:43 | 68.9882 | FALSE | FALSE | -2.2236 | -3.3305 | -1.2068 | -1.7192 | 0.2826 |  |  | none | FALSE | 2 | 66.7646 | FALSE | FALSE | 0.0967 |  | 68.4798 | 0 | 0.2826 | -0.04239 | 0.52849 | 0.61494 | 0.8576 | Normal | 70.195 | 0.59283 | Day | 202601 | 2026-01-29 | 0.59283
2026-01-29 10:58 | 69.2708 | FALSE | FALSE | -2.4874 | -3.7246 | -0.87716 | -1.2504 | 0.2826 |  |  | none | FALSE | 2 | 66.7834 | FALSE | FALSE | 0.121 |  | 68.4657 | 0 | 0.2826 | -0.01413 | 0.53008 | 0.55979 | 0.84115 | Normal | 70.148 | 0.95719 | Day | 202601 | 2026-01-29 | 0.95719
2026-01-29 11:13 | 69.836 | FALSE | FALSE | -3.0812 | -4.6157 | -0.36876 | -0.52527 | 0.5652 |  |  | none | FALSE | 2 | 66.7548 | FALSE | FALSE | 0.162 |  | 68.4798 | 0 | 0.5652 | 0.01413 | 0.54571 | 1.0098 | 0.86249 | Normal | 70.2048 | 1.5724 | Day | 202601 | 2026-01-29 | 1.5724
2026-01-29 11:28 | 69.836 | FALSE | FALSE | -3.1245 | -4.6836 | -0.46862 | -0.66656 | 0 |  |  | none | FALSE | 2 | 66.7115 | FALSE | FALSE | 0.1557 |  | 68.508 | 0 | 0 | 0.02826 | 0.54126 | -0.052211 | 0.89829 | Normal | 70.3046 | 1.4783 | Day | 202601 | 2026-01-29 | 1.4783
2026-01-29 11:43 | 70.3994 | FALSE | FALSE | -3.7958 | -5.699 | -0.12591 | -0.17854 | 0.5634 |  |  | none | FALSE | 2 | 66.6036 | FALSE | FALSE | 0.1819 |  | 68.5645 | 0 | 0.5634 | 0.05643 | 0.55422 | 0.91475 | 0.98042 | Normal | 70.5253 | 1.8716 | Day | 202601 | 2026-01-29 | 1.8716
2026-01-29 11:58 | 70.3994 | FALSE | FALSE | -3.8845 | -5.84 | -0.35577 | -0.50281 | 0 |  |  | none | FALSE | 1 | 66.5149 | FALSE | FALSE | 0.1395 |  | 68.635 | 0 | 0 | 0.07056 | 0.54869 | -0.1286 | 1.0601 | Normal | 70.7552 | 1.6644 | Day | 202601 | 2026-01-29 | 1.6644
2026-01-29 12:13 | 70.682 | FALSE | FALSE | -4.2689 | -6.4278 | -0.34437 | -0.48485 | 0.2826 |  |  | none | FALSE | 1 | 66.4131 | FALSE | FALSE | 0.142 |  | 68.7197 | 0 | 0.2826 | 0.08469 | 0.55042 | 0.35956 | 1.1533 | Normal | 71.0264 | 1.7014 | Day | 202601 | 2026-01-29 | 1.7014
2026-01-29 12:28 | 70.9646 | FALSE | FALSE | -4.6474 | -7.0079 | -0.38359 | -0.53763 | 0.2826 |  |  | none | FALSE | 0 | 66.3172 | FALSE | FALSE | 0.113 |  | 68.8327 | 0 | 0.2826 | 0.11295 | 0.54505 | 0.31126 | 1.2578 | Normal | 71.3482 | 1.695 | Day | 202601 | 2026-01-29 | 1.695
2026-01-29 12:42 | 71.2472 | FALSE | FALSE | -5.0231 | -7.585 | -0.4482 | -0.62514 | 0.2826 |  |  | none | FALSE | 0 | 66.2241 | FALSE | FALSE | 0.1115 |  | 68.9598 | 0 | 0.2826 | 0.12708 | 0.54563 | 0.28503 | 1.3678 | Normal | 71.6954 | 1.6723 | Day | 202601 | 2026-01-29 | 1.6723
2026-01-29 12:57 | 71.5298 | FALSE | FALSE | -5.3914 | -8.1517 | -0.53372 | -0.74063 | 0.2826 |  |  | none | FALSE | 0 | 66.1384 | FALSE | FALSE | 0.1093 |  | 69.101 | 0 | 0.2826 | 0.14121 | 0.54583 | 0.25904 | 1.4813 | Normal | 72.0635 | 1.6397 | Day | 202601 | 2026-01-29 | 1.6397
2026-01-29 13:12 | 71.8124 | FALSE | FALSE | -5.7211 | -8.6563 | -0.63716 | -0.87945 | 0.2826 |  |  | none | FALSE | 0 | 66.0913 | FALSE | FALSE | 0.1066 |  | 69.2704 | 0 | 0.2826 | 0.16947 | 0.53729 | 0.21056 | 1.5896 | Normal | 72.4496 | 1.5992 | Day | 202601 | 2026-01-29 | 1.5992
2026-01-29 13:28 | 71.8124 | FALSE | FALSE | -5.7184 | -8.6519 | -0.9734 | -1.3374 | 0 |  |  | none | FALSE | 0 | 66.094 | FALSE | FALSE | 0.0945 |  | 69.4399 | 0 | 0 | 0.16947 | 0.53729 | -0.31541 | 1.6729 | Normal | 72.7858 | 1.4182 | Day | 202601 | 2026-01-29 | 1.4182
2026-01-29 13:42 | 72.095 | FALSE | FALSE | -5.9814 | -9.0472 | -1.0384 | -1.4199 | 0.2826 |  |  | none | FALSE | 0 | 66.1136 | FALSE | FALSE | 0.0939 |  | 69.6235 | 0 | 0.2826 | 0.1836 | 0.53632 | 0.18459 | 1.755 | Normal | 73.1334 | 1.4083 | Day | 202601 | 2026-01-29 | 1.4083
2026-01-29 13:57 | 72.3758 | FALSE | FALSE | -6.1823 | -9.3397 | -1.1012 | -1.4987 | 0.2808 |  |  | none | FALSE | 0 | 66.1935 | FALSE | FALSE | 0.093 |  | 69.8353 | 0 | 0.2808 | 0.21177 | 0.52522 | 0.13143 | 1.8209 | Normal | 73.477 | 1.3952 | Day | 202601 | 2026-01-29 | 1.3952
2026-01-29 14:12 | 72.095 | FALSE | FALSE | -5.7455 | -8.6594 | -1.6215 | -2.1996 | -0.2808 |  |  | none | FALSE | 0 | 66.3495 | FALSE | FALSE | 0.0746 |  | 70.033 | 0 | -0.2808 | 0.19773 | 0.53485 | -0.8947 | 1.8417 | Normal | 73.7165 | 1.1196 | Day | 202601 | 2026-01-29 | 1.1196
2026-01-29 14:27 | 72.3758 | FALSE | FALSE | -5.4589 | -8.1577 | -1.3662 | -1.8527 | 0.2808 |  |  | none | FALSE | 0 | 66.9169 | FALSE | FALSE | 0.08 |  | 70.3295 | 0 | 0.2808 | 0.29646 | 0.2964 | -0.052834 | 1.7063 | Normal | 73.742 | 1.1993 | Day | 202601 | 2026-01-29 | 1.1993
2026-01-29 14:42 | 72.3758 | FALSE | FALSE | -4.747 | -7.0193 | -1.2473 | -1.6942 | 0 |  |  | none | FALSE | 0 | 67.6288 | FALSE | FALSE | 0.0778 |  | 70.6259 | 0 | 0 | 0.29646 | 0.2964 | -1.0002 | 1.4986 | Normal | 73.6231 | 1.1677 | Day | 202601 | 2026-01-29 | 1.1677
2026-01-29 14:57 | 72.6584 | FALSE | FALSE | -4.5395 | -6.6641 | -0.98273 | -1.3345 | 0.2826 |  |  | none | FALSE | 0 | 68.1189 | FALSE | FALSE | 0.0859 |  | 70.88 | 0 | 0.2826 | 0.25407 | 0.22219 | 0.1284 | 1.3806 | Normal | 73.6411 | 1.2882 | Day | 202601 | 2026-01-29 | 1.2882
2026-01-29 15:12 | 72.941 | FALSE | FALSE | -4.4085 | -6.4327 | -0.76658 | -1.04 | 0.2826 |  |  | none | FALSE | 0 | 68.5325 | FALSE | FALSE | 0.0938 |  | 71.12 | 0 | 0.2826 | 0.24003 | 0.21016 | 0.20256 | 1.2938 | Normal | 73.7076 | 1.4075 | Day | 202601 | 2026-01-29 | 1.4075
2026-01-29 15:27 | 73.2236 | FALSE | FALSE | -4.3646 | -6.3385 | -0.60927 | -0.82521 | 0.2826 |  |  | none | FALSE | 0 | 68.859 | FALSE | FALSE | 0.1007 |  | 71.3459 | 0 | 0.2826 | 0.2259 | 0.19619 | 0.28901 | 1.2435 | Normal | 73.8329 | 1.51 | Day | 202601 | 2026-01-29 | 1.51
2026-01-29 15:41 | 73.2236 | FALSE | FALSE | -4.0256 | -5.8175 | -0.69376 | -0.93856 | 0 |  |  | none | FALSE | 0 | 69.198 | FALSE | FALSE | 0.0941 |  | 71.5577 | 0 | 0 | 0.21177 | 0.20198 | -1.0485 | 1.1798 | Normal | 73.9174 | 1.412 | Day | 202601 | 2026-01-29 | 1.412
2026-01-29 15:56 | 73.2236 | FALSE | FALSE | -3.6789 | -5.2899 | -0.74234 | -1.0036 | 0 |  |  | none | FALSE | 0 | 69.5447 | FALSE | FALSE | 0.0886 |  | 71.7553 | 0 | 0 | 0.19764 | 0.2066 | -0.95665 | 1.1053 | Normal | 73.9659 | 1.3284 | Day | 202601 | 2026-01-29 | 1.3284
2026-01-29 16:12 | 73.5062 | FALSE | FALSE | -3.7156 | -5.3239 | -0.58086 | -0.78402 | 0.2826 |  |  | none | FALSE | 0 | 69.7906 | FALSE | FALSE | 0.0973 |  | 71.9389 | 0 | 0.2826 | 0.18351 | 0.18905 | 0.52414 | 1.0741 | Normal | 74.0871 | 1.4592 | Day | 202601 | 2026-01-29 | 1.4592
2026-01-29 16:27 | 73.5062 | FALSE | FALSE | -3.3986 | -4.8477 | -0.63091 | -0.85101 | 0 |  |  | none | FALSE | 0 | 70.1076 | FALSE | FALSE | 0.0916 |  | 72.1224 | 0 | 0 | 0.18351 | 0.18905 | -0.97068 | 1.0074 | Normal | 74.1371 | 1.3737 | Day | 202601 | 2026-01-29 | 1.3737
2026-01-29 16:41 | 73.5062 | FALSE | FALSE | -3.1613 | -4.494 | -0.70433 | -0.94909 | 0 |  |  | none | FALSE | 0 | 70.3449 | FALSE | FALSE | 0.0847 |  | 72.2777 | 0 | 0 | 0.15534 | 0.17054 | -0.9109 | 0.96641 | Normal | 74.2105 | 1.2712 | Day | 202601 | 2026-01-29 | 1.2712
2026-01-29 16:56 | 73.5062 | FALSE | FALSE | -2.8646 | -4.0551 | -0.71827 | -0.96769 | 0 |  |  | none | FALSE | 0 | 70.6416 | FALSE | FALSE | 0.0799 |  | 72.433 | 0 | 0 | 0.15534 | 0.17054 | -0.9109 | 0.89571 | Normal | 74.2245 | 1.1981 | Day | 202601 | 2026-01-29 | 1.1981
2026-01-29 17:11 | 73.5062 | FALSE | FALSE | -2.5819 | -3.6403 | -0.71796 | -0.96729 | 0 |  |  | none | FALSE | 0 | 70.9243 | FALSE | FALSE | 0.0753 |  | 72.5743 | 0 | 0 | 0.14121 | 0.17114 | -0.8251 | 0.82495 | Normal | 74.2242 | 1.1297 | Day | 202601 | 2026-01-29 | 1.1297
2026-01-29 17:26 | 73.5062 | FALSE | FALSE | -2.3187 | -3.2571 | -0.70893 | -0.95523 | 0 |  |  | none | FALSE | 0 | 71.1875 | FALSE | FALSE | 0.0709 |  | 72.7013 | 0 | 0 | 0.12708 | 0.17052 | -0.74525 | 0.7569 | Normal | 74.2151 | 1.0634 | Day | 202601 | 2026-01-29 | 1.0634
2026-01-29 17:41 | 73.5062 | FALSE | FALSE | -2.0808 | -2.9133 | -0.697 | -0.93931 | 0 |  |  | none | FALSE | 0 | 71.4254 | FALSE | FALSE | 0.0664 |  | 72.8143 | 0 | 0 | 0.11295 | 0.16865 | -0.66972 | 0.69446 | Normal | 74.2032 | 0.99634 | Day | 202601 | 2026-01-29 | 0.99634
2026-01-29 17:56 | 73.5062 | FALSE | FALSE | -1.8743 | -2.6165 | -0.68808 | -0.9274 | 0 |  |  | none | FALSE | 0 | 71.6319 | FALSE | FALSE | 0.0617 |  | 72.9131 | 0 | 0 | 0.09882 | 0.1655 | -0.5971 | 0.64059 | Normal | 74.1943 | 0.92587 | Day | 202601 | 2026-01-29 | 0.92587
2026-01-29 18:11 | 73.5062 | FALSE | FALSE | -1.7043 | -2.3737 | -0.68751 | -0.92664 | 0 |  |  | none | FALSE | 0 | 71.8019 | FALSE | FALSE | 0.0567 |  | 72.9978 | 0 | 0 | 0.08469 | 0.16099 | -0.52607 | 0.59796 | Normal | 74.1937 | 0.85024 | Night | 202601 | 2026-01-29 | 0.85024
2026-01-29 18:26 | 73.5062 | FALSE | FALSE | -1.5001 | -2.0833 | -0.65267 | -0.8801 | 0 |  |  | none | FALSE | 0 | 72.0061 | FALSE | FALSE | 0.0525 |  | 73.0825 | 0 | 0 | 0.08469 | 0.16099 | -0.52607 | 0.53819 | Normal | 74.1589 | 0.7873 | Night | 202601 | 2026-01-29 | 0.7873
2026-01-29 18:30 | 73.5062 | FALSE | FALSE | -1.3381 | -1.8542 | -0.63181 | -0.8522 | 0 |  |  | none | FALSE | 0 | 72.1681 | FALSE | FALSE | 0.0478 |  | 73.153 | 0 | 0 | 0.07056 | 0.15499 | -0.45525 | 0.49248 | Normal | 74.138 | 0.7171 | Night | 202601 | 2026-01-29 | 0.7171
2026-01-29 18:31 | 73.5062 | FALSE | FALSE | -1.2217 | -1.6902 | -0.62845 | -0.84771 | 0 |  |  | none | FALSE | 0 | 72.2845 | FALSE | FALSE | 0.0428 |  | 73.2096 | 0 | 0 | 0.05652 | 0.14748 | -0.38324 | 0.46254 | Normal | 74.1346 | 0.64132 | Night | 202601 | 2026-01-29 | 0.64132
2026-01-29 18:46 | 73.5062 | FALSE | FALSE | -0.99538 | -1.3727 | -0.54322 | -0.73359 | 0 |  |  | none | FALSE | 0 | 72.5108 | FALSE | FALSE | 0.0392 |  | 73.2801 | 0 | 0 | 0.07056 | 0.12539 | -0.56273 | 0.38465 | Normal | 74.0494 | 0.58775 | Night | 202601 | 2026-01-29 | 0.58775
2026-01-29 19:01 | 73.2236 | TRUE | FALSE | -0.54356 | -0.74788 | -0.74138 | -1.0023 | -0.2826 |  |  | none | FALSE | 1 | 72.68 | FALSE | FALSE | 0.0491 |  | 73.3225 | 0 | -0.2826 | 0.04239 | 0.13829 | -2.35 | 0.32123 | Normal | 73.965 | -0.30791 | Night | 202601 | 2026-01-29 | 0.30791
2026-01-29 19:16 | 73.2236 | FALSE | FALSE | -0.32622 | -0.4475 | -0.60882 | -0.82459 | 0 |  |  | none | FALSE | 1 | 72.8974 | FALSE | FALSE | 0.0689 |  | 73.3649 | 0 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.23376 | Normal | 73.8324 | -0.60447 | Night | 202601 | 2026-01-29 | 0.60447
2026-01-29 19:30 | 72.941 | TRUE | FALSE | 0.050115 | 0.068659 | -0.82595 | -1.1197 | -0.2826 | 2026-01-30 03:57 | 2026-01-29 19:30 | lower | TRUE | 2 | 72.9911 | TRUE | FALSE | 0.2648 | 2.2584 | 73.379 | 1 | -0.2826 | 0.01413 | 0.14424 | -2.0571 | 0.19396 | Extreme triggered | 73.7669 | -2.2584 | Night | 202601 | 2026-01-29 | 2.2584
2026-01-29 19:45 | 72.941 | FALSE | FALSE | 0.050115 | 0.068659 | -0.82595 | -1.1197 | 0 |  | 2026-01-29 19:30 | lower | TRUE | 2 | 72.9911 | FALSE | FALSE | 0.322 | 2.2584 | 73.379 | 2 | 0 | 0 | 0.12967 | 0 | 0.19396 | Extreme/elevated | 73.7669 | -2.2584 | Night | 202601 | 2026-01-29 | 2.2584
2026-01-29 20:00 | 72.6584 | TRUE | FALSE | 0.19101 | 0.2622 | -1.1937 | -1.6164 | -0.2826 |  | 2026-01-29 19:30 | lower | TRUE | 3 | 72.8494 | TRUE | TRUE | 0.4413 | 2.4263 | 73.3508 | 3 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.25068 | Persistent | 73.8521 | -2.762 | Night | 202601 | 2026-01-29 | 2.762
2026-01-29 20:15 | 72.3758 | FALSE | FALSE | 0.26887 | 0.37012 | -1.5963 | -2.158 | -0.2826 |  | 2026-01-29 19:30 | lower | TRUE | 3 | 72.6447 | FALSE | TRUE | 0.5016 | 2.5222 | 73.3084 | 4 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.33185 | Persistent | 73.9721 | -2.8102 | Night | 202601 | 2026-01-29 | 2.8102
2026-01-29 20:29 | 72.095 | FALSE | FALSE | 0.29931 | 0.41345 | -2.0146 | -2.7184 | -0.2808 |  | 2026-01-29 19:30 | lower | TRUE | 3 | 72.3943 | FALSE | TRUE | 0.5513 | 2.5574 | 73.2519 | 5 | -0.2808 | -0.05643 | 0.1477 | -1.5191 | 0.42882 | Persistent | 74.1096 | -2.698 | Night | 202601 | 2026-01-29 | 2.698
2026-01-29 20:44 | 72.095 | FALSE | FALSE | 0.095045 | 0.13166 | -2.0777 | -2.8012 | 0 |  | 2026-01-29 19:30 | lower | TRUE | 3 | 72.19 | FALSE | TRUE | 0.5747 | 2.4965 | 73.1814 | 6 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.49567 | Persistent | 74.1727 | -2.1917 | Night | 202601 | 2026-01-29 | 2.1917
2026-01-29 20:59 | 72.095 | FALSE | TRUE | -0.074154 | -0.10296 | -2.1058 | -2.838 | 0 |  | 2026-01-29 19:30 | none | FALSE | 3 | 72.0208 | FALSE | FALSE | 0.61 | 2.4061 | 73.1108 | 7 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.54499 | Confirmed/Materialized Shift | 74.2008 | -1.8639 | Night | 202601 | 2026-01-29 | 1.8639
2026-01-29 21:14 | 71.8124 | FALSE | TRUE | -0.0027657 | -0.0038515 | -2.4302 | -3.2734 | -0.2826 |  | 2026-01-29 19:30 | none | FALSE | 3 | 71.8096 | FALSE | FALSE | 0.6187 | 2.3548 | 73.0261 | 8 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.60825 | Confirmed/Materialized Shift | 74.2426 | -1.9955 | Night | 202601 | 2026-01-29 | 1.9955
2026-01-29 21:29 | 71.8124 | FALSE | TRUE | -0.17912 | -0.25005 | -2.4372 | -3.2825 | 0 |  | 2026-01-29 19:30 | none | FALSE | 2 | 71.6333 | FALSE | FALSE | 0.5722 | 2.2849 | 72.9415 | 9 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.65409 | Confirmed/Materialized Shift | 74.2496 | -1.7262 | Night | 202601 | 2026-01-29 | 1.7262
2026-01-29 21:44 | 71.8124 | FALSE | TRUE | -0.32762 | -0.45831 | -2.4163 | -3.2553 | 0 |  | 2026-01-29 19:30 | none | FALSE | 2 | 71.4848 | FALSE | FALSE | 0.5586 | 2.2087 | 72.8568 | 10 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.68599 | Confirmed/Materialized Shift | 74.2287 | -1.5224 | Night | 202601 | 2026-01-29 | 1.5224
2026-01-29 21:59 | 71.5298 | FALSE | TRUE | -0.22895 | -0.32111 | -2.6852 | -3.6182 | -0.2826 |  | 2026-01-29 19:30 | none | FALSE | 1 | 71.3008 | FALSE | FALSE | 0.541 | 2.1611 | 72.7579 | 11 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.72855 | Confirmed/Materialized Shift | 74.215 | -1.6857 | Night | 202601 | 2026-01-29 | 1.6857
2026-01-29 22:14 | 71.5298 | FALSE | TRUE | -0.3812 | -0.53578 | -2.6398 | -3.5592 | 0 |  | 2026-01-29 19:30 | none | FALSE | 1 | 71.1486 | FALSE | FALSE | 0.5283 | 2.1056 | 72.6591 | 12 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.75526 | Confirmed/Materialized Shift | 74.1696 | -1.4953 | Night | 202601 | 2026-01-29 | 1.4953
2026-01-29 22:29 | 71.2472 | FALSE | TRUE | -0.28109 | -0.39609 | -2.879 | -3.884 | -0.2826 |  | 2026-01-29 19:30 | none | FALSE | 0 | 70.9661 | FALSE | FALSE | 0.5096 | 2.0701 | 72.5462 | 13 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.79003 | Confirmed/Materialized Shift | 74.1262 | -1.6442 | Night | 202601 | 2026-01-29 | 1.6442
2026-01-29 22:44 | 71.2472 | FALSE | TRUE | -0.42769 | -0.60392 | -2.7997 | -3.781 | 0 |  | 2026-01-29 19:30 | none | FALSE | 0 | 70.8195 | FALSE | FALSE | 0.498 | 2.0273 | 72.4332 | 14 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.80685 | Confirmed/Materialized Shift | 74.0469 | -1.4699 | Night | 202601 | 2026-01-29 | 1.4699
2026-01-29 22:59 | 70.9646 | FALSE | TRUE | -0.3161 | -0.44742 | -2.9992 | -4.0549 | -0.2826 |  | 2026-01-29 19:30 | none | FALSE | 0 | 70.6485 | FALSE | FALSE | 0.5079 | 2 | 72.3061 | 15 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.82882 | Confirmed/Materialized Shift | 73.9638 | -1.6186 | Night | 202601 | 2026-01-29 | 1.6186
2026-01-29 23:14 | 70.9646 | FALSE | TRUE | -0.4455 | -0.63174 | -2.8744 | -3.8928 | 0 |  | 2026-01-29 19:30 | none | FALSE | 0 | 70.5191 | FALSE | FALSE | 0.4975 | 1.9665 | 72.1791 | 16 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.82998 | Confirmed/Materialized Shift | 73.839 | -1.4632 | Night | 202601 | 2026-01-29 | 1.4632
2026-01-29 23:28 | 70.682 | FALSE | TRUE | -0.30924 | -0.43944 | -3.0209 | -4.0988 | -0.2826 |  | 2026-01-29 19:30 | none | FALSE | 0 | 70.3728 | FALSE | FALSE | 0.5086 | 1.9466 | 72.0379 | 17 | -0.2826 | -0.14121 | 0.14488 | -0.97592 | 0.83255 | Confirmed/Materialized Shift | 73.7029 | -1.6286 | Night | 202601 | 2026-01-29 | 1.6286
2026-01-29 23:43 | 70.682 | FALSE | TRUE | -0.40452 | -0.57561 | -2.8338 | -3.8547 | 0 |  | 2026-01-29 19:30 | none | FALSE | 0 | 70.2775 | FALSE | FALSE | 0.5 | 1.9218 | 71.8966 | 18 | 0 | -0.14121 | 0.14488 | 0.97468 | 0.80958 | Confirmed/Materialized Shift | 73.5158 | -1.5003 | Night | 202601 | 2026-01-29 | 1.5003
2026-01-29 23:58 | 70.682 | FALSE | TRUE | -0.49155 | -0.70031 | -2.6667 | -3.6356 | 0 |  | 2026-01-29 19:30 | none | FALSE | 0 | 70.1904 | FALSE | FALSE | 0.4918 | 1.8932 | 71.7696 | 19 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.78956 | Confirmed/Materialized Shift | 73.3487 | -1.3774 | Night | 202601 | 2026-01-29 | 1.3774
2026-01-30 00:14 | 70.682 | FALSE | TRUE | -0.53267 | -0.75934 | -2.4536 | -3.3549 | 0 |  | 2026-01-29 19:30 | none | FALSE | 0 | 70.1493 | FALSE | FALSE | 0.4858 | 1.8628 | 71.6425 | 20 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.74658 | Confirmed/Materialized Shift | 73.1356 | -1.2865 | Night | 202601 | 2026-01-30 | 1.2865
2026-01-30 00:28 | 70.3994 | FALSE | TRUE | -0.34408 | -0.49116 | -2.5761 | -3.5301 | -0.2826 |  | 2026-01-29 19:30 | none | FALSE | 0 | 70.0553 | FALSE | FALSE | 0.5019 | 1.8469 | 71.5154 | 21 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.73004 | Confirmed/Materialized Shift | 72.9755 | -1.5287 | Night | 202601 | 2026-01-30 | 1.5287
2026-01-30 00:43 | 70.3994 | FALSE | TRUE | -0.38882 | -0.55538 | -2.3667 | -3.2524 | 0 |  | 2026-01-29 19:30 | none | FALSE | 0 | 70.0106 | FALSE | FALSE | 0.4957 | 1.8282 | 71.3883 | 22 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.68887 | Confirmed/Materialized Shift | 72.7661 | -1.4356 | Night | 202601 | 2026-01-30 | 1.4356
2026-01-30 00:58 | 70.3994 | FALSE | TRUE | -0.43199 | -0.61741 | -2.1839 | -3.0089 | 0 |  | 2026-01-29 19:30 | none | FALSE | 0 | 69.9674 | FALSE | FALSE | 0.4893 | 1.807 | 71.2754 | 23 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.65398 | Confirmed/Materialized Shift | 72.5833 | -1.3394 | Night | 202601 | 2026-01-30 | 1.3394
2026-01-30 01:13 | 70.3994 | FALSE | TRUE | -0.47833 | -0.6841 | -2.0326 | -2.8063 | 0 |  | 2026-01-29 19:30 | none | FALSE | 0 | 69.9211 | FALSE | FALSE | 0.4825 | 1.7833 | 71.1766 | 24 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.62774 | Confirmed/Materialized Shift | 72.432 | -1.238 | Night | 202601 | 2026-01-30 | 1.238
2026-01-30 01:28 | 70.1168 | FALSE | TRUE | -0.30165 | -0.43208 | -2.2233 | -3.0734 | -0.2826 |  | 2026-01-29 19:30 | none | FALSE | 0 | 69.8151 | FALSE | FALSE | 0.5015 | 1.7728 | 71.0776 | 25 | -0.2826 | -0.09891 | 0.13829 | -1.3283 | 0.63125 | Confirmed/Materialized Shift | 72.3401 | -1.5221 | Night | 202601 | 2026-01-30 | 1.5221
2026-01-30 01:43 | 70.1168 | FALSE | TRUE | -0.37466 | -0.53721 | -2.0985 | -2.9059 | 0 |  | 2026-01-29 19:30 | none | FALSE | 0 | 69.7421 | FALSE | FALSE | 0.4929 | 1.7582 | 70.9787 | 26 | 0 | -0.09891 | 0.13829 | 0.71522 | 0.6183 | Confirmed/Materialized Shift | 72.2153 | -1.394 | Night | 202601 | 2026-01-30 | 1.394
2026-01-30 01:58 | 70.1168 | FALSE | TRUE | -0.41258 | -0.59191 | -1.9386 | -2.6905 | 0 |  | 2026-01-29 19:30 | none | FALSE | 0 | 69.7042 | FALSE | FALSE | 0.4865 | 1.7412 | 70.8798 | 27 | 0 | -0.09891 | 0.13829 | 0.71522 | 0.5878 | Confirmed/Materialized Shift | 72.0554 | -1.2981 | Night | 202601 | 2026-01-30 | 1.2981
2026-01-30 02:13 | 70.1168 | FALSE | TRUE | -0.45809 | -0.65763 | -1.8146 | -2.5226 | 0 |  | 2026-01-29 19:30 | none | FALSE | 0 | 69.6587 | FALSE | FALSE | 0.4796 | 1.7217 | 70.795 | 28 | 0 | -0.08478 | 0.13287 | 0.63808 | 0.56817 | Confirmed/Materialized Shift | 71.9314 | -1.1937 | Night | 202601 | 2026-01-30 | 1.1937
2026-01-30 02:27 | 69.836 | FALSE | TRUE | -0.24697 | -0.3549 | -1.9674 | -2.74 | -0.2808 |  | 2026-01-29 19:30 | none | FALSE | 0 | 69.589 | FALSE | FALSE | 0.5036 | 1.7159 | 70.6962 | 29 | -0.2808 | -0.09882 | 0.13817 | -1.3171 | 0.5536 | Confirmed/Materialized Shift | 71.8034 | -1.5539 | Night | 202601 | 2026-01-30 | 1.5539
2026-01-30 02:43 | 69.836 | FALSE | TRUE | -0.27699 | -0.39821 | -1.7998 | -2.5124 | 0 |  | 2026-01-29 19:30 | none | FALSE | 0 | 69.559 | FALSE | FALSE | 0.4978 | 1.7076 | 70.5974 | 30 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.51919 | Confirmed/Materialized Shift | 71.6358 | -1.4665 | Night | 202601 | 2026-01-30 | 1.4665
2026-01-30 02:58 | 69.836 | FALSE | TRUE | -0.31681 | -0.45571 | -1.6702 | -2.3358 | 0 |  | 2026-01-29 19:30 | none | FALSE | 0 | 69.5192 | FALSE | FALSE | 0.4908 | 1.6964 | 70.5127 | 31 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.49676 | Confirmed/Materialized Shift | 71.5062 | -1.3623 | Night | 202601 | 2026-01-30 | 1.3623
2026-01-30 03:13 | 69.836 | FALSE | TRUE | -0.32204 | -0.46327 | -1.5061 | -2.1111 | 0 |  | 2026-01-29 19:30 | none | FALSE | 0 | 69.514 | FALSE | FALSE | 0.4864 | 1.6839 | 70.428 | 32 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.45703 | Confirmed/Materialized Shift | 71.3421 | -1.2954 | Night | 202601 | 2026-01-30 | 1.2954
2026-01-30 03:27 | 69.836 | FALSE | TRUE | -0.34286 | -0.49337 | -1.3858 | -1.9457 | 0 |  | 2026-01-29 19:30 | none | FALSE | 0 | 69.4931 | FALSE | FALSE | 0.4804 | 1.6694 | 70.3575 | 33 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.43216 | Confirmed/Materialized Shift | 71.2218 | -1.2066 | Night | 202601 | 2026-01-30 | 1.2066
2026-01-30 03:42 | 69.5534 | FALSE | TRUE | -0.10906 | -0.15705 | -1.5478 | -2.1769 | -0.2826 |  | 2026-01-29 19:30 | none | FALSE | 0 | 69.4443 | FALSE | FALSE | 0.5158 | 1.6714 | 70.2728 | 34 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.41422 | Confirmed/Materialized Shift | 71.1012 | -1.7367 | Night | 202601 | 2026-01-30 | 1.7367
2026-01-30 03:57 | 69.836 | TRUE | FALSE | -0.40215 | -0.57918 | -1.1628 | -1.6378 | 0.2826 |  |  | none | FALSE | 1 | 69.4339 | FALSE | FALSE | 0.0934 |  | 70.2163 | 0 | 0.2826 | -0.05643 | 0.1477 | 2.2954 | 0.39124 | Persistence ends | 70.9988 | -0.97213 | Night | 202601 | 2026-01-30 | 0.97213
2026-01-30 04:12 | 69.5534 | FALSE | FALSE | -0.15993 | -0.23047 | -1.3447 | -1.8967 | -0.2826 |  |  | none | FALSE | 1 | 69.3935 | FALSE | FALSE | 0.1336 |  | 70.1458 | 0 | -0.2826 | -0.07056 | 0.15534 | -1.365 | 0.37616 | Normal | 70.8981 | -1.5748 | Night | 202601 | 2026-01-30 | 1.5748
2026-01-30 04:27 | 69.5534 | FALSE | FALSE | -0.21632 | -0.31199 | -1.2882 | -1.8185 | 0 |  |  | none | FALSE | 1 | 69.3371 | FALSE | FALSE | 0.1236 |  | 70.0893 | 0 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.37614 | Normal | 70.8416 | -1.4249 | Night | 202601 | 2026-01-30 | 1.4249
2026-01-30 04:42 | 69.5534 | FALSE | FALSE | -0.25467 | -0.36749 | -1.2137 | -1.7151 | 0 |  |  | none | FALSE | 1 | 69.2987 | FALSE | FALSE | 0.1157 |  | 70.0329 | 0 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.36709 | Normal | 70.7671 | -1.3063 | Night | 202601 | 2026-01-30 | 1.3063
2026-01-30 04:57 | 69.5534 | FALSE | FALSE | -0.27357 | -0.39488 | -1.1198 | -1.5844 | 0 |  |  | none | FALSE | 1 | 69.2798 | FALSE | FALSE | 0.1095 |  | 69.9765 | 0 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.34833 | Normal | 70.6732 | -1.2146 | Night | 202601 | 2026-01-30 | 1.2146
2026-01-30 05:12 | 69.5534 | FALSE | FALSE | -0.2696 | -0.38912 | -1.0029 | -1.4214 | 0 |  |  | none | FALSE | 1 | 69.2838 | FALSE | FALSE | 0.1054 |  | 69.9201 | 0 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.31813 | Normal | 70.5563 | -1.1525 | Night | 202601 | 2026-01-30 | 1.1525
2026-01-30 05:27 | 69.5534 | FALSE | FALSE | -0.28983 | -0.41844 | -0.93855 | -1.3314 | 0 |  |  | none | FALSE | 1 | 69.2636 | FALSE | FALSE | 0.099 |  | 69.8778 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.30709 | Normal | 70.4919 | -1.0562 | Night | 202601 | 2026-01-30 | 1.0562
2026-01-30 05:42 | 69.5534 | FALSE | FALSE | -0.29635 | -0.42789 | -0.86047 | -1.222 | 0 |  |  | none | FALSE | 1 | 69.2571 | FALSE | FALSE | 0.0936 |  | 69.8355 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.2892 | Normal | 70.4139 | -0.9753 | Night | 202601 | 2026-01-30 | 0.9753
2026-01-30 05:57 | 69.2708 | FALSE | FALSE | -0.058618 | -0.084694 | -1.0751 | -1.5283 | -0.2826 |  |  | none | FALSE | 1 | 69.2122 | FALSE | FALSE | 0.1481 |  | 69.779 | 0 | -0.2826 | -0.05643 | 0.1477 | -1.5313 | 0.28342 | Normal | 70.3459 | -1.7932 | Night | 202601 | 2026-01-30 | 1.7932
2026-01-30 06:12 | 69.2708 | FALSE | FALSE | -0.078544 | -0.11352 | -0.98214 | -1.398 | 0 |  |  | none | FALSE | 1 | 69.1923 | FALSE | FALSE | 0.1422 |  | 69.7226 | 0 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.26517 | Normal | 70.2529 | -1.7038 | Night | 202601 | 2026-01-30 | 1.7038
2026-01-30 06:26 | 69.2708 | FALSE | FALSE | -0.12341 | -0.17847 | -0.94241 | -1.3422 | 0 |  |  | none | FALSE | 0 | 69.1474 | FALSE | FALSE | 0.1025 |  | 69.6803 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.26645 | Normal | 70.2132 | -1.5369 | Night | 202601 | 2026-01-30 | 1.5369
2026-01-30 06:41 | 69.2708 | FALSE | FALSE | -0.154 | -0.22281 | -0.8884 | -1.2663 | 0 |  |  | none | FALSE | 0 | 69.1168 | FALSE | FALSE | 0.0939 |  | 69.638 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.2606 | Normal | 70.1592 | -1.4091 | Night | 202601 | 2026-01-30 | 1.4091
2026-01-30 06:56 | 69.2708 | FALSE | FALSE | -0.1693 | -0.24501 | -0.8191 | -1.1686 | 0 |  |  | none | FALSE | 0 | 69.1015 | FALSE | FALSE | 0.0877 |  | 69.5957 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.2471 | Normal | 70.0899 | -1.3148 | Night | 202601 | 2026-01-30 | 1.3148
2026-01-30 07:11 | 69.2708 | FALSE | FALSE | -0.16658 | -0.24105 | -0.73178 | -1.0454 | 0 |  |  | none | FALSE | 0 | 69.1042 | FALSE | FALSE | 0.0839 |  | 69.5534 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.22459 | Normal | 70.0026 | -1.2583 | Day | 202601 | 2026-01-30 | 1.2583
2026-01-30 07:26 | 69.2708 | FALSE | FALSE | -0.19108 | -0.2766 | -0.69976 | -1.0001 | 0 |  |  | none | FALSE | 0 | 69.0797 | FALSE | FALSE | 0.0761 |  | 69.5251 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.22271 | Normal | 69.9706 | -1.142 | Day | 202601 | 2026-01-30 | 1.142
2026-01-30 07:30 | 69.2708 | FALSE | FALSE | -0.20786 | -0.30098 | -0.66002 | -0.94383 | 0 |  |  | none | FALSE | 0 | 69.0629 | FALSE | FALSE | 0.0695 |  | 69.4969 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21697 | Normal | 69.9308 | -1.042 | Day | 202601 | 2026-01-30 | 1.042
2026-01-30 07:45 | 69.2708 | FALSE | FALSE | -0.2163 | -0.31323 | -0.61194 | -0.87567 | 0 |  |  | none | FALSE | 0 | 69.0545 | FALSE | FALSE | 0.0637 |  | 69.4686 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.20706 | Normal | 69.8827 | -0.95538 | Day | 202601 | 2026-01-30 | 0.95538
2026-01-30 08:00 | 69.2708 | FALSE | FALSE | -0.21509 | -0.31147 | -0.55421 | -0.79371 | 0 |  |  | none | FALSE | 0 | 69.0557 | FALSE | FALSE | 0.0588 |  | 69.4404 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.19233 | Normal | 69.825 | -0.88163 | Day | 202601 | 2026-01-30 | 0.88163
2026-01-30 08:15 | 69.2708 | FALSE | FALSE | -0.20176 | -0.29212 | -0.48436 | -0.69438 | 0 |  |  | none | FALSE | 0 | 69.069 | FALSE | FALSE | 0.0549 |  | 69.4121 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.17153 | Normal | 69.7552 | -0.82375 | Day | 202601 | 2026-01-30 | 0.82375
2026-01-30 08:30 | 69.2708 | FALSE | FALSE | -0.21467 | -0.31086 | -0.46901 | -0.67251 | 0 |  |  | none | FALSE | 0 | 69.0561 | FALSE | FALSE | 0.0496 |  | 69.398 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.17092 | Normal | 69.7398 | -0.74404 | Day | 202601 | 2026-01-30 | 0.74404
2026-01-30 08:30 | 69.2708 | FALSE | FALSE | -0.17768 | -0.25716 | -0.3755 | -0.53915 | 0 |  |  | none | FALSE | 0 | 69.0931 | FALSE | FALSE | 0.0477 |  | 69.3697 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.13829 | Normal | 69.6463 | -0.71522 | Day | 202601 | 2026-01-30 | 0.71522
2026-01-30 08:45 | 69.5534 | TRUE | FALSE | -0.46028 | -0.66617 | -0.092897 | -0.13338 | 0.2826 |  |  | none | FALSE | 1 | 69.0931 | FALSE | FALSE | 0.1171 |  | 69.3697 | 0 | 0.2826 | 0 | 0.091688 | 3.0822 | 0.13829 | Normal | 69.6463 | 1.3283 | Day | 202601 | 2026-01-30 | 1.3283
2026-01-30 09:00 | 69.5534 | FALSE | FALSE | -0.46028 | -0.66617 | -0.092897 | -0.13338 | 0 |  |  | none | FALSE | 1 | 69.0931 | FALSE | FALSE | 0.1171 |  | 69.3697 | 0 | 0 | 0 | 0.091688 | 0 | 0.13829 | Normal | 69.6463 | 1.3283 | Day | 202601 | 2026-01-30 | 1.3283
2026-01-30 09:15 | 69.5534 | FALSE | FALSE | -0.46028 | -0.66617 | -0.092897 | -0.13338 | 0 |  |  | none | FALSE | 1 | 69.0931 | FALSE | FALSE | 0.1171 |  | 69.3697 | 0 | 0 | 0 | 0.091688 | 0 | 0.13829 | Normal | 69.6463 | 1.3283 | Day | 202601 | 2026-01-30 | 1.3283
2026-01-30 09:30 | 69.836 | TRUE | FALSE | -0.79029 | -1.1446 | 0.11403 | 0.16355 | 0.2826 | 2026-01-30 17:57 | 2026-01-30 09:30 | upper | TRUE | 2 | 69.0457 | TRUE | FALSE | 0.2926 | 2.6745 | 69.3838 | 1 | 0.2826 | 0.01413 | 0.11135 | 2.411 | 0.16906 | Extreme triggered | 69.722 | 2.6745 | Day | 202601 | 2026-01-30 | 2.6745
2026-01-30 09:45 | 69.836 | FALSE | FALSE | -0.82595 | -1.1968 | 0.050115 | 0.071812 | 0 |  | 2026-01-30 09:30 | upper | TRUE | 2 | 69.0101 | FALSE | FALSE | 0.322 | 2.4664 | 69.398 | 2 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.19396 | Extreme/elevated | 69.7859 | 2.2584 | Day | 202601 | 2026-01-30 | 2.2584
2026-01-30 10:00 | 70.1168 | TRUE | FALSE | -1.1915 | -1.7287 | 0.18983 | 0.27147 | 0.2808 |  | 2026-01-30 09:30 | upper | TRUE | 3 | 68.9253 | TRUE | TRUE | 0.441 | 2.5636 | 69.4261 | 3 | 0.2808 | 0.02817 | 0.12619 | 2.0019 | 0.25042 | Persistent | 69.927 | 2.758 | Day | 202601 | 2026-01-30 | 2.758
2026-01-30 10:15 | 70.3994 | FALSE | FALSE | -1.5938 | -2.3163 | 0.26816 | 0.38236 | 0.2826 |  | 2026-01-30 09:30 | upper | TRUE | 3 | 68.8056 | FALSE | TRUE | 0.5016 | 2.625 | 69.4684 | 4 | 0.2826 | 0.0423 | 0.13813 | 1.7397 | 0.3314 | Persistent | 70.1312 | 2.8092 | Day | 202601 | 2026-01-30 | 2.8092
2026-01-30 10:29 | 70.3994 | FALSE | FALSE | -1.6492 | -2.3989 | 0.099845 | 0.14203 | 0 |  | 2026-01-30 09:30 | upper | TRUE | 3 | 68.7502 | FALSE | TRUE | 0.5219 | 2.5516 | 69.5249 | 5 | 0 | 0.05643 | 0.11579 | -0.48734 | 0.38734 | Persistent | 70.2996 | 2.2578 | Day | 202601 | 2026-01-30 | 2.2578
2026-01-30 10:44 | 70.3994 | FALSE | FALSE | -1.6749 | -2.4372 | -0.038726 | -0.054979 | 0 |  | 2026-01-30 09:30 | none | FALSE | 3 | 68.7245 | FALSE | FALSE | 0.5559 | 2.4446 | 69.5813 | 6 | 0 | 0.05643 | 0.11579 | -0.48734 | 0.42841 | Persistent | 70.4381 | 1.9096 | Day | 202601 | 2026-01-30 | 1.9096
2026-01-30 10:59 | 70.682 | FALSE | TRUE | -2.0038 | -2.9176 | 0.056512 | 0.080016 | 0.2826 |  | 2026-01-30 09:30 | upper | TRUE | 3 | 68.6782 | FALSE | TRUE | 0.6268 | 2.3976 | 69.6519 | 7 | 0.2826 | 0.07056 | 0.12539 | 1.6911 | 0.48681 | Confirmed/Materialized Shift | 70.6255 | 2.1161 | Day | 202601 | 2026-01-30 | 2.1161
2026-01-30 11:15 | 70.682 | FALSE | TRUE | -2.0178 | -2.9386 | -0.098639 | -0.13936 | 0 |  | 2026-01-30 09:30 | none | FALSE | 2 | 68.6642 | FALSE | FALSE | 0.578 | 2.3246 | 69.7224 | 8 | 0 | 0.07056 | 0.12539 | -0.56273 | 0.52911 | Confirmed/Materialized Shift | 70.7806 | 1.8136 | Day | 202601 | 2026-01-30 | 1.8136
2026-01-30 11:29 | 70.9646 | FALSE | TRUE | -2.3286 | -3.3927 | -0.013635 | -0.01921 | 0.2826 |  | 2026-01-30 09:30 | none | FALSE | 2 | 68.636 | FALSE | FALSE | 0.5889 | 2.286 | 69.8071 | 9 | 0.2826 | 0.08469 | 0.13273 | 1.4911 | 0.58556 | Confirmed/Materialized Shift | 70.9782 | 1.9767 | Day | 202601 | 2026-01-30 | 1.9767
2026-01-30 11:44 | 70.9646 | FALSE | TRUE | -2.3229 | -3.3841 | -0.17734 | -0.24927 | 0 |  | 2026-01-30 09:30 | none | FALSE | 2 | 68.6417 | FALSE | FALSE | 0.5716 | 2.229 | 69.8918 | 10 | 0 | 0.08469 | 0.13273 | -0.63807 | 0.62507 | Confirmed/Materialized Shift | 71.1419 | 1.7163 | Day | 202601 | 2026-01-30 | 1.7163
2026-01-30 11:59 | 70.9646 | FALSE | TRUE | -2.2896 | -3.3339 | -0.31333 | -0.43959 | 0 |  | 2026-01-30 09:30 | none | FALSE | 1 | 68.675 | FALSE | FALSE | 0.5298 | 2.1644 | 69.9765 | 11 | 0 | 0.08469 | 0.13273 | -0.63807 | 0.65072 | Confirmed/Materialized Shift | 71.2779 | 1.5185 | Day | 202601 | 2026-01-30 | 1.5185
2026-01-30 12:14 | 70.9646 | FALSE | TRUE | -2.2317 | -3.2469 | -0.42483 | -0.59509 | 0 |  | 2026-01-30 09:30 | none | FALSE | 1 | 68.7329 | FALSE | FALSE | 0.5193 | 2.0974 | 70.0612 | 12 | 0 | 0.08469 | 0.13273 | -0.63807 | 0.66413 | Confirmed/Materialized Shift | 71.3894 | 1.3603 | Day | 202601 | 2026-01-30 | 1.3603
2026-01-30 12:29 | 71.2472 | FALSE | TRUE | -2.4612 | -3.578 | -0.28676 | -0.40087 | 0.2826 |  | 2026-01-30 09:30 | none | FALSE | 0 | 68.786 | FALSE | FALSE | 0.5055 | 2.0578 | 70.16 | 13 | 0.2826 | 0.09882 | 0.13817 | 1.3301 | 0.68698 | Confirmed/Materialized Shift | 71.534 | 1.5826 | Day | 202601 | 2026-01-30 | 1.5826
2026-01-30 12:44 | 71.5298 | FALSE | TRUE | -2.693 | -3.9122 | -0.17933 | -0.25008 | 0.2826 |  | 2026-01-30 09:30 | none | FALSE | 0 | 68.8368 | FALSE | FALSE | 0.5167 | 2.0358 | 70.2729 | 14 | 0.2826 | 0.11295 | 0.14193 | 1.1953 | 0.71809 | Confirmed/Materialized Shift | 71.7091 | 1.7503 | Day | 202601 | 2026-01-30 | 1.7503
2026-01-30 12:59 | 71.5298 | FALSE | TRUE | -2.6034 | -3.777 | -0.31556 | -0.43922 | 0 |  | 2026-01-30 09:30 | none | FALSE | 0 | 68.9264 | FALSE | FALSE | 0.5045 | 2.0046 | 70.3859 | 15 | 0 | 0.11295 | 0.14193 | -0.79582 | 0.72973 | Confirmed/Materialized Shift | 71.8454 | 1.5676 | Day | 202601 | 2026-01-30 | 1.5676
2026-01-30 13:14 | 71.5298 | FALSE | TRUE | -2.4766 | -3.5866 | -0.41473 | -0.57646 | 0 |  | 2026-01-30 09:30 | none | FALSE | 0 | 69.0532 | FALSE | FALSE | 0.4951 | 1.9685 | 70.4989 | 16 | 0 | 0.11295 | 0.14193 | -0.79582 | 0.72284 | Confirmed/Materialized Shift | 71.9445 | 1.4262 | Day | 202601 | 2026-01-30 | 1.4262
2026-01-30 13:28 | 71.5298 | FALSE | TRUE | -2.3118 | -3.3398 | -0.47575 | -0.66072 | 0 |  | 2026-01-30 09:30 | none | FALSE | 0 | 69.218 | FALSE | FALSE | 0.4878 | 1.9302 | 70.6118 | 17 | 0 | 0.11295 | 0.14193 | -0.79582 | 0.69688 | Confirmed/Materialized Shift | 72.0056 | 1.3173 | Day | 202601 | 2026-01-30 | 1.3173
2026-01-30 13:43 | 71.8124 | FALSE | TRUE | -2.4864 | -3.5865 | -0.31108 | -0.43132 | 0.2826 |  | 2026-01-30 09:30 | none | FALSE | 0 | 69.326 | FALSE | FALSE | 0.5037 | 1.9093 | 70.7248 | 18 | 0.2826 | 0.11295 | 0.14193 | 1.1953 | 0.69937 | Confirmed/Materialized Shift | 72.1235 | 1.5552 | Day | 202601 | 2026-01-30 | 1.5552
2026-01-30 13:59 | 71.8124 | FALSE | TRUE | -2.3396 | -3.3676 | -0.39019 | -0.54041 | 0 |  | 2026-01-30 09:30 | none | FALSE | 0 | 69.4728 | FALSE | FALSE | 0.4952 | 1.884 | 70.8377 | 19 | 0 | 0.11295 | 0.14193 | -0.79582 | 0.68245 | Confirmed/Materialized Shift | 72.2026 | 1.4282 | Day | 202601 | 2026-01-30 | 1.4282
2026-01-30 14:14 | 72.095 | FALSE | TRUE | -2.4646 | -3.5395 | -0.20413 | -0.28234 | 0.2826 |  | 2026-01-30 09:30 | none | FALSE | 0 | 69.6304 | FALSE | FALSE | 0.5129 | 1.8745 | 70.9648 | 20 | 0.2826 | 0.12708 | 0.14414 | 1.0789 | 0.66717 | Confirmed/Materialized Shift | 72.2991 | 1.694 | Day | 202601 | 2026-01-30 | 1.694
2026-01-30 14:28 | 72.3758 | FALSE | TRUE | -2.6491 | -3.7993 | -0.081071 | -0.11189 | 0.2808 |  | 2026-01-30 09:30 | none | FALSE | 0 | 69.7267 | FALSE | FALSE | 0.5254 | 1.8748 | 71.0918 | 21 | 0.2808 | 0.12699 | 0.14404 | 1.0678 | 0.68255 | Confirmed/Materialized Shift | 72.4569 | 1.8812 | Day | 202601 | 2026-01-30 | 1.8812
2026-01-30 14:43 | 72.3758 | FALSE | TRUE | -2.5027 | -3.5817 | -0.18859 | -0.25989 | 0 |  | 2026-01-30 09:30 | none | FALSE | 0 | 69.8731 | FALSE | FALSE | 0.5146 | 1.8678 | 71.2188 | 22 | 0 | 0.12699 | 0.14404 | -0.88163 | 0.67281 | Confirmed/Materialized Shift | 72.5644 | 1.7197 | Day | 202601 | 2026-01-30 | 1.7197
2026-01-30 14:58 | 72.6584 | FALSE | TRUE | -2.6994 | -3.8586 | -0.074305 | -0.10216 | 0.2826 |  | 2026-01-30 09:30 | none | FALSE | 0 | 69.959 | FALSE | FALSE | 0.5262 | 1.8689 | 71.3458 | 23 | 0.2826 | 0.12708 | 0.14414 | 1.0789 | 0.69343 | Confirmed/Materialized Shift | 72.7327 | 1.8928 | Day | 202601 | 2026-01-30 | 1.8928
2026-01-30 15:13 | 72.941 | FALSE | TRUE | -2.9522 | -4.2181 | -0.016006 | -0.021939 | 0.2826 |  | 2026-01-30 09:30 | none | FALSE | 0 | 69.9888 | FALSE | FALSE | 0.5319 | 1.8734 | 71.4729 | 24 | 0.2826 | 0.12708 | 0.14414 | 1.0789 | 0.74204 | Confirmed/Materialized Shift | 72.957 | 1.9784 | Day | 202601 | 2026-01-30 | 1.9784
2026-01-30 15:28 | 72.941 | FALSE | TRUE | -2.8725 | -4.0996 | -0.19055 | -0.26055 | 0 |  | 2026-01-30 09:30 | none | FALSE | 0 | 70.0685 | FALSE | FALSE | 0.5167 | 1.8686 | 71.6 | 25 | 0 | 0.12708 | 0.14414 | -0.88163 | 0.76577 | Confirmed/Materialized Shift | 73.1315 | 1.7512 | Day | 202601 | 2026-01-30 | 1.7512
2026-01-30 15:43 | 73.2236 | FALSE | TRUE | -3.0677 | -4.3727 | -0.10291 | -0.14035 | 0.2826 |  | 2026-01-30 09:30 | none | FALSE | 0 | 70.1559 | FALSE | FALSE | 0.5247 | 1.8686 | 71.7412 | 26 | 0.2826 | 0.14121 | 0.14488 | 0.97592 | 0.79265 | Confirmed/Materialized Shift | 73.3265 | 1.8702 | Day | 202601 | 2026-01-30 | 1.8702
2026-01-30 15:58 | 73.2236 | FALSE | TRUE | -2.9898 | -4.2569 | -0.2792 | -0.37984 | 0 |  | 2026-01-30 09:30 | none | FALSE | 0 | 70.2338 | FALSE | FALSE | 0.5106 | 1.8608 | 71.8683 | 27 | 0 | 0.12708 | 0.14414 | -0.88163 | 0.81725 | Confirmed/Materialized Shift | 73.5028 | 1.6584 | Day | 202601 | 2026-01-30 | 1.6584
2026-01-30 16:13 | 73.2236 | FALSE | TRUE | -2.8696 | -4.0788 | -0.41313 | -0.56103 | 0 |  | 2026-01-30 09:30 | none | FALSE | 0 | 70.354 | FALSE | FALSE | 0.4998 | 1.8478 | 71.9954 | 28 | 0 | 0.12708 | 0.14414 | -0.88163 | 0.82068 | Confirmed/Materialized Shift | 73.6367 | 1.4966 | Day | 202601 | 2026-01-30 | 1.4966
2026-01-30 16:28 | 73.5062 | FALSE | TRUE | -3.0817 | -4.3758 | -0.31417 | -0.42558 | 0.2826 |  | 2026-01-30 09:30 | none | FALSE | 0 | 70.4245 | FALSE | FALSE | 0.5087 | 1.8403 | 72.1225 | 29 | 0.2826 | 0.12708 | 0.14414 | 1.0789 | 0.84896 | Confirmed/Materialized Shift | 73.8204 | 1.6299 | Day | 202601 | 2026-01-30 | 1.6299
2026-01-30 16:43 | 73.5062 | FALSE | TRUE | -2.9701 | -4.2107 | -0.45675 | -0.61754 | 0 |  | 2026-01-30 09:30 | none | FALSE | 0 | 70.5361 | FALSE | FALSE | 0.4978 | 1.8279 | 72.2495 | 30 | 0 | 0.12708 | 0.14414 | -0.88163 | 0.85671 | Confirmed/Materialized Shift | 73.9629 | 1.4669 | Day | 202601 | 2026-01-30 | 1.4669
2026-01-30 16:58 | 73.5062 | FALSE | TRUE | -2.8186 | -3.9874 | -0.5594 | -0.75527 | 0 |  | 2026-01-30 09:30 | none | FALSE | 0 | 70.6876 | FALSE | FALSE | 0.4892 | 1.812 | 72.3766 | 31 | 0 | 0.12708 | 0.14414 | -0.88163 | 0.84449 | Confirmed/Materialized Shift | 74.0656 | 1.3376 | Day | 202601 | 2026-01-30 | 1.3376
2026-01-30 17:13 | 73.5062 | FALSE | TRUE | -2.6253 | -3.7039 | -0.62032 | -0.83684 | 0 |  | 2026-01-30 09:30 | none | FALSE | 0 | 70.8809 | FALSE | FALSE | 0.4824 | 1.794 | 72.5037 | 32 | 0 | 0.12708 | 0.14414 | -0.88163 | 0.81141 | Confirmed/Materialized Shift | 74.1265 | 1.2355 | Day | 202601 | 2026-01-30 | 1.2355
2026-01-30 17:27 | 73.5062 | FALSE | TRUE | -2.4577 | -3.4592 | -0.67858 | -0.91472 | 0 |  | 2026-01-30 09:30 | none | FALSE | 0 | 71.0485 | FALSE | FALSE | 0.4756 | 1.774 | 72.6166 | 33 | 0 | 0.11295 | 0.14193 | -0.79582 | 0.78407 | Confirmed/Materialized Shift | 74.1848 | 1.1345 | Day | 202601 | 2026-01-30 | 1.1345
2026-01-30 17:42 | 73.7888 | FALSE | TRUE | -2.6232 | -3.686 | -0.50473 | -0.67938 | 0.2826 |  | 2026-01-30 09:30 | none | FALSE | 0 | 71.1656 | FALSE | FALSE | 0.4903 | 1.7617 | 72.7296 | 34 | 0.2826 | 0.11295 | 0.14193 | 1.1953 | 0.78197 | Confirmed/Materialized Shift | 74.2935 | 1.3545 | Day | 202601 | 2026-01-30 | 1.3545
2026-01-30 17:57 | 73.5062 | TRUE | FALSE | -2.1707 | -3.0429 | -0.8151 | -1.0967 | -0.2826 |  |  | none | FALSE | 1 | 71.3355 | FALSE | FALSE | 0.0891 |  | 72.8284 | 0 | -0.2826 | 0.09882 | 0.16582 | -2.3002 | 0.74645 | Persistence ends | 74.3213 | 0.90802 | Day | 202601 | 2026-01-30 | 0.90802
2026-01-30 18:12 | 73.7888 | FALSE | FALSE | -2.2667 | -3.1692 | -0.57177 | -0.76892 | 0.2826 |  |  | none | FALSE | 1 | 71.5221 | FALSE | FALSE | 0.1082 |  | 72.9414 | 0 | 0.2826 | 0.11295 | 0.16897 | 1.004 | 0.70961 | Normal | 74.3606 | 1.1942 | Night | 202601 | 2026-01-30 | 1.1942
2026-01-30 18:27 | 73.5062 | TRUE | FALSE | -1.7391 | -2.4233 | -0.80706 | -1.086 | -0.2826 |  |  | none | FALSE | 2 | 71.7671 | TRUE | FALSE | 0.106 |  | 73.0402 | 0 | -0.2826 | 0.09882 | 0.18948 | -2.013 | 0.63654 | Normal | 74.3133 | 0.73211 | Night | 202601 | 2026-01-30 | 0.73211
2026-01-30 18:30 | 73.5062 | FALSE | FALSE | -1.5298 | -2.1254 | -0.7671 | -1.0328 | 0 |  |  | none | FALSE | 2 | 71.9764 | FALSE | FALSE | 0.1014 |  | 73.1249 | 0 | 0 | 0.08469 | 0.18555 | -0.45642 | 0.57422 | Normal | 74.2733 | 0.66409 | Night | 202601 | 2026-01-30 | 0.66409
2026-01-30 18:31 | 73.7888 | FALSE | FALSE | -1.5691 | -2.1726 | -0.43885 | -0.59122 | 0.2826 |  |  | none | FALSE | 2 | 72.2197 | FALSE | FALSE | 0.1322 |  | 73.2237 | 0 | 0.2826 | 0.09882 | 0.18948 | 0.96991 | 0.50198 | Normal | 74.2277 | 1.1258 | Night | 202601 | 2026-01-30 | 1.1258
2026-01-30 18:46 | 73.5062 | FALSE | FALSE | -1.0696 | -1.4766 | -0.64571 | -0.87079 | -0.2826 |  |  | none | FALSE | 2 | 72.4366 | FALSE | FALSE | 0.0901 |  | 73.2943 | 0 | -0.2826 | 0.07056 | 0.20234 | -1.7454 | 0.42883 | Normal | 74.1519 | 0.49425 | Night | 202601 | 2026-01-30 | 0.49425
2026-01-30 19:01 | 73.2236 | FALSE | FALSE | -0.62957 | -0.86725 | -0.85565 | -1.1551 | -0.2826 |  |  | none | FALSE | 2 | 72.594 | FALSE | FALSE | 0.0774 |  | 73.3366 | 0 | -0.2826 | 0.04239 | 0.21058 | -1.5433 | 0.37131 | Normal | 74.0793 | -0.30444 | Night | 202601 | 2026-01-30 | 0.30444
2026-01-30 19:16 | 73.2236 | FALSE | FALSE | -0.43807 | -0.60186 | -0.74893 | -1.0124 | 0 |  |  | none | FALSE | 2 | 72.7855 | FALSE | FALSE | 0.0921 |  | 73.379 | 0 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.29675 | Normal | 73.9725 | -0.52378 | Night | 202601 | 2026-01-30 | 0.52378
2026-01-30 19:30 | 73.2236 | FALSE | FALSE | -0.31091 | -0.42642 | -0.67829 | -0.91783 | 0 |  |  | none | FALSE | 2 | 72.9127 | FALSE | FALSE | 0.1067 |  | 73.4073 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.2473 | Normal | 73.9019 | -0.74278 | Night | 202601 | 2026-01-30 | 0.74278
2026-01-30 19:45 | 72.941 | FALSE | FALSE | -0.028313 | -0.038832 | -0.96089 | -1.3002 | -0.2826 |  |  | none | FALSE | 2 | 72.9127 | FALSE | FALSE | 0.1828 |  | 73.4073 | 0 | -0.2826 | 0 | 0.20502 | -1.3784 | 0.2473 | Normal | 73.9019 | -1.8855 | Night | 202601 | 2026-01-30 | 1.8855
2026-01-30 20:00 | 72.941 | FALSE | FALSE | -0.028313 | -0.038832 | -0.96089 | -1.3002 | 0 |  |  | none | FALSE | 1 | 72.9127 | FALSE | FALSE | 0.1543 |  | 73.4073 | 0 | 0 | 0 | 0.20502 | 0 | 0.2473 | Normal | 73.9019 | -1.8855 | Night | 202601 | 2026-01-30 | 1.8855
2026-01-30 20:15 | 72.3758 | TRUE | FALSE | 0.31534 | 0.4338 | -1.6629 | -2.2459 | -0.5652 | 2026-01-31 08:45 | 2026-01-30 20:15 | lower | TRUE | 2 | 72.6911 | TRUE | FALSE | 0.31 | 2.936 | 73.3649 | 1 | -0.5652 | -0.04239 | 0.22968 | -2.2763 | 0.33688 | Extreme triggered | 74.0387 | -2.936 | Night | 202601 | 2026-01-30 | 2.936
2026-01-30 20:29 | 72.3758 | FALSE | FALSE | 0.14163 | 0.19531 | -1.7518 | -2.3632 | 0 |  | 2026-01-30 20:15 | lower | TRUE | 1 | 72.5174 | FALSE | FALSE | 0.2996 | 2.6439 | 73.3225 | 2 | 0 | -0.04239 | 0.22968 | 0.18456 | 0.40254 | Extreme/elevated | 74.1276 | -2.3518 | Night | 202601 | 2026-01-30 | 2.3518
2026-01-30 20:44 | 72.3758 | FALSE | FALSE | -0.0051909 | -0.0071727 | -1.8138 | -2.4449 | 0 |  | 2026-01-30 20:15 | none | FALSE | 1 | 72.3706 | FALSE | FALSE | 0.3326 | 2.4255 | 73.2801 | 3 | 0 | -0.04239 | 0.22968 | 0.18456 | 0.45476 | Persistent | 74.1896 | -1.9886 | Night | 202601 | 2026-01-30 | 1.9886
2026-01-30 20:59 | 72.095 | FALSE | FALSE | 0.069968 | 0.096955 | -2.1592 | -2.9078 | -0.2808 |  | 2026-01-30 20:15 | lower | TRUE | 1 | 72.165 | FALSE | TRUE | 0.3994 | 2.3526 | 73.2096 | 4 | -0.2808 | -0.07056 | 0.22215 | -0.9464 | 0.5223 | Persistent | 74.2542 | -2.134 | Night | 202601 | 2026-01-30 | 2.134
2026-01-30 21:14 | 72.095 | FALSE | FALSE | -0.10195 | -0.14162 | -2.19 | -2.948 | 0 |  | 2026-01-30 20:15 | none | FALSE | 1 | 71.993 | FALSE | FALSE | 0.4358 | 2.2465 | 73.139 | 5 | 0 | -0.07056 | 0.22215 | 0.31763 | 0.57298 | Persistent | 74.285 | -1.8221 | Night | 202601 | 2026-01-30 | 1.8221
2026-01-30 21:29 | 71.8124 | FALSE | FALSE | -0.032893 | -0.045825 | -2.5167 | -3.3859 | -0.2826 |  | 2026-01-30 20:15 | none | FALSE | 1 | 71.7795 | FALSE | FALSE | 0.5013 | 2.1968 | 73.0543 | 6 | -0.2826 | -0.08469 | 0.22637 | -0.87428 | 0.6374 | Persistent | 74.3291 | -1.9484 | Night | 202601 | 2026-01-30 | 1.9484
2026-01-30 21:44 | 71.8124 | FALSE | TRUE | -0.21268 | -0.29704 | -2.5271 | -3.3994 | 0 |  | 2026-01-30 20:15 | none | FALSE | 1 | 71.5997 | FALSE | FALSE | 0.5412 | 2.1243 | 72.9696 | 7 | 0 | -0.08469 | 0.22637 | 0.37412 | 0.68495 | Confirmed/Materialized Shift | 74.3395 | -1.6895 | Night | 202601 | 2026-01-30 | 1.6895
2026-01-30 21:59 | 71.5298 | FALSE | TRUE | -0.14606 | -0.20461 | -2.8281 | -3.8033 | -0.2826 |  | 2026-01-30 20:15 | none | FALSE | 1 | 71.3837 | FALSE | FALSE | 0.5488 | 2.0842 | 72.8708 | 8 | -0.2826 | -0.09882 | 0.2296 | -0.80043 | 0.74353 | Confirmed/Materialized Shift | 74.3579 | -1.8036 | Night | 202601 | 2026-01-30 | 1.8036
2026-01-30 22:14 | 71.5298 | FALSE | TRUE | -0.30779 | -0.43215 | -2.7639 | -3.7202 | 0 |  | 2026-01-30 20:15 | none | FALSE | 1 | 71.222 | FALSE | FALSE | 0.5352 | 2.0303 | 72.7579 | 9 | 0 | -0.11295 | 0.21299 | 0.53031 | 0.76792 | Confirmed/Materialized Shift | 74.2937 | -1.5992 | Night | 202601 | 2026-01-30 | 1.5992
2026-01-30 22:29 | 71.5298 | FALSE | TRUE | -0.45736 | -0.64351 | -2.7158 | -3.6579 | 0 |  | 2026-01-30 20:15 | none | FALSE | 1 | 71.0724 | FALSE | FALSE | 0.5235 | 1.9697 | 72.659 | 10 | 0 | -0.09882 | 0.2105 | 0.46945 | 0.7933 | Confirmed/Materialized Shift | 74.2456 | -1.4235 | Night | 202601 | 2026-01-30 | 1.4235
2026-01-30 22:44 | 71.5298 | FALSE | TRUE | -0.55321 | -0.77943 | -2.5858 | -3.4888 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 70.9766 | FALSE | FALSE | 0.4863 | 1.9083 | 72.5461 | 11 | 0 | -0.11295 | 0.19224 | 0.58754 | 0.78475 | Confirmed/Materialized Shift | 74.1156 | -1.295 | Night | 202601 | 2026-01-30 | 1.295
2026-01-30 22:59 | 71.2472 | FALSE | TRUE | -0.41741 | -0.58931 | -2.7893 | -3.7674 | -0.2826 |  | 2026-01-30 20:15 | none | FALSE | 0 | 70.8298 | FALSE | FALSE | 0.4986 | 1.8726 | 72.4331 | 12 | -0.2826 | -0.11295 | 0.19224 | -0.88248 | 0.80167 | Confirmed/Materialized Shift | 74.0365 | -1.4793 | Night | 202601 | 2026-01-30 | 1.4793
2026-01-30 23:14 | 71.2472 | FALSE | TRUE | -0.53034 | -0.74995 | -2.6763 | -3.6204 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 70.7169 | FALSE | FALSE | 0.4892 | 1.8315 | 72.3202 | 13 | 0 | -0.11295 | 0.19224 | 0.58754 | 0.80166 | Confirmed/Materialized Shift | 73.9235 | -1.3384 | Night | 202601 | 2026-01-30 | 1.3384
2026-01-30 23:28 | 70.9646 | FALSE | TRUE | -0.3411 | -0.48298 | -2.7698 | -3.7565 | -0.2826 |  | 2026-01-30 20:15 | none | FALSE | 0 | 70.6235 | FALSE | FALSE | 0.5041 | 1.8122 | 72.179 | 14 | -0.2826 | -0.14121 | 0.17145 | -0.82465 | 0.77773 | Confirmed/Materialized Shift | 73.7344 | -1.5614 | Night | 202601 | 2026-01-30 | 1.5614
2026-01-30 23:43 | 70.9646 | FALSE | TRUE | -0.42635 | -0.60442 | -2.6009 | -3.5355 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 70.5383 | FALSE | FALSE | 0.4958 | 1.7872 | 72.0519 | 15 | 0 | -0.12708 | 0.17083 | 0.74389 | 0.75682 | Confirmed/Materialized Shift | 73.5655 | -1.4367 | Night | 202601 | 2026-01-30 | 1.4367
2026-01-30 23:59 | 70.9646 | FALSE | TRUE | -0.50796 | -0.72096 | -2.4566 | -3.346 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 70.4566 | FALSE | FALSE | 0.4876 | 1.7576 | 71.9389 | 16 | 0 | -0.11295 | 0.16897 | 0.66847 | 0.74115 | Confirmed/Materialized Shift | 73.4212 | -1.3146 | Night | 202601 | 2026-01-30 | 1.3146
2026-01-31 00:14 | 70.9646 | FALSE | TRUE | -0.55138 | -0.78307 | -2.2742 | -3.1051 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 70.4132 | FALSE | FALSE | 0.4813 | 1.726 | 71.826 | 17 | 0 | -0.11295 | 0.16897 | 0.66847 | 0.70639 | Confirmed/Materialized Shift | 73.2388 | -1.2194 | Night | 202601 | 2026-01-31 | 1.2194
2026-01-31 00:28 | 70.682 | FALSE | TRUE | -0.32183 | -0.4574 | -2.3557 | -3.2253 | -0.2826 |  | 2026-01-30 20:15 | none | FALSE | 0 | 70.3602 | FALSE | FALSE | 0.5013 | 1.7145 | 71.6989 | 18 | -0.2826 | -0.12708 | 0.17083 | -0.91037 | 0.66937 | Confirmed/Materialized Shift | 73.0377 | -1.5192 | Night | 202601 | 2026-01-31 | 1.5192
2026-01-31 00:43 | 70.682 | FALSE | TRUE | -0.37331 | -0.53096 | -2.1812 | -2.9936 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 70.3087 | FALSE | FALSE | 0.4944 | 1.6987 | 71.586 | 19 | 0 | -0.11295 | 0.16897 | 0.66847 | 0.63864 | Confirmed/Materialized Shift | 72.8632 | -1.4155 | Night | 202601 | 2026-01-31 | 1.4155
2026-01-31 00:58 | 70.682 | FALSE | TRUE | -0.37654 | -0.53558 | -1.9586 | -2.6962 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 70.3055 | FALSE | FALSE | 0.4903 | 1.6816 | 71.473 | 20 | 0 | -0.11295 | 0.16897 | 0.66847 | 0.58378 | Confirmed/Materialized Shift | 72.6406 | -1.355 | Night | 202601 | 2026-01-31 | 1.355
2026-01-31 01:13 | 70.682 | FALSE | TRUE | -0.43083 | -0.61328 | -1.8435 | -2.5418 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 70.2512 | FALSE | FALSE | 0.4828 | 1.6606 | 71.3883 | 21 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.56858 | Confirmed/Materialized Shift | 72.5255 | -1.2423 | Night | 202601 | 2026-01-31 | 1.2423
2026-01-31 01:28 | 70.682 | FALSE | TRUE | -0.45664 | -0.65025 | -1.6999 | -2.3485 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 70.2254 | FALSE | FALSE | 0.4769 | 1.6376 | 71.3036 | 22 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.53913 | Confirmed/Materialized Shift | 72.3819 | -1.153 | Night | 202601 | 2026-01-31 | 1.153
2026-01-31 01:43 | 70.682 | FALSE | TRUE | -0.44886 | -0.6391 | -1.5227 | -2.1089 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 70.2331 | FALSE | FALSE | 0.4726 | 1.6137 | 71.2189 | 23 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.4929 | Confirmed/Materialized Shift | 72.2047 | -1.0893 | Night | 202601 | 2026-01-31 | 1.0893
2026-01-31 01:58 | 70.3994 | FALSE | TRUE | -0.22512 | -0.3208 | -1.6946 | -2.3506 | -0.2826 |  | 2026-01-30 20:15 | none | FALSE | 0 | 70.1743 | FALSE | FALSE | 0.5021 | 1.6103 | 71.1342 | 24 | -0.2826 | -0.08478 | 0.13287 | -1.4888 | 0.47994 | Confirmed/Materialized Shift | 72.094 | -1.5309 | Night | 202601 | 2026-01-31 | 1.5309
2026-01-31 02:13 | 70.3994 | FALSE | TRUE | -0.25024 | -0.35673 | -1.5502 | -2.1546 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 70.1492 | FALSE | FALSE | 0.4963 | 1.6036 | 71.0494 | 25 | 0 | -0.08478 | 0.13287 | 0.63808 | 0.45011 | Confirmed/Materialized Shift | 71.9496 | -1.444 | Night | 202601 | 2026-01-31 | 1.444
2026-01-31 02:28 | 70.3994 | FALSE | TRUE | -0.29001 | -0.41366 | -1.4487 | -2.0163 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 70.1094 | FALSE | FALSE | 0.4889 | 1.5932 | 70.9787 | 26 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.43467 | Confirmed/Materialized Shift | 71.8481 | -1.3328 | Night | 202601 | 2026-01-31 | 1.3328
2026-01-31 02:43 | 70.3994 | FALSE | TRUE | -0.30316 | -0.43249 | -1.3205 | -1.8412 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 70.0962 | FALSE | FALSE | 0.4835 | 1.5806 | 70.9081 | 27 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.40592 | Confirmed/Materialized Shift | 71.7199 | -1.2532 | Night | 202601 | 2026-01-31 | 1.2532
2026-01-31 02:58 | 70.3994 | FALSE | TRUE | -0.33443 | -0.47732 | -1.2388 | -1.7292 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 70.065 | FALSE | FALSE | 0.4766 | 1.5652 | 70.8516 | 28 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.3933 | Confirmed/Materialized Shift | 71.6382 | -1.1497 | Night | 202601 | 2026-01-31 | 1.1497
2026-01-31 03:13 | 70.1168 | FALSE | TRUE | -0.11981 | -0.17116 | -1.448 | -2.0234 | -0.2826 |  | 2026-01-30 20:15 | none | FALSE | 0 | 69.997 | FALSE | FALSE | 0.513 | 1.5697 | 70.7809 | 29 | -0.2826 | -0.07065 | 0.12555 | -1.6882 | 0.39196 | Confirmed/Materialized Shift | 71.5648 | -1.6943 | Night | 202601 | 2026-01-31 | 1.6943
2026-01-31 03:27 | 70.1168 | FALSE | TRUE | -0.16039 | -0.22927 | -1.3473 | -1.8853 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 69.9564 | FALSE | FALSE | 0.505 | 1.5698 | 70.7103 | 30 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.37692 | Confirmed/Materialized Shift | 71.4641 | -1.5745 | Night | 202601 | 2026-01-31 | 1.5745
2026-01-31 03:42 | 70.1168 | FALSE | TRUE | -0.17002 | -0.24307 | -1.2156 | -1.7042 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 69.9468 | FALSE | FALSE | 0.5006 | 1.5679 | 70.6396 | 31 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.34642 | Confirmed/Materialized Shift | 71.3324 | -1.5092 | Night | 202601 | 2026-01-31 | 1.5092
2026-01-31 03:57 | 70.1168 | FALSE | TRUE | -0.20183 | -0.28869 | -1.1344 | -1.5921 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 69.915 | FALSE | FALSE | 0.4931 | 1.5625 | 70.5831 | 32 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.33406 | Confirmed/Materialized Shift | 71.2512 | -1.3958 | Night | 202601 | 2026-01-31 | 1.3958
2026-01-31 04:12 | 69.836 | FALSE | TRUE | 0.0056495 | 0.0080889 | -1.3474 | -1.8929 | -0.2808 |  | 2026-01-30 20:15 | lower | TRUE | 0 | 69.8416 | FALSE | TRUE | 0.5345 | 1.5763 | 70.5125 | 33 | -0.2808 | -0.07056 | 0.12539 | -1.6767 | 0.33544 | Confirmed/Materialized Shift | 71.1834 | -2.0168 | Night | 202601 | 2026-01-31 | 2.0168
2026-01-31 04:27 | 69.836 | FALSE | TRUE | -0.079903 | -0.11455 | -1.3201 | -1.8552 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 69.7561 | FALSE | FALSE | 0.5181 | 1.582 | 70.4561 | 34 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.35 | Confirmed/Materialized Shift | 71.1561 | -1.7717 | Night | 202601 | 2026-01-31 | 1.7717
2026-01-31 04:42 | 69.836 | FALSE | TRUE | -0.14563 | -0.20897 | -1.273 | -1.7902 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 69.6904 | FALSE | FALSE | 0.506 | 1.5822 | 70.3997 | 35 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.35465 | Confirmed/Materialized Shift | 71.109 | -1.5894 | Night | 202601 | 2026-01-31 | 1.5894
2026-01-31 04:57 | 69.836 | FALSE | TRUE | -0.19234 | -0.27617 | -1.2068 | -1.6987 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 69.6437 | FALSE | FALSE | 0.4967 | 1.5786 | 70.3432 | 36 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.34979 | Confirmed/Materialized Shift | 71.0428 | -1.4501 | Night | 202601 | 2026-01-31 | 1.4501
2026-01-31 05:12 | 69.5534 | FALSE | TRUE | -0.00078764 | -0.0011324 | -1.4393 | -2.0275 | -0.2826 |  | 2026-01-30 20:15 | none | FALSE | 0 | 69.5526 | FALSE | FALSE | 0.5332 | 1.5899 | 70.2727 | 37 | -0.2826 | -0.07056 | 0.12539 | -1.6911 | 0.36003 | Confirmed/Materialized Shift | 70.9927 | -1.9978 | Night | 202601 | 2026-01-31 | 1.9978
2026-01-31 05:27 | 69.5534 | FALSE | TRUE | -0.097897 | -0.14095 | -1.4236 | -2.0057 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 69.4555 | FALSE | FALSE | 0.5162 | 1.5939 | 70.2163 | 38 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.38037 | Confirmed/Materialized Shift | 70.977 | -1.7426 | Night | 202601 | 2026-01-31 | 1.7426
2026-01-31 05:42 | 69.5534 | FALSE | TRUE | -0.17599 | -0.25366 | -1.3888 | -1.9577 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 69.3774 | FALSE | FALSE | 0.5033 | 1.5928 | 70.1598 | 39 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.3912 | Confirmed/Materialized Shift | 70.9422 | -1.5501 | Night | 202601 | 2026-01-31 | 1.5501
2026-01-31 05:57 | 69.5534 | FALSE | TRUE | -0.23663 | -0.34137 | -1.3366 | -1.8855 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 69.3168 | FALSE | FALSE | 0.4932 | 1.5879 | 70.1034 | 40 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.39331 | Confirmed/Materialized Shift | 70.89 | -1.3984 | Night | 202601 | 2026-01-31 | 1.3984
2026-01-31 06:12 | 69.2708 | FALSE | TRUE | -0.058494 | -0.084514 | -1.5826 | -2.2336 | -0.2826 |  | 2026-01-30 20:15 | none | FALSE | 0 | 69.2123 | FALSE | FALSE | 0.5238 | 1.5945 | 70.0328 | 41 | -0.2826 | -0.07056 | 0.12539 | -1.6911 | 0.41026 | Confirmed/Materialized Shift | 70.8534 | -1.8574 | Night | 202601 | 2026-01-31 | 1.8574
2026-01-31 06:26 | 69.2708 | FALSE | TRUE | -0.13668 | -0.1977 | -1.5196 | -2.1466 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 69.1341 | FALSE | FALSE | 0.5113 | 1.5963 | 69.9623 | 42 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.41407 | Confirmed/Materialized Shift | 70.7904 | -1.6699 | Night | 202601 | 2026-01-31 | 1.6699
2026-01-31 06:41 | 69.2708 | FALSE | TRUE | -0.18932 | -0.27405 | -1.4311 | -2.0242 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 69.0815 | FALSE | FALSE | 0.5022 | 1.5948 | 69.8917 | 43 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.40511 | Confirmed/Materialized Shift | 70.7019 | -1.5327 | Night | 202601 | 2026-01-31 | 1.5327
2026-01-31 06:56 | 69.2708 | FALSE | TRUE | -0.25403 | -0.36807 | -1.383 | -1.9574 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 69.0168 | FALSE | FALSE | 0.492 | 1.5899 | 69.8353 | 44 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.40926 | Confirmed/Materialized Shift | 70.6538 | -1.3793 | Night | 202601 | 2026-01-31 | 1.3793
2026-01-31 07:11 | 69.2708 | FALSE | TRUE | -0.30228 | -0.43829 | -1.3184 | -1.8677 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 68.9685 | FALSE | FALSE | 0.4836 | 1.5825 | 69.7789 | 45 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.40517 | Confirmed/Materialized Shift | 70.5892 | -1.2539 | Day | 202601 | 2026-01-31 | 1.2539
2026-01-31 07:26 | 68.9882 | FALSE | TRUE | -0.10829 | -0.15721 | -1.5485 | -2.1953 | -0.2826 |  | 2026-01-30 20:15 | none | FALSE | 0 | 68.8799 | FALSE | FALSE | 0.5159 | 1.5858 | 69.7083 | 46 | -0.2826 | -0.07056 | 0.12539 | -1.6911 | 0.41419 | Confirmed/Materialized Shift | 70.5367 | -1.7386 | Day | 202601 | 2026-01-31 | 1.7386
2026-01-31 07:30 | 68.9882 | FALSE | TRUE | -0.17136 | -0.24901 | -1.4704 | -2.0869 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 68.8168 | FALSE | FALSE | 0.5055 | 1.5858 | 69.6377 | 47 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.41044 | Confirmed/Materialized Shift | 70.4586 | -1.5825 | Day | 202601 | 2026-01-31 | 1.5825
2026-01-31 07:45 | 68.9882 | FALSE | TRUE | -0.20816 | -0.30265 | -1.3661 | -1.9417 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 68.78 | FALSE | FALSE | 0.4981 | 1.5834 | 69.5672 | 48 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.39357 | Confirmed/Materialized Shift | 70.3543 | -1.4711 | Day | 202601 | 2026-01-31 | 1.4711
2026-01-31 08:00 | 68.9882 | FALSE | TRUE | -0.26049 | -0.37902 | -1.3056 | -1.8573 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 68.7277 | FALSE | FALSE | 0.489 | 1.5783 | 69.5107 | 49 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.39152 | Confirmed/Materialized Shift | 70.2938 | -1.3347 | Day | 202601 | 2026-01-31 | 1.3347
2026-01-31 08:16 | 68.9882 | FALSE | TRUE | -0.2954 | -0.43002 | -1.2276 | -1.7483 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 68.6928 | FALSE | FALSE | 0.4816 | 1.5712 | 69.4543 | 50 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.38075 | Confirmed/Materialized Shift | 70.2158 | -1.2242 | Day | 202601 | 2026-01-31 | 1.2242
2026-01-31 08:30 | 68.9882 | FALSE | TRUE | -0.31131 | -0.45329 | -1.1307 | -1.6125 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 68.6769 | FALSE | FALSE | 0.4758 | 1.5627 | 69.3979 | 51 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.36049 | Confirmed/Materialized Shift | 70.1189 | -1.1364 | Day | 202601 | 2026-01-31 | 1.1364
2026-01-31 08:30 | 68.9882 | FALSE | TRUE | -0.30473 | -0.44368 | -1.0112 | -1.4446 | 0 |  | 2026-01-30 20:15 | none | FALSE | 0 | 68.6835 | FALSE | FALSE | 0.4716 | 1.5533 | 69.3414 | 52 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.32899 | Confirmed/Materialized Shift | 69.9994 | -1.0737 | Day | 202601 | 2026-01-31 | 1.0737
2026-01-31 08:45 | 68.9882 | FALSE | FALSE | -0.32172 | -0.46852 | -0.94344 | -1.3491 | 0 |  |  | none | FALSE | 0 | 68.6665 | FALSE | FALSE | 0.0655 |  | 69.2991 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.31629 | Persistence ends | 69.9316 | -0.98284 | Day | 202601 | 2026-01-31 | 0.98284
2026-01-31 09:00 | 68.9882 | FALSE | FALSE | -0.32503 | -0.47336 | -0.86197 | -1.234 | 0 |  |  | none | FALSE | 0 | 68.6632 | FALSE | FALSE | 0.0603 |  | 69.2567 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.29675 | Normal | 69.8502 | -0.90471 | Day | 202601 | 2026-01-31 | 0.90471
2026-01-31 09:15 | 68.9882 | FALSE | FALSE | -0.31168 | -0.45384 | -0.76384 | -1.0951 | 0 |  |  | none | FALSE | 0 | 68.6765 | FALSE | FALSE | 0.0561 |  | 69.2143 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.26888 | Normal | 69.752 | -0.84082 | Day | 202601 | 2026-01-31 | 0.84082
2026-01-31 09:30 | 69.2708 | TRUE | FALSE | -0.53768 | -0.78228 | -0.36812 | -0.52862 | 0.2826 |  |  | none | FALSE | 1 | 68.7331 | FALSE | FALSE | 0.0535 |  | 69.186 | 0 | 0.2826 | -0.02826 | 0.12638 | 2.4597 | 0.22645 | Normal | 69.6389 | 0.37438 | Day | 202601 | 2026-01-31 | 0.37438
2026-01-31 09:45 | 69.5534 | TRUE | FALSE | -0.82028 | -1.1934 | -0.085523 | -0.12281 | 0.2826 |  |  | none | FALSE | 2 | 68.7331 | TRUE | FALSE | 0.1653 |  | 69.186 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.22645 | Normal | 69.6389 | 1.6223 | Day | 202601 | 2026-01-31 | 1.6223
2026-01-31 10:00 | 69.836 | FALSE | FALSE | -1.1504 | -1.6749 | 0.12125 | 0.17393 | 0.2826 | 2026-01-31 15:58 | 2026-01-31 10:00 | upper | TRUE | 2 | 68.6856 | FALSE | FALSE | 0.279 | 2.4713 | 69.2001 | 1 | 0.2826 | 0.01413 | 0.14424 | 1.8612 | 0.2573 | Extreme triggered | 69.7147 | 2.4713 | Day | 202601 | 2026-01-31 | 2.4713
2026-01-31 10:15 | 70.1168 | FALSE | FALSE | -1.5304 | -2.2314 | 0.24654 | 0.35285 | 0.2808 |  | 2026-01-31 10:00 | upper | TRUE | 2 | 68.5864 | FALSE | FALSE | 0.356 | 2.6197 | 69.2283 | 2 | 0.2808 | 0.02817 | 0.15598 | 1.6196 | 0.32097 | Extreme/elevated | 69.8703 | 2.7681 | Day | 202601 | 2026-01-31 | 2.7681
2026-01-31 10:29 | 70.1168 | FALSE | FALSE | -1.6037 | -2.3408 | 0.11688 | 0.16697 | 0 |  | 2026-01-31 10:00 | upper | TRUE | 2 | 68.5131 | FALSE | TRUE | 0.3829 | 2.5179 | 69.2565 | 3 | 0 | 0.02817 | 0.15598 | -0.18059 | 0.37172 | Persistent | 69.9999 | 2.3144 | Day | 202601 | 2026-01-31 | 2.3144
2026-01-31 10:44 | 70.3994 | FALSE | FALSE | -1.9888 | -2.9072 | 0.18413 | 0.26223 | 0.2826 |  | 2026-01-31 10:00 | upper | TRUE | 2 | 68.4106 | FALSE | TRUE | 0.4463 | 2.4905 | 69.3129 | 4 | 0.2826 | 0.05643 | 0.1477 | 1.5313 | 0.45118 | Persistent | 70.2153 | 2.4081 | Day | 202601 | 2026-01-31 | 2.4081
2026-01-31 10:59 | 70.3994 | FALSE | FALSE | -2.0542 | -3.0057 | 0.0058577 | 0.0083213 | 0 |  | 2026-01-31 10:00 | upper | TRUE | 2 | 68.3452 | FALSE | TRUE | 0.477 | 2.3947 | 69.3693 | 5 | 0 | 0.05643 | 0.1477 | -0.38207 | 0.5121 | Persistent | 70.3935 | 2.0114 | Day | 202601 | 2026-01-31 | 2.0114
2026-01-31 11:14 | 70.3994 | FALSE | FALSE | -2.0947 | -3.0667 | -0.14749 | -0.20907 | 0 |  | 2026-01-31 10:00 | none | FALSE | 2 | 68.3047 | FALSE | FALSE | 0.5158 | 2.285 | 69.4258 | 6 | 0 | 0.05643 | 0.1477 | -0.38207 | 0.56055 | Persistent | 70.5469 | 1.7369 | Day | 202601 | 2026-01-31 | 1.7369
2026-01-31 11:29 | 70.3994 | FALSE | TRUE | -2.1164 | -3.0994 | -0.28197 | -0.39893 | 0 |  | 2026-01-31 10:00 | none | FALSE | 2 | 68.283 | FALSE | FALSE | 0.5591 | 2.1771 | 69.4822 | 7 | 0 | 0.05643 | 0.1477 | -0.38207 | 0.59958 | Confirmed/Materialized Shift | 70.6814 | 1.5297 | Day | 202601 | 2026-01-31 | 1.5297
2026-01-31 11:44 | 70.3994 | FALSE | TRUE | -2.1226 | -3.1088 | -0.40109 | -0.56651 | 0 |  | 2026-01-31 10:00 | none | FALSE | 2 | 68.2768 | FALSE | FALSE | 0.5481 | 2.0755 | 69.5386 | 8 | 0 | 0.05643 | 0.1477 | -0.38207 | 0.63093 | Confirmed/Materialized Shift | 70.8005 | 1.3643 | Day | 202601 | 2026-01-31 | 1.3643
2026-01-31 11:59 | 70.682 | FALSE | TRUE | -2.3904 | -3.5003 | -0.27306 | -0.38483 | 0.2826 |  | 2026-01-31 10:00 | none | FALSE | 1 | 68.2916 | FALSE | FALSE | 0.5346 | 2.0216 | 69.6233 | 9 | 0.2826 | 0.08469 | 0.13273 | 1.4911 | 0.66586 | Confirmed/Materialized Shift | 70.9551 | 1.5899 | Day | 202601 | 2026-01-31 | 1.5899
2026-01-31 12:14 | 70.682 | FALSE | TRUE | -2.3503 | -3.4396 | -0.40237 | -0.56604 | 0 |  | 2026-01-31 10:00 | none | FALSE | 0 | 68.3317 | FALSE | FALSE | 0.4944 | 1.9609 | 69.708 | 10 | 0 | 0.08469 | 0.13273 | -0.63807 | 0.68817 | Confirmed/Materialized Shift | 71.0844 | 1.4153 | Day | 202601 | 2026-01-31 | 1.4153
2026-01-31 12:29 | 70.682 | FALSE | TRUE | -2.2874 | -3.3444 | -0.50884 | -0.71475 | 0 |  | 2026-01-31 10:00 | none | FALSE | 0 | 68.3946 | FALSE | FALSE | 0.4848 | 1.8983 | 69.7927 | 11 | 0 | 0.08469 | 0.13273 | -0.63807 | 0.69906 | Confirmed/Materialized Shift | 71.1908 | 1.2721 | Day | 202601 | 2026-01-31 | 1.2721
2026-01-31 12:44 | 70.9646 | FALSE | TRUE | -2.5106 | -3.6676 | -0.36447 | -0.51096 | 0.2826 |  | 2026-01-31 10:00 | none | FALSE | 0 | 68.454 | FALSE | FALSE | 0.4995 | 1.8645 | 69.8915 | 12 | 0.2826 | 0.09882 | 0.13817 | 1.3301 | 0.71877 | Confirmed/Materialized Shift | 71.3291 | 1.4929 | Day | 202601 | 2026-01-31 | 1.4929
2026-01-31 12:59 | 70.9646 | FALSE | TRUE | -2.422 | -3.5336 | -0.47351 | -0.66283 | 0 |  | 2026-01-31 10:00 | none | FALSE | 0 | 68.5426 | FALSE | FALSE | 0.4897 | 1.8246 | 69.9904 | 13 | 0 | 0.09882 | 0.13817 | -0.71522 | 0.72388 | Confirmed/Materialized Shift | 71.4381 | 1.3459 | Day | 202601 | 2026-01-31 | 1.3459
2026-01-31 13:14 | 70.9646 | FALSE | TRUE | -2.3049 | -3.3569 | -0.55401 | -0.77463 | 0 |  | 2026-01-31 10:00 | none | FALSE | 0 | 68.6597 | FALSE | FALSE | 0.4817 | 1.7818 | 70.0892 | 14 | 0 | 0.09882 | 0.13817 | -0.71522 | 0.71472 | Confirmed/Materialized Shift | 71.5186 | 1.2249 | Day | 202601 | 2026-01-31 | 1.2249
2026-01-31 13:28 | 70.9646 | FALSE | TRUE | -2.158 | -3.1364 | -0.60481 | -0.84507 | 0 |  | 2026-01-31 10:00 | none | FALSE | 0 | 68.8066 | FALSE | FALSE | 0.475 | 1.738 | 70.188 | 15 | 0 | 0.09882 | 0.13817 | -0.71522 | 0.69071 | Confirmed/Materialized Shift | 71.5694 | 1.1244 | Day | 202601 | 2026-01-31 | 1.1244
2026-01-31 13:43 | 71.2472 | FALSE | TRUE | -2.2833 | -3.3109 | -0.39081 | -0.54553 | 0.2826 |  | 2026-01-31 10:00 | none | FALSE | 0 | 68.9639 | FALSE | FALSE | 0.4944 | 1.7178 | 70.3009 | 16 | 0.2826 | 0.11295 | 0.14193 | 1.1953 | 0.66853 | Confirmed/Materialized Shift | 71.638 | 1.4154 | Day | 202601 | 2026-01-31 | 1.4154
2026-01-31 13:59 | 71.5298 | FALSE | TRUE | -2.396 | -3.4657 | -0.19239 | -0.26824 | 0.2826 |  | 2026-01-31 10:00 | none | FALSE | 0 | 69.1338 | FALSE | FALSE | 0.5135 | 1.7169 | 70.428 | 17 | 0.2826 | 0.12708 | 0.14414 | 1.0789 | 0.64709 | Confirmed/Materialized Shift | 71.7222 | 1.7027 | Day | 202601 | 2026-01-31 | 1.7027
2026-01-31 14:14 | 71.5298 | FALSE | TRUE | -2.1689 | -3.1269 | -0.21945 | -0.30586 | 0 |  | 2026-01-31 10:00 | none | FALSE | 0 | 69.3609 | FALSE | FALSE | 0.5088 | 1.7122 | 70.5551 | 18 | 0 | 0.12708 | 0.14414 | -0.88163 | 0.59708 | Confirmed/Materialized Shift | 71.7493 | 1.6325 | Day | 202601 | 2026-01-31 | 1.6325
2026-01-31 14:28 | 71.5298 | FALSE | TRUE | -1.9686 | -2.83 | -0.24507 | -0.34144 | 0 |  | 2026-01-31 10:00 | none | FALSE | 0 | 69.5612 | FALSE | FALSE | 0.5038 | 1.7041 | 70.668 | 19 | 0 | 0.11295 | 0.14193 | -0.79582 | 0.55341 | Confirmed/Materialized Shift | 71.7749 | 1.5572 | Day | 202601 | 2026-01-31 | 1.5572
2026-01-31 14:43 | 71.5298 | FALSE | TRUE | -1.8015 | -2.5837 | -0.27568 | -0.38392 | 0 |  | 2026-01-31 10:00 | none | FALSE | 0 | 69.7283 | FALSE | FALSE | 0.4979 | 1.6923 | 70.7669 | 20 | 0 | 0.09882 | 0.13817 | -0.71522 | 0.5193 | Confirmed/Materialized Shift | 71.8055 | 1.4691 | Day | 202601 | 2026-01-31 | 1.4691
2026-01-31 14:58 | 71.5298 | FALSE | TRUE | -1.6725 | -2.3942 | -0.31605 | -0.4399 | 0 |  | 2026-01-31 10:00 | none | FALSE | 0 | 69.8573 | FALSE | FALSE | 0.491 | 1.6767 | 70.8516 | 21 | 0 | 0.08469 | 0.13273 | -0.63807 | 0.49715 | Confirmed/Materialized Shift | 71.8459 | 1.3643 | Day | 202601 | 2026-01-31 | 1.3643
2026-01-31 15:13 | 71.5298 | FALSE | TRUE | -1.5827 | -2.2627 | -0.36749 | -0.51114 | 0 |  | 2026-01-31 10:00 | none | FALSE | 0 | 69.9471 | FALSE | FALSE | 0.4831 | 1.6571 | 70.9222 | 22 | 0 | 0.07065 | 0.12555 | -0.56273 | 0.48754 | Confirmed/Materialized Shift | 71.8973 | 1.2462 | Day | 202601 | 2026-01-31 | 1.2462
2026-01-31 15:28 | 71.5298 | FALSE | TRUE | -1.4702 | -2.0985 | -0.39629 | -0.55097 | 0 |  | 2026-01-31 10:00 | none | FALSE | 0 | 70.0596 | FALSE | FALSE | 0.4767 | 1.6351 | 70.9929 | 23 | 0 | 0.07065 | 0.12555 | -0.56273 | 0.46662 | Confirmed/Materialized Shift | 71.9261 | 1.1507 | Day | 202601 | 2026-01-31 | 1.1507
2026-01-31 15:43 | 71.5298 | FALSE | TRUE | -1.3991 | -1.995 | -0.43829 | -0.609 | 0 |  | 2026-01-31 10:00 | none | FALSE | 0 | 70.1307 | FALSE | FALSE | 0.4697 | 1.6106 | 71.0494 | 24 | 0 | 0.05652 | 0.11598 | -0.48734 | 0.45935 | Confirmed/Materialized Shift | 71.9681 | 1.0459 | Day | 202601 | 2026-01-31 | 1.0459
2026-01-31 15:58 | 71.5298 | FALSE | FALSE | -1.3128 | -1.8697 | -0.46504 | -0.64594 | 0 |  |  | none | FALSE | 0 | 70.217 | FALSE | FALSE | 0.0636 |  | 71.1059 | 0 | 0 | 0.05652 | 0.11598 | -0.48734 | 0.44447 | Persistence ends | 71.9948 | 0.95372 | Day | 202601 | 2026-01-31 | 0.95372
2026-01-31 16:13 | 71.5298 | FALSE | FALSE | -1.2097 | -1.7203 | -0.47495 | -0.65961 | 0 |  |  | none | FALSE | 0 | 70.3201 | FALSE | FALSE | 0.0582 |  | 71.1624 | 0 | 0 | 0.05652 | 0.11598 | -0.48734 | 0.42116 | Normal | 72.0047 | 0.8723 | Day | 202601 | 2026-01-31 | 0.8723
2026-01-31 16:28 | 71.8124 | FALSE | FALSE | -1.3886 | -1.9717 | -0.22991 | -0.31914 | 0.2826 |  |  | none | FALSE | 0 | 70.4238 | FALSE | FALSE | 0.0955 |  | 71.2331 | 0 | 0.2826 | 0.07065 | 0.12555 | 1.6882 | 0.40462 | Normal | 72.0423 | 1.4318 | Day | 202601 | 2026-01-31 | 1.4318
2026-01-31 16:43 | 71.5298 | TRUE | FALSE | -0.9569 | -1.3559 | -0.47648 | -0.66172 | -0.2826 |  |  | none | FALSE | 1 | 70.5729 | FALSE | FALSE | 0.0733 |  | 71.2896 | 0 | -0.2826 | 0.05652 | 0.14784 | -2.2938 | 0.35834 | Normal | 72.0063 | 0.67033 | Day | 202601 | 2026-01-31 | 0.67033
2026-01-31 16:58 | 71.8124 | FALSE | FALSE | -1.1591 | -1.6406 | -0.22654 | -0.31447 | 0.2826 |  |  | none | FALSE | 1 | 70.6533 | FALSE | FALSE | 0.1183 |  | 71.3461 | 0 | 0.2826 | 0.05652 | 0.14784 | 1.5292 | 0.34642 | Normal | 72.0389 | 1.346 | Day | 202601 | 2026-01-31 | 1.346
2026-01-31 17:13 | 71.5298 | FALSE | FALSE | -0.76316 | -1.0784 | -0.48056 | -0.66734 | -0.2826 |  |  | none | FALSE | 1 | 70.7666 | FALSE | FALSE | 0.0589 |  | 71.3885 | 0 | -0.2826 | 0.04239 | 0.16593 | -1.9586 | 0.31093 | Normal | 72.0104 | 0.45445 | Day | 202601 | 2026-01-31 | 0.45445
2026-01-31 17:27 | 71.8124 | FALSE | FALSE | -0.92055 | -1.2985 | -0.18579 | -0.25805 | 0.2826 |  |  | none | FALSE | 1 | 70.8918 | FALSE | FALSE | 0.1171 |  | 71.445 | 0 | 0.2826 | 0.05652 | 0.17396 | 1.2996 | 0.27659 | Normal | 71.9982 | 1.3283 | Day | 202601 | 2026-01-31 | 1.3283
2026-01-31 17:42 | 71.5298 | FALSE | FALSE | -0.56205 | -0.79198 | -0.44901 | -0.62381 | -0.2826 |  |  | none | FALSE | 1 | 70.9677 | FALSE | FALSE | 0.0435 |  | 71.4733 | 0 | -0.2826 | 0.02826 | 0.18107 | -1.7168 | 0.25277 | Normal | 71.9788 | 0.22361 | Day | 202601 | 2026-01-31 | 0.22361
2026-01-31 17:42 | 71.5298 | FALSE | FALSE | -0.47368 | -0.66662 | -0.41716 | -0.57981 | 0 |  |  | none | FALSE | 1 | 71.0561 | FALSE | FALSE | 0.037 |  | 71.5015 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.22271 | Normal | 71.947 | 0.12689 | Day | 202601 | 2026-01-31 | 0.12689
2026-01-31 17:57 | 71.5298 | FALSE | FALSE | -0.36675 | -0.51537 | -0.36675 | -0.51011 | 0 |  |  | none | FALSE | 1 | 71.163 | FALSE | FALSE | 0.0286 |  | 71.5298 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.18338 | Normal | 71.8966 | 0 | Day | 202601 | 2026-01-31 | 0
2026-01-31 18:12 | 71.5298 | FALSE | FALSE | -0.22451 | -0.31485 | -0.28103 | -0.39134 | 0 |  |  | none | FALSE | 1 | 71.3053 | FALSE | FALSE | 0.0435 |  | 71.5581 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.12638 | Normal | 71.8108 | -0.22361 | Night | 202601 | 2026-01-31 | 0.22361
2026-01-31 18:28 | 71.2472 | FALSE | FALSE | 0.058095 | 0.081473 | -0.56363 | -0.78487 | -0.2826 | 2026-02-01 12:47 | 2026-01-31 18:28 | lower | TRUE | 1 | 71.3053 | FALSE | FALSE | 0.2497 | 2.4597 | 71.5581 | 1 | -0.2826 | 0 | 0.18338 | -1.5411 | 0.12638 | Extreme triggered | 71.8108 | -2.4597 | Night | 202601 | 2026-01-31 | 2.4597
2026-01-31 18:42 | 70.9646 | FALSE | FALSE | 0.19845 | 0.27887 | -0.93195 | -1.2962 | -0.2826 |  | 2026-01-31 18:28 | lower | TRUE | 1 | 71.163 | FALSE | FALSE | 0.3483 | 2.7709 | 71.5298 | 2 | -0.2826 | -0.02826 | 0.18107 | -1.4047 | 0.18338 | Extreme/elevated | 71.8966 | -3.0822 | Night | 202601 | 2026-01-31 | 3.0822
2026-01-31 18:57 | 70.682 | FALSE | FALSE | 0.27791 | 0.39164 | -1.3329 | -1.8509 | -0.2826 |  | 2026-01-31 18:28 | lower | TRUE | 0 | 70.9599 | FALSE | TRUE | 0.375 | 2.8652 | 71.4874 | 3 | -0.2826 | -0.04239 | 0.18957 | -1.2671 | 0.26375 | Persistent | 72.0149 | -3.0537 | Night | 202601 | 2026-01-31 | 3.0537
2026-01-31 19:12 | 70.3994 | FALSE | FALSE | 0.3148 | 0.44517 | -1.7482 | -2.4231 | -0.2826 |  | 2026-01-31 18:28 | lower | TRUE | 0 | 70.7142 | FALSE | TRUE | 0.4205 | 2.8685 | 71.4309 | 4 | -0.2826 | -0.05652 | 0.19665 | -1.1497 | 0.35834 | Persistent | 72.1476 | -2.8785 | Night | 202601 | 2026-01-31 | 2.8785
2026-01-31 19:27 | 70.3994 | FALSE | FALSE | 0.12519 | 0.17751 | -1.8248 | -2.5265 | 0 |  | 2026-01-31 18:28 | lower | TRUE | 0 | 70.5246 | FALSE | TRUE | 0.4387 | 2.7537 | 71.3744 | 5 | 0 | -0.05652 | 0.19665 | 0.28742 | 0.42489 | Persistent | 72.2242 | -2.2946 | Night | 202601 | 2026-01-31 | 2.2946
2026-01-31 19:42 | 70.1168 | FALSE | FALSE | 0.17254 | 0.24547 | -2.2013 | -3.0439 | -0.2826 |  | 2026-01-31 18:28 | lower | TRUE | 0 | 70.2893 | FALSE | TRUE | 0.4989 | 2.6848 | 71.3037 | 6 | -0.2826 | -0.07065 | 0.20244 | -1.047 | 0.50719 | Persistent | 72.3181 | -2.3402 | Night | 202601 | 2026-01-31 | 2.3402
2026-01-31 19:57 | 70.1168 | FALSE | TRUE | -0.021173 | -0.030206 | -2.2537 | -3.1141 | 0 |  | 2026-01-31 18:28 | none | FALSE | 0 | 70.0956 | FALSE | FALSE | 0.5309 | 2.5817 | 71.2331 | 7 | 0 | -0.07065 | 0.20244 | 0.34899 | 0.56872 | Confirmed/Materialized Shift | 72.3705 | -1.9628 | Night | 202601 | 2026-01-31 | 1.9628
2026-01-31 20:12 | 69.836 | FALSE | TRUE | 0.025544 | 0.036564 | -2.5992 | -3.5883 | -0.2808 |  | 2026-01-31 18:28 | lower | TRUE | 0 | 69.8615 | FALSE | TRUE | 0.536 | 2.5139 | 71.1484 | 8 | -0.2808 | -0.08469 | 0.20697 | -0.94753 | 0.64342 | Confirmed/Materialized Shift | 72.4352 | -2.0397 | Night | 202601 | 2026-01-31 | 2.0397
2026-01-31 20:27 | 69.5534 | FALSE | TRUE | 0.040216 | 0.057787 | -2.9521 | -4.0716 | -0.2826 |  | 2026-01-31 18:28 | lower | TRUE | 0 | 69.5936 | FALSE | TRUE | 0.537 | 2.463 | 71.0496 | 9 | -0.2826 | -0.09882 | 0.2105 | -0.87306 | 0.72797 | Confirmed/Materialized Shift | 72.5055 | -2.0552 | Night | 202601 | 2026-01-31 | 2.0552
2026-01-31 20:41 | 69.2708 | FALSE | TRUE | 0.027639 | 0.039884 | -3.304 | -4.5525 | -0.2826 |  | 2026-01-31 18:28 | lower | TRUE | 0 | 69.2984 | FALSE | TRUE | 0.5356 | 2.42 | 70.9366 | 10 | -0.2826 | -0.11295 | 0.21299 | -0.79653 | 0.81909 | Confirmed/Materialized Shift | 72.5748 | -2.0337 | Night | 202601 | 2026-01-31 | 2.0337
2026-01-31 20:56 | 69.2708 | FALSE | TRUE | -0.21915 | -0.31736 | -3.3249 | -4.58 | 0 |  | 2026-01-31 18:28 | none | FALSE | 0 | 69.0517 | FALSE | FALSE | 0.5168 | 2.3594 | 70.8237 | 11 | 0 | -0.11295 | 0.21299 | 0.53031 | 0.886 | Confirmed/Materialized Shift | 72.5957 | -1.7527 | Night | 202601 | 2026-01-31 | 1.7527
2026-01-31 21:11 | 68.9882 | FALSE | TRUE | -0.19241 | -0.27968 | -3.5809 | -4.9345 | -0.2826 |  | 2026-01-31 18:28 | none | FALSE | 0 | 68.7958 | FALSE | FALSE | 0.5197 | 2.3124 | 70.6825 | 12 | -0.2826 | -0.14121 | 0.19443 | -0.7272 | 0.94333 | Confirmed/Materialized Shift | 72.5691 | -1.796 | Night | 202601 | 2026-01-31 | 1.796
2026-01-31 21:26 | 68.9882 | FALSE | TRUE | -0.41894 | -0.61097 | -3.5533 | -4.8983 | 0 |  | 2026-01-31 18:28 | none | FALSE | 0 | 68.5693 | FALSE | FALSE | 0.5052 | 2.2559 | 70.5554 | 13 | 0 | -0.12708 | 0.19388 | 0.65545 | 0.99306 | Confirmed/Materialized Shift | 72.5415 | -1.5781 | Night | 202601 | 2026-01-31 | 1.5781
2026-01-31 21:41 | 68.7056 | FALSE | TRUE | -0.36244 | -0.53033 | -3.7513 | -5.1773 | -0.2826 |  | 2026-01-31 18:28 | none | FALSE | 0 | 68.3432 | FALSE | FALSE | 0.5098 | 2.2125 | 70.4 | 14 | -0.2826 | -0.15534 | 0.17085 | -0.74487 | 1.0284 | Confirmed/Materialized Shift | 72.4569 | -1.6476 | Night | 202601 | 2026-01-31 | 1.6476
2026-01-31 21:56 | 68.7056 | FALSE | TRUE | -0.56397 | -0.82764 | -3.6704 | -5.0713 | 0 |  | 2026-01-31 18:28 | none | FALSE | 0 | 68.1416 | FALSE | FALSE | 0.4978 | 2.1628 | 70.2588 | 15 | 0 | -0.14121 | 0.17145 | 0.8236 | 1.0586 | Confirmed/Materialized Shift | 72.376 | -1.4672 | Night | 202601 | 2026-01-31 | 1.4672
2026-01-31 22:11 | 68.423 | FALSE | TRUE | -0.46976 | -0.6913 | -3.8025 | -5.2647 | -0.2826 |  | 2026-01-31 18:28 | none | FALSE | 0 | 67.9532 | FALSE | FALSE | 0.504 | 2.1251 | 70.0893 | 16 | -0.2826 | -0.16947 | 0.14197 | -0.79688 | 1.0681 | Confirmed/Materialized Shift | 72.2255 | -1.5602 | Night | 202601 | 2026-01-31 | 1.5602
2026-01-31 22:26 | 68.1404 | FALSE | TRUE | -0.41252 | -0.60909 | -3.9715 | -5.5074 | -0.2826 |  | 2026-01-31 18:28 | none | FALSE | 0 | 67.7279 | FALSE | FALSE | 0.5082 | 2.0956 | 69.9199 | 17 | -0.2826 | -0.16947 | 0.14197 | -0.79688 | 1.096 | Confirmed/Materialized Shift | 72.1119 | -1.6236 | Night | 202601 | 2026-01-31 | 1.6236
2026-02-01 11:17 | 65.0354 | TRUE | TRUE | 1.5869 | 2.3819 | -7.5326 | -10.3801 | -3.105 |  | 2026-01-31 18:28 | lower | TRUE | 1 | 66.6223 | FALSE | TRUE | 0.6331 | 2.1496 | 69.5952 | 18 | -3.105 | -0.32472 | 0.66844 | -4.1593 | 1.4864 | Confirmed/Materialized Shift | 72.568 | -3.0676 | Day | 202602 | 2026-02-01 | 3.0676
2026-02-01 11:17 | 65.0354 | FALSE | TRUE | 0.77336 | 1.1752 | -7.6967 | -10.5823 | 0 |  | 2026-01-31 18:28 | lower | TRUE | 1 | 65.8088 | FALSE | TRUE | 0.5917 | 2.1653 | 69.2704 | 19 | 0 | -0.32472 | 0.66844 | 0.48579 | 1.7308 | Confirmed/Materialized Shift | 72.7321 | -2.4468 | Day | 202602 | 2026-02-01 | 2.4468
2026-02-01 11:32 | 65.318 | FALSE | TRUE | -0.071797 | -0.11004 | -7.3555 | -10.1213 | 0.2826 |  | 2026-01-31 18:28 | none | FALSE | 1 | 65.2462 | FALSE | FALSE | 0.5593 | 2.1551 | 68.9599 | 20 | 0.2826 | -0.31059 | 0.67858 | 0.87417 | 1.8568 | Confirmed/Materialized Shift | 72.6735 | -1.9613 | Day | 202602 | 2026-02-01 | 1.9613
2026-02-01 11:47 | 65.6006 | FALSE | TRUE | -0.76102 | -1.1737 | -6.9149 | -9.5357 | 0.2826 |  | 2026-01-31 18:28 | none | FALSE | 1 | 64.8396 | FALSE | FALSE | 0.5355 | 2.1288 | 68.6775 | 21 | 0.2826 | -0.28233 | 0.69145 | 0.81702 | 1.919 | Confirmed/Materialized Shift | 72.5155 | -1.6034 | Day | 202602 | 2026-02-01 | 1.6034
2026-02-01 12:03 | 65.8832 | FALSE | TRUE | -1.3328 | -2.0648 | -6.4133 | -8.8708 | 0.2826 |  | 2026-01-31 18:28 | none | FALSE | 1 | 64.5504 | FALSE | FALSE | 0.516 | 2.0917 | 68.4235 | 22 | 0.2826 | -0.25407 | 0.7029 | 0.76351 | 1.9365 | Confirmed/Materialized Shift | 72.2965 | -1.3118 | Day | 202602 | 2026-02-01 | 1.3118
2026-02-01 12:17 | 65.8832 | FALSE | TRUE | -1.5782 | -2.4542 | -6.1788 | -8.5743 | 0 |  | 2026-01-31 18:28 | none | FALSE | 1 | 64.305 | FALSE | FALSE | 0.5077 | 2.0523 | 68.1835 | 23 | 0 | -0.23994 | 0.70513 | 0.34028 | 1.9393 | Confirmed/Materialized Shift | 72.062 | -1.1862 | Day | 202602 | 2026-02-01 | 1.1862
2026-02-01 12:32 | 65.8832 | FALSE | TRUE | -1.7866 | -2.7874 | -5.9356 | -8.2647 | 0 |  | 2026-01-31 18:28 | none | FALSE | 1 | 64.0966 | FALSE | FALSE | 0.5002 | 2.0116 | 67.9577 | 24 | 0 | -0.22581 | 0.70706 | 0.31937 | 1.9306 | Confirmed/Materialized Shift | 71.8188 | -1.0746 | Day | 202602 | 2026-02-01 | 1.0746
2026-02-01 12:47 | 65.8832 | FALSE | FALSE | -1.9387 | -3.0319 | -5.6361 | -7.8805 | 0 |  |  | none | FALSE | 1 | 63.9445 | FALSE | FALSE | 0.0937 |  | 67.7319 | 0 | 0 | -0.22581 | 0.70706 | 0.31937 | 1.8937 | Persistence ends | 71.5193 | -0.97623 | Day | 202602 | 2026-02-01 | 0.97623
2026-02-01 13:02 | 66.164 | FALSE | FALSE | -2.304 | -3.6079 | -5.0445 | -7.0841 | 0.2808 |  |  | none | FALSE | 1 | 63.86 | FALSE | FALSE | 0.0783 |  | 67.5343 | 0 | 0.2808 | -0.19764 | 0.71585 | 0.66836 | 1.8371 | Normal | 71.2085 | -0.74586 | Day | 202602 | 2026-02-01 | 0.74586
2026-02-01 13:04 | 66.164 | FALSE | FALSE | -2.3384 | -3.6637 | -4.6836 | -6.6108 | 0 |  |  | none | FALSE | 1 | 63.8256 | FALSE | FALSE | 0.0731 |  | 67.3366 | 0 | 0 | -0.19764 | 0.71585 | 0.27609 | 1.7555 | Normal | 70.8476 | -0.66797 | Day | 202602 | 2026-02-01 | 0.66797
2026-02-01 13:04 | 66.164 | FALSE | FALSE | -2.3515 | -3.6851 | -4.3296 | -6.1418 | 0 |  |  | none | FALSE | 0 | 63.8125 | FALSE | FALSE | 0.0395 |  | 67.153 | 0 | 0 | -0.1836 | 0.71688 | 0.25611 | 1.6703 | Normal | 70.4936 | -0.59212 | Day | 202602 | 2026-02-01 | 0.59212
2026-02-01 13:41 | 66.7292 | FALSE | FALSE | -2.8638 | -4.4842 | -3.429 | -4.8876 | 0.5652 |  |  | none | FALSE | 0 | 63.8654 | FALSE | FALSE | 0.012 |  | 67.0118 | 0 | 0.5652 | -0.14121 | 0.73554 | 0.96039 | 1.5732 | Normal | 70.1582 | -0.17963 | Day | 202602 | 2026-02-01 | 0.17963
2026-02-01 13:56 | 67.0118 | FALSE | FALSE | -3.0747 | -4.809 | -2.8488 | -4.0779 | 0.2826 |  |  | none | FALSE | 0 | 63.9371 | FALSE | FALSE | 0.0051 |  | 66.8988 | 0 | 0.2826 | -0.11295 | 0.74066 | 0.53405 | 1.4809 | Normal | 69.8606 | 0.076272 | Day | 202602 | 2026-02-01 | 0.076272
2026-02-01 14:11 | 67.0118 | FALSE | FALSE | -2.9712 | -4.6395 | -2.5194 | -3.6234 | 0 |  |  | none | FALSE | 0 | 64.0406 | FALSE | FALSE | 0.011 |  | 66.7859 | 0 | 0 | -0.11295 | 0.74066 | 0.1525 | 1.3726 | Normal | 69.5312 | 0.16457 | Day | 202602 | 2026-02-01 | 0.16457
2026-02-01 14:26 | 67.0118 | FALSE | FALSE | -2.8713 | -4.4766 | -2.2219 | -3.2092 | 0 |  |  | none | FALSE | 0 | 64.1405 | FALSE | FALSE | 0.017 |  | 66.6871 | 0 | 0 | -0.09882 | 0.73995 | 0.13355 | 1.2733 | Normal | 69.2337 | 0.25502 | Day | 202602 | 2026-02-01 | 0.25502
2026-02-01 14:41 | 67.2944 | FALSE | FALSE | -3.0196 | -4.698 | -1.6356 | -2.3729 | 0.2826 |  |  | none | FALSE | 0 | 64.2748 | FALSE | FALSE | 0.0396 |  | 66.6024 | 0 | 0.2826 | -0.08469 | 0.74462 | 0.49326 | 1.1638 | Normal | 68.93 | 0.59461 | Day | 202602 | 2026-02-01 | 0.59461
2026-02-01 14:56 | 67.2944 | FALSE | FALSE | -2.8995 | -4.5027 | -1.3743 | -2.0014 | 0 |  |  | none | FALSE | 0 | 64.3949 | FALSE | FALSE | 0.0476 |  | 66.5318 | 0 | 0 | -0.07056 | 0.74335 | 0.094922 | 1.0685 | Normal | 68.6687 | 0.71371 | Day | 202602 | 2026-02-01 | 0.71371
2026-02-01 15:11 | 67.2944 | FALSE | FALSE | -2.7497 | -4.2601 | -1.0834 | -1.5844 | 0 |  |  | none | FALSE | 0 | 64.5447 | FALSE | FALSE | 0.058 |  | 66.4613 | 0 | 0 | -0.07056 | 0.74335 | 0.094922 | 0.95826 | Normal | 68.3778 | 0.86942 | Day | 202602 | 2026-02-01 | 0.86942
2026-02-01 15:26 | 67.577 | FALSE | FALSE | -2.9236 | -4.522 | -0.60759 | -0.89109 | 0.2826 |  |  | none | FALSE | 0 | 64.6534 | FALSE | FALSE | 0.0875 |  | 66.419 | 0 | 0.2826 | -0.0423 | 0.7456 | 0.43575 | 0.88281 | Normal | 68.1846 | 1.3118 | Day | 202602 | 2026-02-01 | 1.3118
2026-02-01 15:40 | 67.577 | FALSE | FALSE | -2.8513 | -4.4052 | -0.47889 | -0.70368 | 0 |  |  | none | FALSE | 0 | 64.7257 | FALSE | FALSE | 0.095 |  | 66.3908 | 0 | 0 | -0.02817 | 0.74349 | 0.037889 | 0.83255 | Normal | 68.0559 | 1.4248 | Day | 202602 | 2026-02-01 | 1.4248
2026-02-01 15:55 | 67.577 | FALSE | FALSE | -2.6759 | -4.1231 | -0.55767 | -0.81848 | 0 |  |  | none | FALSE | 0 | 64.9011 | FALSE | FALSE | 0.0873 |  | 66.5179 | 0 | 0 | 0.12708 | 0.17083 | -0.74389 | 0.80839 | Normal | 68.1347 | 1.3102 | Day | 202602 | 2026-02-01 | 1.3102
2026-02-01 16:10 | 67.577 | FALSE | FALSE | -2.455 | -3.7699 | -0.59094 | -0.86689 | 0 |  |  | none | FALSE | 0 | 65.122 | FALSE | FALSE | 0.0816 |  | 66.645 | 0 | 0 | 0.12708 | 0.17083 | -0.74389 | 0.76149 | Normal | 68.1679 | 1.224 | Day | 202602 | 2026-02-01 | 1.224
2026-02-01 16:26 | 67.8596 | FALSE | FALSE | -2.5679 | -3.933 | -0.39277 | -0.57547 | 0.2826 |  |  | none | FALSE | 0 | 65.2917 | FALSE | FALSE | 0.098 |  | 66.772 | 0 | 0.2826 | 0.12708 | 0.17083 | 0.91037 | 0.74017 | Normal | 68.2524 | 1.4693 | Day | 202602 | 2026-02-01 | 1.4693
2026-02-01 16:40 | 67.8596 | FALSE | FALSE | -2.423 | -3.7028 | -0.47376 | -0.69331 | 0 |  |  | none | FALSE | 0 | 65.4366 | FALSE | FALSE | 0.0897 |  | 66.885 | 0 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.72418 | Normal | 68.3334 | 1.3458 | Day | 202602 | 2026-02-01 | 1.3458
2026-02-01 16:55 | 67.8596 | FALSE | FALSE | -2.3059 | -3.5176 | -0.55437 | -0.81031 | 0 |  |  | none | FALSE | 0 | 65.5537 | FALSE | FALSE | 0.0816 |  | 66.9838 | 0 | 0 | 0.09882 | 0.16582 | -0.59594 | 0.71508 | Normal | 68.414 | 1.2247 | Day | 202602 | 2026-02-01 | 1.2247
2026-02-01 17:10 | 67.8596 | FALSE | FALSE | -2.1592 | -3.2865 | -0.6053 | -0.88411 | 0 |  |  | none | FALSE | 0 | 65.7004 | FALSE | FALSE | 0.0749 |  | 67.0826 | 0 | 0 | 0.09882 | 0.16582 | -0.59594 | 0.69114 | Normal | 68.4649 | 1.1242 | Day | 202602 | 2026-02-01 | 1.1242
2026-02-01 17:25 | 67.577 | FALSE | FALSE | -1.686 | -2.5588 | -0.86667 | -1.2663 | -0.2826 |  |  | none | FALSE | 0 | 65.891 | FALSE | FALSE | 0.0428 |  | 67.1673 | 0 | -0.2826 | 0.08469 | 0.18555 | -1.9794 | 0.63817 | Normal | 68.4437 | 0.64196 | Day | 202602 | 2026-02-01 | 0.64196
2026-02-01 17:30 | 67.8596 | FALSE | FALSE | -1.7518 | -2.6499 | -0.56486 | -0.82552 | 0.2826 |  |  | none | FALSE | 0 | 66.1078 | FALSE | FALSE | 0.0683 |  | 67.2661 | 0 | 0.2826 | 0.09882 | 0.18948 | 0.96991 | 0.57916 | Normal | 68.4245 | 1.0247 | Day | 202602 | 2026-02-01 | 1.0247
2026-02-01 18:02 | 67.2944 | TRUE | FALSE | -1.0074 | -1.5198 | -1.064 | -1.5565 | -0.5652 |  |  | none | FALSE | 1 | 66.287 | FALSE | FALSE | 0.0322 |  | 67.3227 | 0 | -0.5652 | 0.05652 | 0.23555 | -2.6394 | 0.51785 | Normal | 68.3584 | -0.054572 | Day | 202602 | 2026-02-01 | 0.054572
2026-02-02 11:31 | 65.0354 | TRUE | FALSE | 0.86042 | 1.3057 | -3.6012 | -5.2468 | -2.259 | 2026-02-02 12:46 | 2026-02-02 11:31 | lower | TRUE | 2 | 65.8958 | TRUE | FALSE | 0.3313 | 3.2557 | 67.2662 | 1 | -2.259 | -0.05643 | 0.56928 | -3.8691 | 0.68521 | Extreme triggered | 68.6366 | -3.2557 | Day | 202602 | 2026-02-02 | 3.2557
2026-02-02 11:31 | 65.0354 | FALSE | FALSE | 0.54451 | 0.83029 | -3.8043 | -5.5263 | 0 |  | 2026-02-02 11:31 | lower | TRUE | 2 | 65.5799 | FALSE | FALSE | 0.3493 | 2.9619 | 67.2098 | 2 | 0 | -0.05643 | 0.56928 | 0.099126 | 0.81495 | Extreme/elevated | 68.8397 | -2.6681 | Day | 202602 | 2026-02-02 | 2.6681
2026-02-02 11:46 | 65.318 | FALSE | FALSE | -0.0064409 | -0.0098619 | -3.6489 | -5.2908 | 0.2826 |  | 2026-02-02 11:31 | none | FALSE | 2 | 65.3116 | FALSE | FALSE | 0.3614 | 2.6389 | 67.1392 | 3 | 0.2826 | -0.07056 | 0.5564 | 0.63473 | 0.91384 | Persistent | 68.9669 | -1.993 | Day | 202602 | 2026-02-02 | 1.993
2026-02-02 12:01 | 65.8832 | FALSE | FALSE | -0.71238 | -1.0931 | -3.1116 | -4.5099 | 0.5652 |  | 2026-02-02 11:31 | none | FALSE | 2 | 65.1708 | FALSE | FALSE | 0.3694 | 2.2929 | 67.0828 | 4 | 0.5652 | -0.05643 | 0.56928 | 1.092 | 0.956 | Persistent | 68.9948 | -1.2548 | Day | 202602 | 2026-02-02 | 1.2548
2026-02-02 12:16 | 65.8832 | FALSE | FALSE | -0.84283 | -1.2958 | -3.1292 | -4.5342 | 0 |  | 2026-02-02 11:31 | none | FALSE | 2 | 65.0404 | FALSE | FALSE | 0.4196 | 2.0646 | 67.0264 | 5 | 0 | -0.05643 | 0.56928 | 0.099126 | 0.993 | Persistent | 69.0124 | -1.1512 | Day | 202602 | 2026-02-02 | 1.1512
2026-02-02 12:31 | 65.8832 | FALSE | FALSE | -0.96408 | -1.485 | -3.1376 | -4.5458 | 0 |  | 2026-02-02 11:31 | none | FALSE | 2 | 64.9191 | FALSE | FALSE | 0.4707 | 1.8971 | 66.9699 | 6 | 0 | -0.05643 | 0.56928 | 0.099126 | 1.0254 | Persistent | 69.0208 | -1.0598 | Day | 202602 | 2026-02-02 | 1.0598
2026-02-02 12:46 | 66.164 | FALSE | FALSE | -1.3259 | -2.045 | -2.8248 | -4.0945 | 0.2808 |  |  | none | FALSE | 2 | 64.8381 | FALSE | FALSE | 0.1053 |  | 66.9134 | 0 | 0.2808 | -0.05652 | 0.56922 | 0.5926 | 1.0377 | Persistence ends | 68.9888 | -0.72222 | Day | 202602 | 2026-02-02 | 0.72222
2026-02-02 13:01 | 66.164 | FALSE | FALSE | -1.4002 | -2.1621 | -2.7861 | -4.0407 | 0 |  |  | none | FALSE | 2 | 64.7638 | FALSE | FALSE | 0.1013 |  | 66.8569 | 0 | 0 | -0.05652 | 0.56922 | 0.099293 | 1.0466 | Normal | 68.9501 | -0.66207 | Day | 202602 | 2026-02-02 | 0.66207
2026-02-02 13:16 | 66.4466 | FALSE | FALSE | -1.7223 | -2.6609 | -2.4581 | -3.5674 | 0.2826 |  |  | none | FALSE | 2 | 64.7243 | FALSE | FALSE | 0.0806 |  | 66.8145 | 0 | 0.2826 | -0.04239 | 0.57418 | 0.566 | 1.0451 | Normal | 68.9047 | -0.35205 | Day | 202602 | 2026-02-02 | 0.35205
2026-02-02 13:30 | 66.7292 | FALSE | FALSE | -2.0163 | -3.1158 | -2.1022 | -3.0541 | 0.2826 |  |  | none | FALSE | 1 | 64.7129 | FALSE | FALSE | 0.0314 |  | 66.7721 | 0 | 0.2826 | -0.04239 | 0.57418 | 0.566 | 1.0296 | Normal | 68.8314 | -0.041695 | Day | 202602 | 2026-02-02 | 0.041695
2026-02-02 13:45 | 66.7292 | FALSE | FALSE | -2.0235 | -3.1273 | -2.0246 | -2.9447 | 0 |  |  | none | FALSE | 0 | 64.7057 | FALSE | FALSE | 0 |  | 66.7297 | 0 | 0 | -0.04239 | 0.57418 | 0.073826 | 1.012 | Normal | 68.7538 | -0.00053358 | Day | 202602 | 2026-02-02 | 0.00053358
2026-02-02 14:00 | 66.7292 | FALSE | FALSE | -2.0263 | -3.1317 | -1.9426 | -2.8289 | 0 |  |  | none | FALSE | 0 | 64.7029 | FALSE | FALSE | 0.0028 |  | 66.6873 | 0 | 0 | -0.04239 | 0.57418 | 0.073826 | 0.99224 | Normal | 68.6718 | 0.042177 | Day | 202602 | 2026-02-02 | 0.042177
2026-02-02 14:15 | 67.0118 | FALSE | FALSE | -2.2996 | -3.5536 | -1.5942 | -2.3237 | 0.2826 |  |  | none | FALSE | 0 | 64.7122 | FALSE | FALSE | 0.0242 |  | 66.6591 | 0 | 0.2826 | -0.02826 | 0.57874 | 0.53713 | 0.97344 | Normal | 68.606 | 0.36233 | Day | 202602 | 2026-02-02 | 0.36233
2026-02-02 14:30 | 67.0118 | FALSE | FALSE | -2.2674 | -3.5021 | -1.4772 | -2.1569 | 0 |  |  | none | FALSE | 0 | 64.7444 | FALSE | FALSE | 0.0281 |  | 66.6167 | 0 | 0 | -0.04239 | 0.57418 | 0.073826 | 0.93616 | Normal | 68.489 | 0.42205 | Day | 202602 | 2026-02-02 | 0.42205
2026-02-02 14:45 | 67.2944 | FALSE | FALSE | -2.5153 | -3.8829 | -1.1034 | -1.6132 | 0.2826 |  |  | none | FALSE | 0 | 64.7791 | FALSE | FALSE | 0.052 |  | 66.5884 | 0 | 0.2826 | -0.02826 | 0.57874 | 0.53713 | 0.90466 | Normal | 68.3978 | 0.78036 | Day | 202602 | 2026-02-02 | 0.78036
2026-02-02 15:00 | 67.2944 | FALSE | FALSE | -2.4764 | -3.8205 | -1.0079 | -1.4757 | 0 |  |  | none | FALSE | 0 | 64.818 | FALSE | FALSE | 0.0562 |  | 66.5602 | 0 | 0 | -0.02826 | 0.57874 | 0.04883 | 0.87107 | Normal | 68.3023 | 0.8429 | Day | 202602 | 2026-02-02 | 0.8429
2026-02-02 15:15 | 67.577 | FALSE | FALSE | -2.7328 | -4.2145 | -0.67093 | -0.98307 | 0.2826 |  |  | none | FALSE | 0 | 64.8442 | FALSE | FALSE | 0.0808 |  | 66.546 | 0 | 0.2826 | -0.01413 | 0.5829 | 0.50906 | 0.85094 | Normal | 68.2479 | 1.2115 | Day | 202602 | 2026-02-02 | 1.2115
2026-02-02 15:30 | 67.577 | FALSE | FALSE | -2.7328 | -4.2145 | -0.67093 | -0.98307 | 0 |  |  | none | FALSE | 0 | 64.8442 | FALSE | FALSE | 0.0808 |  | 66.546 | 0 | 0 | 0 | 0.57947 | 0 | 0.85094 | Normal | 68.2479 | 1.2115 | Day | 202602 | 2026-02-02 | 1.2115
2026-02-02 15:45 | 67.8596 | FALSE | FALSE | -3.0154 | -4.6503 | -0.38833 | -0.569 | 0.2826 |  |  | none | FALSE | 0 | 64.8442 | FALSE | FALSE | 0.1029 |  | 66.546 | 0 | 0.2826 | 0 | 0.57947 | 0.48769 | 0.85094 | Normal | 68.2479 | 1.5436 | Day | 202602 | 2026-02-02 | 1.5436
2026-02-02 16:00 | 67.8596 | FALSE | FALSE | -3.0568 | -4.7171 | -0.48625 | -0.71146 | 0 |  |  | none | FALSE | 0 | 64.8028 | FALSE | FALSE | 0.0967 |  | 66.5743 | 0 | 0 | 0.02826 | 0.56403 | -0.050104 | 0.88577 | Normal | 68.3459 | 1.451 | Day | 202602 | 2026-02-02 | 1.451
2026-02-02 16:15 | 67.8596 | FALSE | FALSE | -2.8481 | -4.3809 | -0.55992 | -0.81836 | 0 |  |  | none | FALSE | 0 | 65.0115 | FALSE | FALSE | 0.0895 |  | 66.7155 | 0 | 0 | 0.14121 | 0.17145 | -0.8236 | 0.852 | Normal | 68.4195 | 1.3428 | Day | 202602 | 2026-02-02 | 1.3428
2026-02-02 16:29 | 68.1404 | FALSE | FALSE | -2.893 | -4.4339 | -0.35373 | -0.51643 | 0.2808 |  |  | none | FALSE | 0 | 65.2474 | FALSE | FALSE | 0.1043 |  | 66.8708 | 0 | 0.2808 | 0.15525 | 0.17078 | 0.73517 | 0.81168 | Normal | 68.4941 | 1.5642 | Day | 202602 | 2026-02-02 | 1.5642
2026-02-02 16:44 | 68.1404 | FALSE | FALSE | -2.6723 | -4.0818 | -0.41525 | -0.60571 | 0 |  |  | none | FALSE | 0 | 65.4681 | FALSE | FALSE | 0.0975 |  | 67.0119 | 0 | 0 | 0.14112 | 0.17138 | -0.82345 | 0.77188 | Normal | 68.5557 | 1.462 | Day | 202602 | 2026-02-02 | 1.462
2026-02-02 16:59 | 68.1404 | FALSE | FALSE | -2.5419 | -3.875 | -0.51061 | -0.74378 | 0 |  |  | none | FALSE | 0 | 65.5985 | FALSE | FALSE | 0.0887 |  | 67.1248 | 0 | 0 | 0.11286 | 0.14182 | -0.79582 | 0.76313 | Normal | 68.651 | 1.3309 | Day | 202602 | 2026-02-02 | 1.3309
2026-02-02 17:15 | 68.423 | FALSE | FALSE | -2.6852 | -4.0847 | -0.34264 | -0.49827 | 0.2826 |  |  | none | FALSE | 0 | 65.7378 | FALSE | FALSE | 0.1032 |  | 67.2517 | 0 | 0.2826 | 0.12699 | 0.14404 | 1.0803 | 0.75695 | Normal | 68.7656 | 1.5473 | Day | 202602 | 2026-02-02 | 1.5473
2026-02-02 17:29 | 68.1404 | TRUE | FALSE | -2.1936 | -3.3264 | -0.64202 | -0.93341 | -0.2826 |  |  | none | FALSE | 1 | 65.9468 | FALSE | FALSE | 0.1015 |  | 67.3646 | 0 | -0.2826 | 0.11286 | 0.16887 | -2.3417 | 0.70891 | Normal | 68.7824 | 1.0944 | Day | 202602 | 2026-02-02 | 1.0944
2026-02-02 17:29 | 68.423 | FALSE | FALSE | -2.3198 | -3.5094 | -0.42892 | -0.62295 | 0.2826 |  |  | none | FALSE | 1 | 66.1032 | FALSE | FALSE | 0.1203 |  | 67.4775 | 0 | 0.2826 | 0.11295 | 0.16897 | 1.004 | 0.68718 | Normal | 68.8519 | 1.3758 | Day | 202602 | 2026-02-02 | 1.3758
2026-02-02 17:44 | 68.423 | FALSE | FALSE | -2.121 | -3.1989 | -0.45595 | -0.66196 | 0 |  |  | none | FALSE | 1 | 66.302 | FALSE | FALSE | 0.1147 |  | 67.5905 | 0 | 0 | 0.11295 | 0.16897 | -0.66847 | 0.64423 | Normal | 68.879 | 1.2922 | Day | 202602 | 2026-02-02 | 1.2922
2026-02-02 18:00 | 68.423 | FALSE | FALSE | -1.9541 | -2.9399 | -0.48674 | -0.70634 | 0 |  |  | none | FALSE | 1 | 66.4689 | FALSE | FALSE | 0.1087 |  | 67.6893 | 0 | 0 | 0.09882 | 0.16582 | -0.59594 | 0.61021 | Normal | 68.9097 | 1.2023 | Day | 202602 | 2026-02-02 | 1.2023
2026-02-02 18:15 | 68.1404 | FALSE | FALSE | -1.5282 | -2.2942 | -0.76718 | -1.1134 | -0.2826 |  |  | none | FALSE | 1 | 66.6122 | FALSE | FALSE | 0.0728 |  | 67.7599 | 0 | -0.2826 | 0.07056 | 0.18038 | -1.9579 | 0.57385 | Normal | 68.9076 | 0.6631 | Night | 202602 | 2026-02-02 | 0.6631
2026-02-02 18:29 | 68.1404 | FALSE | FALSE | -1.3602 | -2.0369 | -0.74033 | -1.0748 | 0 |  |  | none | FALSE | 1 | 66.7802 | FALSE | FALSE | 0.0679 |  | 67.8304 | 0 | 0 | 0.07056 | 0.18038 | -0.39118 | 0.52514 | Normal | 68.8807 | 0.59024 | Night | 202602 | 2026-02-02 | 0.59024
2026-02-02 18:30 | 68.1404 | FALSE | FALSE | -1.1598 | -1.7315 | -0.68095 | -0.98945 | 0 |  |  | none | FALSE | 1 | 66.9806 | FALSE | FALSE | 0.0633 |  | 67.901 | 0 | 0 | 0.07056 | 0.18038 | -0.39118 | 0.46018 | Normal | 68.8214 | 0.52023 | Night | 202602 | 2026-02-02 | 0.52023
2026-02-03 11:44 | 67.0118 | TRUE | FALSE | -0.031154 | -0.046512 | -1.8096 | -2.6293 | -1.1286 |  |  | none | FALSE | 2 | 66.9806 | TRUE | FALSE | 0.186 |  | 67.901 | 0 | -1.1286 | 0 | 0.31719 | -3.5581 | 0.46018 | Normal | 68.8214 | -1.9323 | Day | 202602 | 2026-02-03 | 1.9323
2026-02-03 11:44 | 67.0118 | FALSE | FALSE | -0.031154 | -0.046512 | -1.8096 | -2.6293 | 0 |  |  | none | FALSE | 2 | 66.9806 | FALSE | FALSE | 0.186 |  | 67.901 | 0 | 0 | 0 | 0.31719 | 0 | 0.46018 | Normal | 68.8214 | -1.9323 | Day | 202602 | 2026-02-03 | 1.9323
2026-02-03 11:59 | 67.2944 | FALSE | FALSE | -0.31375 | -0.46843 | -1.527 | -2.2187 | 0.2826 |  |  | none | FALSE | 2 | 66.9806 | FALSE | FALSE | 0.145 |  | 67.901 | 0 | 0.2826 | 0 | 0.31719 | 0.89094 | 0.46018 | Normal | 68.8214 | -1.3182 | Day | 202602 | 2026-02-03 | 1.3182
2026-02-03 12:14 | 67.577 | FALSE | FALSE | -0.55116 | -0.82232 | -1.2274 | -1.7839 | 0.2826 |  |  | none | FALSE | 1 | 67.0258 | FALSE | FALSE | 0.0793 |  | 67.9151 | 0 | 0.2826 | 0.01413 | 0.32343 | 0.83008 | 0.44465 | Normal | 68.8044 | -0.76045 | Day | 202602 | 2026-02-03 | 0.76045
2026-02-03 12:29 | 68.1404 | FALSE | FALSE | -1.0769 | -1.6059 | -0.68274 | -0.99202 | 0.5634 |  |  | none | FALSE | 1 | 67.0635 | FALSE | FALSE | 0.0584 |  | 67.9433 | 0 | 0.5634 | 0.02817 | 0.3413 | 1.5682 | 0.43992 | Normal | 68.8231 | 0.44804 | Day | 202602 | 2026-02-03 | 0.44804
2026-02-03 12:43 | 68.1404 | FALSE | FALSE | -1.0354 | -1.5429 | -0.6975 | -1.0133 | 0 |  |  | none | FALSE | 1 | 67.105 | FALSE | FALSE | 0.0546 |  | 67.9715 | 0 | 0 | 0.02817 | 0.3413 | -0.082538 | 0.43322 | Normal | 68.8379 | 0.38994 | Day | 202602 | 2026-02-03 | 0.38994
2026-02-03 12:58 | 68.423 | FALSE | FALSE | -1.3109 | -1.9532 | -0.46414 | -0.67377 | 0.2826 |  |  | none | FALSE | 1 | 67.1121 | FALSE | FALSE | 0.0922 |  | 67.9996 | 0 | 0.2826 | 0.02817 | 0.3413 | 0.74548 | 0.44375 | Normal | 68.8871 | 0.95405 | Day | 202602 | 2026-02-03 | 0.95405
2026-02-03 13:13 | 68.7056 | FALSE | FALSE | -1.6022 | -2.3877 | -0.27491 | -0.39853 | 0.2826 |  |  | none | FALSE | 1 | 67.1034 | FALSE | FALSE | 0.1229 |  | 68.0419 | 0 | 0.2826 | 0.0423 | 0.34589 | 0.69473 | 0.46928 | Normal | 68.9805 | 1.4142 | Day | 202602 | 2026-02-03 | 1.4142
2026-02-03 13:28 | 68.7056 | FALSE | FALSE | -1.6007 | -2.3854 | -0.35798 | -0.51833 | 0 |  |  | none | FALSE | 1 | 67.1049 | FALSE | FALSE | 0.1132 |  | 68.0842 | 0 | 0 | 0.0423 | 0.34589 | -0.12229 | 0.48967 | Normal | 69.0636 | 1.2689 | Day | 202602 | 2026-02-03 | 1.2689
2026-02-03 13:43 | 68.9882 | FALSE | FALSE | -1.9212 | -2.8647 | -0.1981 | -0.28633 | 0.2826 |  |  | none | FALSE | 1 | 67.067 | FALSE | FALSE | 0.137 |  | 68.1266 | 0 | 0.2826 | 0.04239 | 0.34595 | 0.69434 | 0.52984 | Normal | 69.1863 | 1.6261 | Day | 202602 | 2026-02-03 | 1.6261
2026-02-03 13:58 | 68.9882 | FALSE | FALSE | -1.9468 | -2.9039 | -0.30846 | -0.44513 | 0 |  |  | none | FALSE | 0 | 67.0414 | FALSE | FALSE | 0.0969 |  | 68.169 | 0 | 0 | 0.04239 | 0.34595 | -0.12253 | 0.56382 | Normal | 69.2967 | 1.4529 | Day | 202602 | 2026-02-03 | 1.4529
2026-02-03 14:13 | 69.5534 | FALSE | FALSE | -2.5998 | -3.8829 | 0.027705 | 0.039849 | 0.5652 | 2026-02-03 17:10 | 2026-02-03 14:13 | upper | TRUE | 0 | 66.9536 | FALSE | FALSE | 0.1933 | 2.0431 | 68.2397 | 1 | 0.5652 | 0.07065 | 0.36488 | 1.3554 | 0.64301 | Extreme triggered | 69.5257 | 2.0431 | Day | 202602 | 2026-02-03 | 2.0431
2026-02-03 15:35 | 70.3994 | FALSE | FALSE | -3.6695 | -5.4991 | 0.45229 | 0.64662 | 0.846 |  | 2026-02-03 14:13 | upper | TRUE | 0 | 66.7299 | FALSE | FALSE | 0.2851 | 2.3027 | 68.3385 | 2 | 0.846 | 0.09882 | 0.40196 | 1.8588 | 0.80431 | Extreme/elevated | 69.9471 | 2.5623 | Day | 202602 | 2026-02-03 | 2.5623
2026-02-03 16:13 | 70.682 | FALSE | FALSE | -4.1315 | -6.2081 | 0.30133 | 0.42814 | 0.2826 |  | 2026-02-03 14:13 | upper | TRUE | 0 | 66.5505 | FALSE | TRUE | 0.3257 | 2.3067 | 68.4656 | 3 | 0.2826 | 0.12708 | 0.39352 | 0.39521 | 0.95755 | Persistent | 70.3807 | 2.3147 | Day | 202602 | 2026-02-03 | 2.3147
2026-02-03 16:13 | 70.682 | FALSE | FALSE | -4.2593 | -6.4125 | -0.052382 | -0.074054 | 0 |  | 2026-02-03 14:13 | none | FALSE | 0 | 66.4227 | FALSE | FALSE | 0.3587 | 2.2179 | 68.5785 | 4 | 0 | 0.11295 | 0.39271 | -0.28762 | 1.0779 | Persistent | 70.7344 | 1.9514 | Day | 202602 | 2026-02-03 | 1.9514
2026-02-03 16:46 | 70.682 | FALSE | FALSE | -4.3401 | -6.542 | -0.35903 | -0.50538 | 0 |  | 2026-02-03 14:13 | none | FALSE | 0 | 66.3419 | FALSE | FALSE | 0.3987 | 2.1132 | 68.6915 | 5 | 0 | 0.11295 | 0.39271 | -0.28762 | 1.1748 | Persistent | 71.041 | 1.6944 | Day | 202602 | 2026-02-03 | 1.6944
2026-02-03 16:46 | 70.682 | FALSE | FALSE | -4.3847 | -6.6137 | -0.62955 | -0.88281 | 0 |  | 2026-02-03 14:13 | none | FALSE | 0 | 66.2973 | FALSE | FALSE | 0.4427 | 2.0106 | 68.8044 | 6 | 0 | 0.11295 | 0.39271 | -0.28762 | 1.2536 | Persistent | 71.3115 | 1.4978 | Day | 202602 | 2026-02-03 | 1.4978
2026-02-03 17:07 | 70.3994 | FALSE | TRUE | -4.0656 | -6.129 | -1.1015 | -1.5406 | -0.2826 |  | 2026-02-03 14:13 | none | FALSE | 0 | 66.3338 | FALSE | FALSE | 0.4765 | 1.8873 | 68.9174 | 7 | -0.2826 | 0.11295 | 0.39271 | -1.0072 | 1.2918 | Confirmed/Materialized Shift | 71.5009 | 1.1473 | Day | 202602 | 2026-02-03 | 1.1473
2026-02-03 17:07 | 70.3994 | FALSE | TRUE | -4.0066 | -6.0346 | -1.2684 | -1.7698 | 0 |  | 2026-02-03 14:13 | none | FALSE | 0 | 66.3928 | FALSE | FALSE | 0.4692 | 1.7811 | 69.0303 | 8 | 0 | 0.11295 | 0.39271 | -0.28762 | 1.3187 | Confirmed/Materialized Shift | 71.6678 | 1.0382 | Day | 202602 | 2026-02-03 | 1.0382
2026-02-03 17:10 | 70.3994 | FALSE | FALSE | -3.9264 | -5.9068 | -1.4142 | -1.9692 | 0 |  |  | none | FALSE | 0 | 66.473 | FALSE | FALSE | 0.0627 |  | 69.1433 | 0 | 0 | 0.11295 | 0.39271 | -0.28762 | 1.3351 | Persistence ends | 71.8136 | 0.94082 | Day | 202602 | 2026-02-03 | 0.94082
2026-02-03 18:46 | 70.1168 | FALSE | FALSE | -3.3227 | -4.9745 | -1.6861 | -2.3483 | -0.2826 |  |  | none | FALSE | 0 | 66.7941 | FALSE | FALSE | 0.0436 |  | 69.2985 | 0 | -0.2826 | 0.15525 | 0.28186 | -1.5534 | 1.2522 | Normal | 71.8029 | 0.65347 | Night | 202602 | 2026-02-03 | 0.65347
2026-02-03 18:47 | 69.836 | FALSE | FALSE | -2.6652 | -3.9678 | -1.8727 | -2.6115 | -0.2808 |  |  | none | FALSE | 0 | 67.1708 | FALSE | FALSE | 0.0233 |  | 69.4397 | 0 | -0.2808 | 0.14121 | 0.29661 | -1.4228 | 1.1345 | Normal | 71.7087 | 0.3493 | Night | 202602 | 2026-02-03 | 0.3493
2026-02-03 19:02 | 69.836 | FALSE | FALSE | -2.3049 | -3.4131 | -1.7665 | -2.4671 | 0 |  |  | none | FALSE | 0 | 67.5311 | FALSE | FALSE | 0.0176 |  | 69.5668 | 0 | 0 | 0.12708 | 0.29625 | -0.42897 | 1.0179 | Normal | 71.6025 | 0.26447 | Night | 202602 | 2026-02-03 | 0.26447
2026-02-03 19:17 | 70.1168 | FALSE | FALSE | -2.2414 | -3.3022 | -1.3954 | -1.9512 | 0.2808 |  |  | none | FALSE | 0 | 67.8754 | FALSE | FALSE | 0.031 |  | 69.6938 | 0 | 0.2808 | 0.12699 | 0.2962 | 0.51928 | 0.90918 | Normal | 71.5122 | 0.46526 | Night | 202602 | 2026-02-03 | 0.46526
2026-02-03 19:32 | 69.836 | FALSE | FALSE | -1.7225 | -2.5288 | -1.6076 | -2.2502 | -0.2808 |  |  | none | FALSE | 0 | 68.1135 | FALSE | FALSE | 0.0046 |  | 69.7786 | 0 | -0.2808 | 0.08478 | 0.29084 | -1.257 | 0.83253 | Normal | 71.4436 | 0.068971 | Night | 202602 | 2026-02-03 | 0.068971
2026-02-03 19:46 | 69.836 | FALSE | FALSE | -1.4484 | -2.1179 | -1.5031 | -2.107 | 0 |  |  | none | FALSE | 0 | 68.3876 | FALSE | FALSE | 0.0025 |  | 69.8634 | 0 | 0 | 0.08478 | 0.29084 | -0.2915 | 0.73788 | Normal | 71.3391 | -0.037079 | Night | 202602 | 2026-02-03 | 0.037079
2026-02-03 20:01 | 69.836 | FALSE | FALSE | -1.2136 | -1.7685 | -1.4096 | -1.9785 | 0 |  |  | none | FALSE | 0 | 68.6224 | FALSE | FALSE | 0.01 |  | 69.934 | 0 | 0 | 0.07065 | 0.28757 | -0.24568 | 0.65579 | Normal | 71.2456 | -0.14945 | Night | 202602 | 2026-02-03 | 0.14945
2026-02-03 20:16 | 69.5534 | FALSE | FALSE | -0.77094 | -1.1208 | -1.6169 | -2.2719 | -0.2826 |  |  | none | FALSE | 0 | 68.7825 | FALSE | FALSE | 0.0472 |  | 69.9764 | 0 | -0.2826 | 0.04239 | 0.29336 | -1.1078 | 0.59697 | Normal | 71.1703 | -0.70858 | Night | 202602 | 2026-02-03 | 0.70858
2026-02-03 20:31 | 69.2708 | FALSE | FALSE | -0.35561 | -0.51602 | -1.8233 | -2.5647 | -0.2826 |  |  | none | FALSE | 0 | 68.9152 | FALSE | FALSE | 0.0898 |  | 70.0047 | 0 | -0.2826 | 0.02826 | 0.30218 | -1.0287 | 0.54474 | Normal | 71.0941 | -1.3472 | Night | 202602 | 2026-02-03 | 1.3472
2026-02-03 20:46 | 69.2708 | FALSE | FALSE | -0.29219 | -0.4236 | -1.7882 | -2.5165 | 0 |  |  | none | FALSE | 0 | 68.9786 | FALSE | FALSE | 0.0959 |  | 70.0188 | 0 | 0 | 0.01413 | 0.29621 | -0.047703 | 0.52009 | Normal | 71.059 | -1.4382 | Night | 202602 | 2026-02-03 | 1.4382
2026-02-03 21:01 | 69.2708 | FALSE | FALSE | -0.22546 | -0.32654 | -1.7497 | -2.4637 | 0 |  |  | none | FALSE | 0 | 69.0453 | FALSE | FALSE | 0.1029 |  | 70.0329 | 0 | 0 | 0.01413 | 0.29621 | -0.047703 | 0.49379 | Normal | 71.0205 | -1.5434 | Night | 202602 | 2026-02-03 | 1.5434
2026-02-03 21:16 | 68.9882 | FALSE | FALSE | -0.05747 | -0.083373 | -2.0904 | -2.941 | -0.2826 |  |  | none | FALSE | 0 | 68.9307 | FALSE | FALSE | 0.1262 |  | 70.0047 | 0 | -0.2826 | -0.02826 | 0.27294 | -0.93184 | 0.53696 | Normal | 71.0786 | -1.893 | Night | 202602 | 2026-02-03 | 1.893
2026-02-03 21:31 | 68.9882 | FALSE | FALSE | -0.20174 | -0.29328 | -2.0935 | -2.9453 | 0 |  |  | none | FALSE | 0 | 68.7865 | FALSE | FALSE | 0.1099 |  | 69.9341 | 0 | 0 | -0.07056 | 0.18008 | 0.39183 | 0.57382 | Normal | 71.0817 | -1.6484 | Night | 202602 | 2026-02-03 | 1.6484
2026-02-03 21:46 | 68.9882 | FALSE | FALSE | -0.3039 | -0.44246 | -2.0263 | -2.8534 | 0 |  |  | none | FALSE | 0 | 68.6843 | FALSE | FALSE | 0.0986 |  | 69.8494 | 0 | 0 | -0.08469 | 0.16099 | 0.52607 | 0.58255 | Normal | 71.0145 | -1.4783 | Night | 202602 | 2026-02-03 | 1.4783
2026-02-03 22:01 | 68.7056 | FALSE | FALSE | -0.15745 | -0.22969 | -2.2474 | -3.1675 | -0.2826 |  |  | none | FALSE | 0 | 68.5482 | FALSE | FALSE | 0.1159 |  | 69.7506 | 0 | -0.2826 | -0.09882 | 0.1655 | -1.1105 | 0.60122 | Normal | 70.953 | -1.7381 | Night | 202602 | 2026-02-03 | 1.7381
2026-02-03 22:16 | 68.7056 | FALSE | FALSE | -0.25882 | -0.37813 | -2.1512 | -3.0359 | 0 |  |  | none | FALSE | 0 | 68.4468 | FALSE | FALSE | 0.1047 |  | 69.6518 | 0 | 0 | -0.09882 | 0.1655 | 0.5971 | 0.60249 | Normal | 70.8568 | -1.5704 | Night | 202602 | 2026-02-03 | 1.5704
2026-02-03 22:31 | 68.7056 | FALSE | FALSE | -0.32564 | -0.47622 | -2.0203 | -2.8566 | 0 |  |  | none | FALSE | 0 | 68.38 | FALSE | FALSE | 0.0963 |  | 69.5529 | 0 | 0 | -0.09882 | 0.1655 | 0.5971 | 0.58649 | Normal | 70.7259 | -1.4448 | Night | 202602 | 2026-02-03 | 1.4448
2026-02-03 22:45 | 68.7056 | FALSE | FALSE | -0.39752 | -0.58196 | -1.9228 | -2.7225 | 0 |  |  | none | FALSE | 0 | 68.3081 | FALSE | FALSE | 0.0876 |  | 69.4683 | 0 | 0 | -0.08469 | 0.16099 | 0.52607 | 0.58009 | Normal | 70.6284 | -1.3147 | Night | 202602 | 2026-02-03 | 1.3147
2026-02-03 23:00 | 68.423 | FALSE | FALSE | -0.21648 | -0.31739 | -2.1094 | -2.9906 | -0.2826 |  |  | none | FALSE | 0 | 68.2065 | FALSE | FALSE | 0.1085 |  | 69.3694 | 0 | -0.2826 | -0.09882 | 0.1655 | -1.1105 | 0.58146 | Normal | 70.5324 | -1.6277 | Night | 202602 | 2026-02-03 | 1.6277
2026-02-03 23:15 | 68.423 | FALSE | FALSE | -0.28221 | -0.41416 | -1.9775 | -2.8089 | 0 |  |  | none | FALSE | 0 | 68.1408 | FALSE | FALSE | 0.1 |  | 69.2706 | 0 | 0 | -0.09882 | 0.1655 | 0.5971 | 0.56492 | Normal | 70.4005 | -1.5004 | Night | 202602 | 2026-02-03 | 1.5004
2026-02-03 23:30 | 68.1404 | FALSE | FALSE | -0.13204 | -0.19415 | -2.1948 | -3.1205 | -0.2826 |  |  | none | FALSE | 0 | 68.0084 | FALSE | FALSE | 0.1182 |  | 69.1718 | 0 | -0.2826 | -0.09882 | 0.1655 | -1.1105 | 0.58172 | Normal | 70.3352 | -1.773 | Night | 202602 | 2026-02-03 | 1.773
2026-02-03 23:45 | 68.1404 | FALSE | FALSE | -0.25937 | -0.38209 | -2.1526 | -3.0623 | 0 |  |  | none | FALSE | 0 | 67.881 | FALSE | FALSE | 0.1047 |  | 69.087 | 0 | 0 | -0.08478 | 0.1611 | 0.52625 | 0.60299 | Normal | 70.293 | -1.5699 | Night | 202602 | 2026-02-03 | 1.5699
2026-02-04 | 68.1404 | FALSE | FALSE | -0.36074 | -0.53222 | -2.0844 | -2.9682 | 0 |  |  | none | FALSE | 0 | 67.7797 | FALSE | FALSE | 0.094 |  | 69.0022 | 0 | 0 | -0.08478 | 0.1611 | 0.52625 | 0.61129 | Normal | 70.2248 | -1.4099 | Night | 202602 | 2026-02-03 | 1.4099
2026-02-04 00:15 | 68.1404 | FALSE | FALSE | -0.39819 | -0.58781 | -1.9242 | -2.7464 | 0 |  |  | none | FALSE | 0 | 67.7422 | FALSE | FALSE | 0.0876 |  | 68.9034 | 0 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.58061 | Normal | 70.0646 | -1.3142 | Night | 202602 | 2026-02-04 | 1.3142
2026-02-04 00:30 | 68.1404 | FALSE | FALSE | -0.4432 | -0.65468 | -1.7997 | -2.5732 | 0 |  |  | none | FALSE | 0 | 67.6972 | FALSE | FALSE | 0.0806 |  | 68.8186 | 0 | 0 | -0.08478 | 0.13287 | 0.63808 | 0.56072 | Normal | 69.9401 | -1.2096 | Night | 202602 | 2026-02-04 | 1.2096
2026-02-04 00:45 | 68.1404 | FALSE | FALSE | -0.45835 | -0.67721 | -1.6453 | -2.3576 | 0 |  |  | none | FALSE | 0 | 67.682 | FALSE | FALSE | 0.0752 |  | 68.7339 | 0 | 0 | -0.08478 | 0.13287 | 0.63808 | 0.52591 | Normal | 69.7857 | -1.1285 | Night | 202602 | 2026-02-04 | 1.1285
2026-02-04 01:00 | 68.1404 | FALSE | FALSE | -0.43708 | -0.64558 | -1.4544 | -2.0899 | 0 |  |  | none | FALSE | 0 | 67.7033 | FALSE | FALSE | 0.0717 |  | 68.6491 | 0 | 0 | -0.08478 | 0.13287 | 0.63808 | 0.47288 | Normal | 69.5948 | -1.0757 | Night | 202602 | 2026-02-04 | 1.0757
2026-02-04 01:15 | 68.1404 | FALSE | FALSE | -0.43131 | -0.63701 | -1.3074 | -1.8825 | 0 |  |  | none | FALSE | 0 | 67.7091 | FALSE | FALSE | 0.0672 |  | 68.5784 | 0 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.43467 | Normal | 69.4478 | -1.0077 | Night | 202602 | 2026-02-04 | 1.0077
2026-02-04 01:30 | 68.423 | TRUE | FALSE | -0.69464 | -1.0256 | -0.92072 | -1.3278 | 0.2826 |  |  | none | FALSE | 1 | 67.7284 | FALSE | FALSE | 0.0472 |  | 68.536 | 0 | 0.2826 | -0.04239 | 0.13829 | 2.35 | 0.40384 | Normal | 69.3437 | -0.27991 | Night | 202602 | 2026-02-04 | 0.27991
2026-02-04 01:44 | 68.1404 | FALSE | FALSE | -0.40801 | -0.60238 | -1.0862 | -1.5691 | -0.2826 |  |  | none | FALSE | 1 | 67.7324 | FALSE | FALSE | 0.0891 |  | 68.4795 | 0 | -0.2826 | -0.05652 | 0.14784 | -1.5292 | 0.37356 | Normal | 69.2266 | -0.9078 | Night | 202602 | 2026-02-04 | 0.9078
2026-02-04 01:59 | 67.8596 | FALSE | FALSE | -0.14801 | -0.21859 | -1.2467 | -1.8041 | -0.2808 |  |  | none | FALSE | 1 | 67.7116 | FALSE | FALSE | 0.1336 |  | 68.409 | 0 | -0.2808 | -0.07056 | 0.15534 | -1.3535 | 0.34869 | Normal | 69.1063 | -1.5755 | Night | 202602 | 2026-02-04 | 1.5755
2026-02-04 02:14 | 67.8596 | FALSE | FALSE | -0.18958 | -0.28015 | -1.1754 | -1.7027 | 0 |  |  | none | FALSE | 1 | 67.67 | FALSE | FALSE | 0.1249 |  | 68.3525 | 0 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.34125 | Normal | 69.035 | -1.4445 | Night | 202602 | 2026-02-04 | 1.4445
2026-02-04 02:29 | 67.8596 | FALSE | FALSE | -0.21041 | -0.31103 | -1.0834 | -1.5715 | 0 |  |  | none | FALSE | 1 | 67.6492 | FALSE | FALSE | 0.1185 |  | 68.2961 | 0 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.32346 | Normal | 68.943 | -1.3495 | Night | 202602 | 2026-02-04 | 1.3495
2026-02-04 02:44 | 67.8596 | FALSE | FALSE | -0.20675 | -0.3056 | -0.96689 | -1.4048 | 0 |  |  | none | FALSE | 1 | 67.6529 | FALSE | FALSE | 0.1149 |  | 68.2397 | 0 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.29341 | Normal | 68.8265 | -1.2954 | Night | 202602 | 2026-02-04 | 1.2954
2026-02-04 02:59 | 67.577 | FALSE | FALSE | -0.0083288 | -0.012326 | -1.2208 | -1.7745 | -0.2826 |  |  | none | FALSE | 1 | 67.5687 | FALSE | FALSE | 0.1601 |  | 68.1832 | 0 | -0.2826 | -0.05643 | 0.1477 | -1.5313 | 0.30728 | Normal | 68.7978 | -1.9729 | Night | 202602 | 2026-02-04 | 1.9729
2026-02-04 03:14 | 67.8596 | FALSE | FALSE | -0.29725 | -0.43997 | -0.85993 | -1.2514 | 0.2826 |  |  | none | FALSE | 1 | 67.5623 | FALSE | FALSE | 0.0934 |  | 68.1409 | 0 | 0.2826 | -0.0423 | 0.16579 | 1.9597 | 0.2893 | Normal | 68.7195 | -0.9725 | Night | 202602 | 2026-02-04 | 0.9725
2026-02-04 03:29 | 67.8596 | FALSE | FALSE | -0.28705 | -0.42481 | -0.76513 | -1.115 | 0 |  |  | none | FALSE | 1 | 67.5725 | FALSE | FALSE | 0.0892 |  | 68.0986 | 0 | 0 | -0.0423 | 0.16579 | 0.25514 | 0.26305 | Normal | 68.6247 | -0.90874 | Night | 202602 | 2026-02-04 | 0.90874
2026-02-04 03:44 | 67.8596 | FALSE | FALSE | -0.2546 | -0.3766 | -0.64808 | -0.946 | 0 |  |  | none | FALSE | 1 | 67.605 | FALSE | FALSE | 0.0867 |  | 68.0563 | 0 | 0 | -0.0423 | 0.16579 | 0.25514 | 0.22567 | Normal | 68.5077 | -0.8718 | Night | 202602 | 2026-02-04 | 0.8718
2026-02-04 03:59 | 67.577 | FALSE | FALSE | -0.027982 | -0.041425 | -0.90206 | -1.3173 | -0.2826 |  |  | none | FALSE | 0 | 67.549 | FALSE | FALSE | 0.1253 |  | 68.014 | 0 | -0.2826 | -0.0423 | 0.16579 | -1.4494 | 0.23251 | Normal | 68.4791 | -1.8797 | Night | 202602 | 2026-02-04 | 1.8797
2026-02-04 04:14 | 67.577 | FALSE | FALSE | -0.067551 | -0.10006 | -0.85703 | -1.2523 | 0 |  |  | none | FALSE | 0 | 67.5094 | FALSE | FALSE | 0.1139 |  | 67.9717 | 0 | 0 | -0.0423 | 0.16579 | 0.25514 | 0.23115 | Normal | 68.434 | -1.7078 | Night | 202602 | 2026-02-04 | 1.7078
2026-02-04 04:29 | 67.577 | FALSE | FALSE | -0.12045 | -0.17856 | -0.85359 | -1.2474 | 0 |  |  | none | FALSE | 0 | 67.4566 | FALSE | FALSE | 0.1004 |  | 67.9436 | 0 | 0 | -0.02817 | 0.15598 | 0.18059 | 0.24351 | Normal | 68.4306 | -1.5054 | Night | 202602 | 2026-02-04 | 1.5054
2026-02-04 04:43 | 67.577 | FALSE | FALSE | -0.16556 | -0.2456 | -0.84236 | -1.2312 | 0 |  |  | none | FALSE | 0 | 67.4114 | FALSE | FALSE | 0.0895 |  | 67.9154 | 0 | 0 | -0.02817 | 0.15598 | 0.18059 | 0.25198 | Normal | 68.4194 | -1.343 | Night | 202602 | 2026-02-04 | 1.343
2026-02-04 04:58 | 67.577 | FALSE | FALSE | -0.20367 | -0.30229 | -0.82413 | -1.2048 | 0 |  |  | none | FALSE | 0 | 67.3733 | FALSE | FALSE | 0.0805 |  | 67.8872 | 0 | 0 | -0.02817 | 0.15598 | 0.18059 | 0.25695 | Normal | 68.4011 | -1.2074 | Night | 202602 | 2026-02-04 | 1.2074
2026-02-04 05:13 | 67.2944 | FALSE | FALSE | -0.012542 | -0.018641 | -1.1136 | -1.6279 | -0.2826 |  |  | none | FALSE | 0 | 67.2819 | FALSE | FALSE | 0.1304 |  | 67.8449 | 0 | -0.2826 | -0.0423 | 0.16579 | -1.4494 | 0.28154 | Normal | 68.408 | -1.9555 | Night | 202602 | 2026-02-04 | 1.9555
2026-02-04 05:28 | 67.577 | FALSE | FALSE | -0.31741 | -0.47192 | -0.79693 | -1.1656 | 0.2826 |  |  | none | FALSE | 0 | 67.2596 | FALSE | FALSE | 0.0574 |  | 67.8168 | 0 | 0.2826 | -0.02817 | 0.18094 | 1.7176 | 0.27859 | Normal | 68.3739 | -0.86063 | Night | 202602 | 2026-02-04 | 0.86063
2026-02-04 05:43 | 67.8596 | FALSE | FALSE | -0.59349 | -0.8823 | -0.47973 | -0.70198 | 0.2826 |  |  | none | FALSE | 0 | 67.2661 | FALSE | FALSE | 0.0141 |  | 67.8027 | 0 | 0.2826 | -0.01404 | 0.19383 | 1.5304 | 0.2683 | Normal | 68.3393 | 0.212 | Night | 202602 | 2026-02-04 | 0.212
2026-02-04 05:58 | 67.8596 | FALSE | FALSE | -0.58453 | -0.86886 | -0.44269 | -0.64813 | 0 |  |  | none | FALSE | 0 | 67.2751 | FALSE | FALSE | 0.0184 |  | 67.7887 | 0 | 0 | -0.01404 | 0.19383 | 0.072436 | 0.2568 | Normal | 68.3023 | 0.27616 | Night | 202602 | 2026-02-04 | 0.27616
2026-02-04 06:13 | 67.577 | FALSE | FALSE | -0.31029 | -0.46129 | -0.67731 | -0.99234 | -0.2826 |  |  | none | FALSE | 0 | 67.2667 | FALSE | FALSE | 0.0496 |  | 67.7605 | 0 | -0.2826 | -0.02817 | 0.20284 | -1.2543 | 0.2469 | Normal | 68.2543 | -0.74325 | Night | 202602 | 2026-02-04 | 0.74325
2026-02-04 06:28 | 67.8596 | FALSE | FALSE | -0.51478 | -0.76439 | -0.26026 | -0.38206 | 0.2826 |  |  | none | FALSE | 0 | 67.3448 | FALSE | FALSE | 0.0438 |  | 67.7323 | 0 | 0.2826 | -0.02817 | 0.20284 | 1.5321 | 0.19376 | Normal | 68.1199 | 0.6568 | Night | 202602 | 2026-02-04 | 0.6568
2026-02-04 06:43 | 67.8596 | FALSE | FALSE | -0.48436 | -0.7189 | -0.20176 | -0.29644 | 0 |  |  | none | FALSE | 0 | 67.3752 | FALSE | FALSE | 0.0549 |  | 67.7183 | 0 | 0 | -0.01404 | 0.19383 | 0.072436 | 0.17153 | Normal | 68.0614 | 0.82375 | Night | 202602 | 2026-02-04 | 0.82375
2026-02-04 06:58 | 67.8596 | FALSE | FALSE | -0.48436 | -0.7189 | -0.20176 | -0.29644 | 0 |  |  | none | FALSE | 0 | 67.3752 | FALSE | FALSE | 0.0549 |  | 67.7183 | 0 | 0 | 0 | 0.18338 | 0 | 0.17153 | Normal | 68.0614 | 0.82375 | Night | 202602 | 2026-02-04 | 0.82375
2026-02-04 07:13 | 67.8596 | FALSE | FALSE | -0.48436 | -0.7189 | -0.20176 | -0.29644 | 0 |  |  | none | FALSE | 0 | 67.3752 | FALSE | FALSE | 0.0549 |  | 67.7183 | 0 | 0 | 0 | 0.18338 | 0 | 0.17153 | Normal | 68.0614 | 0.82375 | Day | 202602 | 2026-02-04 | 0.82375
2026-02-04 07:28 | 67.8596 | FALSE | FALSE | -0.48436 | -0.7189 | -0.20176 | -0.29644 | 0 |  |  | none | FALSE | 0 | 67.3752 | FALSE | FALSE | 0.0549 |  | 67.7183 | 0 | 0 | 0 | 0.18338 | 0 | 0.17153 | Normal | 68.0614 | 0.82375 | Day | 202602 | 2026-02-04 | 0.82375
2026-02-04 07:30 | 67.8596 | FALSE | FALSE | -0.48436 | -0.7189 | -0.20176 | -0.29644 | 0 |  |  | none | FALSE | 0 | 67.3752 | FALSE | FALSE | 0.0549 |  | 67.7183 | 0 | 0 | 0 | 0.18338 | 0 | 0.17153 | Normal | 68.0614 | 0.82375 | Day | 202602 | 2026-02-04 | 0.82375
2026-02-04 07:45 | 67.8596 | FALSE | FALSE | -0.46901 | -0.69595 | -0.21467 | -0.31534 | 0 |  |  | none | FALSE | 0 | 67.3906 | FALSE | FALSE | 0.0496 |  | 67.7324 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.17092 | Normal | 68.0743 | 0.74404 | Day | 202602 | 2026-02-04 | 0.74404
2026-02-04 08:00 | 67.8596 | FALSE | FALSE | -0.46901 | -0.69595 | -0.21467 | -0.31534 | 0 |  |  | none | FALSE | 0 | 67.3906 | FALSE | FALSE | 0.0496 |  | 67.7324 | 0 | 0 | 0 | 0.15881 | 0 | 0.17092 | Normal | 68.0743 | 0.74404 | Day | 202602 | 2026-02-04 | 0.74404
2026-02-04 08:15 | 67.8596 | FALSE | FALSE | -0.46901 | -0.69595 | -0.21467 | -0.31534 | 0 |  |  | none | FALSE | 0 | 67.3906 | FALSE | FALSE | 0.0496 |  | 67.7324 | 0 | 0 | 0 | 0.15881 | 0 | 0.17092 | Normal | 68.0743 | 0.74404 | Day | 202602 | 2026-02-04 | 0.74404
2026-02-04 08:30 | 68.1404 | FALSE | FALSE | -0.77819 | -1.1552 | 0.0096683 | 0.014191 | 0.2808 | 2026-02-04 12:59 | 2026-02-04 08:30 | upper | TRUE | 0 | 67.3622 | FALSE | FALSE | 0.1938 | 2.0503 | 67.7465 | 1 | 0.2808 | 0.01404 | 0.17077 | 1.5621 | 0.19213 | Extreme triggered | 68.1307 | 2.0503 | Day | 202602 | 2026-02-04 | 2.0503
2026-02-04 08:45 | 68.1404 | FALSE | FALSE | -0.77921 | -1.1568 | -0.047688 | -0.069936 | 0 |  | 2026-02-04 08:30 | none | FALSE | 0 | 67.3612 | FALSE | FALSE | 0.2322 | 1.9098 | 67.7746 | 2 | 0 | 0.02817 | 0.15598 | -0.18059 | 0.20672 | Extreme/elevated | 68.1881 | 1.7693 | Day | 202602 | 2026-02-04 | 1.7693
2026-02-04 08:45 | 68.1404 | FALSE | FALSE | -0.77065 | -1.1439 | -0.095467 | -0.13991 | 0 |  | 2026-02-04 08:30 | none | FALSE | 0 | 67.3698 | FALSE | FALSE | 0.2754 | 1.7929 | 67.8028 | 3 | 0 | 0.02817 | 0.15598 | -0.18059 | 0.21653 | Persistent | 68.2359 | 1.5591 | Day | 202602 | 2026-02-04 | 1.5591
2026-02-04 09:00 | 68.7056 | TRUE | FALSE | -1.4251 | -2.1182 | 0.26758 | 0.39099 | 0.5652 |  | 2026-02-04 08:30 | upper | TRUE | 1 | 67.2805 | FALSE | TRUE | 0.4521 | 2.0758 | 67.8592 | 4 | 0.5652 | 0.05643 | 0.19654 | 2.5886 | 0.28939 | Persistent | 68.438 | 2.9247 | Day | 202602 | 2026-02-04 | 2.9247
2026-02-04 09:15 | 68.423 | FALSE | FALSE | -1.1359 | -1.6882 | -0.093022 | -0.13577 | -0.2826 |  | 2026-02-04 08:30 | none | FALSE | 1 | 67.2871 | FALSE | FALSE | 0.4274 | 2.0001 | 67.9015 | 5 | -0.2826 | 0.0423 | 0.21047 | -1.5437 | 0.30724 | Persistent | 68.516 | 1.6972 | Day | 202602 | 2026-02-04 | 1.6972
2026-02-04 09:30 | 68.7056 | FALSE | FALSE | -1.4391 | -2.1394 | 0.056172 | 0.081825 | 0.2826 |  | 2026-02-04 08:30 | upper | TRUE | 1 | 67.2665 | FALSE | TRUE | 0.5156 | 2.0272 | 67.958 | 6 | 0.2826 | 0.05643 | 0.21687 | 1.0429 | 0.34573 | Persistent | 68.6494 | 2.1625 | Day | 202602 | 2026-02-04 | 2.1625
2026-02-04 09:44 | 68.7056 | FALSE | TRUE | -1.3714 | -2.0367 | -0.017282 | -0.025147 | 0 |  | 2026-02-04 08:30 | none | FALSE | 1 | 67.3342 | FALSE | FALSE | 0.5586 | 2.0162 | 68.0285 | 7 | 0 | 0.07056 | 0.20234 | -0.34872 | 0.34718 | Confirmed/Materialized Shift | 68.7229 | 1.9502 | Day | 202602 | 2026-02-04 | 1.9502
2026-02-04 09:59 | 68.9882 | FALSE | TRUE | -1.6715 | -2.483 | 0.10672 | 0.15494 | 0.2826 |  | 2026-02-04 08:30 | upper | TRUE | 1 | 67.3167 | FALSE | TRUE | 0.5801 | 2.0483 | 68.0991 | 8 | 0.2826 | 0.07056 | 0.20234 | 1.0479 | 0.39119 | Confirmed/Materialized Shift | 68.8815 | 2.2728 | Day | 202602 | 2026-02-04 | 2.2728
2026-02-04 10:14 | 69.5534 | TRUE | TRUE | -2.3772 | -3.5387 | 0.36209 | 0.52331 | 0.5652 |  | 2026-02-04 08:30 | upper | TRUE | 2 | 67.1762 | TRUE | TRUE | 0.6384 | 2.1228 | 68.1838 | 9 | 0.5652 | 0.08469 | 0.22637 | 2.1227 | 0.50377 | Confirmed/Materialized Shift | 69.1913 | 2.7188 | Day | 202602 | 2026-02-04 | 2.7188
2026-02-04 10:30 | 69.836 | FALSE | TRUE | -2.7889 | -4.1597 | 0.31785 | 0.45722 | 0.2826 |  | 2026-02-04 08:30 | upper | TRUE | 2 | 67.0471 | FALSE | TRUE | 0.6248 | 2.1619 | 68.2826 | 10 | 0.2826 | 0.09882 | 0.2296 | 0.80043 | 0.61777 | Confirmed/Materialized Shift | 69.5181 | 2.5145 | Day | 202602 | 2026-02-04 | 2.5145
2026-02-04 10:44 | 70.1168 | FALSE | TRUE | -3.1432 | -4.6932 | 0.2712 | 0.38828 | 0.2808 |  | 2026-02-04 08:30 | upper | TRUE | 2 | 66.9736 | FALSE | TRUE | 0.6157 | 2.1816 | 68.4096 | 11 | 0.2808 | 0.12699 | 0.2144 | 0.7174 | 0.71801 | Confirmed/Materialized Shift | 69.8456 | 2.3777 | Day | 202602 | 2026-02-04 | 2.3777
2026-02-04 10:59 | 70.3994 | FALSE | TRUE | -3.5254 | -5.2717 | 0.20026 | 0.28528 | 0.2826 |  | 2026-02-04 08:30 | upper | TRUE | 2 | 66.874 | FALSE | TRUE | 0.6065 | 2.1865 | 68.5366 | 12 | 0.2826 | 0.12699 | 0.2144 | 0.72579 | 0.83128 | Confirmed/Materialized Shift | 70.1991 | 2.2409 | Day | 202602 | 2026-02-04 | 2.2409
2026-02-04 11:14 | 70.682 | FALSE | TRUE | -3.8892 | -5.8228 | 0.11942 | 0.16924 | 0.2826 |  | 2026-02-04 08:30 | upper | TRUE | 2 | 66.7928 | FALSE | TRUE | 0.5989 | 2.1819 | 68.6777 | 13 | 0.2826 | 0.14112 | 0.2149 | 0.65834 | 0.94244 | Confirmed/Materialized Shift | 70.5626 | 2.1267 | Day | 202602 | 2026-02-04 | 2.1267
2026-02-04 11:29 | 70.9646 | FALSE | TRUE | -4.232 | -6.3417 | 0.031311 | 0.044141 | 0.2826 |  | 2026-02-04 08:30 | upper | TRUE | 1 | 66.7326 | FALSE | TRUE | 0.5639 | 2.171 | 68.8329 | 14 | 0.2826 | 0.15525 | 0.21443 | 0.59391 | 1.0502 | Confirmed/Materialized Shift | 70.9333 | 2.0298 | Day | 202602 | 2026-02-04 | 2.0298
2026-02-04 11:44 | 71.2472 | FALSE | TRUE | -4.551 | -6.8235 | -0.061262 | -0.085911 | 0.2826 |  | 2026-02-04 08:30 | none | FALSE | 1 | 66.6962 | FALSE | FALSE | 0.5584 | 2.1561 | 69.0023 | 15 | 0.2826 | 0.16938 | 0.21296 | 0.53164 | 1.1531 | Confirmed/Materialized Shift | 71.3085 | 1.9469 | Day | 202602 | 2026-02-04 | 1.9469
2026-02-04 11:59 | 71.5298 | FALSE | TRUE | -4.8432 | -7.2627 | -0.15532 | -0.21667 | 0.2826 |  | 2026-02-04 08:30 | none | FALSE | 1 | 66.6866 | FALSE | FALSE | 0.5536 | 2.1386 | 69.1858 | 16 | 0.2826 | 0.18351 | 0.21049 | 0.47075 | 1.2496 | Confirmed/Materialized Shift | 71.6851 | 1.8757 | Day | 202602 | 2026-02-04 | 1.8757
2026-02-04 12:14 | 71.8124 | FALSE | TRUE | -5.1055 | -7.6536 | -0.24765 | -0.34367 | 0.2826 |  | 2026-02-04 08:30 | none | FALSE | 1 | 66.7069 | FALSE | FALSE | 0.5496 | 2.1195 | 69.3835 | 17 | 0.2826 | 0.19764 | 0.20698 | 0.41047 | 1.3383 | Confirmed/Materialized Shift | 72.06 | 1.815 | Day | 202602 | 2026-02-04 | 1.815
2026-02-04 12:29 | 72.095 | FALSE | TRUE | -5.3342 | -7.99 | -0.33471 | -0.46212 | 0.2826 |  | 2026-02-04 08:30 | none | FALSE | 1 | 66.7608 | FALSE | FALSE | 0.5462 | 2.0998 | 69.5952 | 18 | 0.2826 | 0.21177 | 0.20238 | 0.34999 | 1.4172 | Confirmed/Materialized Shift | 72.4297 | 1.7638 | Day | 202602 | 2026-02-04 | 1.7638
2026-02-04 12:43 | 71.8124 | TRUE | TRUE | -4.8953 | -7.3155 | -0.85632 | -1.1784 | -0.2826 |  | 2026-02-04 08:30 | none | FALSE | 1 | 66.9171 | FALSE | FALSE | 0.5222 | 2.0632 | 69.7929 | 19 | -0.2826 | 0.19764 | 0.22638 | -2.1214 | 1.4379 | Confirmed/Materialized Shift | 72.6687 | 1.4045 | Day | 202602 | 2026-02-04 | 1.4045
2026-02-04 12:59 | 71.2472 | TRUE | FALSE | -4.0792 | -6.0731 | -1.5093 | -2.0745 | -0.5652 |  |  | none | FALSE | 2 | 67.168 | TRUE | FALSE | 0.1185 |  | 69.9623 | 0 | -0.5652 | 0.16938 | 0.28103 | -2.6139 | 1.3971 | Persistence ends | 72.7565 | 0.91969 | Day | 202602 | 2026-02-04 | 0.91969
2026-02-04 13:14 | 71.5298 | FALSE | FALSE | -4.1377 | -6.1397 | -1.3416 | -1.841 | 0.2826 |  |  | none | FALSE | 2 | 67.3921 | FALSE | FALSE | 0.1252 |  | 70.1317 | 0 | 0.2826 | 0.16947 | 0.28107 | 0.4025 | 1.3698 | Normal | 72.8714 | 1.0206 | Day | 202602 | 2026-02-04 | 1.0206
2026-02-04 13:29 | 71.8124 | FALSE | FALSE | -4.166 | -6.1586 | -1.1719 | -1.6057 | 0.2826 |  |  | none | FALSE | 2 | 67.6464 | FALSE | FALSE | 0.1319 |  | 70.3153 | 0 | 0.2826 | 0.1836 | 0.2792 | 0.35458 | 1.3345 | Normal | 72.9843 | 1.1218 | Day | 202602 | 2026-02-04 | 1.1218
2026-02-04 13:43 | 72.095 | FALSE | FALSE | -4.1568 | -6.1184 | -0.9929 | -1.3585 | 0.2826 |  |  | none | FALSE | 2 | 67.9382 | FALSE | FALSE | 0.1391 |  | 70.5131 | 0 | 0.2826 | 0.19773 | 0.27656 | 0.30688 | 1.2874 | Normal | 73.0879 | 1.2288 | Day | 202602 | 2026-02-04 | 1.2288
2026-02-04 13:58 | 72.095 | FALSE | FALSE | -3.932 | -5.7685 | -1.107 | -1.5123 | 0 |  |  | none | FALSE | 2 | 68.163 | FALSE | FALSE | 0.1319 |  | 70.6825 | 0 | 0 | 0.16947 | 0.2657 | -0.63783 | 1.2598 | Normal | 73.202 | 1.1212 | Day | 202602 | 2026-02-04 | 1.1212
2026-02-04 14:13 | 72.3758 | FALSE | FALSE | -3.8856 | -5.6733 | -0.8944 | -1.2207 | 0.2808 |  |  | none | FALSE | 2 | 68.4902 | FALSE | FALSE | 0.1406 |  | 70.8802 | 0 | 0.2808 | 0.19764 | 0.24424 | 0.34048 | 1.195 | Normal | 73.2702 | 1.2516 | Day | 202602 | 2026-02-04 | 1.2516
2026-02-04 14:28 | 72.3758 | FALSE | FALSE | -3.5584 | -5.1708 | -0.93417 | -1.2743 | 0 |  |  | none | FALSE | 2 | 68.8174 | FALSE | FALSE | 0.135 |  | 71.0637 | 0 | 0 | 0.18351 | 0.24723 | -0.74228 | 1.1231 | Normal | 73.31 | 1.1683 | Day | 202602 | 2026-02-04 | 1.1683
2026-02-04 14:43 | 72.3758 | FALSE | FALSE | -3.1524 | -4.554 | -0.89521 | -1.2218 | 0 |  |  | none | FALSE | 2 | 69.2234 | FALSE | FALSE | 0.1315 |  | 71.2472 | 0 | 0 | 0.18351 | 0.24723 | -0.74228 | 1.0119 | Normal | 73.271 | 1.1153 | Day | 202602 | 2026-02-04 | 1.1153
2026-02-04 14:58 | 72.3758 | FALSE | FALSE | -2.7393 | -3.9338 | -0.8209 | -1.1215 | 0 |  |  | none | FALSE | 2 | 69.6365 | FALSE | FALSE | 0.129 |  | 71.4166 | 0 | 0 | 0.16938 | 0.24933 | -0.67934 | 0.89006 | Normal | 73.1967 | 1.0777 | Day | 202602 | 2026-02-04 | 1.0777
2026-02-04 15:13 | 72.6584 | FALSE | FALSE | -2.7179 | -3.886 | -0.54473 | -0.74414 | 0.2826 |  |  | none | FALSE | 1 | 69.9405 | FALSE | FALSE | 0.1174 |  | 71.5718 | 0 | 0.2826 | 0.15525 | 0.23321 | 0.54608 | 0.81565 | Normal | 73.2031 | 1.3321 | Day | 202602 | 2026-02-04 | 1.3321
2026-02-04 15:28 | 72.6584 | FALSE | FALSE | -2.4258 | -3.454 | -0.53493 | -0.73084 | 0 |  |  | none | FALSE | 0 | 70.2326 | FALSE | FALSE | 0.0852 |  | 71.713 | 0 | 0 | 0.14112 | 0.23364 | -0.60399 | 0.74019 | Normal | 73.1933 | 1.2773 | Day | 202602 | 2026-02-04 | 1.2773
2026-02-04 15:43 | 72.941 | FALSE | FALSE | -2.4611 | -3.492 | -0.28746 | -0.39255 | 0.2826 |  |  | none | FALSE | 0 | 70.4799 | FALSE | FALSE | 0.1054 |  | 71.8542 | 0 | 0.2826 | 0.14121 | 0.2337 | 0.605 | 0.68715 | Normal | 73.2285 | 1.5817 | Day | 202602 | 2026-02-04 | 1.5817
2026-02-04 15:58 | 72.941 | FALSE | FALSE | -2.2341 | -3.1596 | -0.31454 | -0.42937 | 0 |  |  | none | FALSE | 0 | 70.7069 | FALSE | FALSE | 0.1004 |  | 71.9812 | 0 | 0 | 0.12708 | 0.23325 | -0.54483 | 0.63715 | Normal | 73.2555 | 1.5063 | Day | 202602 | 2026-02-04 | 1.5063
2026-02-04 16:13 | 72.941 | FALSE | FALSE | -2.0337 | -2.8681 | -0.34006 | -0.46406 | 0 |  |  | none | FALSE | 0 | 70.9073 | FALSE | FALSE | 0.0951 |  | 72.0942 | 0 | 0 | 0.11295 | 0.23188 | -0.4871 | 0.59344 | Normal | 73.2811 | 1.427 | Day | 202602 | 2026-02-04 | 1.427
2026-02-04 16:28 | 72.941 | FALSE | FALSE | -1.866 | -2.6254 | -0.37 | -0.50469 | 0 |  |  | none | FALSE | 0 | 71.075 | FALSE | FALSE | 0.0892 |  | 72.193 | 0 | 0 | 0.09882 | 0.2296 | -0.4304 | 0.55899 | Normal | 73.311 | 1.3381 | Day | 202602 | 2026-02-04 | 1.3381
2026-02-04 16:42 | 72.941 | FALSE | FALSE | -1.7353 | -2.437 | -0.40869 | -0.55718 | 0 |  |  | none | FALSE | 0 | 71.2057 | FALSE | FALSE | 0.0825 |  | 72.2777 | 0 | 0 | 0.08469 | 0.22637 | -0.37412 | 0.53599 | Normal | 73.3497 | 1.2375 | Day | 202602 | 2026-02-04 | 1.2375
2026-02-04 16:57 | 72.941 | FALSE | FALSE | -1.643 | -2.3044 | -0.45753 | -0.62334 | 0 |  |  | none | FALSE | 0 | 71.298 | FALSE | FALSE | 0.0752 |  | 72.3483 | 0 | 0 | 0.07056 | 0.22215 | -0.31763 | 0.52513 | Normal | 73.3985 | 1.1287 | Day | 202602 | 2026-02-04 | 1.1287
2026-02-04 17:12 | 72.941 | FALSE | FALSE | -1.5866 | -2.2236 | -0.51401 | -0.69976 | 0 |  |  | none | FALSE | 0 | 71.3544 | FALSE | FALSE | 0.0681 |  | 72.4047 | 0 | 0 | 0.05643 | 0.21687 | -0.2602 | 0.52516 | Normal | 73.455 | 1.0212 | Day | 202602 | 2026-02-04 | 1.0212
2026-02-04 17:27 | 72.941 | FALSE | FALSE | -1.5598 | -2.1852 | -0.57182 | -0.77785 | 0 |  |  | none | FALSE | 0 | 71.3812 | FALSE | FALSE | 0.0618 |  | 72.447 | 0 | 0 | 0.0423 | 0.21047 | -0.20097 | 0.53291 | Normal | 73.5128 | 0.927 | Day | 202602 | 2026-02-04 | 0.927
2026-02-04 17:42 | 72.941 | FALSE | FALSE | -1.4812 | -2.0728 | -0.60606 | -0.82404 | 0 |  |  | none | FALSE | 0 | 71.4598 | FALSE | FALSE | 0.0559 |  | 72.5034 | 0 | 0 | 0.05643 | 0.19654 | -0.28712 | 0.52182 | Normal | 73.5471 | 0.83857 | Day | 202602 | 2026-02-04 | 0.83857
2026-02-04 17:57 | 72.941 | FALSE | FALSE | -1.2287 | -1.7134 | -0.52293 | -0.71182 | 0 |  |  | none | FALSE | 0 | 71.7123 | FALSE | FALSE | 0.0537 |  | 72.5881 | 0 | 0 | 0.08469 | 0.13273 | -0.63807 | 0.43791 | Normal | 73.4639 | 0.80585 | Day | 202602 | 2026-02-04 | 0.80585
2026-02-04 18:12 | 72.941 | FALSE | FALSE | -1.0148 | -1.4109 | -0.45015 | -0.61336 | 0 |  |  | none | FALSE | 0 | 71.9262 | FALSE | FALSE | 0.0514 |  | 72.6587 | 0 | 0 | 0.07056 | 0.12539 | -0.56273 | 0.36624 | Normal | 73.3911 | 0.77089 | Night | 202602 | 2026-02-04 | 0.77089
2026-02-04 18:27 | 72.941 | FALSE | FALSE | -0.8497 | -1.1786 | -0.3979 | -0.54255 | 0 |  |  | none | FALSE | 0 | 72.0913 | FALSE | FALSE | 0.0483 |  | 72.7151 | 0 | 0 | 0.05643 | 0.11579 | -0.48734 | 0.3119 | Normal | 73.3389 | 0.72427 | Night | 202602 | 2026-02-04 | 0.72427
2026-02-04 18:42 | 72.3758 | TRUE | FALSE | -0.22249 | -0.30836 | -0.92917 | -1.2675 | -0.5652 |  |  | none | FALSE | 1 | 72.1533 | FALSE | FALSE | 0.1104 |  | 72.7291 | 0 | -0.5652 | 0.01404 | 0.17077 | -3.3919 | 0.28791 | Normal | 73.305 | -1.2272 | Night | 202602 | 2026-02-04 | 1.2272
2026-02-04 18:42 | 72.3758 | FALSE | FALSE | -0.15451 | -0.21395 | -0.88927 | -1.2138 | 0 |  |  | none | FALSE | 1 | 72.2213 | FALSE | FALSE | 0.1224 |  | 72.7432 | 0 | 0 | 0.01404 | 0.17077 | -0.082216 | 0.26095 | Normal | 73.2651 | -1.4079 | Night | 202602 | 2026-02-04 | 1.4079
2026-02-04 18:57 | 72.3758 | FALSE | FALSE | -0.15451 | -0.21395 | -0.88927 | -1.2138 | 0 |  |  | none | FALSE | 1 | 72.2213 | FALSE | FALSE | 0.1224 |  | 72.7432 | 0 | 0 | 0 | 0.15881 | 0 | 0.26095 | Normal | 73.2651 | -1.4079 | Night | 202602 | 2026-02-04 | 1.4079
2026-02-04 19:12 | 72.3758 | FALSE | FALSE | -0.15451 | -0.21395 | -0.88927 | -1.2138 | 0 |  |  | none | FALSE | 1 | 72.2213 | FALSE | FALSE | 0.1224 |  | 72.7432 | 0 | 0 | 0 | 0.15881 | 0 | 0.26095 | Normal | 73.2651 | -1.4079 | Night | 202602 | 2026-02-04 | 1.4079
2026-02-04 19:27 | 72.3758 | FALSE | FALSE | -0.15451 | -0.21395 | -0.88927 | -1.2138 | 0 |  |  | none | FALSE | 1 | 72.2213 | FALSE | FALSE | 0.1224 |  | 72.7432 | 0 | 0 | 0 | 0.15881 | 0 | 0.26095 | Normal | 73.2651 | -1.4079 | Night | 202602 | 2026-02-04 | 1.4079
2026-02-04 19:41 | 72.3758 | FALSE | FALSE | -0.15451 | -0.21395 | -0.88927 | -1.2138 | 0 |  |  | none | FALSE | 1 | 72.2213 | FALSE | FALSE | 0.1224 |  | 72.7432 | 0 | 0 | 0 | 0.15881 | 0 | 0.26095 | Normal | 73.2651 | -1.4079 | Night | 202602 | 2026-02-04 | 1.4079
2026-02-04 19:56 | 72.095 | FALSE | FALSE | 0.023378 | 0.032416 | -1.2166 | -1.6595 | -0.2808 | 2026-02-05 08:30 | 2026-02-04 19:56 | lower | TRUE | 1 | 72.1184 | FALSE | FALSE | 0.2243 | 2.0784 | 72.715 | 1 | -0.2808 | -0.02817 | 0.15598 | -1.6196 | 0.29832 | Extreme triggered | 73.3116 | -2.0784 | Night | 202602 | 2026-02-04 | 2.0784
2026-02-04 20:11 | 71.8124 | FALSE | FALSE | 0.1397 | 0.19416 | -1.5809 | -2.154 | -0.2826 |  | 2026-02-04 19:56 | lower | TRUE | 1 | 71.9521 | FALSE | FALSE | 0.302 | 2.233 | 72.6727 | 2 | -0.2826 | -0.0423 | 0.16579 | -1.4494 | 0.3603 | Extreme/elevated | 73.3933 | -2.3877 | Night | 202602 | 2026-02-04 | 2.3877
2026-02-04 20:26 | 71.8124 | FALSE | FALSE | -0.00019339 | -0.0002693 | -1.608 | -2.1901 | 0 |  | 2026-02-04 19:56 | none | FALSE | 1 | 71.8122 | FALSE | FALSE | 0.3333 | 2.1552 | 72.6163 | 3 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.40204 | Persistent | 73.4204 | -1.9995 | Night | 202602 | 2026-02-04 | 1.9995
2026-02-04 20:41 | 71.5298 | FALSE | FALSE | 0.092943 | 0.12977 | -1.9389 | -2.6391 | -0.2826 |  | 2026-02-04 19:56 | lower | TRUE | 1 | 71.6227 | FALSE | TRUE | 0.4039 | 2.1668 | 72.5457 | 4 | -0.2826 | -0.07056 | 0.15534 | -1.365 | 0.46149 | Persistent | 73.4687 | -2.2014 | Night | 202602 | 2026-02-04 | 2.2014
2026-02-04 20:56 | 71.5298 | FALSE | FALSE | -0.062267 | -0.087126 | -1.953 | -2.6577 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 71.4675 | FALSE | FALSE | 0.4108 | 2.1087 | 72.4752 | 5 | 0 | -0.07056 | 0.15534 | 0.45424 | 0.50381 | Persistent | 73.4828 | -1.8764 | Night | 202602 | 2026-02-04 | 1.8764
2026-02-04 21:11 | 71.2472 | FALSE | FALSE | 0.022165 | 0.0311 | -2.2644 | -3.0803 | -0.2826 |  | 2026-02-04 19:56 | lower | TRUE | 0 | 71.2694 | FALSE | TRUE | 0.4788 | 2.0972 | 72.3905 | 6 | -0.2826 | -0.08469 | 0.16132 | -1.2268 | 0.56055 | Persistent | 73.5116 | -2.0395 | Night | 202602 | 2026-02-04 | 2.0395
2026-02-04 21:26 | 71.2472 | FALSE | TRUE | -0.1406 | -0.19774 | -2.2578 | -3.0716 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 71.1066 | FALSE | FALSE | 0.5177 | 2.0498 | 72.3058 | 7 | 0 | -0.08469 | 0.16132 | 0.52499 | 0.59959 | Confirmed/Materialized Shift | 73.505 | -1.7655 | Night | 202602 | 2026-02-04 | 1.7655
2026-02-04 21:41 | 70.9646 | FALSE | TRUE | -0.057895 | -0.081649 | -2.5426 | -3.459 | -0.2826 |  | 2026-02-04 19:56 | none | FALSE | 0 | 70.9067 | FALSE | FALSE | 0.5274 | 2.0324 | 72.207 | 8 | -0.2826 | -0.09882 | 0.16582 | -1.1083 | 0.65013 | Confirmed/Materialized Shift | 73.5072 | -1.9109 | Night | 202602 | 2026-02-04 | 1.9109
2026-02-04 21:56 | 70.9646 | FALSE | TRUE | -0.22066 | -0.31192 | -2.5077 | -3.4132 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 70.7439 | FALSE | FALSE | 0.5118 | 1.9929 | 72.1081 | 9 | 0 | -0.09882 | 0.16582 | 0.59594 | 0.6821 | Confirmed/Materialized Shift | 73.4723 | -1.6765 | Night | 202602 | 2026-02-04 | 1.6765
2026-02-04 22:11 | 70.9646 | FALSE | TRUE | -0.35142 | -0.49767 | -2.4409 | -3.3252 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 70.6132 | FALSE | FALSE | 0.4998 | 1.9432 | 72.0093 | 10 | 0 | -0.09882 | 0.16582 | 0.59594 | 0.69807 | Confirmed/Materialized Shift | 73.4055 | -1.4966 | Night | 202602 | 2026-02-04 | 1.4966
2026-02-04 22:26 | 70.682 | FALSE | TRUE | -0.22911 | -0.3252 | -2.6579 | -3.624 | -0.2826 |  | 2026-02-04 19:56 | none | FALSE | 0 | 70.4529 | FALSE | FALSE | 0.5122 | 1.9196 | 71.8964 | 11 | -0.2826 | -0.11295 | 0.16897 | -1.004 | 0.72174 | Confirmed/Materialized Shift | 73.3399 | -1.6826 | Night | 202602 | 2026-02-04 | 1.6826
2026-02-04 22:40 | 70.682 | FALSE | TRUE | -0.35139 | -0.49962 | -2.5542 | -3.4877 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 70.3306 | FALSE | FALSE | 0.5011 | 1.8859 | 71.7834 | 12 | 0 | -0.11295 | 0.16897 | 0.66847 | 0.7264 | Confirmed/Materialized Shift | 73.2362 | -1.5163 | Night | 202602 | 2026-02-04 | 1.5163
2026-02-04 22:55 | 70.3994 | FALSE | TRUE | -0.21405 | -0.30498 | -2.7279 | -3.7304 | -0.2826 |  | 2026-02-04 19:56 | none | FALSE | 0 | 70.1853 | FALSE | FALSE | 0.5139 | 1.8723 | 71.6563 | 13 | -0.2826 | -0.12708 | 0.17083 | -0.91037 | 0.7355 | Confirmed/Materialized Shift | 73.1273 | -1.709 | Night | 202602 | 2026-02-04 | 1.709
2026-02-04 23:10 | 70.3994 | FALSE | TRUE | -0.3127 | -0.44616 | -2.5724 | -3.5252 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 70.0867 | FALSE | FALSE | 0.5044 | 1.8505 | 71.5293 | 14 | 0 | -0.12708 | 0.17083 | 0.74389 | 0.72128 | Confirmed/Materialized Shift | 72.9718 | -1.5665 | Night | 202602 | 2026-02-04 | 1.5665
2026-02-04 23:26 | 70.3994 | FALSE | TRUE | -0.43789 | -0.6259 | -2.5 | -3.4293 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 69.9615 | FALSE | FALSE | 0.4936 | 1.8207 | 71.4304 | 15 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.73446 | Confirmed/Materialized Shift | 72.8994 | -1.4038 | Night | 202602 | 2026-02-04 | 1.4038
2026-02-04 23:40 | 70.1168 | FALSE | TRUE | -0.30901 | -0.44265 | -2.7104 | -3.7217 | -0.2826 |  | 2026-02-04 19:56 | none | FALSE | 0 | 69.8078 | FALSE | FALSE | 0.506 | 1.8063 | 71.3175 | 16 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.75485 | Confirmed/Materialized Shift | 72.8272 | -1.5906 | Night | 202602 | 2026-02-04 | 1.5906
2026-02-04 23:55 | 70.1168 | FALSE | TRUE | -0.42658 | -0.61212 | -2.6021 | -3.5783 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 69.6902 | FALSE | FALSE | 0.4958 | 1.7846 | 71.2045 | 17 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.75716 | Confirmed/Materialized Shift | 72.7189 | -1.4366 | Night | 202602 | 2026-02-04 | 1.4366
2026-02-05 00:10 | 70.1168 | FALSE | TRUE | -0.50836 | -0.73032 | -2.4579 | -3.3868 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 69.6084 | FALSE | FALSE | 0.4876 | 1.7585 | 71.0916 | 18 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.74158 | Confirmed/Materialized Shift | 72.5747 | -1.3145 | Night | 202602 | 2026-02-05 | 1.3145
2026-02-05 00:25 | 70.1168 | FALSE | TRUE | -0.55197 | -0.79347 | -2.2757 | -3.1435 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 69.5648 | FALSE | FALSE | 0.4813 | 1.7301 | 70.9786 | 19 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.70691 | Confirmed/Materialized Shift | 72.3925 | -1.2192 | Night | 202602 | 2026-02-05 | 1.2192
2026-02-05 00:40 | 69.836 | FALSE | TRUE | -0.32408 | -0.46622 | -2.3554 | -3.2627 | -0.2808 |  | 2026-02-04 19:56 | none | FALSE | 0 | 69.5119 | FALSE | FALSE | 0.5011 | 1.7194 | 70.8517 | 20 | -0.2808 | -0.12699 | 0.14404 | -1.0678 | 0.66987 | Confirmed/Materialized Shift | 72.1914 | -1.5162 | Night | 202602 | 2026-02-05 | 1.5162
2026-02-05 00:55 | 69.836 | FALSE | TRUE | -0.37514 | -0.54007 | -2.1805 | -3.0278 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 69.4609 | FALSE | FALSE | 0.4942 | 1.7048 | 70.7387 | 21 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.63892 | Confirmed/Materialized Shift | 72.0165 | -1.4129 | Night | 202602 | 2026-02-05 | 1.4129
2026-02-05 01:10 | 69.836 | FALSE | TRUE | -0.42925 | -0.61845 | -2.037 | -2.8342 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 69.4068 | FALSE | FALSE | 0.4869 | 1.6866 | 70.6399 | 22 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.61656 | Confirmed/Materialized Shift | 71.873 | -1.3038 | Night | 202602 | 2026-02-05 | 1.3038
2026-02-05 01:25 | 69.5534 | FALSE | TRUE | -0.22061 | -0.31819 | -2.1677 | -3.0224 | -0.2826 |  | 2026-02-04 19:56 | none | FALSE | 0 | 69.3328 | FALSE | FALSE | 0.5087 | 1.6841 | 70.5269 | 23 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.59707 | Confirmed/Materialized Shift | 71.7211 | -1.6305 | Night | 202602 | 2026-02-05 | 1.6305
2026-02-05 01:39 | 69.5534 | FALSE | TRUE | -0.29689 | -0.42868 | -2.0463 | -2.858 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 69.2565 | FALSE | FALSE | 0.4995 | 1.6762 | 70.4281 | 24 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.5858 | Confirmed/Materialized Shift | 71.5997 | -1.4932 | Night | 202602 | 2026-02-05 | 1.4932
2026-02-05 01:54 | 69.5534 | FALSE | TRUE | -0.33635 | -0.48594 | -1.8881 | -2.6429 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 69.217 | FALSE | FALSE | 0.493 | 1.6649 | 70.3293 | 25 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.55612 | Confirmed/Materialized Shift | 71.4415 | -1.3952 | Night | 202602 | 2026-02-05 | 1.3952
2026-02-05 02:10 | 69.2708 | FALSE | TRUE | -0.16036 | -0.23203 | -2.0797 | -2.9148 | -0.2826 |  | 2026-02-04 19:56 | none | FALSE | 0 | 69.1104 | FALSE | FALSE | 0.5142 | 1.6668 | 70.2305 | 26 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.56001 | Confirmed/Materialized Shift | 71.3505 | -1.7137 | Night | 202602 | 2026-02-05 | 1.7137
2026-02-05 02:25 | 69.2708 | FALSE | TRUE | -0.22984 | -0.3329 | -1.9515 | -2.7401 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 69.041 | FALSE | FALSE | 0.5052 | 1.6635 | 70.1316 | 27 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.54534 | Confirmed/Materialized Shift | 71.2223 | -1.5785 | Night | 202602 | 2026-02-05 | 1.5785
2026-02-05 02:39 | 69.2708 | FALSE | TRUE | -0.30521 | -0.44255 | -1.8575 | -2.6115 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 68.9656 | FALSE | FALSE | 0.4957 | 1.6554 | 70.047 | 28 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.54068 | Confirmed/Materialized Shift | 71.1283 | -1.4355 | Night | 202602 | 2026-02-05 | 1.4355
2026-02-05 02:54 | 68.9882 | FALSE | TRUE | -0.12953 | -0.18811 | -2.0494 | -2.885 | -0.2826 |  | 2026-02-04 19:56 | none | FALSE | 0 | 68.8587 | FALSE | FALSE | 0.5175 | 1.6591 | 69.9481 | 29 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.54474 | Confirmed/Materialized Shift | 71.0376 | -1.7622 | Night | 202602 | 2026-02-05 | 1.7622
2026-02-05 03:09 | 68.9882 | FALSE | TRUE | -0.19827 | -0.28823 | -1.9205 | -2.7084 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 68.7899 | FALSE | FALSE | 0.5084 | 1.658 | 69.8493 | 30 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.5297 | Confirmed/Materialized Shift | 70.9087 | -1.6257 | Night | 202602 | 2026-02-05 | 1.6257
2026-02-05 03:24 | 68.9882 | FALSE | TRUE | -0.27346 | -0.39796 | -1.8263 | -2.579 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 68.7147 | FALSE | FALSE | 0.4986 | 1.6522 | 69.7646 | 31 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.52494 | Confirmed/Materialized Shift | 70.8145 | -1.4791 | Night | 202602 | 2026-02-05 | 1.4791
2026-02-05 03:39 | 68.7056 | FALSE | TRUE | -0.09813 | -0.14303 | -2.0186 | -2.8541 | -0.2826 |  | 2026-02-04 19:56 | none | FALSE | 0 | 68.6075 | FALSE | FALSE | 0.521 | 1.6573 | 69.6658 | 32 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.52917 | Confirmed/Materialized Shift | 70.7242 | -1.8146 | Night | 202602 | 2026-02-05 | 1.8146
2026-02-05 03:54 | 68.7056 | FALSE | TRUE | -0.20647 | -0.30141 | -1.9575 | -2.7702 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 68.4991 | FALSE | FALSE | 0.5079 | 1.6561 | 69.5811 | 33 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.54099 | Confirmed/Materialized Shift | 70.6631 | -1.6184 | Night | 202602 | 2026-02-05 | 1.6184
2026-02-05 04:09 | 68.7056 | FALSE | TRUE | -0.28662 | -0.41892 | -1.8683 | -2.6473 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 68.419 | FALSE | FALSE | 0.4979 | 1.6506 | 69.4964 | 34 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.53873 | Confirmed/Materialized Shift | 70.5739 | -1.468 | Night | 202602 | 2026-02-05 | 1.468
2026-02-05 04:24 | 68.7056 | FALSE | TRUE | -0.33824 | -0.49473 | -1.7505 | -2.4845 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 68.3674 | FALSE | FALSE | 0.4902 | 1.642 | 69.4117 | 35 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.52219 | Confirmed/Materialized Shift | 70.4561 | -1.3523 | Night | 202602 | 2026-02-05 | 1.3523
2026-02-05 04:39 | 68.7056 | FALSE | TRUE | -0.39887 | -0.58393 | -1.67 | -2.373 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 68.3067 | FALSE | FALSE | 0.4819 | 1.6306 | 69.3412 | 36 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.51722 | Confirmed/Materialized Shift | 70.3756 | -1.2288 | Night | 202602 | 2026-02-05 | 1.2288
2026-02-05 04:54 | 68.423 | FALSE | TRUE | -0.21088 | -0.30916 | -1.8779 | -2.6712 | -0.2826 |  | 2026-02-04 19:56 | none | FALSE | 0 | 68.2121 | FALSE | FALSE | 0.5064 | 1.6296 | 69.2565 | 37 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.52219 | Confirmed/Materialized Shift | 70.3009 | -1.5962 | Night | 202602 | 2026-02-05 | 1.5962
2026-02-05 05:09 | 68.423 | FALSE | TRUE | -0.27636 | -0.40553 | -1.774 | -2.5271 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 68.1466 | FALSE | FALSE | 0.4974 | 1.6252 | 69.1718 | 38 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.51258 | Confirmed/Materialized Shift | 70.197 | -1.4608 | Night | 202602 | 2026-02-05 | 1.4608
2026-02-05 05:24 | 68.423 | FALSE | TRUE | -0.31097 | -0.45656 | -1.6392 | -2.3396 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 68.112 | FALSE | FALSE | 0.4908 | 1.6184 | 69.0871 | 39 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.48754 | Confirmed/Materialized Shift | 70.0622 | -1.3622 | Night | 202602 | 2026-02-05 | 1.3622
2026-02-05 05:38 | 68.423 | FALSE | TRUE | -0.35762 | -0.5254 | -1.5445 | -2.2075 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 68.0654 | FALSE | FALSE | 0.4832 | 1.6092 | 69.0165 | 40 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.47554 | Confirmed/Materialized Shift | 69.9675 | -1.248 | Night | 202602 | 2026-02-05 | 1.248
2026-02-05 05:53 | 68.423 | FALSE | TRUE | -0.38067 | -0.55946 | -1.4263 | -2.042 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 68.0423 | FALSE | FALSE | 0.4772 | 1.5982 | 68.9458 | 41 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.45174 | Confirmed/Materialized Shift | 69.8493 | -1.1573 | Night | 202602 | 2026-02-05 | 1.1573
2026-02-05 06:08 | 68.1404 | FALSE | TRUE | -0.14871 | -0.21872 | -1.59 | -2.2802 | -0.2826 |  | 2026-02-04 19:56 | none | FALSE | 0 | 67.9917 | FALSE | FALSE | 0.5105 | 1.5996 | 68.861 | 42 | -0.2826 | -0.08478 | 0.13287 | -1.4888 | 0.43467 | Confirmed/Materialized Shift | 69.7304 | -1.6579 | Night | 202602 | 2026-02-05 | 1.6579
2026-02-05 06:23 | 68.1404 | FALSE | TRUE | -0.21208 | -0.31221 | -1.512 | -2.1708 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 67.9283 | FALSE | FALSE | 0.5005 | 1.5974 | 68.7904 | 43 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.43103 | Confirmed/Materialized Shift | 69.6524 | -1.508 | Night | 202602 | 2026-02-05 | 1.508
2026-02-05 06:38 | 68.1404 | FALSE | TRUE | -0.25043 | -0.36888 | -1.4091 | -2.026 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 67.89 | FALSE | FALSE | 0.4931 | 1.5929 | 68.7197 | 44 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.41488 | Confirmed/Materialized Shift | 69.5495 | -1.3964 | Night | 202602 | 2026-02-05 | 1.3964
2026-02-05 06:53 | 67.8596 | FALSE | TRUE | -0.041712 | -0.061505 | -1.5926 | -2.2931 | -0.2808 |  | 2026-02-04 19:56 | none | FALSE | 0 | 67.8179 | FALSE | FALSE | 0.5265 | 1.5997 | 68.635 | 45 | -0.2808 | -0.08469 | 0.13273 | -1.4775 | 0.40858 | Confirmed/Materialized Shift | 69.4522 | -1.8979 | Night | 202602 | 2026-02-05 | 1.8979
2026-02-05 07:08 | 67.8596 | FALSE | TRUE | -0.12474 | -0.18416 | -1.5345 | -2.2113 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 67.7349 | FALSE | FALSE | 0.5133 | 1.6018 | 68.5645 | 46 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.41481 | Confirmed/Materialized Shift | 69.3941 | -1.6993 | Day | 202602 | 2026-02-05 | 1.6993
2026-02-05 07:23 | 67.8596 | FALSE | TRUE | -0.18231 | -0.26938 | -1.4509 | -2.0934 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 67.6773 | FALSE | FALSE | 0.5036 | 1.6008 | 68.4939 | 47 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.40831 | Confirmed/Materialized Shift | 69.3105 | -1.5535 | Day | 202602 | 2026-02-05 | 1.5535
2026-02-05 07:30 | 67.8596 | FALSE | TRUE | -0.21313 | -0.31507 | -1.3407 | -1.9374 | 0 |  | 2026-02-04 19:56 | none | FALSE | 0 | 67.6465 | FALSE | FALSE | 0.4968 | 1.5977 | 68.4234 | 48 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.38845 | Confirmed/Materialized Shift | 69.2003 | -1.4513 | Day | 202602 | 2026-02-05 | 1.4513
2026-02-05 07:45 | 67.577 | FALSE | TRUE | -0.040435 | -0.059871 | -1.592 | -2.3017 | -0.2826 |  | 2026-02-04 19:56 | none | FALSE | 0 | 67.5366 | FALSE | FALSE | 0.5267 | 1.6039 | 68.3528 | 49 | -0.2826 | -0.07056 | 0.12539 | -1.6911 | 0.40812 | Confirmed/Materialized Shift | 69.169 | -1.9009 | Day | 202602 | 2026-02-05 | 1.9009
2026-02-05 08:00 | 67.8596 | TRUE | TRUE | -0.35002 | -0.51848 | -1.2236 | -1.7711 | 0.2826 |  | 2026-02-04 19:56 | none | FALSE | 1 | 67.5096 | FALSE | FALSE | 0.5026 | 1.594 | 68.2964 | 50 | 0.2826 | -0.05643 | 0.1477 | 2.2954 | 0.3934 | Confirmed/Materialized Shift | 69.0832 | -1.1103 | Day | 202602 | 2026-02-05 | 1.1103
2026-02-05 08:15 | 67.577 | FALSE | TRUE | -0.12982 | -0.19248 | -1.4274 | -2.0686 | -0.2826 |  | 2026-02-04 19:56 | none | FALSE | 1 | 67.4472 | FALSE | FALSE | 0.5397 | 1.5954 | 68.2258 | 51 | -0.2826 | -0.07056 | 0.15534 | -1.365 | 0.38931 | Confirmed/Materialized Shift | 69.0044 | -1.6665 | Day | 202602 | 2026-02-05 | 1.6665
2026-02-05 08:30 | 67.8596 | FALSE | FALSE | -0.43668 | -0.64768 | -1.0845 | -1.573 | 0.2826 |  |  | none | FALSE | 1 | 67.4229 | FALSE | FALSE | 0.0854 |  | 68.1835 | 0 | 0.2826 | -0.0423 | 0.16579 | 1.9597 | 0.3803 | Persistence ends | 68.9441 | -0.85173 | Day | 202602 | 2026-02-05 | 0.85173
2026-02-05 08:45 | 67.8596 | FALSE | FALSE | -0.45028 | -0.66799 | -1.0135 | -1.4716 | 0 |  |  | none | FALSE | 1 | 67.4093 | FALSE | FALSE | 0.0799 |  | 68.1412 | 0 | 0 | -0.0423 | 0.16579 | 0.25514 | 0.36595 | Normal | 68.8731 | -0.76954 | Day | 202602 | 2026-02-05 | 0.76954
2026-02-05 08:45 | 67.8596 | FALSE | FALSE | -0.4519 | -0.6704 | -0.93052 | -1.3527 | 0 |  |  | none | FALSE | 1 | 67.4077 | FALSE | FALSE | 0.0747 |  | 68.0989 | 0 | 0 | -0.0423 | 0.16579 | 0.25514 | 0.34561 | Normal | 68.7901 | -0.69244 | Day | 202602 | 2026-02-05 | 0.69244
2026-02-05 09:00 | 68.1404 | FALSE | FALSE | -0.70005 | -1.038 | -0.56055 | -0.81593 | 0.2808 |  |  | none | FALSE | 1 | 67.4403 | FALSE | FALSE | 0.0433 |  | 68.0707 | 0 | 0.2808 | -0.02826 | 0.18077 | 1.7097 | 0.31515 | Normal | 68.701 | 0.22132 | Day | 202602 | 2026-02-05 | 0.22132
2026-02-05 09:15 | 68.1404 | FALSE | FALSE | -0.65485 | -0.97035 | -0.45883 | -0.66885 | 0 |  |  | none | FALSE | 1 | 67.4856 | FALSE | FALSE | 0.052 |  | 68.0424 | 0 | 0 | -0.02826 | 0.18077 | 0.15633 | 0.27842 | Normal | 68.5992 | 0.35202 | Day | 202602 | 2026-02-05 | 0.35202
2026-02-05 09:30 | 68.423 | FALSE | FALSE | -0.93745 | -1.3891 | -0.17623 | -0.25689 | 0.2826 |  |  | none | FALSE | 1 | 67.4856 | FALSE | FALSE | 0.1197 |  | 68.0424 | 0 | 0.2826 | 0 | 0.18308 | 1.5436 | 0.27842 | Normal | 68.5992 | 1.367 | Day | 202602 | 2026-02-05 | 1.367
2026-02-05 09:44 | 68.423 | FALSE | FALSE | -0.93745 | -1.3891 | -0.17623 | -0.25689 | 0 |  |  | none | FALSE | 1 | 67.4856 | FALSE | FALSE | 0.1197 |  | 68.0424 | 0 | 0 | 0 | 0.18308 | 0 | 0.27842 | Normal | 68.5992 | 1.367 | Day | 202602 | 2026-02-05 | 1.367
2026-02-05 09:59 | 68.7056 | FALSE | FALSE | -1.2584 | -1.8658 | 0.039712 | 0.057834 | 0.2826 | 2026-02-05 17:40 | 2026-02-05 09:59 | upper | TRUE | 1 | 67.4472 | FALSE | FALSE | 0.2277 | 2.1303 | 68.0565 | 1 | 0.2826 | 0.01413 | 0.19368 | 1.3861 | 0.30468 | Extreme triggered | 68.6659 | 2.1303 | Day | 202602 | 2026-02-05 | 2.1303
2026-02-05 10:14 | 68.9882 | FALSE | FALSE | -1.6262 | -2.4141 | 0.18062 | 0.26251 | 0.2826 |  | 2026-02-05 09:59 | upper | TRUE | 0 | 67.362 | FALSE | FALSE | 0.2809 | 2.3151 | 68.0848 | 2 | 0.2826 | 0.02826 | 0.2027 | 1.2548 | 0.3614 | Extreme/elevated | 68.8076 | 2.4998 | Day | 202602 | 2026-02-05 | 2.4998
2026-02-05 10:22 | 69.5534 | TRUE | FALSE | -2.3811 | -3.5448 | 0.44309 | 0.64114 | 0.5652 |  | 2026-02-05 09:59 | upper | TRUE | 1 | 67.1723 | FALSE | TRUE | 0.3943 | 2.5149 | 68.1413 | 3 | 0.5652 | 0.05652 | 0.23532 | 2.1616 | 0.4845 | Persistent | 69.1103 | 2.9145 | Day | 202602 | 2026-02-05 | 2.9145
2026-02-05 10:22 | 69.5534 | FALSE | FALSE | -2.4981 | -3.7254 | 0.18484 | 0.26646 | 0 |  | 2026-02-05 09:59 | upper | TRUE | 1 | 67.0553 | FALSE | TRUE | 0.4118 | 2.4661 | 68.212 | 4 | 0 | 0.07065 | 0.222 | -0.31825 | 0.57831 | Persistent | 69.3686 | 2.3196 | Day | 202602 | 2026-02-05 | 2.3196
2026-02-05 10:37 | 69.5534 | FALSE | FALSE | -2.5725 | -3.8407 | -0.030928 | -0.044447 | 0 |  | 2026-02-05 09:59 | none | FALSE | 1 | 66.9809 | FALSE | FALSE | 0.4445 | 2.3634 | 68.2826 | 5 | 0 | 0.07065 | 0.222 | -0.31825 | 0.65086 | Persistent | 69.5843 | 1.9525 | Day | 202602 | 2026-02-05 | 1.9525
2026-02-05 10:52 | 69.5534 | FALSE | FALSE | -2.6176 | -3.9106 | -0.21732 | -0.31147 | 0 |  | 2026-02-05 09:59 | none | FALSE | 1 | 66.9358 | FALSE | FALSE | 0.4843 | 2.2517 | 68.3533 | 6 | 0 | 0.07065 | 0.222 | -0.31825 | 0.70873 | Persistent | 69.7707 | 1.6934 | Day | 202602 | 2026-02-05 | 1.6934
2026-02-05 11:07 | 69.836 | FALSE | TRUE | -2.9265 | -4.3739 | -0.15868 | -0.2267 | 0.2826 |  | 2026-02-05 09:59 | none | FALSE | 1 | 66.9095 | FALSE | FALSE | 0.5482 | 2.1863 | 68.4521 | 7 | 0.2826 | 0.09882 | 0.2105 | 0.87306 | 0.7713 | Confirmed/Materialized Shift | 69.9947 | 1.7943 | Day | 202602 | 2026-02-05 | 1.7943
2026-02-05 11:21 | 70.1168 | FALSE | TRUE | -3.2358 | -4.8381 | -0.13204 | -0.18796 | 0.2808 |  | 2026-02-05 09:59 | none | FALSE | 1 | 66.881 | FALSE | FALSE | 0.5514 | 2.1434 | 68.5649 | 8 | 0.2808 | 0.11286 | 0.21291 | 0.78877 | 0.84195 | Confirmed/Materialized Shift | 70.2488 | 1.8432 | Day | 202602 | 2026-02-05 | 1.8432
2026-02-05 11:36 | 70.1168 | FALSE | TRUE | -3.2234 | -4.8188 | -0.34542 | -0.49022 | 0 |  | 2026-02-05 09:59 | none | FALSE | 1 | 66.8934 | FALSE | FALSE | 0.5361 | 2.0845 | 68.6778 | 9 | 0 | 0.11286 | 0.21291 | -0.53008 | 0.89222 | Confirmed/Materialized Shift | 70.4622 | 1.6129 | Day | 202602 | 2026-02-05 | 1.6129
2026-02-05 11:51 | 70.1168 | FALSE | TRUE | -3.177 | -4.746 | -0.52468 | -0.74274 | 0 |  | 2026-02-05 09:59 | none | FALSE | 1 | 66.9398 | FALSE | FALSE | 0.5241 | 2.0193 | 68.7906 | 10 | 0 | 0.11286 | 0.21291 | -0.53008 | 0.92542 | Confirmed/Materialized Shift | 70.6415 | 1.433 | Day | 202602 | 2026-02-05 | 1.433
2026-02-05 12:06 | 70.3994 | FALSE | TRUE | -3.3588 | -5.0101 | -0.42353 | -0.59801 | 0.2826 |  | 2026-02-05 09:59 | none | FALSE | 1 | 67.0406 | FALSE | FALSE | 0.532 | 1.9769 | 68.9318 | 11 | 0.2826 | 0.14112 | 0.19436 | 0.72792 | 0.94558 | Confirmed/Materialized Shift | 70.8229 | 1.5521 | Day | 202602 | 2026-02-05 | 1.5521
2026-02-05 12:21 | 70.3994 | FALSE | TRUE | -3.2694 | -4.8702 | -0.5881 | -0.82846 | 0 |  | 2026-02-05 09:59 | none | FALSE | 1 | 67.13 | FALSE | FALSE | 0.5212 | 1.928 | 69.0588 | 12 | 0 | 0.12699 | 0.19381 | -0.65524 | 0.96437 | Confirmed/Materialized Shift | 70.9875 | 1.3902 | Day | 202602 | 2026-02-05 | 1.3902
2026-02-05 12:36 | 70.682 | FALSE | TRUE | -3.3944 | -5.0446 | -0.45841 | -0.64438 | 0.2826 |  | 2026-02-05 09:59 | none | FALSE | 0 | 67.2876 | FALSE | FALSE | 0.5016 | 1.8969 | 69.214 | 13 | 0.2826 | 0.15525 | 0.17078 | 0.74571 | 0.9632 | Confirmed/Materialized Shift | 71.1404 | 1.5241 | Day | 202602 | 2026-02-05 | 1.5241
2026-02-05 12:51 | 70.682 | FALSE | TRUE | -3.249 | -4.8182 | -0.59528 | -0.83516 | 0 |  | 2026-02-05 09:59 | none | FALSE | 0 | 67.433 | FALSE | FALSE | 0.492 | 1.86 | 69.3551 | 14 | 0 | 0.14112 | 0.17138 | -0.82345 | 0.96108 | Confirmed/Materialized Shift | 71.2773 | 1.3806 | Day | 202602 | 2026-02-05 | 1.3806
2026-02-05 13:06 | 70.9646 | FALSE | TRUE | -3.3693 | -4.9846 | -0.4609 | -0.64528 | 0.2826 |  | 2026-02-05 09:59 | none | FALSE | 0 | 67.5953 | FALSE | FALSE | 0.5012 | 1.8373 | 69.5104 | 15 | 0.2826 | 0.15525 | 0.17078 | 0.74571 | 0.95756 | Confirmed/Materialized Shift | 71.4255 | 1.5187 | Day | 202602 | 2026-02-05 | 1.5187
2026-02-05 13:21 | 70.9646 | FALSE | TRUE | -3.1531 | -4.6498 | -0.55513 | -0.77619 | 0 |  | 2026-02-05 09:59 | none | FALSE | 0 | 67.8115 | FALSE | FALSE | 0.4934 | 1.81 | 69.6656 | 16 | 0 | 0.15525 | 0.17078 | -0.90908 | 0.92705 | Confirmed/Materialized Shift | 71.5197 | 1.4012 | Day | 202602 | 2026-02-05 | 1.4012
2026-02-05 13:36 | 71.2472 | FALSE | TRUE | -3.2628 | -4.7993 | -0.41033 | -0.57262 | 0.2826 |  | 2026-02-05 09:59 | none | FALSE | 0 | 67.9844 | FALSE | FALSE | 0.5035 | 1.7949 | 69.821 | 17 | 0.2826 | 0.15534 | 0.17085 | 0.74487 | 0.91828 | Confirmed/Materialized Shift | 71.6575 | 1.5532 | Day | 202602 | 2026-02-05 | 1.5532
2026-02-05 13:51 | 71.2472 | FALSE | TRUE | -3.033 | -4.4463 | -0.49121 | -0.68472 | 0 |  | 2026-02-05 09:59 | none | FALSE | 0 | 68.2142 | FALSE | FALSE | 0.4962 | 1.7753 | 69.9763 | 18 | 0 | 0.15534 | 0.17085 | -0.90923 | 0.88105 | Confirmed/Materialized Shift | 71.7384 | 1.4425 | Day | 202602 | 2026-02-05 | 1.4425
2026-02-05 14:06 | 71.5298 | FALSE | TRUE | -3.1312 | -4.5779 | -0.33491 | -0.46603 | 0.2826 |  | 2026-02-05 09:59 | none | FALSE | 0 | 68.3986 | FALSE | FALSE | 0.5076 | 1.7668 | 70.1316 | 19 | 0.2826 | 0.15534 | 0.17085 | 0.74487 | 0.86653 | Confirmed/Materialized Shift | 71.8647 | 1.6135 | Day | 202602 | 2026-02-05 | 1.6135
2026-02-05 14:20 | 71.5298 | FALSE | TRUE | -2.8856 | -4.2037 | -0.4 | -0.55609 | 0 |  | 2026-02-05 09:59 | none | FALSE | 0 | 68.6442 | FALSE | FALSE | 0.5009 | 1.7541 | 70.287 | 20 | 0 | 0.15534 | 0.17085 | -0.90923 | 0.8214 | Confirmed/Materialized Shift | 71.9298 | 1.513 | Day | 202602 | 2026-02-05 | 1.513
2026-02-05 14:35 | 71.5298 | FALSE | TRUE | -2.6552 | -3.8551 | -0.45196 | -0.62788 | 0 |  | 2026-02-05 09:59 | none | FALSE | 0 | 68.8746 | FALSE | FALSE | 0.4945 | 1.7381 | 70.4282 | 21 | 0 | 0.14121 | 0.17145 | -0.8236 | 0.77678 | Confirmed/Materialized Shift | 71.9818 | 1.4182 | Day | 202602 | 2026-02-05 | 1.4182
2026-02-05 14:51 | 71.8124 | FALSE | TRUE | -2.7584 | -3.9945 | -0.2724 | -0.37789 | 0.2826 |  | 2026-02-05 09:59 | none | FALSE | 0 | 69.054 | FALSE | FALSE | 0.5094 | 1.7337 | 70.5694 | 22 | 0.2826 | 0.14121 | 0.17145 | 0.82465 | 0.7577 | Confirmed/Materialized Shift | 72.0848 | 1.6405 | Day | 202602 | 2026-02-05 | 1.6405
2026-02-05 15:06 | 71.8124 | FALSE | TRUE | -2.6632 | -3.8514 | -0.40314 | -0.55824 | 0 |  | 2026-02-05 09:59 | none | FALSE | 0 | 69.1492 | FALSE | FALSE | 0.4983 | 1.7224 | 70.6824 | 23 | 0 | 0.11295 | 0.14193 | -0.79582 | 0.76659 | Confirmed/Materialized Shift | 72.2155 | 1.4741 | Day | 202602 | 2026-02-05 | 1.4741
2026-02-05 15:20 | 71.8124 | FALSE | TRUE | -2.5328 | -3.6559 | -0.49864 | -0.68958 | 0 |  | 2026-02-05 09:59 | none | FALSE | 0 | 69.2796 | FALSE | FALSE | 0.4895 | 1.7066 | 70.7953 | 24 | 0 | 0.11295 | 0.14193 | -0.79582 | 0.75786 | Confirmed/Materialized Shift | 72.311 | 1.342 | Day | 202602 | 2026-02-05 | 1.342
2026-02-05 15:35 | 71.8124 | FALSE | TRUE | -2.3659 | -3.4068 | -0.55764 | -0.77054 | 0 |  | 2026-02-05 09:59 | none | FALSE | 0 | 69.4465 | FALSE | FALSE | 0.4825 | 1.6878 | 70.9083 | 25 | 0 | 0.11295 | 0.14193 | -0.79582 | 0.73089 | Confirmed/Materialized Shift | 72.37 | 1.237 | Day | 202602 | 2026-02-05 | 1.237
2026-02-05 15:50 | 71.8124 | FALSE | TRUE | -2.1582 | -3.0985 | -0.57583 | -0.79547 | 0 |  | 2026-02-05 09:59 | none | FALSE | 0 | 69.6542 | FALSE | FALSE | 0.4772 | 1.6674 | 71.0212 | 26 | 0 | 0.11295 | 0.14193 | -0.79582 | 0.68351 | Confirmed/Materialized Shift | 72.3882 | 1.1575 | Day | 202602 | 2026-02-05 | 1.1575
2026-02-05 16:05 | 71.8124 | FALSE | TRUE | -1.9822 | -2.8386 | -0.59746 | -0.82511 | 0 |  | 2026-02-05 09:59 | none | FALSE | 0 | 69.8302 | FALSE | FALSE | 0.4716 | 1.6454 | 71.12 | 27 | 0 | 0.09882 | 0.13817 | -0.71522 | 0.64492 | Confirmed/Materialized Shift | 72.4099 | 1.0736 | Day | 202602 | 2026-02-05 | 1.0736
2026-02-05 16:20 | 72.095 | FALSE | TRUE | -2.1452 | -3.0668 | -0.39308 | -0.54226 | 0.2826 |  | 2026-02-05 09:59 | none | FALSE | 0 | 69.9498 | FALSE | FALSE | 0.492 | 1.6359 | 71.2189 | 28 | 0.2826 | 0.09891 | 0.13829 | 1.3283 | 0.63457 | Confirmed/Materialized Shift | 72.4881 | 1.3806 | Day | 202602 | 2026-02-05 | 1.3806
2026-02-05 16:35 | 72.095 | FALSE | TRUE | -1.9918 | -2.8412 | -0.43749 | -0.60317 | 0 |  | 2026-02-05 09:59 | none | FALSE | 0 | 70.1032 | FALSE | FALSE | 0.4853 | 1.6236 | 71.3179 | 29 | 0 | 0.09891 | 0.13829 | -0.71522 | 0.60732 | Confirmed/Materialized Shift | 72.5325 | 1.2796 | Day | 202602 | 2026-02-05 | 1.2796
2026-02-05 16:50 | 72.095 | FALSE | TRUE | -1.7997 | -2.5602 | -0.4432 | -0.61099 | 0 |  | 2026-02-05 09:59 | none | FALSE | 0 | 70.2953 | FALSE | FALSE | 0.4806 | 1.6098 | 71.4168 | 30 | 0 | 0.09891 | 0.13829 | -0.71522 | 0.56072 | Confirmed/Materialized Shift | 72.5382 | 1.2096 | Day | 202602 | 2026-02-05 | 1.2096
2026-02-05 16:55 | 72.095 | FALSE | TRUE | -1.6453 | -2.3354 | -0.45835 | -0.63175 | 0 |  | 2026-02-05 09:59 | none | FALSE | 0 | 70.4497 | FALSE | FALSE | 0.4752 | 1.5943 | 71.5015 | 31 | 0 | 0.08478 | 0.13287 | -0.63808 | 0.52591 | Confirmed/Materialized Shift | 72.5534 | 1.1285 | Day | 202602 | 2026-02-05 | 1.1285
2026-02-05 17:10 | 72.095 | FALSE | TRUE | -1.4544 | -2.0589 | -0.43708 | -0.6026 | 0 |  | 2026-02-05 09:59 | none | FALSE | 0 | 70.6406 | FALSE | FALSE | 0.4717 | 1.5781 | 71.5863 | 32 | 0 | 0.08478 | 0.13287 | -0.63808 | 0.47288 | Confirmed/Materialized Shift | 72.5321 | 1.0757 | Day | 202602 | 2026-02-05 | 1.0757
2026-02-05 17:25 | 72.095 | FALSE | TRUE | -1.3074 | -1.8469 | -0.43131 | -0.5947 | 0 |  | 2026-02-05 09:59 | none | FALSE | 0 | 70.7876 | FALSE | FALSE | 0.4672 | 1.5608 | 71.657 | 33 | 0 | 0.07065 | 0.12555 | -0.56273 | 0.43467 | Confirmed/Materialized Shift | 72.5263 | 1.0077 | Day | 202602 | 2026-02-05 | 1.0077
2026-02-05 17:40 | 72.095 | FALSE | FALSE | -1.1257 | -1.5861 | -0.39092 | -0.5393 | 0 |  |  | none | FALSE | 0 | 70.9693 | FALSE | FALSE | 0.0646 |  | 71.7276 | 0 | 0 | 0.07065 | 0.12555 | -0.56273 | 0.37915 | Persistence ends | 72.4859 | 0.96896 | Day | 202602 | 2026-02-05 | 0.96896
2026-02-05 17:54 | 71.8124 | TRUE | FALSE | -0.71051 | -0.99929 | -0.62573 | -0.86382 | -0.2826 |  |  | none | FALSE | 1 | 71.1019 | FALSE | FALSE | 0.037 |  | 71.77 | 0 | -0.2826 | 0.04239 | 0.13829 | -2.35 | 0.33406 | Normal | 72.4381 | 0.12689 | Day | 202602 | 2026-02-05 | 0.12689
2026-02-05 18:09 | 71.8124 | FALSE | FALSE | -0.55013 | -0.77197 | -0.55013 | -0.76024 | 0 |  |  | none | FALSE | 1 | 71.2623 | FALSE | FALSE | 0.0286 |  | 71.8124 | 0 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.27506 | Normal | 72.3625 | 0 | Night | 202602 | 2026-02-05 | 0
2026-02-05 18:24 | 71.8124 | FALSE | FALSE | -0.45343 | -0.63542 | -0.50995 | -0.7051 | 0 |  |  | none | FALSE | 1 | 71.359 | FALSE | FALSE | 0.0364 |  | 71.8407 | 0 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.24084 | Normal | 72.3223 | -0.11734 | Night | 202602 | 2026-02-05 | 0.11734
2026-02-05 18:30 | 71.8124 | FALSE | FALSE | -0.33678 | -0.47118 | -0.44982 | -0.62248 | 0 |  |  | none | FALSE | 1 | 71.4756 | FALSE | FALSE | 0.0477 |  | 71.8689 | 0 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.19665 | Normal | 72.2622 | -0.28742 | Night | 202602 | 2026-02-05 | 0.28742
2026-02-05 18:31 | 71.8124 | FALSE | FALSE | -0.29032 | -0.40592 | -0.43162 | -0.59745 | 0 |  |  | none | FALSE | 1 | 71.5221 | FALSE | FALSE | 0.0547 |  | 71.883 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.18049 | Normal | 72.244 | -0.39144 | Night | 202602 | 2026-02-05 | 0.39144
2026-02-05 18:46 | 71.8124 | FALSE | FALSE | -0.23809 | -0.33264 | -0.40765 | -0.56445 | 0 |  |  | none | FALSE | 1 | 71.5743 | FALSE | FALSE | 0.0636 |  | 71.8972 | 0 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.16143 | Normal | 72.22 | -0.52517 | Night | 202602 | 2026-02-05 | 0.52517
2026-02-05 19:01 | 71.5298 | TRUE | FALSE | 0.044515 | 0.062194 | -0.69025 | -0.95575 | -0.2826 | 2026-02-06 00:58 | 2026-02-05 19:01 | lower | TRUE | 2 | 71.5743 | TRUE | FALSE | 0.266 | 2.2757 | 71.8972 | 1 | -0.2826 | 0 | 0.12967 | -2.1794 | 0.16143 | Extreme triggered | 72.22 | -2.2757 | Night | 202602 | 2026-02-05 | 2.2757
2026-02-05 19:16 | 71.5298 | FALSE | FALSE | -0.0077242 | -0.0108 | -0.71422 | -0.98863 | 0 |  | 2026-02-05 19:01 | none | FALSE | 2 | 71.5221 | FALSE | FALSE | 0.3019 | 2.1165 | 71.883 | 2 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.18049 | Extreme/elevated | 72.244 | -1.9572 | Night | 202602 | 2026-02-05 | 1.9572
2026-02-05 19:30 | 71.2472 | TRUE | FALSE | 0.14824 | 0.20763 | -1.0669 | -1.4754 | -0.2826 |  | 2026-02-05 19:01 | lower | TRUE | 3 | 71.3954 | TRUE | TRUE | 0.4335 | 2.2928 | 71.8548 | 3 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.22968 | Persistent | 72.3141 | -2.6454 | Night | 202602 | 2026-02-05 | 2.6454
2026-02-05 19:45 | 70.9646 | FALSE | FALSE | 0.23961 | 0.33652 | -1.456 | -2.0105 | -0.2826 |  | 2026-02-05 19:01 | lower | TRUE | 3 | 71.2042 | FALSE | TRUE | 0.5001 | 2.4166 | 71.8124 | 4 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.30409 | Persistent | 72.4206 | -2.788 | Night | 202602 | 2026-02-05 | 2.788
2026-02-05 20:00 | 70.682 | FALSE | FALSE | 0.28303 | 0.39882 | -1.8647 | -2.5704 | -0.2826 |  | 2026-02-05 19:01 | lower | TRUE | 2 | 70.965 | FALSE | TRUE | 0.5239 | 2.4764 | 71.7559 | 5 | -0.2826 | -0.05652 | 0.14784 | -1.5292 | 0.39543 | Persistent | 72.5467 | -2.7157 | Night | 202602 | 2026-02-05 | 2.7157
2026-02-05 20:15 | 70.3994 | FALSE | FALSE | 0.29027 | 0.41063 | -2.2814 | -3.1389 | -0.2826 |  | 2026-02-05 19:01 | lower | TRUE | 2 | 70.6897 | FALSE | TRUE | 0.5722 | 2.4942 | 71.6852 | 6 | -0.2826 | -0.07065 | 0.15546 | -1.3633 | 0.49778 | Persistent | 72.6808 | -2.5831 | Night | 202602 | 2026-02-05 | 2.5831
2026-02-05 20:29 | 70.1168 | FALSE | TRUE | 0.26901 | 0.38219 | -2.6983 | -3.7057 | -0.2826 |  | 2026-02-05 19:01 | lower | TRUE | 2 | 70.3858 | FALSE | TRUE | 0.62 | 2.4869 | 71.6004 | 7 | -0.2826 | -0.08478 | 0.16143 | -1.2254 | 0.60732 | Confirmed/Materialized Shift | 72.8151 | -2.4429 | Night | 202602 | 2026-02-05 | 2.4429
2026-02-05 20:44 | 70.1168 | FALSE | TRUE | 0.026031 | 0.037111 | -2.7434 | -3.7654 | 0 |  | 2026-02-05 19:01 | lower | TRUE | 2 | 70.1428 | FALSE | TRUE | 0.593 | 2.4308 | 71.5015 | 8 | 0 | -0.09891 | 0.13829 | 0.71522 | 0.67935 | Confirmed/Materialized Shift | 72.8602 | -2.0383 | Night | 202602 | 2026-02-05 | 2.0383
2026-02-05 20:59 | 69.5534 | TRUE | TRUE | 0.23899 | 0.34243 | -3.4031 | -4.6646 | -0.5634 |  | 2026-02-05 19:01 | lower | TRUE | 3 | 69.7924 | TRUE | TRUE | 0.6392 | 2.4165 | 71.3745 | 9 | -0.5634 | -0.12708 | 0.17068 | -2.5564 | 0.79104 | Confirmed/Materialized Shift | 72.9565 | -2.3021 | Night | 202602 | 2026-02-05 | 2.3021
2026-02-05 21:14 | 69.2708 | FALSE | TRUE | 0.16208 | 0.23343 | -3.7628 | -5.1522 | -0.2826 |  | 2026-02-05 19:01 | lower | TRUE | 3 | 69.4329 | FALSE | TRUE | 0.6311 | 2.3929 | 71.2332 | 10 | -0.2826 | -0.14121 | 0.1713 | -0.8254 | 0.90019 | Confirmed/Materialized Shift | 73.0336 | -2.18 | Night | 202602 | 2026-02-05 | 2.18
2026-02-05 21:29 | 68.9882 | FALSE | TRUE | 0.078613 | 0.11382 | -4.1008 | -5.6107 | -0.2826 |  | 2026-02-05 19:01 | lower | TRUE | 2 | 69.0668 | FALSE | TRUE | 0.5957 | 2.3643 | 71.0779 | 11 | -0.2826 | -0.15534 | 0.17069 | -0.74556 | 1.0055 | Confirmed/Materialized Shift | 73.089 | -2.0782 | Night | 202602 | 2026-02-05 | 2.0782
2026-02-05 21:44 | 68.9882 | FALSE | TRUE | -0.22073 | -0.32099 | -4.0895 | -5.5961 | 0 |  | 2026-02-05 19:01 | none | FALSE | 2 | 68.7675 | FALSE | FALSE | 0.5768 | 2.3168 | 70.9226 | 12 | 0 | -0.15534 | 0.17069 | 0.91006 | 1.0776 | Confirmed/Materialized Shift | 73.0777 | -1.7952 | Night | 202602 | 2026-02-05 | 1.7952
2026-02-05 21:59 | 68.7056 | FALSE | TRUE | -0.2479 | -0.36213 | -4.3429 | -5.9452 | -0.2826 |  | 2026-02-05 19:01 | none | FALSE | 1 | 68.4577 | FALSE | FALSE | 0.5475 | 2.2758 | 70.7531 | 13 | -0.2826 | -0.16947 | 0.16884 | -0.67003 | 1.1477 | Confirmed/Materialized Shift | 73.0485 | -1.784 | Night | 202602 | 2026-02-05 | 1.784
2026-02-05 22:14 | 68.7056 | FALSE | TRUE | -0.49925 | -0.73196 | -4.2553 | -5.8323 | 0 |  | 2026-02-05 19:01 | none | FALSE | 1 | 68.2064 | FALSE | FALSE | 0.5339 | 2.2261 | 70.5836 | 14 | 0 | -0.16947 | 0.16884 | 1.0037 | 1.1886 | Confirmed/Materialized Shift | 72.9609 | -1.58 | Night | 202602 | 2026-02-05 | 1.58
2026-02-05 22:29 | 68.423 | FALSE | TRUE | -0.49791 | -0.73302 | -4.4802 | -6.1454 | -0.2826 |  | 2026-02-05 19:01 | none | FALSE | 1 | 67.9251 | FALSE | FALSE | 0.5352 | 2.1844 | 70.4142 | 15 | -0.2826 | -0.16947 | 0.16884 | -0.67003 | 1.2445 | Confirmed/Materialized Shift | 72.9032 | -1.5999 | Night | 202602 | 2026-02-05 | 1.5999
2026-02-05 22:44 | 68.1404 | FALSE | TRUE | -0.50413 | -0.74536 | -4.6845 | -6.4325 | -0.2826 |  | 2026-02-05 19:01 | none | FALSE | 1 | 67.6363 | FALSE | FALSE | 0.536 | 2.1486 | 70.2306 | 16 | -0.2826 | -0.1836 | 0.16571 | -0.59743 | 1.2971 | Confirmed/Materialized Shift | 72.8249 | -1.6114 | Night | 202602 | 2026-02-05 | 1.6114
2026-02-05 22:59 | 68.1404 | FALSE | TRUE | -0.73567 | -1.0914 | -4.5488 | -6.2579 | 0 |  | 2026-02-05 19:01 | none | FALSE | 1 | 67.4047 | FALSE | FALSE | 0.5248 | 2.1071 | 70.047 | 17 | 0 | -0.1836 | 0.16571 | 1.108 | 1.3211 | Confirmed/Materialized Shift | 72.6892 | -1.4431 | Night | 202602 | 2026-02-05 | 1.4431
2026-02-05 23:14 | 67.8596 | FALSE | TRUE | -0.68759 | -1.0236 | -4.667 | -6.4349 | -0.2808 |  | 2026-02-05 19:01 | none | FALSE | 1 | 67.172 | FALSE | FALSE | 0.5277 | 2.0726 | 69.8493 | 18 | -0.2808 | -0.19764 | 0.16117 | -0.51598 | 1.3387 | Confirmed/Materialized Shift | 72.5266 | -1.4864 | Night | 202602 | 2026-02-05 | 1.4864
2026-02-05 23:28 | 67.577 | FALSE | TRUE | -0.63295 | -0.94548 | -4.754 | -6.5726 | -0.2826 |  | 2026-02-05 19:01 | none | FALSE | 0 | 66.9441 | FALSE | FALSE | 0.502 | 2.044 | 69.6376 | 19 | -0.2826 | -0.21177 | 0.15521 | -0.45636 | 1.3467 | Confirmed/Materialized Shift | 72.331 | -1.53 | Night | 202602 | 2026-02-05 | 1.53
2026-02-05 23:43 | 67.8596 | TRUE | TRUE | -1.0197 | -1.5256 | -4.1803 | -5.8028 | 0.2826 |  | 2026-02-05 19:01 | none | FALSE | 1 | 66.8399 | FALSE | FALSE | 0.5096 | 2.0026 | 69.4399 | 20 | 0.2826 | -0.19764 | 0.18542 | 2.59 | 1.3 | Confirmed/Materialized Shift | 72.0399 | -1.2156 | Night | 202602 | 2026-02-05 | 1.2156
2026-02-05 23:58 | 67.577 | FALSE | TRUE | -0.8659 | -1.298 | -4.1964 | -5.8468 | -0.2826 |  | 2026-02-05 19:01 | none | FALSE | 1 | 66.7111 | FALSE | FALSE | 0.5163 | 1.9699 | 69.2423 | 21 | -0.2826 | -0.19764 | 0.18542 | -0.4582 | 1.2656 | Confirmed/Materialized Shift | 71.7734 | -1.3158 | Night | 202602 | 2026-02-05 | 1.3158
2026-02-06 00:14 | 67.2944 | FALSE | TRUE | -0.696 | -1.0451 | -4.1682 | -5.8327 | -0.2826 |  | 2026-02-05 19:01 | none | FALSE | 1 | 66.5984 | FALSE | FALSE | 0.5237 | 1.9453 | 69.0305 | 22 | -0.2826 | -0.21177 | 0.18027 | -0.39292 | 1.2161 | Confirmed/Materialized Shift | 71.4626 | -1.4277 | Night | 202602 | 2026-02-06 | 1.4277
2026-02-06 00:28 | 67.2944 | FALSE | TRUE | -0.7747 | -1.1646 | -3.8516 | -5.4137 | 0 |  | 2026-02-05 19:01 | none | FALSE | 1 | 66.5197 | FALSE | FALSE | 0.5173 | 1.9185 | 68.8329 | 23 | 0 | -0.19764 | 0.18542 | 1.0659 | 1.1566 | Confirmed/Materialized Shift | 71.146 | -1.3302 | Night | 202602 | 2026-02-06 | 1.3302
2026-02-06 00:43 | 67.2944 | FALSE | TRUE | -0.82461 | -1.2406 | -3.5345 | -4.9902 | 0 |  | 2026-02-05 19:01 | none | FALSE | 1 | 66.4698 | FALSE | FALSE | 0.5115 | 1.8904 | 68.6493 | 24 | 0 | -0.18351 | 0.18933 | 0.96924 | 1.0898 | Confirmed/Materialized Shift | 70.8289 | -1.2433 | Night | 202602 | 2026-02-06 | 1.2433
2026-02-06 00:58 | 67.577 | TRUE | FALSE | -1.0882 | -1.6367 | -2.9224 | -4.1453 | 0.2826 |  |  | none | FALSE | 2 | 66.4888 | TRUE | FALSE | 0.1181 |  | 68.4941 | 0 | 0.2826 | -0.15525 | 0.2143 | 2.0432 | 1.0027 | Persistence ends | 70.4994 | -0.91467 | Night | 202602 | 2026-02-06 | 0.91467
2026-02-06 01:13 | 67.8596 | FALSE | FALSE | -1.3019 | -1.956 | -2.3169 | -3.3015 | 0.2826 |  |  | none | FALSE | 2 | 66.5577 | FALSE | FALSE | 0.0945 |  | 68.3671 | 0 | 0.2826 | -0.12699 | 0.23307 | 1.7574 | 0.90469 | Normal | 70.1765 | -0.56097 | Night | 202602 | 2026-02-06 | 0.56097
2026-02-06 01:28 | 67.8596 | FALSE | FALSE | -1.2271 | -1.8415 | -2.0164 | -2.8856 | 0 |  |  | none | FALSE | 2 | 66.6325 | FALSE | FALSE | 0.0896 |  | 68.2542 | 0 | 0 | -0.11286 | 0.2317 | 0.4871 | 0.81086 | Normal | 69.876 | -0.48671 | Night | 202602 | 2026-02-06 | 0.48671
2026-02-06 01:43 | 67.8596 | FALSE | FALSE | -1.0889 | -1.6308 | -1.6525 | -2.3773 | 0 |  |  | none | FALSE | 2 | 66.7707 | FALSE | FALSE | 0.0846 |  | 68.1414 | 0 | 0 | -0.11286 | 0.2317 | 0.4871 | 0.68535 | Normal | 69.5121 | -0.41116 | Night | 202602 | 2026-02-06 | 0.41116
2026-02-06 01:58 | 67.577 | FALSE | FALSE | -0.75304 | -1.1269 | -1.6842 | -2.4316 | -0.2826 |  |  | none | FALSE | 2 | 66.824 | FALSE | FALSE | 0.1081 |  | 68.0426 | 0 | -0.2826 | -0.09882 | 0.2105 | -0.87306 | 0.6093 | Normal | 69.2612 | -0.7641 | Night | 202602 | 2026-02-06 | 0.7641
2026-02-06 02:13 | 67.577 | FALSE | FALSE | -0.70671 | -1.0568 | -1.4685 | -2.1268 | 0 |  |  | none | FALSE | 1 | 66.8703 | FALSE | FALSE | 0.0753 |  | 67.9579 | 0 | 0 | -0.08469 | 0.20697 | 0.40919 | 0.54379 | Normal | 69.0455 | -0.70041 | Night | 202602 | 2026-02-06 | 0.70041
2026-02-06 02:27 | 67.577 | FALSE | FALSE | -0.67403 | -1.0075 | -1.2947 | -1.8798 | 0 |  |  | none | FALSE | 1 | 66.903 | FALSE | FALSE | 0.0706 |  | 67.8873 | 0 | 0 | -0.07056 | 0.20234 | 0.34872 | 0.49217 | Normal | 68.8717 | -0.63051 | Night | 202602 | 2026-02-06 | 0.63051
2026-02-06 02:43 | 67.577 | FALSE | FALSE | -0.60469 | -0.9029 | -1.0842 | -1.5791 | 0 |  |  | none | FALSE | 1 | 66.9723 | FALSE | FALSE | 0.0664 |  | 67.8168 | 0 | 0 | -0.07056 | 0.20234 | 0.34872 | 0.42223 | Normal | 68.6612 | -0.56785 | Night | 202602 | 2026-02-06 | 0.56785
2026-02-06 02:58 | 67.577 | FALSE | FALSE | -0.55523 | -0.82843 | -0.92189 | -1.3458 | 0 |  |  | none | FALSE | 1 | 67.0218 | FALSE | FALSE | 0.0617 |  | 67.7603 | 0 | 0 | -0.05643 | 0.19654 | 0.28712 | 0.36928 | Normal | 68.4989 | -0.49645 | Night | 202602 | 2026-02-06 | 0.49645
2026-02-06 03:13 | 67.577 | FALSE | FALSE | -0.46558 | -0.69374 | -0.71938 | -1.0533 | 0 |  |  | none | FALSE | 1 | 67.1114 | FALSE | FALSE | 0.0571 |  | 67.7039 | 0 | 0 | -0.05643 | 0.19654 | 0.28712 | 0.29624 | Normal | 68.2964 | -0.42837 | Night | 202602 | 2026-02-06 | 0.42837
2026-02-06 03:27 | 67.577 | FALSE | FALSE | -0.40327 | -0.60034 | -0.57247 | -0.84003 | 0 |  |  | none | FALSE | 0 | 67.1737 | FALSE | FALSE | 0.0231 |  | 67.6616 | 0 | 0 | -0.0423 | 0.18945 | 0.22327 | 0.24394 | Normal | 68.1495 | -0.34681 | Night | 202602 | 2026-02-06 | 0.34681
2026-02-06 03:42 | 67.577 | FALSE | FALSE | -0.37707 | -0.56112 | -0.48993 | -0.71978 | 0 |  |  | none | FALSE | 0 | 67.1999 | FALSE | FALSE | 0.0174 |  | 67.6334 | 0 | 0 | -0.02817 | 0.18094 | 0.15569 | 0.21675 | Normal | 68.0669 | -0.26035 | Night | 202602 | 2026-02-06 | 0.26035
2026-02-06 03:57 | 67.577 | FALSE | FALSE | -0.33388 | -0.49652 | -0.3904 | -0.57439 | 0 |  |  | none | FALSE | 0 | 67.2431 | FALSE | FALSE | 0.0104 |  | 67.6053 | 0 | 0 | -0.02817 | 0.18094 | 0.15569 | 0.18107 | Normal | 67.9674 | -0.15607 | Night | 202602 | 2026-02-06 | 0.15607
2026-02-06 04:12 | 67.2944 | FALSE | FALSE | -0.08415 | -0.1252 | -0.64935 | -0.95572 | -0.2826 |  |  | none | FALSE | 0 | 67.2102 | FALSE | FALSE | 0.1027 |  | 67.577 | 0 | -0.2826 | -0.02826 | 0.18107 | -1.4047 | 0.18338 | Normal | 67.9438 | -1.5411 | Night | 202602 | 2026-02-06 | 1.5411
2026-02-06 04:27 | 67.2944 | FALSE | FALSE | -0.11945 | -0.17781 | -0.65639 | -0.96597 | 0 |  |  | none | FALSE | 0 | 67.175 | FALSE | FALSE | 0.0923 |  | 67.5629 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.19396 | Normal | 67.9508 | -1.3842 | Night | 202602 | 2026-02-06 | 1.3842
2026-02-06 04:42 | 67.2944 | FALSE | FALSE | -0.13894 | -0.20689 | -0.61936 | -0.91198 | 0 |  |  | none | FALSE | 0 | 67.1555 | FALSE | FALSE | 0.0845 |  | 67.5346 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.18957 | Normal | 67.9138 | -1.2671 | Night | 202602 | 2026-02-06 | 1.2671
2026-02-06 04:57 | 67.2944 | FALSE | FALSE | -0.16722 | -0.2491 | -0.61938 | -0.912 | 0 |  |  | none | FALSE | 0 | 67.1272 | FALSE | FALSE | 0.0766 |  | 67.5205 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.19665 | Normal | 67.9138 | -1.1497 | Night | 202602 | 2026-02-06 | 1.1497
2026-02-06 05:12 | 67.2944 | FALSE | FALSE | -0.16722 | -0.2491 | -0.61938 | -0.912 | 0 |  |  | none | FALSE | 0 | 67.1272 | FALSE | FALSE | 0.0766 |  | 67.5205 | 0 | 0 | 0 | 0.12967 | 0 | 0.19665 | Normal | 67.9138 | -1.1497 | Night | 202602 | 2026-02-06 | 1.1497
2026-02-06 05:27 | 67.2944 | FALSE | FALSE | -0.16722 | -0.2491 | -0.61938 | -0.912 | 0 |  |  | none | FALSE | 0 | 67.1272 | FALSE | FALSE | 0.0766 |  | 67.5205 | 0 | 0 | 0 | 0.12967 | 0 | 0.19665 | Normal | 67.9138 | -1.1497 | Night | 202602 | 2026-02-06 | 1.1497
2026-02-06 05:42 | 67.2944 | FALSE | FALSE | -0.16722 | -0.2491 | -0.61938 | -0.912 | 0 |  |  | none | FALSE | 0 | 67.1272 | FALSE | FALSE | 0.0766 |  | 67.5205 | 0 | 0 | 0 | 0.12967 | 0 | 0.19665 | Normal | 67.9138 | -1.1497 | Night | 202602 | 2026-02-06 | 1.1497
2026-02-06 05:57 | 67.2944 | FALSE | FALSE | -0.19293 | -0.28752 | -0.61683 | -0.90829 | 0 |  |  | none | FALSE | 0 | 67.1015 | FALSE | FALSE | 0.0698 |  | 67.5063 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.20244 | Normal | 67.9112 | -1.047 | Night | 202602 | 2026-02-06 | 1.047
2026-02-06 06:12 | 67.2944 | FALSE | FALSE | -0.19546 | -0.2913 | -0.56284 | -0.82944 | 0 |  |  | none | FALSE | 0 | 67.0989 | FALSE | FALSE | 0.0646 |  | 67.4781 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18957 | Normal | 67.8572 | -0.96896 | Night | 202602 | 2026-02-06 | 0.96896
2026-02-06 06:26 | 67.2944 | FALSE | FALSE | -0.18641 | -0.27777 | -0.49727 | -0.73352 | 0 |  |  | none | FALSE | 0 | 67.108 | FALSE | FALSE | 0.0606 |  | 67.4498 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.17092 | Normal | 67.7917 | -0.90938 | Night | 202602 | 2026-02-06 | 0.90938
2026-02-06 06:41 | 67.2944 | FALSE | FALSE | -0.16132 | -0.2403 | -0.41566 | -0.61388 | 0 |  |  | none | FALSE | 0 | 67.1331 | FALSE | FALSE | 0.0588 |  | 67.4216 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.14424 | Normal | 67.7101 | -0.88163 | Night | 202602 | 2026-02-06 | 0.88163
2026-02-06 06:56 | 67.2944 | FALSE | FALSE | -0.17104 | -0.25482 | -0.39712 | -0.58667 | 0 |  |  | none | FALSE | 0 | 67.1234 | FALSE | FALSE | 0.0531 |  | 67.4074 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14204 | Normal | 67.6915 | -0.79582 | Night | 202602 | 2026-02-06 | 0.79582
2026-02-06 07:11 | 67.2944 | FALSE | FALSE | -0.17768 | -0.26473 | -0.3755 | -0.55489 | 0 |  |  | none | FALSE | 0 | 67.1167 | FALSE | FALSE | 0.0477 |  | 67.3933 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13829 | Normal | 67.6699 | -0.71522 | Day | 202602 | 2026-02-06 | 0.71522
2026-02-06 07:26 | 67.2944 | FALSE | FALSE | -0.18096 | -0.26963 | -0.35052 | -0.51817 | 0 |  |  | none | FALSE | 0 | 67.1134 | FALSE | FALSE | 0.0425 |  | 67.3792 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13287 | Normal | 67.6449 | -0.63808 | Day | 202602 | 2026-02-06 | 0.63808
2026-02-06 07:30 | 67.2944 | FALSE | FALSE | -0.18045 | -0.26887 | -0.32175 | -0.47584 | 0 |  |  | none | FALSE | 0 | 67.114 | FALSE | FALSE | 0.0375 |  | 67.365 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.12555 | Normal | 67.6161 | -0.56273 | Day | 202602 | 2026-02-06 | 0.56273
2026-02-06 07:45 | 67.2944 | FALSE | FALSE | -0.17543 | -0.26138 | -0.28847 | -0.42684 | 0 |  |  | none | FALSE | 0 | 67.119 | FALSE | FALSE | 0.0325 |  | 67.3509 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.11598 | Normal | 67.5829 | -0.48734 | Day | 202602 | 2026-02-06 | 0.48734
2026-02-06 08:00 | 67.2944 | FALSE | FALSE | -0.16467 | -0.2453 | -0.24945 | -0.36932 | 0 |  |  | none | FALSE | 0 | 67.1297 | FALSE | FALSE | 0.0273 |  | 67.3368 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.10353 | Normal | 67.5438 | -0.40945 | Day | 202602 | 2026-02-06 | 0.40945
2026-02-06 08:15 | 67.577 | TRUE | FALSE | -0.44727 | -0.66628 | 0.03315 | 0.04908 | 0.2826 | 2026-02-06 13:59 | 2026-02-06 08:15 | upper | TRUE | 1 | 67.1297 | FALSE | FALSE | 0.2404 | 2.3202 | 67.3368 | 1 | 0.2826 | 0 | 0.091688 | 3.0822 | 0.10353 | Extreme triggered | 67.5438 | 2.3202 | Day | 202602 | 2026-02-06 | 2.3202
2026-02-06 08:30 | 67.577 | FALSE | FALSE | -0.44727 | -0.66628 | 0.03315 | 0.04908 | 0 |  | 2026-02-06 08:15 | upper | TRUE | 1 | 67.1297 | FALSE | FALSE | 0.2975 | 2.3202 | 67.3368 | 2 | 0 | 0 | 0.091688 | 0 | 0.10353 | Extreme/elevated | 67.5438 | 2.3202 | Day | 202602 | 2026-02-06 | 2.3202
2026-02-06 08:30 | 67.577 | FALSE | FALSE | -0.44727 | -0.66628 | 0.03315 | 0.04908 | 0 |  | 2026-02-06 08:15 | upper | TRUE | 1 | 67.1297 | FALSE | TRUE | 0.3547 | 2.3202 | 67.3368 | 3 | 0 | 0 | 0.091688 | 0 | 0.10353 | Persistent | 67.5438 | 2.3202 | Day | 202602 | 2026-02-06 | 2.3202
2026-02-06 08:30 | 67.577 | FALSE | FALSE | -0.45803 | -0.68242 | -0.0058732 | -0.0086903 | 0 |  | 2026-02-06 08:15 | none | FALSE | 1 | 67.119 | FALSE | FALSE | 0.3871 | 2.2275 | 67.3509 | 4 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.11598 | Persistent | 67.5829 | 1.9494 | Day | 202602 | 2026-02-06 | 1.9494
2026-02-06 08:45 | 67.577 | FALSE | FALSE | -0.46305 | -0.68994 | -0.039147 | -0.057895 | 0 |  | 2026-02-06 08:15 | none | FALSE | 1 | 67.114 | FALSE | FALSE | 0.4268 | 2.1196 | 67.365 | 5 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.12555 | Persistent | 67.6161 | 1.6882 | Day | 202602 | 2026-02-06 | 1.6882
2026-02-06 08:46 | 67.577 | FALSE | FALSE | -0.46356 | -0.6907 | -0.067916 | -0.1004 | 0 |  | 2026-02-06 08:15 | none | FALSE | 1 | 67.1134 | FALSE | FALSE | 0.4707 | 2.0145 | 67.3792 | 6 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.13287 | Persistent | 67.6449 | 1.4888 | Day | 202602 | 2026-02-06 | 1.4888
2026-02-06 09:01 | 67.8596 | TRUE | TRUE | -0.79029 | -1.1783 | 0.11403 | 0.16833 | 0.2826 |  | 2026-02-06 08:15 | upper | TRUE | 2 | 67.0693 | TRUE | TRUE | 0.6354 | 2.1088 | 67.4074 | 7 | 0.2826 | 0.02826 | 0.086982 | 2.924 | 0.16906 | Confirmed/Materialized Shift | 67.7456 | 2.6745 | Day | 202602 | 2026-02-06 | 2.6745
2026-02-06 09:16 | 68.1404 | TRUE | TRUE | -1.1567 | -1.7269 | 0.22461 | 0.33071 | 0.2808 |  | 2026-02-06 08:15 | upper | TRUE | 3 | 66.9837 | TRUE | TRUE | 0.6833 | 2.2157 | 67.4497 | 8 | 0.2808 | 0.0423 | 0.10331 | 2.3086 | 0.23303 | Confirmed/Materialized Shift | 67.9158 | 2.9639 | Day | 202602 | 2026-02-06 | 2.9639
2026-02-06 09:31 | 68.1404 | FALSE | TRUE | -1.2006 | -1.7936 | 0.096077 | 0.1412 | 0 |  | 2026-02-06 08:15 | upper | TRUE | 3 | 66.9398 | FALSE | TRUE | 0.6422 | 2.2304 | 67.492 | 9 | 0 | 0.0423 | 0.10331 | -0.40945 | 0.27614 | Confirmed/Materialized Shift | 68.0443 | 2.3479 | Day | 202602 | 2026-02-06 | 2.3479
2026-02-06 09:45 | 68.423 | FALSE | TRUE | -1.5571 | -2.3286 | 0.192 | 0.2814 | 0.2826 |  | 2026-02-06 08:15 | upper | TRUE | 3 | 66.8659 | FALSE | TRUE | 0.6566 | 2.2636 | 67.5485 | 10 | 0.2826 | 0.05643 | 0.11579 | 1.9532 | 0.34126 | Confirmed/Materialized Shift | 68.231 | 2.5626 | Day | 202602 | 2026-02-06 | 2.5626
2026-02-06 10:00 | 68.7056 | FALSE | TRUE | -1.9311 | -2.8919 | 0.24207 | 0.35358 | 0.2826 |  | 2026-02-06 08:15 | upper | TRUE | 2 | 66.7745 | FALSE | TRUE | 0.6287 | 2.2917 | 67.619 | 11 | 0.2826 | 0.07056 | 0.12539 | 1.6911 | 0.42225 | Confirmed/Materialized Shift | 68.4635 | 2.5733 | Day | 202602 | 2026-02-06 | 2.5733
2026-02-06 10:15 | 69.2708 | TRUE | TRUE | -2.6594 | -3.9924 | 0.44649 | 0.64873 | 0.5652 |  | 2026-02-06 08:15 | upper | TRUE | 3 | 66.6114 | TRUE | TRUE | 0.6729 | 2.3347 | 67.7178 | 12 | 0.5652 | 0.09882 | 0.16582 | 2.8125 | 0.55323 | Confirmed/Materialized Shift | 68.8243 | 2.8071 | Day | 202602 | 2026-02-06 | 2.8071
2026-02-06 10:30 | 69.5534 | FALSE | TRUE | -3.0798 | -4.6332 | 0.36536 | 0.52806 | 0.2826 |  | 2026-02-06 08:15 | upper | TRUE | 3 | 66.4736 | FALSE | TRUE | 0.6549 | 2.3504 | 67.8308 | 13 | 0.2826 | 0.11295 | 0.16897 | 1.004 | 0.67862 | Confirmed/Materialized Shift | 69.188 | 2.5384 | Day | 202602 | 2026-02-06 | 2.5384
2026-02-06 10:45 | 69.836 | FALSE | TRUE | -3.4781 | -5.2415 | 0.27811 | 0.39983 | 0.2826 |  | 2026-02-06 08:15 | upper | TRUE | 3 | 66.3579 | FALSE | TRUE | 0.6422 | 2.3502 | 67.9579 | 14 | 0.2826 | 0.12708 | 0.17083 | 0.91037 | 0.8 | Confirmed/Materialized Shift | 69.5579 | 2.3476 | Day | 202602 | 2026-02-06 | 2.3476
2026-02-06 11:00 | 70.1168 | FALSE | TRUE | -3.8521 | -5.8132 | 0.18347 | 0.26236 | 0.2808 |  | 2026-02-06 08:15 | upper | TRUE | 3 | 66.2647 | FALSE | TRUE | 0.6324 | 2.3402 | 68.099 | 15 | 0.2808 | 0.14112 | 0.17138 | 0.81505 | 0.91716 | Confirmed/Materialized Shift | 69.9333 | 2.2 | Day | 202602 | 2026-02-06 | 2.2
2026-02-06 11:15 | 70.3994 | FALSE | TRUE | -4.2045 | -6.3517 | 0.08577 | 0.12198 | 0.2826 |  | 2026-02-06 08:15 | upper | TRUE | 3 | 66.1949 | FALSE | TRUE | 0.6246 | 2.3241 | 68.2542 | 16 | 0.2826 | 0.15525 | 0.17078 | 0.74571 | 1.0297 | Confirmed/Materialized Shift | 70.3136 | 2.0833 | Day | 202602 | 2026-02-06 | 2.0833
2026-02-06 11:30 | 70.682 | FALSE | TRUE | -4.5315 | -6.8503 | -0.014761 | -0.020879 | 0.2826 |  | 2026-02-06 08:15 | none | FALSE | 2 | 66.1505 | FALSE | FALSE | 0.5896 | 2.3043 | 68.4236 | 17 | 0.2826 | 0.16938 | 0.16894 | 0.67019 | 1.1366 | Confirmed/Materialized Shift | 70.6968 | 1.987 | Day | 202602 | 2026-02-06 | 1.987
2026-02-06 11:44 | 70.9646 | FALSE | TRUE | -4.8305 | -7.3042 | -0.11562 | -0.16267 | 0.2826 |  | 2026-02-06 08:15 | none | FALSE | 1 | 66.1341 | FALSE | FALSE | 0.5557 | 2.2822 | 68.6071 | 18 | 0.2826 | 0.18351 | 0.16581 | 0.5976 | 1.2365 | Confirmed/Materialized Shift | 71.0802 | 1.9065 | Day | 202602 | 2026-02-06 | 1.9065
2026-02-06 12:00 | 71.2472 | FALSE | TRUE | -5.0988 | -7.7081 | -0.21394 | -0.29937 | 0.2826 |  | 2026-02-06 08:15 | none | FALSE | 1 | 66.1484 | FALSE | FALSE | 0.5512 | 2.2588 | 68.8048 | 19 | 0.2826 | 0.19764 | 0.16133 | 0.52661 | 1.3282 | Confirmed/Materialized Shift | 71.4611 | 1.8389 | Day | 202602 | 2026-02-06 | 1.8389
2026-02-06 12:15 | 71.5298 | FALSE | TRUE | -5.3329 | -8.0561 | -0.3064 | -0.42653 | 0.2826 |  | 2026-02-06 08:15 | none | FALSE | 1 | 66.1969 | FALSE | FALSE | 0.5474 | 2.235 | 69.0165 | 20 | 0.2826 | 0.21177 | 0.15538 | 0.45585 | 1.4098 | Confirmed/Materialized Shift | 71.8362 | 1.7827 | Day | 202602 | 2026-02-06 | 1.7827
2026-02-06 12:30 | 71.8124 | FALSE | TRUE | -5.5792 | -8.4236 | -0.41108 | -0.56918 | 0.2826 |  | 2026-02-06 08:15 | none | FALSE | 1 | 66.2332 | FALSE | FALSE | 0.5436 | 2.2108 | 69.2283 | 21 | 0.2826 | 0.21177 | 0.15538 | 0.45585 | 1.4976 | Confirmed/Materialized Shift | 72.2235 | 1.7255 | Day | 202602 | 2026-02-06 | 1.7255
2026-02-06 12:44 | 71.8124 | FALSE | TRUE | -5.4729 | -8.2499 | -0.72831 | -1.004 | 0 |  | 2026-02-06 08:15 | none | FALSE | 0 | 66.3395 | FALSE | FALSE | 0.502 | 2.1798 | 69.4401 | 22 | 0 | 0.21177 | 0.15538 | -1.3629 | 1.5503 | Confirmed/Materialized Shift | 72.5407 | 1.5302 | Day | 202602 | 2026-02-06 | 1.5302
2026-02-06 12:59 | 72.095 | FALSE | TRUE | -5.6153 | -8.4466 | -0.75723 | -1.0394 | 0.2826 |  | 2026-02-06 08:15 | none | FALSE | 0 | 66.4797 | FALSE | FALSE | 0.5016 | 2.1514 | 69.666 | 23 | 0.2826 | 0.2259 | 0.14777 | 0.3837 | 1.5931 | Confirmed/Materialized Shift | 72.8522 | 1.5247 | Day | 202602 | 2026-02-06 | 1.5247
2026-02-06 13:14 | 72.3758 | FALSE | TRUE | -5.7159 | -8.5748 | -0.7762 | -1.0611 | 0.2808 |  | 2026-02-06 08:15 | none | FALSE | 0 | 66.6599 | FALSE | FALSE | 0.5015 | 2.1251 | 69.9059 | 24 | 0.2808 | 0.23994 | 0.13821 | 0.29564 | 1.623 | Confirmed/Materialized Shift | 73.152 | 1.5218 | Day | 202602 | 2026-02-06 | 1.5218
2026-02-06 13:29 | 72.3758 | FALSE | TRUE | -5.4606 | -8.1604 | -1.0007 | -1.3638 | 0 |  | 2026-02-06 08:15 | none | FALSE | 0 | 66.9152 | FALSE | FALSE | 0.492 | 2.0953 | 70.1459 | 25 | 0 | 0.23994 | 0.13821 | -1.7361 | 1.6153 | Confirmed/Materialized Shift | 73.3765 | 1.3805 | Day | 202602 | 2026-02-06 | 1.3805
2026-02-06 13:44 | 72.6584 | FALSE | TRUE | -5.4373 | -8.0886 | -0.92035 | -1.2508 | 0.2826 |  | 2026-02-06 08:15 | none | FALSE | 0 | 67.2211 | FALSE | FALSE | 0.4947 | 2.0694 | 70.3999 | 26 | 0.2826 | 0.25407 | 0.12632 | 0.22585 | 1.5894 | Confirmed/Materialized Shift | 73.5788 | 1.4209 | Day | 202602 | 2026-02-06 | 1.4209
2026-02-06 13:59 | 72.095 | TRUE | FALSE | -4.5102 | -6.6734 | -1.5436 | -2.0962 | -0.5634 |  |  | none | FALSE | 1 | 67.5848 | FALSE | FALSE | 0.0939 |  | 70.6117 | 0 | -0.5634 | 0.21177 | 0.22182 | -3.4947 | 1.5135 | Persistence ends | 73.6386 | 0.98006 | Day | 202602 | 2026-02-06 | 0.98006
2026-02-06 14:14 | 72.095 | FALSE | FALSE | -4.1448 | -6.0997 | -1.5737 | -2.1361 | 0 |  |  | none | FALSE | 1 | 67.9502 | FALSE | FALSE | 0.0885 |  | 70.8094 | 0 | 0 | 0.19773 | 0.22606 | -0.87467 | 1.4296 | Normal | 73.6687 | 0.89924 | Day | 202602 | 2026-02-06 | 0.89924
2026-02-06 14:29 | 72.095 | FALSE | FALSE | -3.7067 | -5.4201 | -1.5311 | -2.0795 | 0 |  |  | none | FALSE | 1 | 68.3883 | FALSE | FALSE | 0.084 |  | 71.0072 | 0 | 0 | 0.19773 | 0.22606 | -0.87467 | 1.3095 | Normal | 73.6261 | 0.83075 | Day | 202602 | 2026-02-06 | 0.83075
2026-02-06 14:44 | 72.3758 | FALSE | FALSE | -3.5548 | -5.1653 | -1.2129 | -1.6481 | 0.2808 |  |  | none | FALSE | 1 | 68.821 | FALSE | FALSE | 0.0941 |  | 71.2048 | 0 | 0.2808 | 0.19764 | 0.22603 | 0.36792 | 1.1919 | Normal | 73.5887 | 0.98244 | Day | 202602 | 2026-02-06 | 0.98244
2026-02-06 14:59 | 72.6584 | FALSE | FALSE | -3.4119 | -4.9272 | -0.89999 | -1.2235 | 0.2826 |  |  | none | FALSE | 1 | 69.2465 | FALSE | FALSE | 0.1062 |  | 71.4025 | 0 | 0.2826 | 0.19764 | 0.22603 | 0.37588 | 1.078 | Normal | 73.5584 | 1.1651 | Day | 202602 | 2026-02-06 | 1.1651
2026-02-06 15:14 | 72.095 | TRUE | FALSE | -2.4771 | -3.5581 | -1.3744 | -1.8707 | -0.5634 |  |  | none | FALSE | 2 | 69.6179 | TRUE | FALSE | 0.0953 |  | 71.5437 | 0 | -0.5634 | 0.14121 | 0.26666 | -2.6423 | 0.96287 | Normal | 73.4694 | 0.5726 | Day | 202602 | 2026-02-06 | 0.5726
2026-02-06 15:29 | 72.095 | FALSE | FALSE | -2.1185 | -3.0275 | -1.27 | -1.7311 | 0 |  |  | none | FALSE | 2 | 69.9765 | FALSE | FALSE | 0.0905 |  | 71.6707 | 0 | 0 | 0.12708 | 0.26626 | -0.47727 | 0.84714 | Normal | 73.365 | 0.50082 | Day | 202602 | 2026-02-06 | 0.50082
2026-02-06 15:43 | 72.095 | FALSE | FALSE | -1.7763 | -2.526 | -1.1536 | -1.575 | 0 |  |  | none | FALSE | 2 | 70.3187 | FALSE | FALSE | 0.0855 |  | 71.7837 | 0 | 0 | 0.11295 | 0.26507 | -0.42611 | 0.73247 | Normal | 73.2486 | 0.42501 | Day | 202602 | 2026-02-06 | 0.42501
2026-02-06 15:58 | 72.095 | FALSE | FALSE | -1.4535 | -2.0576 | -1.0287 | -1.4068 | 0 |  |  | none | FALSE | 2 | 70.6415 | FALSE | FALSE | 0.08 |  | 71.8826 | 0 | 0 | 0.09891 | 0.26314 | -0.37588 | 0.62055 | Normal | 73.1237 | 0.34228 | Day | 202602 | 2026-02-06 | 0.34228
2026-02-06 16:13 | 72.095 | FALSE | FALSE | -1.1554 | -1.6288 | -0.9002 | -1.2332 | 0 |  |  | none | FALSE | 2 | 70.9396 | FALSE | FALSE | 0.0737 |  | 71.9674 | 0 | 0 | 0.08478 | 0.26033 | -0.32566 | 0.51391 | Normal | 72.9952 | 0.24833 | Day | 202602 | 2026-02-06 | 0.24833
2026-02-06 16:28 | 72.095 | FALSE | FALSE | -0.88823 | -1.2474 | -0.77429 | -1.0626 | 0 |  |  | none | FALSE | 1 | 71.2068 | FALSE | FALSE | 0.0377 |  | 72.038 | 0 | 0 | 0.07065 | 0.25667 | -0.27525 | 0.41563 | Normal | 72.8693 | 0.13707 | Day | 202602 | 2026-02-06 | 0.13707
2026-02-06 16:43 | 72.095 | FALSE | FALSE | -0.66049 | -0.9246 | -0.65959 | -0.90659 | 0 |  |  | none | FALSE | 1 | 71.4345 | FALSE | FALSE | 0.0287 |  | 72.0945 | 0 | 0 | 0.05652 | 0.25213 | -0.22417 | 0.33002 | Normal | 72.7546 | 0.0013636 | Day | 202602 | 2026-02-06 | 0.0013636
2026-02-06 16:58 | 72.095 | FALSE | FALSE | -0.48429 | -0.67629 | -0.56817 | -0.78193 | 0 |  |  | none | FALSE | 1 | 71.6107 | FALSE | FALSE | 0.0392 |  | 72.1369 | 0 | 0 | 0.04239 | 0.24665 | -0.17186 | 0.26312 | Normal | 72.6632 | -0.1594 | Day | 202602 | 2026-02-06 | 0.1594
2026-02-06 17:13 | 72.095 | FALSE | FALSE | -0.37289 | -0.51991 | -0.51329 | -0.70693 | 0 |  |  | none | FALSE | 1 | 71.7221 | FALSE | FALSE | 0.0497 |  | 72.1652 | 0 | 0 | 0.02826 | 0.24018 | -0.11766 | 0.22154 | Normal | 72.6083 | -0.31687 | Day | 202602 | 2026-02-06 | 0.31687
2026-02-06 17:28 | 72.095 | FALSE | FALSE | -0.32837 | -0.45755 | -0.49703 | -0.68469 | 0 |  |  | none | FALSE | 1 | 71.7666 | FALSE | FALSE | 0.0558 |  | 72.1793 | 0 | 0 | 0.01413 | 0.23262 | -0.060743 | 0.20635 | Normal | 72.592 | -0.40868 | Day | 202602 | 2026-02-06 | 0.40868
2026-02-06 17:43 | 72.095 | FALSE | FALSE | -0.27921 | -0.38878 | -0.47613 | -0.65608 | 0 |  |  | none | FALSE | 0 | 71.8158 | FALSE | FALSE | 0.0348 |  | 72.1935 | 0 | 0 | 0.01413 | 0.23262 | -0.060743 | 0.18883 | Normal | 72.5711 | -0.52141 | Day | 202602 | 2026-02-06 | 0.52141
2026-02-06 17:58 | 72.095 | FALSE | FALSE | -0.27921 | -0.38878 | -0.47613 | -0.65608 | 0 |  |  | none | FALSE | 0 | 71.8158 | FALSE | FALSE | 0.0348 |  | 72.1935 | 0 | 0 | 0 | 0.22387 | 0 | 0.18883 | Normal | 72.5711 | -0.52141 | Day | 202602 | 2026-02-06 | 0.52141
2026-02-06 18:13 | 72.095 | FALSE | FALSE | -0.2855 | -0.39758 | -0.45434 | -0.62625 | 0 |  |  | none | FALSE | 0 | 71.8095 | FALSE | FALSE | 0.0304 |  | 72.1794 | 0 | 0 | -0.01404 | 0.21392 | 0.065632 | 0.18496 | Normal | 72.5493 | -0.45642 | Night | 202602 | 2026-02-06 | 0.45642
2026-02-06 18:28 | 72.095 | FALSE | FALSE | -0.28933 | -0.40294 | -0.43009 | -0.59303 | 0 |  |  | none | FALSE | 0 | 71.8057 | FALSE | FALSE | 0.0261 |  | 72.1654 | 0 | 0 | -0.01404 | 0.21392 | 0.065632 | 0.17986 | Normal | 72.5251 | -0.39131 | Night | 202602 | 2026-02-06 | 0.39131
2026-02-06 18:30 | 72.095 | FALSE | FALSE | -0.23333 | -0.3247 | -0.31775 | -0.43881 | 0 |  |  | none | FALSE | 0 | 71.8617 | FALSE | FALSE | 0.0204 |  | 72.1372 | 0 | 0 | -0.02817 | 0.20231 | 0.13924 | 0.13777 | Normal | 72.4128 | -0.30638 | Night | 202602 | 2026-02-06 | 0.30638
2026-02-06 18:31 | 72.095 | FALSE | FALSE | -0.23333 | -0.3247 | -0.31775 | -0.43881 | 0 |  |  | none | FALSE | 0 | 71.8617 | FALSE | FALSE | 0.0204 |  | 72.1372 | 0 | 0 | 0 | 0.1583 | 0 | 0.13777 | Normal | 72.4128 | -0.30638 | Night | 202602 | 2026-02-06 | 0.30638
2026-02-06 18:46 | 71.8124 | FALSE | FALSE | -0.00063681 | -0.00088677 | -0.622 | -0.8587 | -0.2826 |  |  | none | FALSE | 0 | 71.8118 | FALSE | FALSE | 0.1331 |  | 72.1231 | 0 | -0.2826 | -0.01413 | 0.17045 | -1.5751 | 0.15566 | Normal | 72.4344 | -1.9959 | Night | 202602 | 2026-02-06 | 1.9959
2026-02-06 19:01 | 71.8124 | FALSE | FALSE | -0.044378 | -0.061835 | -0.63748 | -0.87989 | 0 |  |  | none | FALSE | 0 | 71.768 | FALSE | FALSE | 0.116 |  | 72.1089 | 0 | 0 | -0.01413 | 0.17045 | 0.082899 | 0.17046 | Normal | 72.4499 | -1.7397 | Night | 202602 | 2026-02-06 | 1.7397
2026-02-06 19:16 | 71.5298 | FALSE | FALSE | 0.13149 | 0.18348 | -0.94221 | -1.3001 | -0.2826 | 2026-02-07 07:28 | 2026-02-06 19:16 | lower | TRUE | 0 | 71.6613 | FALSE | FALSE | 0.2337 | 2.6487 | 72.0666 | 1 | -0.2826 | -0.0423 | 0.16563 | -1.4508 | 0.20268 | Extreme triggered | 72.472 | -2.6487 | Night | 202602 | 2026-02-06 | 2.6487
2026-02-06 19:30 | 71.2472 | FALSE | FALSE | 0.28954 | 0.40474 | -1.2082 | -1.6676 | -0.2826 |  | 2026-02-06 19:16 | lower | TRUE | 0 | 71.5367 | FALSE | FALSE | 0.3317 | 2.9547 | 71.9961 | 2 | -0.2826 | -0.07056 | 0.15516 | -1.3666 | 0.22968 | Extreme/elevated | 72.4554 | -3.2606 | Night | 202602 | 2026-02-06 | 3.2606
2026-02-06 19:45 | 71.2472 | FALSE | FALSE | 0.1413 | 0.19793 | -1.2717 | -1.7536 | 0 |  | 2026-02-06 19:16 | lower | TRUE | 0 | 71.3885 | FALSE | TRUE | 0.3381 | 2.8031 | 71.9537 | 3 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.2826 | Persistent | 72.5189 | -2.5 | Night | 202602 | 2026-02-06 | 2.5
2026-02-06 20:00 | 70.9646 | FALSE | FALSE | 0.22001 | 0.30907 | -1.6452 | -2.2657 | -0.2826 |  | 2026-02-06 19:16 | lower | TRUE | 0 | 71.1846 | FALSE | TRUE | 0.4031 | 2.7567 | 71.8972 | 4 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.35629 | Persistent | 72.6098 | -2.6175 | Night | 202602 | 2026-02-06 | 2.6175
2026-02-06 20:15 | 70.682 | FALSE | FALSE | 0.25606 | 0.36096 | -2.033 | -2.7958 | -0.2826 |  | 2026-02-06 19:16 | lower | TRUE | 0 | 70.9381 | FALSE | TRUE | 0.4575 | 2.7207 | 71.8265 | 5 | -0.2826 | -0.07065 | 0.12555 | -1.6882 | 0.44424 | Persistent | 72.715 | -2.5764 | Night | 202602 | 2026-02-06 | 2.5764
2026-02-06 20:29 | 70.3994 | FALSE | FALSE | 0.25943 | 0.36715 | -2.4253 | -3.3303 | -0.2826 |  | 2026-02-06 19:16 | lower | TRUE | 0 | 70.6588 | FALSE | TRUE | 0.5081 | 2.6804 | 71.7417 | 6 | -0.2826 | -0.08478 | 0.13287 | -1.4888 | 0.54146 | Persistent | 72.8247 | -2.4791 | Night | 202602 | 2026-02-06 | 2.4791
2026-02-06 21:46 | 70.1168 | FALSE | TRUE | 0.23719 | 0.33713 | -2.8149 | -3.8596 | -0.2826 |  | 2026-02-06 19:16 | lower | TRUE | 0 | 70.354 | FALSE | TRUE | 0.5579 | 2.6358 | 71.6428 | 7 | -0.2826 | -0.09891 | 0.13829 | -1.3283 | 0.64443 | Confirmed/Materialized Shift | 72.9317 | -2.3681 | Night | 202602 | 2026-02-06 | 2.3681
2026-02-06 21:46 | 70.3994 | TRUE | TRUE | -0.22458 | -0.32002 | -2.5419 | -3.4849 | 0.2826 |  | 2026-02-06 19:16 | none | FALSE | 1 | 70.1748 | FALSE | FALSE | 0.5403 | 2.5157 | 71.5581 | 8 | 0.2826 | -0.08478 | 0.16143 | 2.2757 | 0.69162 | Confirmed/Materialized Shift | 72.9413 | -1.6753 | Night | 202602 | 2026-02-06 | 1.6753
2026-02-06 22:01 | 70.1168 | FALSE | TRUE | -0.15724 | -0.22476 | -2.8419 | -3.8953 | -0.2826 |  | 2026-02-06 19:16 | none | FALSE | 1 | 69.9596 | FALSE | FALSE | 0.5479 | 2.4351 | 71.4591 | 9 | -0.2826 | -0.09891 | 0.16593 | -1.1071 | 0.74979 | Confirmed/Materialized Shift | 72.9587 | -1.7903 | Night | 202602 | 2026-02-06 | 1.7903
2026-02-06 22:16 | 70.1168 | FALSE | TRUE | -0.33827 | -0.48478 | -2.8251 | -3.8731 | 0 |  | 2026-02-06 19:16 | none | FALSE | 1 | 69.7785 | FALSE | FALSE | 0.5334 | 2.3488 | 71.3602 | 10 | 0 | -0.09891 | 0.16593 | 0.59611 | 0.79085 | Confirmed/Materialized Shift | 72.9419 | -1.5723 | Night | 202602 | 2026-02-06 | 1.5723
2026-02-06 22:31 | 70.1168 | FALSE | TRUE | -0.49024 | -0.70409 | -2.7793 | -3.8127 | 0 |  | 2026-02-06 19:16 | none | FALSE | 1 | 69.6266 | FALSE | FALSE | 0.5219 | 2.2626 | 71.2613 | 11 | 0 | -0.09891 | 0.16593 | 0.59611 | 0.81738 | Confirmed/Materialized Shift | 72.8961 | -1.4002 | Night | 202602 | 2026-02-06 | 1.4002
2026-02-06 22:46 | 70.1168 | FALSE | TRUE | -0.61592 | -0.88621 | -2.7072 | -3.7174 | 0 |  | 2026-02-06 19:16 | none | FALSE | 1 | 69.5009 | FALSE | FALSE | 0.5125 | 2.1789 | 71.1624 | 12 | 0 | -0.09891 | 0.16593 | 0.59611 | 0.83077 | Confirmed/Materialized Shift | 72.824 | -1.2586 | Night | 202602 | 2026-02-06 | 1.2586
2026-02-06 23:01 | 69.836 | FALSE | TRUE | -0.4878 | -0.7034 | -2.9147 | -4.0065 | -0.2808 |  | 2026-02-06 19:16 | none | FALSE | 1 | 69.3482 | FALSE | FALSE | 0.5237 | 2.1211 | 71.0495 | 13 | -0.2808 | -0.11295 | 0.16897 | -0.99338 | 0.85063 | Confirmed/Materialized Shift | 72.7507 | -1.4265 | Night | 202602 | 2026-02-06 | 1.4265
2026-02-06 23:16 | 69.836 | FALSE | TRUE | -0.60842 | -0.87887 | -2.8095 | -3.8674 | 0 |  | 2026-02-06 19:16 | none | FALSE | 1 | 69.2276 | FALSE | FALSE | 0.5144 | 2.0615 | 70.9365 | 14 | 0 | -0.11295 | 0.16897 | 0.66847 | 0.85447 | Confirmed/Materialized Shift | 72.6455 | -1.288 | Night | 202602 | 2026-02-06 | 1.288
2026-02-06 23:31 | 69.836 | FALSE | TRUE | -0.69742 | -1.0087 | -2.6726 | -3.6859 | 0 |  | 2026-02-06 19:16 | none | FALSE | 1 | 69.1386 | FALSE | FALSE | 0.5067 | 2.0023 | 70.8236 | 15 | 0 | -0.11295 | 0.16897 | 0.66847 | 0.84249 | Confirmed/Materialized Shift | 72.5086 | -1.1722 | Night | 202602 | 2026-02-06 | 1.1722
2026-02-06 23:45 | 69.5534 | FALSE | TRUE | -0.5214 | -0.7553 | -2.8076 | -3.88 | -0.2826 |  | 2026-02-06 19:16 | none | FALSE | 1 | 69.032 | FALSE | FALSE | 0.5201 | 1.963 | 70.6965 | 16 | -0.2826 | -0.12708 | 0.17083 | -0.91037 | 0.83224 | Confirmed/Materialized Shift | 72.361 | -1.3735 | Night | 202602 | 2026-02-06 | 1.3735
2026-02-07 | 69.5534 | FALSE | TRUE | -0.58582 | -0.84941 | -2.6178 | -3.6273 | 0 |  | 2026-02-06 19:16 | none | FALSE | 1 | 68.9676 | FALSE | FALSE | 0.5131 | 1.9221 | 70.5694 | 17 | 0 | -0.12708 | 0.17083 | 0.74389 | 0.80091 | Confirmed/Materialized Shift | 72.1712 | -1.2686 | Night | 202602 | 2026-02-07 | 1.2686
2026-02-07 00:15 | 69.5534 | FALSE | TRUE | -0.60278 | -0.87421 | -2.3806 | -3.3095 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 68.9506 | FALSE | FALSE | 0.4795 | 1.8815 | 70.4423 | 18 | 0 | -0.12708 | 0.17083 | 0.74389 | 0.74585 | Confirmed/Materialized Shift | 71.934 | -1.1918 | Night | 202602 | 2026-02-07 | 1.1918
2026-02-07 00:30 | 69.5534 | FALSE | TRUE | -0.61781 | -0.89621 | -2.1698 | -3.0252 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 68.9356 | FALSE | FALSE | 0.4742 | 1.8411 | 70.3294 | 19 | 0 | -0.11295 | 0.16897 | 0.66847 | 0.6969 | Confirmed/Materialized Shift | 71.7232 | -1.1135 | Night | 202602 | 2026-02-07 | 1.1135
2026-02-07 00:45 | 69.2708 | FALSE | TRUE | -0.35207 | -0.51085 | -2.2151 | -3.0986 | -0.2826 |  | 2026-02-06 19:16 | none | FALSE | 0 | 68.9187 | FALSE | FALSE | 0.4968 | 1.8216 | 70.2023 | 20 | -0.2826 | -0.12708 | 0.17083 | -0.91037 | 0.64178 | Confirmed/Materialized Shift | 71.4859 | -1.4514 | Night | 202602 | 2026-02-07 | 1.4514
2026-02-07 01:00 | 69.2708 | FALSE | TRUE | -0.36699 | -0.53261 | -2.0041 | -2.8118 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 68.9038 | FALSE | FALSE | 0.4921 | 1.8006 | 70.0893 | 21 | 0 | -0.11295 | 0.16897 | 0.66847 | 0.59277 | Confirmed/Materialized Shift | 71.2749 | -1.3809 | Night | 202602 | 2026-02-07 | 1.3809
2026-02-07 01:15 | 68.9882 | FALSE | TRUE | -0.16281 | -0.23655 | -2.1392 | -3.0076 | -0.2826 |  | 2026-02-06 19:16 | none | FALSE | 0 | 68.8254 | FALSE | FALSE | 0.5145 | 1.7968 | 69.9764 | 22 | -0.2826 | -0.11295 | 0.16897 | -1.004 | 0.5755 | Confirmed/Materialized Shift | 71.1274 | -1.7171 | Night | 202602 | 2026-02-07 | 1.7171
2026-02-07 01:30 | 68.9882 | FALSE | TRUE | -0.19091 | -0.2775 | -1.9414 | -2.7371 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 68.7973 | FALSE | FALSE | 0.5095 | 1.7901 | 69.8635 | 23 | 0 | -0.11295 | 0.16897 | 0.66847 | 0.53308 | Confirmed/Materialized Shift | 70.9296 | -1.6419 | Night | 202602 | 2026-02-07 | 1.6419
2026-02-07 01:45 | 68.9882 | FALSE | TRUE | -0.22437 | -0.32629 | -1.7772 | -2.5114 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 68.7638 | FALSE | FALSE | 0.5034 | 1.7802 | 69.7646 | 24 | 0 | -0.09882 | 0.16582 | 0.59594 | 0.5004 | Confirmed/Materialized Shift | 70.7654 | -1.5516 | Night | 202602 | 2026-02-07 | 1.5516
2026-02-07 02:00 | 68.7056 | FALSE | TRUE | -0.049453 | -0.07203 | -1.9699 | -2.7872 | -0.2826 |  | 2026-02-06 19:16 | none | FALSE | 0 | 68.6561 | FALSE | FALSE | 0.5268 | 1.785 | 69.6658 | 25 | -0.2826 | -0.09882 | 0.16582 | -1.1083 | 0.50483 | Confirmed/Materialized Shift | 70.6755 | -1.902 | Night | 202602 | 2026-02-07 | 1.902
2026-02-07 02:15 | 68.7056 | FALSE | TRUE | -0.1589 | -0.23182 | -1.9099 | -2.7047 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 68.5467 | FALSE | FALSE | 0.5129 | 1.7815 | 69.5811 | 26 | 0 | -0.08469 | 0.16132 | 0.52499 | 0.51721 | Confirmed/Materialized Shift | 70.6155 | -1.6928 | Night | 202602 | 2026-02-07 | 1.6928
2026-02-07 02:30 | 68.7056 | FALSE | TRUE | -0.26744 | -0.39077 | -1.8774 | -2.6598 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 68.4382 | FALSE | FALSE | 0.5001 | 1.7711 | 69.5106 | 27 | 0 | -0.07056 | 0.15534 | 0.45424 | 0.5362 | Confirmed/Materialized Shift | 70.583 | -1.5012 | Night | 202602 | 2026-02-07 | 1.5012
2026-02-07 02:44 | 68.7056 | FALSE | TRUE | -0.32372 | -0.4734 | -1.7643 | -2.5036 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 68.3819 | FALSE | FALSE | 0.492 | 1.7571 | 69.4259 | 28 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.522 | Confirmed/Materialized Shift | 70.4699 | -1.3798 | Night | 202602 | 2026-02-07 | 1.3798
2026-02-07 02:59 | 68.423 | FALSE | TRUE | -0.16393 | -0.24015 | -2.0003 | -2.8404 | -0.2826 |  | 2026-02-06 19:16 | none | FALSE | 0 | 68.2591 | FALSE | FALSE | 0.5131 | 1.7551 | 69.3412 | 29 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.54105 | Confirmed/Materialized Shift | 70.4233 | -1.697 | Night | 202602 | 2026-02-07 | 1.697
2026-02-07 03:14 | 68.423 | FALSE | TRUE | -0.25811 | -0.37866 | -1.9251 | -2.7365 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 68.1649 | FALSE | FALSE | 0.5018 | 1.7475 | 69.2565 | 30 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.5458 | Confirmed/Materialized Shift | 70.3481 | -1.5271 | Night | 202602 | 2026-02-07 | 1.5271
2026-02-07 03:29 | 68.423 | FALSE | TRUE | -0.32443 | -0.47642 | -1.822 | -2.5938 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 68.0986 | FALSE | FALSE | 0.493 | 1.7361 | 69.1718 | 31 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.53662 | Confirmed/Materialized Shift | 70.245 | -1.3954 | Night | 202602 | 2026-02-07 | 1.3954
2026-02-07 03:44 | 68.423 | FALSE | TRUE | -0.3614 | -0.53099 | -1.6896 | -2.4099 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 68.0616 | FALSE | FALSE | 0.4863 | 1.7223 | 69.0871 | 32 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.51275 | Confirmed/Materialized Shift | 70.1126 | -1.2952 | Night | 202602 | 2026-02-07 | 1.2952
2026-02-07 03:59 | 68.423 | FALSE | TRUE | -0.40925 | -0.60172 | -1.5962 | -2.2796 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 68.0137 | FALSE | FALSE | 0.4789 | 1.706 | 69.0165 | 33 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.50136 | Confirmed/Materialized Shift | 70.0192 | -1.1837 | Night | 202602 | 2026-02-07 | 1.1837
2026-02-07 04:14 | 68.423 | FALSE | TRUE | -0.43488 | -0.63963 | -1.4805 | -2.1179 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 67.9881 | FALSE | FALSE | 0.4728 | 1.6879 | 68.9458 | 34 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.47884 | Confirmed/Materialized Shift | 69.9035 | -1.0918 | Night | 202602 | 2026-02-07 | 1.0918
2026-02-07 04:29 | 68.1404 | FALSE | TRUE | -0.20491 | -0.30163 | -1.6462 | -2.3589 | -0.2826 |  | 2026-02-06 19:16 | none | FALSE | 0 | 67.9355 | FALSE | FALSE | 0.5038 | 1.6842 | 68.861 | 35 | -0.2826 | -0.08478 | 0.13287 | -1.4888 | 0.46277 | Confirmed/Materialized Shift | 69.7866 | -1.5572 | Night | 202602 | 2026-02-07 | 1.5572
2026-02-07 04:44 | 68.1404 | FALSE | TRUE | -0.26873 | -0.39593 | -1.5687 | -2.2503 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 67.8717 | FALSE | FALSE | 0.4943 | 1.6767 | 68.7904 | 36 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.45935 | Confirmed/Materialized Shift | 69.7091 | -1.415 | Night | 202602 | 2026-02-07 | 1.415
2026-02-07 04:59 | 68.1404 | FALSE | TRUE | -0.30914 | -0.45575 | -1.4678 | -2.1087 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 67.8313 | FALSE | FALSE | 0.4869 | 1.6667 | 68.7197 | 37 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.44424 | Confirmed/Materialized Shift | 69.6082 | -1.3041 | Night | 202602 | 2026-02-07 | 1.3041
2026-02-07 05:14 | 68.1404 | FALSE | TRUE | -0.32361 | -0.47718 | -1.341 | -1.93 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 67.8168 | FALSE | FALSE | 0.4815 | 1.655 | 68.6491 | 38 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.41614 | Confirmed/Materialized Shift | 69.4814 | -1.2224 | Night | 202602 | 2026-02-07 | 1.2224
2026-02-07 05:29 | 68.1404 | FALSE | TRUE | -0.30628 | -0.45151 | -1.1823 | -1.7056 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 67.8341 | FALSE | FALSE | 0.4785 | 1.6427 | 68.5784 | 39 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.37215 | Confirmed/Materialized Shift | 69.3227 | -1.177 | Night | 202602 | 2026-02-07 | 1.177
2026-02-07 05:43 | 68.1404 | FALSE | TRUE | -0.31132 | -0.45898 | -1.0743 | -1.5522 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 67.8291 | FALSE | FALSE | 0.4734 | 1.6292 | 68.5219 | 40 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.34642 | Confirmed/Materialized Shift | 69.2147 | -1.1013 | Night | 202602 | 2026-02-07 | 1.1013
2026-02-07 05:58 | 68.1404 | FALSE | TRUE | -0.29075 | -0.42852 | -0.94073 | -1.3618 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 67.8496 | FALSE | FALSE | 0.4704 | 1.6152 | 68.4654 | 41 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.30787 | Confirmed/Materialized Shift | 69.0811 | -1.0556 | Night | 202602 | 2026-02-07 | 1.0556
2026-02-07 06:13 | 67.8596 | FALSE | TRUE | -0.071483 | -0.10545 | -1.1702 | -1.6952 | -0.2808 |  | 2026-02-06 19:16 | none | FALSE | 0 | 67.7881 | FALSE | FALSE | 0.518 | 1.6189 | 68.409 | 42 | -0.2808 | -0.05643 | 0.11579 | -1.9377 | 0.31042 | Confirmed/Materialized Shift | 69.0298 | -1.7697 | Night | 202602 | 2026-02-07 | 1.7697
2026-02-07 06:29 | 67.8596 | FALSE | TRUE | -0.11117 | -0.1641 | -1.097 | -1.5909 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 67.7484 | FALSE | FALSE | 0.5088 | 1.6192 | 68.3525 | 43 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.30205 | Confirmed/Materialized Shift | 68.9566 | -1.6319 | Night | 202602 | 2026-02-07 | 1.6319
2026-02-07 06:43 | 67.8596 | FALSE | TRUE | -0.12707 | -0.18761 | -1.0001 | -1.4523 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 67.7325 | FALSE | FALSE | 0.5033 | 1.6176 | 68.2961 | 44 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.28179 | Confirmed/Materialized Shift | 68.8597 | -1.549 | Night | 202602 | 2026-02-07 | 1.549
2026-02-07 06:58 | 67.8596 | FALSE | TRUE | -0.16695 | -0.24663 | -0.95535 | -1.3883 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 67.6926 | FALSE | FALSE | 0.4937 | 1.6129 | 68.2538 | 45 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.28058 | Confirmed/Materialized Shift | 68.815 | -1.405 | Night | 202602 | 2026-02-07 | 1.405
2026-02-07 07:13 | 67.8596 | FALSE | TRUE | -0.19317 | -0.28547 | -0.89697 | -1.3046 | 0 |  | 2026-02-06 19:16 | none | FALSE | 0 | 67.6664 | FALSE | FALSE | 0.4861 | 1.6059 | 68.2115 | 46 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.27253 | Confirmed/Materialized Shift | 68.7566 | -1.2912 | Day | 202602 | 2026-02-07 | 1.2912
2026-02-07 07:28 | 68.1404 | TRUE | FALSE | -0.45052 | -0.66556 | -0.5362 | -0.78076 | 0.2808 |  |  | none | FALSE | 1 | 67.6899 | FALSE | FALSE | 0.0401 |  | 68.1832 | 0 | 0.2808 | -0.02826 | 0.12596 | 2.4536 | 0.24668 | Persistence ends | 68.6766 | -0.17367 | Day | 202602 | 2026-02-07 | 0.17367
2026-02-07 07:30 | 68.1404 | FALSE | FALSE | -0.41318 | -0.61007 | -0.44234 | -0.64498 | 0 |  |  | none | FALSE | 1 | 67.7272 | FALSE | FALSE | 0.0331 |  | 68.155 | 0 | 0 | -0.02826 | 0.12596 | 0.22436 | 0.21388 | Normal | 68.5827 | -0.068168 | Day | 202602 | 2026-02-07 | 0.068168
2026-02-07 07:45 | 68.1404 | FALSE | FALSE | -0.40828 | -0.60279 | -0.40918 | -0.59692 | 0 |  |  | none | FALSE | 1 | 67.7321 | FALSE | FALSE | 0.0287 |  | 68.1409 | 0 | 0 | -0.01413 | 0.11087 | 0.12744 | 0.20437 | Normal | 68.5496 | -0.0022019 | Day | 202602 | 2026-02-07 | 0.0022019
2026-02-07 08:00 | 68.423 | TRUE | FALSE | -0.69088 | -1.02 | -0.12658 | -0.18466 | 0.2826 |  |  | none | FALSE | 2 | 67.7321 | TRUE | FALSE | 0.1492 |  | 68.1409 | 0 | 0.2826 | 0 | 0.12925 | 2.1864 | 0.20437 | Normal | 68.5496 | 1.3806 | Day | 202602 | 2026-02-07 | 1.3806
2026-02-07 08:15 | 68.7056 | FALSE | FALSE | -1.016 | -1.501 | 0.085207 | 0.12417 | 0.2826 | 2026-02-07 13:28 | 2026-02-07 08:15 | upper | TRUE | 2 | 67.6896 | FALSE | FALSE | 0.272 | 2.3662 | 68.155 | 1 | 0.2826 | 0.01413 | 0.14387 | 1.866 | 0.23271 | Extreme triggered | 68.6204 | 2.3662 | Day | 202602 | 2026-02-07 | 2.3662
2026-02-07 08:30 | 68.7056 | FALSE | FALSE | -1.0508 | -1.5531 | 0.02222 | 0.032352 | 0 |  | 2026-02-07 08:15 | upper | TRUE | 2 | 67.6548 | FALSE | FALSE | 0.3105 | 2.2263 | 68.1691 | 2 | 0 | 0.01413 | 0.14387 | -0.098211 | 0.25713 | Extreme/elevated | 68.6834 | 2.0864 | Day | 202602 | 2026-02-07 | 2.0864
2026-02-07 08:30 | 68.7056 | FALSE | FALSE | -1.0797 | -1.5966 | -0.035005 | -0.050924 | 0 |  | 2026-02-07 08:15 | none | FALSE | 2 | 67.6259 | FALSE | FALSE | 0.3535 | 2.109 | 68.1832 | 3 | 0 | 0.01413 | 0.14387 | -0.098211 | 0.27868 | Persistent | 68.7406 | 1.8744 | Day | 202602 | 2026-02-07 | 1.8744
2026-02-07 08:45 | 68.9882 | FALSE | FALSE | -1.4337 | -2.1222 | 0.11973 | 0.17386 | 0.2826 |  | 2026-02-07 08:15 | upper | TRUE | 2 | 67.5545 | FALSE | TRUE | 0.4433 | 2.1729 | 68.2115 | 4 | 0.2826 | 0.02826 | 0.1558 | 1.6325 | 0.32848 | Persistent | 68.8685 | 2.3645 | Day | 202602 | 2026-02-07 | 2.3645
2026-02-07 09:00 | 69.2708 | FALSE | FALSE | -1.8111 | -2.6847 | 0.1945 | 0.28157 | 0.2826 |  | 2026-02-07 08:15 | upper | TRUE | 2 | 67.4597 | FALSE | TRUE | 0.5083 | 2.2345 | 68.268 | 5 | 0.2826 | 0.05652 | 0.14748 | 1.533 | 0.40414 | Persistent | 69.0763 | 2.4813 | Day | 202602 | 2026-02-07 | 2.4813
2026-02-07 09:15 | 69.836 | TRUE | FALSE | -2.5496 | -3.7892 | 0.41679 | 0.6004 | 0.5652 |  | 2026-02-07 08:15 | upper | TRUE | 3 | 67.2864 | TRUE | TRUE | 0.614 | 2.3257 | 68.3528 | 6 | 0.5652 | 0.08478 | 0.18537 | 2.5917 | 0.5332 | Persistent | 69.4192 | 2.7817 | Day | 202602 | 2026-02-07 | 2.7817
2026-02-07 09:30 | 69.836 | FALSE | TRUE | -2.6477 | -3.9407 | 0.14918 | 0.21408 | 0 |  | 2026-02-07 08:15 | upper | TRUE | 2 | 67.1883 | FALSE | TRUE | 0.6064 | 2.3133 | 68.4376 | 7 | 0 | 0.08478 | 0.18537 | -0.45737 | 0.62462 | Confirmed/Materialized Shift | 69.6868 | 2.2388 | Day | 202602 | 2026-02-07 | 2.2388
2026-02-07 09:45 | 70.1168 | FALSE | TRUE | -3.0276 | -4.5129 | 0.13315 | 0.19026 | 0.2808 |  | 2026-02-07 08:15 | upper | TRUE | 2 | 67.0892 | FALSE | TRUE | 0.6027 | 2.2972 | 68.5364 | 8 | 0.2808 | 0.09882 | 0.1892 | 0.96184 | 0.72362 | Confirmed/Materialized Shift | 69.9836 | 2.184 | Day | 202602 | 2026-02-07 | 2.184
2026-02-07 10:00 | 70.3994 | FALSE | TRUE | -3.4049 | -5.0823 | 0.095214 | 0.13543 | 0.2826 |  | 2026-02-07 08:15 | upper | TRUE | 2 | 66.9945 | FALSE | TRUE | 0.5981 | 2.2769 | 68.6493 | 9 | 0.2826 | 0.11295 | 0.19196 | 0.88376 | 0.82742 | Confirmed/Materialized Shift | 70.3042 | 2.1151 | Day | 202602 | 2026-02-07 | 2.1151
2026-02-07 10:15 | 70.682 | FALSE | TRUE | -3.7726 | -5.6384 | 0.038547 | 0.054565 | 0.2826 |  | 2026-02-07 08:15 | upper | TRUE | 1 | 66.9094 | FALSE | TRUE | 0.5647 | 2.2534 | 68.7764 | 10 | 0.2826 | 0.12708 | 0.19361 | 0.80328 | 0.93351 | Confirmed/Materialized Shift | 70.6435 | 2.0413 | Day | 202602 | 2026-02-07 | 2.0413
2026-02-07 10:29 | 70.9646 | FALSE | TRUE | -4.1265 | -6.1739 | -0.032624 | -0.045951 | 0.2826 |  | 2026-02-07 08:15 | none | FALSE | 1 | 66.8381 | FALSE | FALSE | 0.5598 | 2.2275 | 68.9176 | 11 | 0.2826 | 0.14121 | 0.19416 | 0.72823 | 1.0398 | Confirmed/Materialized Shift | 70.9972 | 1.9686 | Day | 202602 | 2026-02-07 | 1.9686
2026-02-07 10:44 | 71.2472 | FALSE | TRUE | -4.4209 | -6.6155 | -0.1005 | -0.14087 | 0.2826 |  | 2026-02-07 08:15 | none | FALSE | 1 | 66.8263 | FALSE | FALSE | 0.556 | 2.2011 | 69.087 | 12 | 0.2826 | 0.16938 | 0.16894 | 0.67019 | 1.1303 | Confirmed/Materialized Shift | 71.3477 | 1.9111 | Day | 202602 | 2026-02-07 | 1.9111
2026-02-07 10:59 | 71.5298 | FALSE | TRUE | -4.6899 | -7.0166 | -0.17136 | -0.239 | 0.2826 |  | 2026-02-07 08:15 | none | FALSE | 1 | 66.8399 | FALSE | FALSE | 0.5525 | 2.1748 | 69.2705 | 13 | 0.2826 | 0.18351 | 0.16581 | 0.5976 | 1.2153 | Confirmed/Materialized Shift | 71.7012 | 1.859 | Day | 202602 | 2026-02-07 | 1.859
2026-02-07 11:14 | 71.8124 | FALSE | TRUE | -4.9297 | -7.3707 | -0.24124 | -0.3348 | 0.2826 |  | 2026-02-07 08:15 | none | FALSE | 1 | 66.8827 | FALSE | FALSE | 0.5495 | 2.149 | 69.4682 | 14 | 0.2826 | 0.19764 | 0.16133 | 0.52661 | 1.2927 | Confirmed/Materialized Shift | 72.0536 | 1.8134 | Day | 202602 | 2026-02-07 | 1.8134
2026-02-07 11:29 | 72.095 | FALSE | TRUE | -5.136 | -7.6704 | -0.30592 | -0.42254 | 0.2826 |  | 2026-02-07 08:15 | none | FALSE | 1 | 66.959 | FALSE | FALSE | 0.5469 | 2.1241 | 69.6799 | 15 | 0.2826 | 0.21177 | 0.15538 | 0.45585 | 1.3605 | Confirmed/Materialized Shift | 72.4009 | 1.7751 | Day | 202602 | 2026-02-07 | 1.7751
2026-02-07 11:44 | 72.095 | FALSE | TRUE | -4.9863 | -7.4302 | -0.57973 | -0.79771 | 0 |  | 2026-02-07 08:15 | none | FALSE | 0 | 67.1087 | FALSE | FALSE | 0.5056 | 2.0903 | 69.8917 | 16 | 0 | 0.21177 | 0.15538 | -1.3629 | 1.3915 | Confirmed/Materialized Shift | 72.6747 | 1.5834 | Day | 202602 | 2026-02-07 | 1.5834
2026-02-07 11:59 | 72.3758 | FALSE | TRUE | -5.1376 | -7.6409 | -0.59295 | -0.81261 | 0.2808 |  | 2026-02-07 08:15 | none | FALSE | 0 | 67.2382 | FALSE | FALSE | 0.5057 | 2.0606 | 70.1035 | 17 | 0.2808 | 0.21177 | 0.15538 | 0.44427 | 1.4326 | Confirmed/Materialized Shift | 72.9688 | 1.5861 | Day | 202602 | 2026-02-07 | 1.5861
2026-02-07 12:14 | 72.6584 | FALSE | TRUE | -5.2544 | -7.7954 | -0.59636 | -0.81409 | 0.2826 |  | 2026-02-07 08:15 | none | FALSE | 0 | 67.404 | FALSE | FALSE | 0.5062 | 2.0346 | 70.3294 | 18 | 0.2826 | 0.2259 | 0.14777 | 0.3837 | 1.4627 | Confirmed/Materialized Shift | 73.2548 | 1.5923 | Day | 202602 | 2026-02-07 | 1.5923
2026-02-07 12:29 | 72.941 | FALSE | TRUE | -5.3283 | -7.8807 | -0.58517 | -0.79586 | 0.2826 |  | 2026-02-07 08:15 | none | FALSE | 0 | 67.6127 | FALSE | FALSE | 0.5069 | 2.0119 | 70.5694 | 19 | 0.2826 | 0.24003 | 0.13824 | 0.30795 | 1.4784 | Confirmed/Materialized Shift | 73.5262 | 1.6042 | Day | 202602 | 2026-02-07 | 1.6042
2026-02-07 12:44 | 73.2236 | FALSE | TRUE | -5.4163 | -7.9878 | -0.58801 | -0.79663 | 0.2826 |  | 2026-02-07 08:15 | none | FALSE | 0 | 67.8073 | FALSE | FALSE | 0.5072 | 1.9918 | 70.8094 | 20 | 0.2826 | 0.24003 | 0.13824 | 0.30795 | 1.5011 | Confirmed/Materialized Shift | 73.8116 | 1.6083 | Day | 202602 | 2026-02-07 | 1.6083
2026-02-07 12:59 | 73.2236 | FALSE | TRUE | -5.2038 | -7.6504 | -0.82725 | -1.1171 | 0 |  | 2026-02-07 08:15 | none | FALSE | 0 | 68.0198 | FALSE | FALSE | 0.4968 | 1.966 | 71.0353 | 21 | 0 | 0.2259 | 0.14777 | -1.5287 | 1.5078 | Confirmed/Materialized Shift | 74.0509 | 1.4513 | Day | 202602 | 2026-02-07 | 1.4513
2026-02-07 13:14 | 72.941 | TRUE | TRUE | -4.6139 | -6.7526 | -1.2261 | -1.6532 | -0.2826 |  | 2026-02-07 08:15 | none | FALSE | 1 | 68.3271 | FALSE | FALSE | 0.5059 | 1.9294 | 71.2471 | 22 | -0.2826 | 0.21177 | 0.18041 | -2.7402 | 1.46 | Confirmed/Materialized Shift | 74.1671 | 1.1602 | Day | 202602 | 2026-02-07 | 1.1602
2026-02-07 13:28 | 72.6584 | TRUE | FALSE | -3.9379 | -5.7303 | -1.5106 | -2.0367 | -0.2826 |  |  | none | FALSE | 2 | 68.7205 | TRUE | FALSE | 0.1165 |  | 71.4447 | 0 | -0.2826 | 0.19764 | 0.20698 | -2.3202 | 1.3621 | Persistence ends | 74.169 | 0.89101 | Day | 202602 | 2026-02-07 | 0.89101
2026-02-07 13:43 | 72.3758 | FALSE | FALSE | -3.2542 | -4.7079 | -1.7308 | -2.3356 | -0.2826 |  |  | none | FALSE | 2 | 69.1216 | FALSE | FALSE | 0.0979 |  | 71.6141 | 0 | -0.2826 | 0.16938 | 0.23186 | -1.9494 | 1.2463 | Normal | 74.1066 | 0.61117 | Day | 202602 | 2026-02-07 | 0.61117
2026-02-07 13:59 | 72.3758 | FALSE | FALSE | -2.8597 | -4.1137 | -1.6468 | -2.2248 | 0 |  |  | none | FALSE | 2 | 69.5161 | FALSE | FALSE | 0.093 |  | 71.7694 | 0 | 0 | 0.15525 | 0.23321 | -0.66572 | 1.1266 | Normal | 74.0226 | 0.53826 | Day | 202602 | 2026-02-07 | 0.53826
2026-02-07 14:14 | 72.3758 | FALSE | FALSE | -2.553 | -3.6564 | -1.5942 | -2.1551 | 0 |  |  | none | FALSE | 2 | 69.8228 | FALSE | FALSE | 0.088 |  | 71.8964 | 0 | 0 | 0.12699 | 0.2144 | -0.5923 | 1.0368 | Normal | 73.97 | 0.46242 | Day | 202602 | 2026-02-07 | 0.46242
2026-02-07 14:28 | 72.3758 | FALSE | FALSE | -2.1927 | -3.1243 | -1.4878 | -2.0143 | 0 |  |  | none | FALSE | 2 | 70.1831 | FALSE | FALSE | 0.0827 |  | 72.0234 | 0 | 0 | 0.12699 | 0.2144 | -0.5923 | 0.92013 | Normal | 73.8636 | 0.38303 | Day | 202602 | 2026-02-07 | 0.38303
2026-02-07 14:39 | 72.6584 | FALSE | FALSE | -2.1322 | -3.0233 | -1.1163 | -1.5131 | 0.2826 |  |  | none | FALSE | 2 | 70.5262 | FALSE | FALSE | 0.0988 |  | 72.1504 | 0 | 0.2826 | 0.12708 | 0.21447 | 0.72514 | 0.81213 | Normal | 73.7747 | 0.62547 | Day | 202602 | 2026-02-07 | 0.62547
2026-02-07 14:39 | 72.6584 | FALSE | FALSE | -1.8069 | -2.5502 | -1.0168 | -1.3802 | 0 |  |  | none | FALSE | 2 | 70.8515 | FALSE | FALSE | 0.0944 |  | 72.2634 | 0 | 0 | 0.11295 | 0.21299 | -0.53031 | 0.70592 | Normal | 73.6752 | 0.55957 | Day | 202602 | 2026-02-07 | 0.55957
2026-02-07 16:03 | 71.5298 | TRUE | FALSE | -0.47803 | -0.67279 | -2.03 | -2.7596 | -1.1286 |  |  | none | FALSE | 3 | 71.0518 | TRUE | FALSE | 0.1682 |  | 72.3058 | 0 | -1.1286 | 0.04239 | 0.34603 | -3.3841 | 0.62701 | Normal | 73.5598 | -1.2376 | Day | 202602 | 2026-02-07 | 1.2376
2026-02-07 16:33 | 71.2472 | FALSE | FALSE | -0.12267 | -0.17247 | -2.2681 | -3.0852 | -0.2826 |  |  | none | FALSE | 3 | 71.1245 | FALSE | FALSE | 0.2054 |  | 72.3199 | 0 | -0.2826 | 0.01413 | 0.34845 | -0.85157 | 0.59769 | Normal | 73.5153 | -1.7948 | Day | 202602 | 2026-02-07 | 1.7948
2026-02-07 16:33 | 71.2472 | FALSE | FALSE | -0.12267 | -0.17247 | -2.2681 | -3.0852 | 0 |  |  | none | FALSE | 2 | 71.1245 | FALSE | FALSE | 0.1768 |  | 72.3199 | 0 | 0 | 0 | 0.34267 | 0 | 0.59769 | Normal | 73.5153 | -1.7948 | Day | 202602 | 2026-02-07 | 1.7948
2026-02-07 16:48 | 71.8124 | FALSE | FALSE | -0.64064 | -0.90013 | -1.6839 | -2.2912 | 0.5652 |  |  | none | FALSE | 1 | 71.1718 | FALSE | FALSE | 0.0884 |  | 72.334 | 0 | 0.5652 | 0.01413 | 0.36031 | 1.5294 | 0.58114 | Normal | 73.4963 | -0.89762 | Day | 202602 | 2026-02-07 | 0.89762
2026-02-07 17:03 | 72.095 | FALSE | FALSE | -0.88911 | -1.2486 | -1.3954 | -1.8988 | 0.2826 |  |  | none | FALSE | 1 | 71.2059 | FALSE | FALSE | 0.0581 |  | 72.3482 | 0 | 0.2826 | 0.01413 | 0.36031 | 0.7451 | 0.57114 | Normal | 73.4904 | -0.44327 | Day | 202602 | 2026-02-07 | 0.44327
2026-02-07 17:19 | 72.3758 | FALSE | FALSE | -1.1496 | -1.6141 | -1.1225 | -1.5272 | 0.2808 |  |  | none | FALSE | 1 | 71.2262 | FALSE | FALSE | 0.0302 |  | 72.3622 | 0 | 0.2808 | 0.01404 | 0.36024 | 0.7405 | 0.56803 | Normal | 73.4983 | 0.023925 | Day | 202602 | 2026-02-07 | 0.023925
2026-02-07 17:30 | 72.3758 | FALSE | FALSE | -1.1286 | -1.5841 | -1.1295 | -1.5367 | 0 |  |  | none | FALSE | 1 | 71.2472 | FALSE | FALSE | 0.0286 |  | 72.3762 | 0 | 0 | 0.01404 | 0.36024 | -0.038974 | 0.56454 | Normal | 73.5053 | -0.00079711 | Day | 202602 | 2026-02-07 | 0.00079711
2026-02-07 17:31 | 72.3758 | FALSE | FALSE | -1.1286 | -1.5841 | -1.1295 | -1.5367 | 0 |  |  | none | FALSE | 1 | 71.2472 | FALSE | FALSE | 0.0286 |  | 72.3762 | 0 | 0 | 0 | 0.35473 | 0 | 0.56454 | Normal | 73.5053 | -0.00079711 | Day | 202602 | 2026-02-07 | 0.00079711
2026-02-07 17:46 | 72.3758 | FALSE | FALSE | -1.1349 | -1.5931 | -1.1076 | -1.5072 | 0 |  |  | none | FALSE | 1 | 71.2409 | FALSE | FALSE | 0.0302 |  | 72.3621 | 0 | 0 | -0.01413 | 0.34845 | 0.040551 | 0.56063 | Normal | 73.4834 | 0.024401 | Day | 202602 | 2026-02-07 | 0.024401
2026-02-07 18:01 | 72.3758 | FALSE | FALSE | -1.1298 | -1.5857 | -1.0459 | -1.4245 | 0 |  |  | none | FALSE | 1 | 71.246 | FALSE | FALSE | 0.0337 |  | 72.3339 | 0 | 0 | -0.02826 | 0.34144 | 0.082766 | 0.54391 | Normal | 73.4217 | 0.077109 | Day | 202602 | 2026-02-07 | 0.077109
2026-02-07 18:16 | 72.3758 | FALSE | FALSE | -1.0891 | -1.5277 | -0.9204 | -1.2557 | 0 |  |  | none | FALSE | 0 | 71.2867 | FALSE | FALSE | 0.0112 |  | 72.2915 | 0 | 0 | -0.04239 | 0.33366 | 0.12704 | 0.50236 | Normal | 73.2962 | 0.16787 | Night | 202602 | 2026-02-07 | 0.16787
2026-02-07 18:30 | 72.3758 | FALSE | FALSE | -1.0325 | -1.4473 | -0.77909 | -1.065 | 0 |  |  | none | FALSE | 0 | 71.3433 | FALSE | FALSE | 0.0187 |  | 72.2491 | 0 | 0 | -0.04239 | 0.33366 | 0.12704 | 0.45291 | Normal | 73.1549 | 0.27979 | Night | 202602 | 2026-02-07 | 0.27979
2026-02-07 18:45 | 72.095 | FALSE | FALSE | -0.73508 | -1.0301 | -0.95864 | -1.3122 | -0.2808 |  |  | none | FALSE | 0 | 71.3599 | FALSE | FALSE | 0.0176 |  | 72.2068 | 0 | -0.2808 | -0.0423 | 0.33359 | -0.71494 | 0.42343 | Normal | 73.0536 | -0.26399 | Night | 202602 | 2026-02-07 | 0.26399
2026-02-07 19:00 | 72.095 | FALSE | FALSE | -0.73707 | -1.0329 | -0.90429 | -1.2388 | 0 |  |  | none | FALSE | 0 | 71.3579 | FALSE | FALSE | 0.0136 |  | 72.1786 | 0 | 0 | -0.02817 | 0.32883 | 0.085667 | 0.41034 | Normal | 72.9993 | -0.20376 | Night | 202602 | 2026-02-07 | 0.20376
2026-02-07 19:15 | 71.8124 | FALSE | FALSE | -0.49276 | -0.69091 | -1.1688 | -1.6016 | -0.2826 |  |  | none | FALSE | 0 | 71.3196 | FALSE | FALSE | 0.0543 |  | 72.1504 | 0 | -0.2826 | -0.02817 | 0.32883 | -0.77374 | 0.4154 | Normal | 72.9812 | -0.81377 | Night | 202602 | 2026-02-07 | 0.81377
2026-02-07 19:29 | 71.8124 | FALSE | FALSE | -0.52694 | -0.73919 | -1.1467 | -1.5717 | 0 |  |  | none | FALSE | 0 | 71.2855 | FALSE | FALSE | 0.0494 |  | 72.1223 | 0 | 0 | -0.02817 | 0.32883 | 0.085667 | 0.4184 | Normal | 72.9591 | -0.7406 | Night | 202602 | 2026-02-07 | 0.7406
2026-02-07 19:44 | 71.5298 | FALSE | FALSE | -0.31763 | -0.44604 | -1.418 | -1.9438 | -0.2826 |  |  | none | FALSE | 0 | 71.2122 | FALSE | FALSE | 0.0845 |  | 72.08 | 0 | -0.2826 | -0.0423 | 0.33359 | -0.72034 | 0.4339 | Normal | 72.9478 | -1.268 | Night | 202602 | 2026-02-07 | 1.268
2026-02-07 19:59 | 71.5298 | FALSE | FALSE | -0.38142 | -0.5361 | -1.3972 | -1.9158 | 0 |  |  | none | FALSE | 0 | 71.1484 | FALSE | FALSE | 0.0761 |  | 72.0377 | 0 | 0 | -0.0423 | 0.33359 | 0.1268 | 0.44465 | Normal | 72.927 | -1.1422 | Night | 202602 | 2026-02-07 | 1.1422
2026-02-07 20:15 | 71.5298 | FALSE | FALSE | -0.41494 | -0.58349 | -1.3178 | -1.809 | 0 |  |  | none | FALSE | 0 | 71.1149 | FALSE | FALSE | 0.0695 |  | 71.9812 | 0 | 0 | -0.05643 | 0.32498 | 0.17364 | 0.43319 | Normal | 72.8476 | -1.0421 | Night | 202602 | 2026-02-07 | 1.0421
2026-02-07 20:29 | 71.2472 | FALSE | FALSE | -0.20056 | -0.28229 | -1.5275 | -2.099 | -0.2826 |  |  | none | FALSE | 0 | 71.0466 | FALSE | FALSE | 0.1024 |  | 71.9107 | 0 | -0.2826 | -0.07056 | 0.32852 | -0.64543 | 0.43202 | Normal | 72.7747 | -1.5358 | Night | 202602 | 2026-02-07 | 1.5358
2026-02-07 20:44 | 71.2472 | FALSE | FALSE | -0.24946 | -0.35136 | -1.5482 | -2.1267 | 0 |  |  | none | FALSE | 0 | 70.9977 | FALSE | FALSE | 0.0963 |  | 71.8966 | 0 | 0 | -0.01413 | 0.21429 | 0.065939 | 0.4494 | Normal | 72.7954 | -1.4449 | Night | 202602 | 2026-02-07 | 1.4449
2026-02-07 20:59 | 70.9646 | FALSE | FALSE | -0.031437 | -0.04432 | -1.8671 | -2.5636 | -0.2826 |  |  | none | FALSE | 0 | 70.9332 | FALSE | FALSE | 0.1289 |  | 71.8824 | 0 | -0.2826 | -0.01413 | 0.21429 | -1.2528 | 0.47463 | Normal | 72.8317 | -1.9338 | Night | 202602 | 2026-02-07 | 1.9338
2026-02-07 21:14 | 70.9646 | FALSE | FALSE | -0.092627 | -0.1307 | -1.9 | -2.6076 | 0 |  |  | none | FALSE | 0 | 70.872 | FALSE | FALSE | 0.1209 |  | 71.8683 | 0 | 0 | -0.01413 | 0.21429 | 0.065939 | 0.49816 | Normal | 72.8646 | -1.8141 | Night | 202602 | 2026-02-07 | 1.8141
2026-02-07 21:29 | 70.9646 | FALSE | FALSE | -0.21404 | -0.30252 | -1.9366 | -2.6565 | 0 |  |  | none | FALSE | 0 | 70.7506 | FALSE | FALSE | 0.1068 |  | 71.8259 | 0 | 0 | -0.04239 | 0.1656 | 0.25597 | 0.53767 | Normal | 72.9012 | -1.6019 | Night | 202602 | 2026-02-07 | 1.6019
2026-02-07 21:44 | 70.682 | FALSE | FALSE | -0.10809 | -0.15316 | -2.2546 | -3.0912 | -0.2826 |  |  | none | FALSE | 0 | 70.5739 | FALSE | FALSE | 0.1211 |  | 71.7553 | 0 | -0.2826 | -0.07065 | 0.15512 | -1.3664 | 0.59067 | Normal | 72.9366 | -1.817 | Night | 202602 | 2026-02-07 | 1.817
2026-02-07 21:59 | 70.682 | FALSE | FALSE | -0.24707 | -0.35078 | -2.2242 | -3.0508 | 0 |  |  | none | FALSE | 0 | 70.4349 | FALSE | FALSE | 0.1067 |  | 71.6706 | 0 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.61782 | Normal | 72.9062 | -1.6001 | Night | 202602 | 2026-02-07 | 1.6001
2026-02-07 22:14 | 70.3994 | FALSE | FALSE | -0.13958 | -0.19867 | -2.4843 | -3.4085 | -0.2826 |  |  | none | FALSE | 0 | 70.2598 | FALSE | FALSE | 0.1191 |  | 71.5717 | 0 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.65596 | Normal | 72.8837 | -1.7872 | Night | 202602 | 2026-02-07 | 1.7872
2026-02-07 22:28 | 70.3994 | FALSE | FALSE | -0.28046 | -0.39998 | -2.4275 | -3.3332 | 0 |  |  | none | FALSE | 0 | 70.1189 | FALSE | FALSE | 0.1057 |  | 71.4729 | 0 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.67699 | Normal | 72.8269 | -1.5857 | Night | 202602 | 2026-02-07 | 1.5857
2026-02-07 22:43 | 70.3994 | FALSE | FALSE | -0.39027 | -0.55746 | -2.3397 | -3.2165 | 0 |  |  | none | FALSE | 0 | 70.0091 | FALSE | FALSE | 0.0952 |  | 71.3741 | 0 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.68249 | Normal | 72.7391 | -1.4282 | Night | 202602 | 2026-02-07 | 1.4282
2026-02-07 22:59 | 70.3994 | FALSE | FALSE | -0.46978 | -0.67179 | -2.2215 | -3.0591 | 0 |  |  | none | FALSE | 0 | 69.9296 | FALSE | FALSE | 0.0868 |  | 71.2753 | 0 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.67283 | Normal | 72.6209 | -1.3018 | Night | 202602 | 2026-02-07 | 1.3018
2026-02-07 23:14 | 70.1168 | FALSE | FALSE | -0.29038 | -0.41585 | -2.3814 | -3.2848 | -0.2826 |  |  | none | FALSE | 0 | 69.8264 | FALSE | FALSE | 0.1044 |  | 71.1623 | 0 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.66795 | Normal | 72.4982 | -1.5653 | Night | 202602 | 2026-02-07 | 1.5653
2026-02-07 23:28 | 70.1168 | FALSE | FALSE | -0.35235 | -0.50506 | -2.2175 | -3.0656 | 0 |  |  | none | FALSE | 0 | 69.7644 | FALSE | FALSE | 0.0968 |  | 71.0494 | 0 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.64247 | Normal | 72.3343 | -1.4516 | Night | 202602 | 2026-02-07 | 1.4516
2026-02-07 23:43 | 70.1168 | FALSE | FALSE | -0.41645 | -0.59748 | -2.0838 | -2.8861 | 0 |  |  | none | FALSE | 0 | 69.7004 | FALSE | FALSE | 0.0889 |  | 70.9505 | 0 | 0 | -0.09891 | 0.13829 | 0.71522 | 0.62506 | Normal | 72.2006 | -1.3337 | Night | 202602 | 2026-02-07 | 1.3337
2026-02-07 23:58 | 69.836 | FALSE | FALSE | -0.22109 | -0.31759 | -2.2241 | -3.0865 | -0.2808 |  |  | none | FALSE | 0 | 69.6149 | FALSE | FALSE | 0.1092 |  | 70.8375 | 0 | -0.2808 | -0.11295 | 0.14193 | -1.1826 | 0.61131 | Normal | 72.0601 | -1.6383 | Night | 202602 | 2026-02-07 | 1.6383
2026-02-08 00:13 | 69.836 | FALSE | FALSE | -0.30757 | -0.44236 | -2.113 | -2.9368 | 0 |  |  | none | FALSE | 0 | 69.5284 | FALSE | FALSE | 0.0994 |  | 70.7387 | 0 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.60513 | Normal | 71.949 | -1.4917 | Night | 202602 | 2026-02-08 | 1.4917
2026-02-08 00:28 | 69.5534 | FALSE | FALSE | -0.13765 | -0.1983 | -2.2824 | -3.1772 | -0.2826 |  |  | none | FALSE | 0 | 69.4157 | FALSE | FALSE | 0.1182 |  | 70.6257 | 0 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.605 | Normal | 71.8358 | -1.7725 | Night | 202602 | 2026-02-08 | 1.7725
2026-02-08 00:43 | 69.5534 | FALSE | FALSE | -0.24836 | -0.35835 | -2.1954 | -3.0599 | 0 |  |  | none | FALSE | 0 | 69.305 | FALSE | FALSE | 0.1062 |  | 70.5269 | 0 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.61094 | Normal | 71.7488 | -1.5935 | Night | 202602 | 2026-02-08 | 1.5935
2026-02-08 00:58 | 69.5534 | FALSE | FALSE | -0.32516 | -0.46969 | -2.0746 | -2.8963 | 0 |  |  | none | FALSE | 0 | 69.2282 | FALSE | FALSE | 0.0972 |  | 70.4281 | 0 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.59993 | Normal | 71.628 | -1.458 | Night | 202602 | 2026-02-08 | 1.458
2026-02-08 01:13 | 69.2708 | FALSE | FALSE | -0.14409 | -0.20845 | -2.2328 | -3.1227 | -0.2826 |  |  | none | FALSE | 0 | 69.1267 | FALSE | FALSE | 0.1172 |  | 70.3152 | 0 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.59423 | Normal | 71.5036 | -1.7575 | Night | 202602 | 2026-02-08 | 1.7575
2026-02-08 01:28 | 69.2708 | FALSE | FALSE | -0.24527 | -0.35534 | -2.1364 | -2.9918 | 0 |  |  | none | FALSE | 0 | 69.0255 | FALSE | FALSE | 0.1059 |  | 70.2163 | 0 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.59541 | Normal | 71.4072 | -1.5881 | Night | 202602 | 2026-02-08 | 1.5881
2026-02-08 01:43 | 68.9882 | FALSE | FALSE | -0.092346 | -0.13404 | -2.3227 | -3.2572 | -0.2826 |  |  | none | FALSE | 0 | 68.8959 | FALSE | FALSE | 0.1231 |  | 70.1034 | 0 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.60377 | Normal | 71.3109 | -1.8471 | Night | 202602 | 2026-02-08 | 1.8471
2026-02-08 01:58 | 68.9882 | FALSE | FALSE | -0.21761 | -0.31643 | -2.2503 | -3.1589 | 0 |  |  | none | FALSE | 0 | 68.7706 | FALSE | FALSE | 0.1098 |  | 70.0046 | 0 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.61699 | Normal | 71.2385 | -1.6473 | Night | 202602 | 2026-02-08 | 1.6473
2026-02-08 02:13 | 68.7056 | FALSE | FALSE | -0.090764 | -0.13228 | -2.4628 | -3.4605 | -0.2826 |  |  | none | FALSE | 0 | 68.6148 | FALSE | FALSE | 0.1239 |  | 69.8916 | 0 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.63839 | Normal | 71.1684 | -1.8578 | Night | 202602 | 2026-02-08 | 1.8578
2026-02-08 02:27 | 68.7056 | FALSE | FALSE | -0.20373 | -0.29741 | -2.3499 | -3.3071 | 0 |  |  | none | FALSE | 0 | 68.5019 | FALSE | FALSE | 0.1121 |  | 69.7787 | 0 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.6384 | Normal | 71.0555 | -1.6809 | Night | 202602 | 2026-02-08 | 1.6809
2026-02-08 02:42 | 68.7056 | FALSE | FALSE | -0.31405 | -0.4592 | -2.2626 | -3.1881 | 0 |  |  | none | FALSE | 0 | 68.3915 | FALSE | FALSE | 0.1008 |  | 69.6799 | 0 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.64415 | Normal | 70.9682 | -1.5125 | Night | 202602 | 2026-02-08 | 1.5125
2026-02-08 02:57 | 68.7056 | FALSE | FALSE | -0.39225 | -0.57419 | -2.1431 | -3.0249 | 0 |  |  | none | FALSE | 0 | 68.3134 | FALSE | FALSE | 0.0921 |  | 69.581 | 0 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.63384 | Normal | 70.8487 | -1.3812 | Night | 202602 | 2026-02-08 | 1.3812
2026-02-08 03:12 | 68.423 | FALSE | FALSE | -0.24739 | -0.36288 | -2.3658 | -3.3421 | -0.2826 |  |  | none | FALSE | 0 | 68.1756 | FALSE | FALSE | 0.1081 |  | 69.4822 | 0 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.6533 | Normal | 70.7888 | -1.6213 | Night | 202602 | 2026-02-08 | 1.6213
2026-02-08 03:27 | 68.423 | FALSE | FALSE | -0.35307 | -0.51869 | -2.2739 | -3.2163 | 0 |  |  | none | FALSE | 0 | 68.0699 | FALSE | FALSE | 0.0975 |  | 69.3834 | 0 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.65673 | Normal | 70.6969 | -1.4624 | Night | 202602 | 2026-02-08 | 1.4624
2026-02-08 03:42 | 68.423 | FALSE | FALSE | -0.4272 | -0.62827 | -2.1503 | -3.047 | 0 |  |  | none | FALSE | 0 | 67.9958 | FALSE | FALSE | 0.0891 |  | 69.2846 | 0 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.64438 | Normal | 70.5733 | -1.337 | Night | 202602 | 2026-02-08 | 1.337
2026-02-08 03:57 | 68.1404 | FALSE | FALSE | -0.24203 | -0.35646 | -2.3045 | -3.2713 | -0.2826 |  |  | none | FALSE | 0 | 67.8984 | FALSE | FALSE | 0.108 |  | 69.1716 | 0 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.63662 | Normal | 70.4449 | -1.6198 | Night | 202602 | 2026-02-08 | 1.6198
2026-02-08 04:12 | 68.1404 | FALSE | FALSE | -0.33876 | -0.49963 | -2.2036 | -3.1326 | 0 |  |  | none | FALSE | 0 | 67.8016 | FALSE | FALSE | 0.0978 |  | 69.0728 | 0 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.63558 | Normal | 70.344 | -1.467 | Night | 202602 | 2026-02-08 | 1.467
2026-02-08 04:27 | 68.1404 | FALSE | FALSE | -0.40266 | -0.59444 | -2.0698 | -2.948 | 0 |  |  | none | FALSE | 0 | 67.7377 | FALSE | FALSE | 0.0899 |  | 68.974 | 0 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.61812 | Normal | 70.2102 | -1.3486 | Night | 202602 | 2026-02-08 | 1.3486
2026-02-08 04:42 | 68.1404 | FALSE | FALSE | -0.43079 | -0.63623 | -1.9003 | -2.7132 | 0 |  |  | none | FALSE | 0 | 67.7096 | FALSE | FALSE | 0.0841 |  | 68.8752 | 0 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.58278 | Normal | 70.0407 | -1.2608 | Night | 202602 | 2026-02-08 | 1.2608
2026-02-08 04:57 | 68.1404 | FALSE | FALSE | -0.46695 | -0.69001 | -1.7669 | -2.5275 | 0 |  |  | none | FALSE | 0 | 67.6734 | FALSE | FALSE | 0.0776 |  | 68.7904 | 0 | 0 | -0.08478 | 0.13287 | 0.63808 | 0.55847 | Normal | 69.9073 | -1.1639 | Night | 202602 | 2026-02-08 | 1.1639
2026-02-08 05:12 | 68.1404 | FALSE | FALSE | -0.47213 | -0.69771 | -1.6025 | -2.2978 | 0 |  |  | none | FALSE | 0 | 67.6683 | FALSE | FALSE | 0.0726 |  | 68.7056 | 0 | 0 | -0.08478 | 0.13287 | 0.63808 | 0.51866 | Normal | 69.7429 | -1.0897 | Night | 202602 | 2026-02-08 | 1.0897
2026-02-08 05:26 | 68.1404 | FALSE | FALSE | -0.49082 | -0.72554 | -1.4799 | -2.1257 | 0 |  |  | none | FALSE | 0 | 67.6496 | FALSE | FALSE | 0.0669 |  | 68.635 | 0 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.49269 | Normal | 69.6203 | -1.0038 | Night | 202602 | 2026-02-08 | 1.0038
2026-02-08 05:41 | 68.423 | TRUE | FALSE | -0.73304 | -1.0829 | -1.0439 | -1.5027 | 0.2826 |  |  | none | FALSE | 1 | 67.69 | FALSE | FALSE | 0.0519 |  | 68.5784 | 0 | 0.2826 | -0.05652 | 0.14784 | 2.2938 | 0.44424 | Normal | 69.4669 | -0.34988 | Night | 202602 | 2026-02-08 | 0.34988
2026-02-08 05:56 | 68.1404 | FALSE | FALSE | -0.41277 | -0.60946 | -1.1475 | -1.6562 | -0.2826 |  |  | none | FALSE | 1 | 67.7276 | FALSE | FALSE | 0.0914 |  | 68.5078 | 0 | -0.2826 | -0.07065 | 0.15546 | -1.3633 | 0.39008 | Normal | 69.2879 | -0.94182 | Night | 202602 | 2026-02-08 | 0.94182
2026-02-08 06:11 | 68.1404 | FALSE | FALSE | -0.39698 | -0.586 | -1.0187 | -1.473 | 0 |  |  | none | FALSE | 1 | 67.7434 | FALSE | FALSE | 0.0871 |  | 68.4513 | 0 | 0 | -0.05652 | 0.14784 | 0.3823 | 0.35392 | Normal | 69.1591 | -0.87834 | Night | 202602 | 2026-02-08 | 0.87834
2026-02-08 06:26 | 68.1404 | FALSE | FALSE | -0.35108 | -0.51789 | -0.85976 | -1.246 | 0 |  |  | none | FALSE | 1 | 67.7893 | FALSE | FALSE | 0.0846 |  | 68.3947 | 0 | 0 | -0.05652 | 0.14784 | 0.3823 | 0.30271 | Normal | 69.0002 | -0.84022 | Night | 202602 | 2026-02-08 | 0.84022
2026-02-08 06:41 | 68.1404 | FALSE | FALSE | -0.33434 | -0.49309 | -0.75824 | -1.1005 | 0 |  |  | none | FALSE | 1 | 67.8061 | FALSE | FALSE | 0.0803 |  | 68.3524 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.27315 | Normal | 68.8986 | -0.77596 | Night | 202602 | 2026-02-08 | 0.77596
2026-02-08 06:56 | 68.1404 | FALSE | FALSE | -0.29435 | -0.43384 | -0.63347 | -0.92109 | 0 |  |  | none | FALSE | 1 | 67.8461 | FALSE | FALSE | 0.0773 |  | 68.31 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.23195 | Normal | 68.7739 | -0.73101 | Night | 202602 | 2026-02-08 | 0.73101
2026-02-08 07:11 | 68.1404 | FALSE | FALSE | -0.28875 | -0.42556 | -0.57135 | -0.83152 | 0 |  |  | none | FALSE | 1 | 67.8516 | FALSE | FALSE | 0.0724 |  | 68.2817 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21503 | Normal | 68.7118 | -0.65713 | Day | 202602 | 2026-02-08 | 0.65713
2026-02-08 07:26 | 68.1404 | FALSE | FALSE | -0.27161 | -0.4002 | -0.49769 | -0.72509 | 0 |  |  | none | FALSE | 1 | 67.8688 | FALSE | FALSE | 0.0678 |  | 68.2534 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.19233 | Normal | 68.6381 | -0.58775 | Day | 202602 | 2026-02-08 | 0.58775
2026-02-08 07:41 | 68.1404 | FALSE | FALSE | -0.23809 | -0.35063 | -0.40765 | -0.59469 | 0 |  |  | none | FALSE | 1 | 67.9023 | FALSE | FALSE | 0.0636 |  | 68.2252 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.16143 | Normal | 68.548 | -0.52517 | Day | 202602 | 2026-02-08 | 0.52517
2026-02-08 07:56 | 68.1404 | FALSE | FALSE | -0.17543 | -0.25812 | -0.28847 | -0.42157 | 0 |  |  | none | FALSE | 1 | 67.965 | FALSE | FALSE | 0.0611 |  | 68.1969 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.11598 | Normal | 68.4289 | -0.48734 | Day | 202602 | 2026-02-08 | 0.48734
2026-02-08 08:11 | 68.423 | TRUE | FALSE | -0.45803 | -0.67393 | -0.0058732 | -0.0085829 | 0.2826 |  |  | none | FALSE | 1 | 67.965 | FALSE | FALSE | 0.1585 |  | 68.1969 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.11598 | Normal | 68.4289 | 1.9494 | Day | 202602 | 2026-02-08 | 1.9494
2026-02-08 08:25 | 68.423 | FALSE | FALSE | -0.45803 | -0.67393 | -0.0058732 | -0.0085829 | 0 |  |  | none | FALSE | 1 | 67.965 | FALSE | FALSE | 0.1585 |  | 68.1969 | 0 | 0 | 0 | 0.12967 | 0 | 0.11598 | Normal | 68.4289 | 1.9494 | Day | 202602 | 2026-02-08 | 1.9494
2026-02-08 08:30 | 68.7056 | FALSE | FALSE | -0.80548 | -1.1863 | 0.18362 | 0.26798 | 0.2826 | 2026-02-08 14:14 | 2026-02-08 08:30 | upper | TRUE | 1 | 67.9001 | FALSE | FALSE | 0.2978 | 3.1811 | 68.2111 | 1 | 0.2826 | 0.01413 | 0.14424 | 1.8612 | 0.15546 | Extreme triggered | 68.522 | 3.1811 | Day | 202602 | 2026-02-08 | 3.1811
2026-02-08 08:46 | 68.7056 | FALSE | FALSE | -0.84544 | -1.2459 | 0.087142 | 0.127 | 0 |  | 2026-02-08 08:30 | upper | TRUE | 1 | 67.8602 | FALSE | FALSE | 0.3068 | 2.8204 | 68.2393 | 2 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.18957 | Extreme/elevated | 68.6185 | 2.4597 | Day | 202602 | 2026-02-08 | 2.4597
2026-02-08 09:01 | 68.9882 | FALSE | FALSE | -1.2087 | -1.7833 | 0.20431 | 0.29703 | 0.2826 |  | 2026-02-08 08:30 | upper | TRUE | 1 | 67.7795 | FALSE | TRUE | 0.3876 | 2.8182 | 68.2817 | 3 | 0.2826 | 0.04239 | 0.13829 | 1.737 | 0.2511 | Persistent | 68.7839 | 2.8137 | Day | 202602 | 2026-02-08 | 2.8137
2026-02-08 09:16 | 68.9882 | FALSE | FALSE | -1.2519 | -1.8482 | 0.076308 | 0.11073 | 0 |  | 2026-02-08 08:30 | upper | TRUE | 1 | 67.7363 | FALSE | TRUE | 0.4078 | 2.6785 | 68.3241 | 4 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.2939 | Persistent | 68.9119 | 2.2596 | Day | 202602 | 2026-02-08 | 2.2596
2026-02-08 09:30 | 69.2708 | FALSE | FALSE | -1.6069 | -2.3748 | 0.1735 | 0.2511 | 0.2826 |  | 2026-02-08 08:30 | upper | TRUE | 1 | 67.6639 | FALSE | TRUE | 0.4799 | 2.6397 | 68.3806 | 5 | 0.2826 | 0.05652 | 0.14784 | 1.5292 | 0.35834 | Persistent | 69.0973 | 2.4842 | Day | 202602 | 2026-02-08 | 2.4842
2026-02-08 09:30 | 69.2708 | FALSE | FALSE | -1.6429 | -2.4293 | 0.024427 | 0.035275 | 0 |  | 2026-02-08 08:30 | upper | TRUE | 1 | 67.6279 | FALSE | TRUE | 0.5088 | 2.5431 | 68.4371 | 6 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.40462 | Persistent | 69.2464 | 2.0604 | Day | 202602 | 2026-02-08 | 2.0604
2026-02-08 09:45 | 69.2708 | FALSE | TRUE | -1.6542 | -2.4464 | -0.099893 | -0.144 | 0 |  | 2026-02-08 08:30 | none | FALSE | 1 | 67.6166 | FALSE | FALSE | 0.5467 | 2.433 | 68.4937 | 7 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.43852 | Confirmed/Materialized Shift | 69.3707 | 1.7722 | Day | 202602 | 2026-02-08 | 1.7722
2026-02-08 10:00 | 69.5534 | FALSE | TRUE | -1.9681 | -2.912 | 0.010145 | 0.014588 | 0.2826 |  | 2026-02-08 08:30 | upper | TRUE | 1 | 67.5853 | FALSE | TRUE | 0.5633 | 2.3814 | 68.5643 | 8 | 0.2826 | 0.07065 | 0.15546 | 1.3633 | 0.48948 | Confirmed/Materialized Shift | 69.5433 | 2.0207 | Day | 202602 | 2026-02-08 | 2.0207
2026-02-08 10:15 | 70.1168 | TRUE | TRUE | -2.6642 | -3.9498 | 0.27141 | 0.38859 | 0.5634 |  | 2026-02-08 08:30 | upper | TRUE | 1 | 67.4526 | FALSE | TRUE | 0.5922 | 2.3895 | 68.649 | 9 | 0.5634 | 0.08469 | 0.18541 | 2.5819 | 0.5982 | Confirmed/Materialized Shift | 69.8454 | 2.4537 | Day | 202602 | 2026-02-08 | 2.4537
2026-02-08 10:30 | 70.3994 | FALSE | TRUE | -3.0404 | -4.5137 | 0.23452 | 0.33424 | 0.2826 |  | 2026-02-08 08:30 | upper | TRUE | 1 | 67.359 | FALSE | TRUE | 0.5842 | 2.384 | 68.7619 | 10 | 0.2826 | 0.11295 | 0.16881 | 1.005 | 0.70147 | Confirmed/Materialized Shift | 70.1649 | 2.3343 | Day | 202602 | 2026-02-08 | 2.3343
2026-02-08 10:45 | 70.3994 | FALSE | TRUE | -3.073 | -4.5643 | -0.023932 | -0.033983 | 0 |  | 2026-02-08 08:30 | none | FALSE | 1 | 67.3264 | FALSE | FALSE | 0.5598 | 2.3462 | 68.8749 | 11 | 0 | 0.11295 | 0.16881 | -0.66909 | 0.77422 | Confirmed/Materialized Shift | 70.4233 | 1.9691 | Day | 202602 | 2026-02-08 | 1.9691
2026-02-08 11:00 | 70.9646 | TRUE | TRUE | -3.7147 | -5.5237 | 0.18229 | 0.25754 | 0.5652 |  | 2026-02-08 08:30 | upper | TRUE | 2 | 67.2499 | TRUE | TRUE | 0.6042 | 2.3346 | 69.0161 | 12 | 0.5652 | 0.14121 | 0.19429 | 2.1822 | 0.8831 | Confirmed/Materialized Shift | 70.7823 | 2.2064 | Day | 202602 | 2026-02-08 | 2.2064
2026-02-08 11:15 | 71.2472 | FALSE | TRUE | -4.0517 | -6.0297 | 0.099805 | 0.14028 | 0.2826 |  | 2026-02-08 08:30 | upper | TRUE | 2 | 67.1955 | FALSE | TRUE | 0.5972 | 2.3166 | 69.1714 | 13 | 0.2826 | 0.15534 | 0.19376 | 0.6568 | 0.98798 | Confirmed/Materialized Shift | 71.1474 | 2.101 | Day | 202602 | 2026-02-08 | 2.101
2026-02-08 11:29 | 71.8124 | FALSE | TRUE | -4.695 | -6.9952 | 0.21972 | 0.30691 | 0.5652 |  | 2026-02-08 08:30 | upper | TRUE | 2 | 67.1174 | FALSE | TRUE | 0.6036 | 2.308 | 69.355 | 14 | 0.5652 | 0.1836 | 0.21041 | 1.8136 | 1.1188 | Confirmed/Materialized Shift | 71.5927 | 2.1964 | Day | 202602 | 2026-02-08 | 2.1964
2026-02-08 11:44 | 71.8124 | FALSE | TRUE | -4.6874 | -6.9831 | -0.1399 | -0.19444 | 0 |  | 2026-02-08 08:30 | none | FALSE | 2 | 67.125 | FALSE | FALSE | 0.5827 | 2.2798 | 69.5386 | 15 | 0 | 0.1836 | 0.21041 | -0.87258 | 1.2068 | Confirmed/Materialized Shift | 71.9523 | 1.8841 | Day | 202602 | 2026-02-08 | 1.8841
2026-02-08 11:59 | 72.095 | FALSE | TRUE | -4.9326 | -7.3443 | -0.21534 | -0.29781 | 0.2826 |  | 2026-02-08 08:30 | none | FALSE | 2 | 67.1624 | FALSE | FALSE | 0.5793 | 2.2518 | 69.7364 | 16 | 0.2826 | 0.19773 | 0.20689 | 0.41021 | 1.287 | Confirmed/Materialized Shift | 72.3103 | 1.8327 | Day | 202602 | 2026-02-08 | 1.8327
2026-02-08 12:14 | 72.3758 | FALSE | TRUE | -5.1419 | -7.6477 | -0.28655 | -0.39436 | 0.2808 |  | 2026-02-08 08:30 | none | FALSE | 2 | 67.2339 | FALSE | FALSE | 0.5764 | 2.2246 | 69.9481 | 17 | 0.2808 | 0.21177 | 0.20224 | 0.34132 | 1.3571 | Confirmed/Materialized Shift | 72.6623 | 1.7889 | Day | 202602 | 2026-02-08 | 1.7889
2026-02-08 12:29 | 72.6584 | FALSE | TRUE | -5.3146 | -7.8918 | -0.34592 | -0.47384 | 0.2826 |  | 2026-02-08 08:30 | none | FALSE | 2 | 67.3438 | FALSE | FALSE | 0.5742 | 2.1985 | 70.174 | 18 | 0.2826 | 0.2259 | 0.19646 | 0.28861 | 1.4151 | Confirmed/Materialized Shift | 73.0043 | 1.7556 | Day | 202602 | 2026-02-08 | 1.7556
2026-02-08 12:44 | 72.941 | FALSE | TRUE | -5.5011 | -8.1571 | -0.419 | -0.57115 | 0.2826 |  | 2026-02-08 08:30 | none | FALSE | 1 | 67.4399 | FALSE | FALSE | 0.543 | 2.1732 | 70.3999 | 19 | 0.2826 | 0.2259 | 0.19646 | 0.28861 | 1.48 | Confirmed/Materialized Shift | 73.36 | 1.7169 | Day | 202602 | 2026-02-08 | 1.7169
2026-02-08 12:59 | 72.941 | FALSE | TRUE | -5.3291 | -7.8818 | -0.69875 | -0.94887 | 0 |  | 2026-02-08 08:30 | none | FALSE | 1 | 67.6119 | FALSE | FALSE | 0.531 | 2.1413 | 70.6258 | 20 | 0 | 0.2259 | 0.19646 | -1.1499 | 1.507 | Confirmed/Materialized Shift | 73.6397 | 1.5363 | Day | 202602 | 2026-02-08 | 1.5363
2026-02-08 13:14 | 73.2236 | FALSE | TRUE | -5.4562 | -8.0514 | -0.71249 | -0.96365 | 0.2826 |  | 2026-02-08 08:30 | none | FALSE | 1 | 67.7674 | FALSE | FALSE | 0.5311 | 2.1126 | 70.8517 | 21 | 0.2826 | 0.2259 | 0.19646 | 0.28861 | 1.5422 | Confirmed/Materialized Shift | 73.9361 | 1.538 | Day | 202602 | 2026-02-08 | 1.538
2026-02-08 13:29 | 73.2236 | FALSE | TRUE | -5.2303 | -7.6923 | -0.93836 | -1.2653 | 0 |  | 2026-02-08 08:30 | none | FALSE | 0 | 67.9933 | FALSE | FALSE | 0.4928 | 2.0798 | 71.0776 | 22 | 0 | 0.2259 | 0.19646 | -1.1499 | 1.5422 | Confirmed/Materialized Shift | 74.162 | 1.3915 | Day | 202602 | 2026-02-08 | 1.3915
2026-02-08 13:44 | 73.2236 | FALSE | TRUE | -4.996 | -7.3225 | -1.1276 | -1.5166 | 0 |  | 2026-02-08 08:30 | none | FALSE | 0 | 68.2276 | FALSE | FALSE | 0.4842 | 2.0443 | 71.2894 | 23 | 0 | 0.21177 | 0.20224 | -1.0471 | 1.5309 | Confirmed/Materialized Shift | 74.3512 | 1.2634 | Day | 202602 | 2026-02-08 | 1.2634
2026-02-08 13:59 | 73.2236 | FALSE | TRUE | -4.6987 | -6.857 | -1.2539 | -1.6836 | 0 |  | 2026-02-08 08:30 | none | FALSE | 0 | 68.5249 | FALSE | FALSE | 0.4772 | 2.0074 | 71.5012 | 24 | 0 | 0.21177 | 0.20224 | -1.0471 | 1.4882 | Confirmed/Materialized Shift | 74.4775 | 1.1574 | Day | 202602 | 2026-02-08 | 1.1574
2026-02-08 14:14 | 72.941 | TRUE | FALSE | -4.1034 | -5.961 | -1.5908 | -2.1344 | -0.2826 |  |  | none | FALSE | 1 | 68.8376 | FALSE | FALSE | 0.0874 |  | 71.6847 | 0 | -0.2826 | 0.18351 | 0.22948 | -2.0312 | 1.4235 | Persistence ends | 74.5318 | 0.88252 | Day | 202602 | 2026-02-08 | 0.88252
2026-02-08 14:28 | 72.6584 | FALSE | FALSE | -3.4421 | -4.973 | -1.8335 | -2.4613 | -0.2826 |  |  | none | FALSE | 1 | 69.2163 | FALSE | FALSE | 0.0692 |  | 71.8541 | 0 | -0.2826 | 0.16938 | 0.24922 | -1.8135 | 1.3189 | Normal | 74.4919 | 0.60985 | Day | 202602 | 2026-02-08 | 0.60985
2026-02-08 14:43 | 72.3758 | FALSE | FALSE | -2.7136 | -3.8953 | -1.9806 | -2.6637 | -0.2826 |  |  | none | FALSE | 1 | 69.6622 | FALSE | FALSE | 0.0494 |  | 72.0093 | 0 | -0.2826 | 0.15525 | 0.26673 | -1.6416 | 1.1736 | Normal | 74.3564 | 0.31228 | Day | 202602 | 2026-02-08 | 0.31228
2026-02-08 14:58 | 72.3758 | FALSE | FALSE | -2.2707 | -3.239 | -1.82 | -2.453 | 0 |  |  | none | FALSE | 1 | 70.1051 | FALSE | FALSE | 0.0433 |  | 72.1504 | 0 | 0 | 0.14112 | 0.26711 | -0.52832 | 1.0227 | Normal | 74.1958 | 0.22036 | Day | 202602 | 2026-02-08 | 0.22036
2026-02-08 15:14 | 72.3758 | FALSE | FALSE | -1.9207 | -2.7261 | -1.6959 | -2.2895 | 0 |  |  | none | FALSE | 1 | 70.4551 | FALSE | FALSE | 0.0369 |  | 72.2634 | 0 | 0 | 0.11295 | 0.24935 | -0.45297 | 0.90413 | Normal | 74.0717 | 0.12433 | Day | 202602 | 2026-02-08 | 0.12433
2026-02-08 15:28 | 72.3758 | FALSE | FALSE | -1.5947 | -2.253 | -1.5675 | -2.1199 | 0 |  |  | none | FALSE | 1 | 70.7811 | FALSE | FALSE | 0.0297 |  | 72.3622 | 0 | 0 | 0.09882 | 0.24723 | -0.39971 | 0.79055 | Normal | 73.9433 | 0.01719 | Day | 202602 | 2026-02-08 | 0.01719
2026-02-08 15:43 | 72.6584 | FALSE | FALSE | -1.4692 | -2.0637 | -1.1027 | -1.4949 | 0.2826 |  |  | none | FALSE | 1 | 71.1892 | FALSE | FALSE | 0.0476 |  | 72.4752 | 0 | 0.2826 | 0.11295 | 0.24935 | 0.68036 | 0.64296 | Normal | 73.7611 | 0.285 | Day | 202602 | 2026-02-08 | 0.285
2026-02-08 15:58 | 72.3758 | FALSE | FALSE | -0.90447 | -1.2655 | -1.2443 | -1.6902 | -0.2826 |  |  | none | FALSE | 1 | 71.4713 | FALSE | FALSE | 0.0497 |  | 72.5457 | 0 | -0.2826 | 0.07056 | 0.24032 | -1.4695 | 0.53719 | Normal | 73.6201 | -0.31631 | Day | 202602 | 2026-02-08 | 0.31631
2026-02-08 16:13 | 72.3758 | FALSE | FALSE | -0.66359 | -0.92536 | -1.1163 | -1.5189 | 0 |  |  | none | FALSE | 1 | 71.7122 | FALSE | FALSE | 0.0625 |  | 72.6021 | 0 | 0 | 0.05643 | 0.23546 | -0.23966 | 0.44497 | Normal | 73.4921 | -0.50868 | Day | 202602 | 2026-02-08 | 0.50868
2026-02-08 16:28 | 72.3758 | FALSE | FALSE | -0.56288 | -0.78381 | -1.0719 | -1.4594 | 0 |  |  | none | FALSE | 1 | 71.8129 | FALSE | FALSE | 0.0701 |  | 72.6303 | 0 | 0 | 0.02817 | 0.20284 | -0.13888 | 0.4087 | Normal | 73.4477 | -0.62276 | Day | 202602 | 2026-02-08 | 0.62276
2026-02-08 16:43 | 72.941 | TRUE | FALSE | -0.98515 | -1.3691 | -0.47665 | -0.64923 | 0.5652 |  |  | none | FALSE | 1 | 71.9559 | FALSE | FALSE | 0.075 |  | 72.6868 | 0 | 0.5652 | 0.05643 | 0.23546 | 2.1608 | 0.36545 | Normal | 73.4176 | 0.69572 | Day | 202602 | 2026-02-08 | 0.69572
2026-02-08 16:58 | 73.2236 | FALSE | FALSE | -1.193 | -1.6562 | -0.23215 | -0.31604 | 0.2826 |  |  | none | FALSE | 1 | 72.0306 | FALSE | FALSE | 0.1185 |  | 72.7432 | 0 | 0.2826 | 0.05643 | 0.23546 | 0.96055 | 0.35629 | Normal | 73.4558 | 1.3484 | Day | 202602 | 2026-02-08 | 1.3484
2026-02-08 17:13 | 73.2236 | FALSE | FALSE | -1.1594 | -1.6088 | -0.28334 | -0.38545 | 0 |  |  | none | FALSE | 1 | 72.0642 | FALSE | FALSE | 0.1095 |  | 72.7856 | 0 | 0 | 0.04239 | 0.22968 | -0.18456 | 0.36068 | Normal | 73.5069 | 1.2144 | Day | 202602 | 2026-02-08 | 1.2144
2026-02-08 17:27 | 73.2236 | FALSE | FALSE | -1.1541 | -1.6013 | -0.33454 | -0.45479 | 0 |  |  | none | FALSE | 1 | 72.0695 | FALSE | FALSE | 0.102 |  | 72.8138 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.37215 | Normal | 73.5581 | 1.1011 | Day | 202602 | 2026-02-08 | 1.1011
2026-02-08 17:30 | 73.2236 | FALSE | FALSE | -1.1606 | -1.6105 | -0.36928 | -0.50179 | 0 |  |  | none | FALSE | 1 | 72.063 | FALSE | FALSE | 0.0975 |  | 72.828 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.38246 | Normal | 73.5929 | 1.0345 | Day | 202602 | 2026-02-08 | 1.0345
2026-02-08 17:31 | 73.5062 | FALSE | FALSE | -1.4721 | -2.0436 | -0.17215 | -0.23365 | 0.2826 |  |  | none | FALSE | 1 | 72.0341 | FALSE | FALSE | 0.134 |  | 72.8562 | 0 | 0.2826 | 0.02826 | 0.22271 | 1.142 | 0.41106 | Normal | 73.6783 | 1.5812 | Day | 202602 | 2026-02-08 | 1.5812
2026-02-08 17:46 | 73.5062 | FALSE | FALSE | -1.4935 | -2.074 | -0.22181 | -0.30085 | 0 |  |  | none | FALSE | 1 | 72.0127 | FALSE | FALSE | 0.1274 |  | 72.8704 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.42883 | Normal | 73.728 | 1.4828 | Day | 202602 | 2026-02-08 | 1.4828
2026-02-08 18:01 | 73.5062 | FALSE | FALSE | -1.5126 | -2.101 | -0.26911 | -0.36477 | 0 |  |  | none | FALSE | 1 | 71.9936 | FALSE | FALSE | 0.1216 |  | 72.8845 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.44542 | Normal | 73.7753 | 1.3958 | Day | 202602 | 2026-02-08 | 1.3958
2026-02-08 18:16 | 73.2236 | FALSE | FALSE | -1.23 | -1.7084 | -0.55171 | -0.74783 | -0.2826 |  |  | none | FALSE | 1 | 71.9936 | FALSE | FALSE | 0.0793 |  | 72.8845 | 0 | -0.2826 | 0 | 0.22459 | -1.2583 | 0.44542 | Normal | 73.7753 | 0.76135 | Night | 202602 | 2026-02-08 | 0.76135
2026-02-08 18:30 | 73.2236 | FALSE | FALSE | -1.23 | -1.7084 | -0.55171 | -0.74783 | 0 |  |  | none | FALSE | 1 | 71.9936 | FALSE | FALSE | 0.0793 |  | 72.8845 | 0 | 0 | 0 | 0.22459 | 0 | 0.44542 | Normal | 73.7753 | 0.76135 | Night | 202602 | 2026-02-08 | 0.76135
2026-02-08 18:45 | 73.2236 | FALSE | FALSE | -1.2285 | -1.7063 | -0.57849 | -0.78384 | 0 |  |  | none | FALSE | 0 | 71.9951 | FALSE | FALSE | 0.048 |  | 72.8986 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.45174 | Normal | 73.8021 | 0.71942 | Night | 202602 | 2026-02-08 | 0.71942
2026-02-08 19:00 | 72.941 | FALSE | FALSE | -0.92474 | -1.2841 | -0.86822 | -1.1763 | -0.2826 |  |  | none | FALSE | 0 | 72.0163 | FALSE | FALSE | 0.0042 |  | 72.9127 | 0 | -0.2826 | 0.01413 | 0.21454 | -1.3831 | 0.44824 | Normal | 73.8092 | 0.063047 | Night | 202602 | 2026-02-08 | 0.063047
2026-02-08 19:15 | 72.941 | FALSE | FALSE | -0.86011 | -1.1933 | -0.86011 | -1.1654 | 0 |  |  | none | FALSE | 0 | 72.0809 | FALSE | FALSE | 0 |  | 72.941 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.43005 | Normal | 73.8011 | 0 | Night | 202602 | 2026-02-08 | 0
2026-02-08 19:29 | 72.6584 | FALSE | FALSE | -0.53303 | -0.73903 | -1.1265 | -1.5267 | -0.2826 |  |  | none | FALSE | 0 | 72.1254 | FALSE | FALSE | 0.0477 |  | 72.9551 | 0 | -0.2826 | 0.01413 | 0.21454 | -1.3831 | 0.41488 | Normal | 73.7849 | -0.71522 | Night | 202602 | 2026-02-08 | 0.71522
2026-02-08 19:44 | 72.3758 | FALSE | FALSE | -0.25043 | -0.34721 | -1.4091 | -1.9097 | -0.2826 |  |  | none | FALSE | 0 | 72.1254 | FALSE | FALSE | 0.0931 |  | 72.9551 | 0 | -0.2826 | 0 | 0.22459 | -1.2583 | 0.41488 | Normal | 73.7849 | -1.3964 | Night | 202602 | 2026-02-08 | 1.3964
2026-02-08 19:59 | 72.3758 | FALSE | FALSE | -0.25043 | -0.34721 | -1.4091 | -1.9097 | 0 |  |  | none | FALSE | 0 | 72.1254 | FALSE | FALSE | 0.0931 |  | 72.9551 | 0 | 0 | 0 | 0.22459 | 0 | 0.41488 | Normal | 73.7849 | -1.3964 | Night | 202602 | 2026-02-08 | 1.3964
2026-02-08 20:15 | 72.095 | FALSE | FALSE | -0.074889 | -0.10398 | -1.7388 | -2.355 | -0.2808 |  |  | none | FALSE | 0 | 72.0201 | FALSE | FALSE | 0.1223 |  | 72.927 | 0 | -0.2808 | -0.02817 | 0.2226 | -1.1349 | 0.45342 | Normal | 73.8338 | -1.8348 | Night | 202602 | 2026-02-08 | 1.8348
2026-02-08 20:29 | 72.095 | FALSE | FALSE | -0.13251 | -0.18413 | -1.7683 | -2.3941 | 0 |  |  | none | FALSE | 0 | 71.9625 | FALSE | FALSE | 0.1147 |  | 72.9129 | 0 | 0 | -0.01404 | 0.21442 | 0.065479 | 0.47521 | Normal | 73.8633 | -1.7212 | Night | 202602 | 2026-02-08 | 1.7212
2026-02-08 20:44 | 71.8124 | FALSE | FALSE | 0.026305 | 0.036617 | -2.1184 | -2.8654 | -0.2826 | 2026-02-09 08:00 | 2026-02-08 20:44 | lower | TRUE | 0 | 71.8387 | FALSE | FALSE | 0.1938 | 2.0503 | 72.8847 | 1 | -0.2826 | -0.02817 | 0.2226 | -1.143 | 0.52302 | Extreme triggered | 73.9308 | -2.0503 | Night | 202602 | 2026-02-08 | 2.0503
2026-02-08 20:59 | 71.8124 | FALSE | FALSE | -0.086496 | -0.12059 | -2.1749 | -2.9395 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 71.7259 | FALSE | FALSE | 0.2374 | 1.9486 | 72.8566 | 2 | 0 | -0.02817 | 0.2226 | 0.12655 | 0.56534 | Extreme/elevated | 73.9873 | -1.847 | Night | 202602 | 2026-02-08 | 1.847
2026-02-08 21:14 | 71.5298 | FALSE | FALSE | -0.019148 | -0.026776 | -2.5316 | -3.4182 | -0.2826 |  | 2026-02-08 20:44 | none | FALSE | 0 | 71.5107 | FALSE | FALSE | 0.3028 | 1.9558 | 72.786 | 3 | -0.2826 | -0.07056 | 0.18038 | -1.1755 | 0.63768 | Persistent | 74.0614 | -1.97 | Night | 202602 | 2026-02-08 | 1.97
2026-02-08 21:29 | 71.5298 | FALSE | FALSE | -0.20262 | -0.28407 | -2.5457 | -3.4366 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 71.3272 | FALSE | FALSE | 0.3422 | 1.8931 | 72.7013 | 4 | 0 | -0.08469 | 0.16132 | 0.52499 | 0.68707 | Persistent | 74.0755 | -1.7051 | Night | 202602 | 2026-02-08 | 1.7051
2026-02-08 21:44 | 71.5298 | FALSE | FALSE | -0.35871 | -0.504 | -2.5324 | -3.4193 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 71.1711 | FALSE | FALSE | 0.386 | 1.8152 | 72.6166 | 5 | 0 | -0.08469 | 0.16132 | 0.52499 | 0.72277 | Persistent | 74.0622 | -1.5037 | Night | 202602 | 2026-02-08 | 1.5037
2026-02-08 21:59 | 71.2472 | FALSE | FALSE | -0.26748 | -0.37683 | -2.8087 | -3.7927 | -0.2826 |  | 2026-02-08 20:44 | none | FALSE | 0 | 70.9797 | FALSE | FALSE | 0.453 | 1.788 | 72.5178 | 6 | -0.2826 | -0.09882 | 0.16582 | -1.1083 | 0.76905 | Persistent | 74.0559 | -1.6522 | Night | 202602 | 2026-02-08 | 1.6522
2026-02-08 22:14 | 71.2472 | FALSE | TRUE | -0.42809 | -0.60448 | -2.7717 | -3.7446 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 70.8191 | FALSE | FALSE | 0.4977 | 1.7419 | 72.419 | 7 | 0 | -0.09882 | 0.16582 | 0.59594 | 0.79994 | Confirmed/Materialized Shift | 74.0189 | -1.4649 | Night | 202602 | 2026-02-08 | 1.4649
2026-02-08 22:28 | 70.9646 | FALSE | TRUE | -0.31223 | -0.44192 | -2.9669 | -4.013 | -0.2826 |  | 2026-02-08 20:44 | none | FALSE | 0 | 70.6524 | FALSE | FALSE | 0.5079 | 1.7265 | 72.2919 | 8 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.81978 | Confirmed/Materialized Shift | 73.9315 | -1.6191 | Night | 202602 | 2026-02-08 | 1.6191
2026-02-08 22:43 | 70.9646 | FALSE | TRUE | -0.43702 | -0.61964 | -2.8375 | -3.8447 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 70.5276 | FALSE | FALSE | 0.4977 | 1.6976 | 72.1648 | 9 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.81863 | Confirmed/Materialized Shift | 73.8021 | -1.4662 | Night | 202602 | 2026-02-08 | 1.4662
2026-02-08 22:59 | 70.682 | FALSE | TRUE | -0.29568 | -0.42008 | -2.9789 | -4.0441 | -0.2826 |  | 2026-02-08 20:44 | none | FALSE | 0 | 70.3863 | FALSE | FALSE | 0.5093 | 1.6917 | 72.0236 | 10 | -0.2826 | -0.14121 | 0.14488 | -0.97592 | 0.81865 | Confirmed/Materialized Shift | 73.6609 | -1.6388 | Night | 202602 | 2026-02-08 | 1.6388
2026-02-08 23:14 | 70.682 | FALSE | TRUE | -0.42514 | -0.60512 | -2.8542 | -3.8814 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 70.2569 | FALSE | FALSE | 0.4988 | 1.6726 | 71.8966 | 11 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.81984 | Confirmed/Materialized Shift | 73.5362 | -1.4814 | Night | 202602 | 2026-02-08 | 1.4814
2026-02-08 23:28 | 70.3994 | FALSE | TRUE | -0.28898 | -0.41217 | -3.0009 | -4.0883 | -0.2826 |  | 2026-02-08 20:44 | none | FALSE | 0 | 70.1104 | FALSE | FALSE | 0.5099 | 1.6706 | 71.7553 | 12 | -0.2826 | -0.14121 | 0.14488 | -0.97592 | 0.82246 | Confirmed/Materialized Shift | 73.4003 | -1.6486 | Night | 202602 | 2026-02-08 | 1.6486
2026-02-08 23:43 | 70.3994 | FALSE | TRUE | -0.38371 | -0.54803 | -2.8132 | -3.8425 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 70.0157 | FALSE | FALSE | 0.5013 | 1.659 | 71.6141 | 13 | 0 | -0.14121 | 0.14488 | 0.97468 | 0.79922 | Confirmed/Materialized Shift | 73.2126 | -1.5199 | Night | 202602 | 2026-02-08 | 1.5199
2026-02-08 23:58 | 70.1168 | FALSE | TRUE | -0.24775 | -0.35459 | -2.96 | -4.0505 | -0.2826 |  | 2026-02-08 20:44 | none | FALSE | 0 | 69.869 | FALSE | FALSE | 0.5127 | 1.6613 | 71.4729 | 14 | -0.2826 | -0.14121 | 0.14488 | -0.97592 | 0.80194 | Confirmed/Materialized Shift | 73.0768 | -1.6911 | Night | 202602 | 2026-02-08 | 1.6911
2026-02-09 00:13 | 70.1168 | FALSE | TRUE | -0.34133 | -0.48918 | -2.7711 | -3.8019 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 69.7755 | FALSE | FALSE | 0.5041 | 1.6546 | 71.3317 | 15 | 0 | -0.14121 | 0.14488 | 0.97468 | 0.77812 | Confirmed/Materialized Shift | 72.8879 | -1.5613 | Night | 202602 | 2026-02-09 | 1.5613
2026-02-09 00:28 | 70.1168 | FALSE | TRUE | -0.42679 | -0.61241 | -2.6024 | -3.5788 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 69.69 | FALSE | FALSE | 0.4958 | 1.641 | 71.2046 | 16 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.75731 | Confirmed/Materialized Shift | 72.7192 | -1.4364 | Night | 202602 | 2026-02-09 | 1.4364
2026-02-09 00:43 | 69.836 | FALSE | TRUE | -0.28537 | -0.4103 | -2.7686 | -3.8133 | -0.2808 |  | 2026-02-08 20:44 | none | FALSE | 0 | 69.5506 | FALSE | FALSE | 0.5084 | 1.6401 | 71.0776 | 17 | -0.2808 | -0.12699 | 0.14404 | -1.0678 | 0.7635 | Confirmed/Materialized Shift | 72.6046 | -1.6262 | Night | 202602 | 2026-02-09 | 1.6262
2026-02-09 00:58 | 69.836 | FALSE | TRUE | -0.37988 | -0.54694 | -2.6092 | -3.6016 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 69.4561 | FALSE | FALSE | 0.4994 | 1.6319 | 70.9506 | 18 | 0 | -0.12699 | 0.14404 | 0.88163 | 0.74727 | Confirmed/Materialized Shift | 72.4452 | -1.4916 | Night | 202602 | 2026-02-09 | 1.4916
2026-02-09 01:13 | 69.5534 | FALSE | TRUE | -0.24672 | -0.35598 | -2.7871 | -3.8527 | -0.2826 |  | 2026-02-08 20:44 | none | FALSE | 0 | 69.3067 | FALSE | FALSE | 0.5116 | 1.6341 | 70.8236 | 19 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.75844 | Confirmed/Materialized Shift | 72.3405 | -1.6747 | Night | 202602 | 2026-02-09 | 1.6747
2026-02-09 01:28 | 69.5534 | FALSE | TRUE | -0.35099 | -0.50719 | -2.6372 | -3.6531 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 69.2024 | FALSE | FALSE | 0.502 | 1.6289 | 70.6965 | 20 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.74704 | Confirmed/Materialized Shift | 72.1906 | -1.5302 | Night | 202602 | 2026-02-09 | 1.5302
2026-02-09 01:43 | 69.5534 | FALSE | TRUE | -0.45023 | -0.65153 | -2.5105 | -3.4837 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 69.1032 | FALSE | FALSE | 0.4928 | 1.6176 | 70.5835 | 21 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.74018 | Confirmed/Materialized Shift | 72.0639 | -1.3917 | Night | 202602 | 2026-02-09 | 1.3917
2026-02-09 01:58 | 69.2708 | FALSE | TRUE | -0.28688 | -0.41586 | -2.6582 | -3.6956 | -0.2826 |  | 2026-02-08 20:44 | none | FALSE | 0 | 68.9839 | FALSE | FALSE | 0.5074 | 1.6173 | 70.4565 | 22 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.73627 | Confirmed/Materialized Shift | 71.929 | -1.6104 | Night | 202602 | 2026-02-09 | 1.6104
2026-02-09 02:13 | 69.2708 | FALSE | TRUE | -0.39973 | -0.5804 | -2.5451 | -3.544 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 68.8711 | FALSE | FALSE | 0.4971 | 1.6103 | 70.3435 | 23 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.73622 | Confirmed/Materialized Shift | 71.8159 | -1.4571 | Night | 202602 | 2026-02-09 | 1.4571
2026-02-09 02:27 | 68.9882 | FALSE | TRUE | -0.25181 | -0.36634 | -2.7083 | -3.7774 | -0.2826 |  | 2026-02-08 20:44 | none | FALSE | 0 | 68.7364 | FALSE | FALSE | 0.5106 | 1.6124 | 70.2164 | 24 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.74002 | Confirmed/Materialized Shift | 71.6965 | -1.6597 | Night | 202602 | 2026-02-09 | 1.6597
2026-02-09 02:42 | 68.9882 | FALSE | TRUE | -0.34002 | -0.4953 | -2.5423 | -3.5542 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 68.6482 | FALSE | FALSE | 0.5019 | 1.609 | 70.0893 | 25 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.72058 | Confirmed/Materialized Shift | 71.5305 | -1.5281 | Night | 202602 | 2026-02-09 | 1.5281
2026-02-09 02:57 | 68.7056 | FALSE | TRUE | -0.20273 | -0.29594 | -2.7161 | -3.8029 | -0.2826 |  | 2026-02-08 20:44 | none | FALSE | 0 | 68.5029 | FALSE | FALSE | 0.5148 | 1.6134 | 69.9623 | 26 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.7297 | Confirmed/Materialized Shift | 71.4217 | -1.7222 | Night | 202602 | 2026-02-09 | 1.7222
2026-02-09 03:12 | 68.7056 | FALSE | TRUE | -0.30105 | -0.4401 | -2.5602 | -3.5925 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 68.4046 | FALSE | FALSE | 0.5053 | 1.6121 | 69.8352 | 27 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.71532 | Confirmed/Materialized Shift | 71.2658 | -1.5791 | Night | 202602 | 2026-02-09 | 1.5791
2026-02-09 03:27 | 68.7056 | FALSE | TRUE | -0.39513 | -0.57843 | -2.4284 | -3.4138 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 68.3105 | FALSE | FALSE | 0.496 | 1.606 | 69.7222 | 28 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.70588 | Confirmed/Materialized Shift | 71.134 | -1.4402 | Night | 202602 | 2026-02-09 | 1.4402
2026-02-09 03:42 | 68.7056 | FALSE | TRUE | -0.44983 | -0.65904 | -2.2572 | -3.1808 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 68.2558 | FALSE | FALSE | 0.489 | 1.5966 | 69.6093 | 29 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.67676 | Confirmed/Materialized Shift | 70.9628 | -1.3353 | Night | 202602 | 2026-02-09 | 1.3353
2026-02-09 03:57 | 68.7056 | FALSE | TRUE | -0.50684 | -0.74318 | -2.1166 | -2.9886 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 68.1988 | FALSE | FALSE | 0.4818 | 1.5843 | 69.5105 | 30 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.65585 | Confirmed/Materialized Shift | 70.8222 | -1.2272 | Night | 202602 | 2026-02-09 | 1.2272
2026-02-09 04:12 | 68.423 | FALSE | TRUE | -0.30097 | -0.44182 | -2.25 | -3.1837 | -0.2826 |  | 2026-02-08 20:44 | none | FALSE | 0 | 68.122 | FALSE | FALSE | 0.5019 | 1.5825 | 69.3975 | 31 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.63775 | Confirmed/Materialized Shift | 70.673 | -1.5281 | Night | 202602 | 2026-02-09 | 1.5281
2026-02-09 04:27 | 68.423 | FALSE | TRUE | -0.37904 | -0.55706 | -2.1304 | -3.0196 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 68.044 | FALSE | FALSE | 0.4931 | 1.5767 | 69.2987 | 32 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.62737 | Confirmed/Materialized Shift | 70.5534 | -1.3958 | Night | 202602 | 2026-02-09 | 1.3958
2026-02-09 04:42 | 68.1404 | FALSE | TRUE | -0.19886 | -0.29269 | -2.2896 | -3.2508 | -0.2826 |  | 2026-02-08 20:44 | none | FALSE | 0 | 67.9415 | FALSE | FALSE | 0.512 | 1.5798 | 69.1857 | 33 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.62211 | Confirmed/Materialized Shift | 70.43 | -1.6803 | Night | 202602 | 2026-02-09 | 1.6803
2026-02-09 04:57 | 68.1404 | FALSE | TRUE | -0.30027 | -0.44261 | -2.1933 | -3.1185 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 67.8401 | FALSE | FALSE | 0.5012 | 1.578 | 69.0869 | 34 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.6234 | Confirmed/Materialized Shift | 70.3337 | -1.5183 | Night | 202602 | 2026-02-09 | 1.5183
2026-02-09 05:12 | 68.1404 | FALSE | TRUE | -0.36831 | -0.54346 | -2.0637 | -2.9396 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 67.7721 | FALSE | FALSE | 0.4929 | 1.5728 | 68.9881 | 35 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.60801 | Confirmed/Materialized Shift | 70.2041 | -1.3942 | Night | 202602 | 2026-02-09 | 1.3942
2026-02-09 05:26 | 67.8596 | FALSE | TRUE | -0.17808 | -0.26311 | -2.2094 | -3.1531 | -0.2808 |  | 2026-02-08 20:44 | none | FALSE | 0 | 67.6815 | FALSE | FALSE | 0.5134 | 1.5763 | 68.8752 | 36 | -0.2808 | -0.11286 | 0.14182 | -1.1842 | 0.59686 | Confirmed/Materialized Shift | 70.069 | -1.7016 | Night | 202602 | 2026-02-09 | 1.7016
2026-02-09 05:41 | 67.8596 | FALSE | TRUE | -0.26922 | -0.39831 | -2.1029 | -3.0057 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 67.5904 | FALSE | FALSE | 0.5031 | 1.5755 | 68.7764 | 37 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.59303 | Confirmed/Materialized Shift | 69.9625 | -1.546 | Night | 202602 | 2026-02-09 | 1.546
2026-02-09 05:56 | 67.8596 | FALSE | TRUE | -0.32488 | -0.48106 | -1.9609 | -2.8085 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 67.5347 | FALSE | FALSE | 0.4954 | 1.5717 | 68.6776 | 38 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.57145 | Confirmed/Materialized Shift | 69.8205 | -1.4315 | Night | 202602 | 2026-02-09 | 1.4315
2026-02-09 06:11 | 67.8596 | FALSE | TRUE | -0.38713 | -0.57376 | -1.8538 | -2.6591 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 67.4725 | FALSE | FALSE | 0.4873 | 1.565 | 68.5929 | 39 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.56022 | Confirmed/Materialized Shift | 69.7134 | -1.309 | Night | 202602 | 2026-02-09 | 1.309
2026-02-09 06:26 | 67.8596 | FALSE | TRUE | -0.42104 | -0.62434 | -1.7183 | -2.4696 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 67.4386 | FALSE | FALSE | 0.4809 | 1.5562 | 68.5082 | 40 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.53484 | Confirmed/Materialized Shift | 69.5779 | -1.2128 | Night | 202602 | 2026-02-09 | 1.2128
2026-02-09 06:41 | 67.8596 | FALSE | TRUE | -0.42226 | -0.62616 | -1.5501 | -2.2333 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 67.4373 | FALSE | FALSE | 0.4762 | 1.5461 | 68.4235 | 41 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.4931 | Confirmed/Materialized Shift | 69.4097 | -1.1437 | Night | 202602 | 2026-02-09 | 1.1437
2026-02-09 06:56 | 67.8596 | FALSE | TRUE | -0.438 | -0.64964 | -1.4248 | -2.0564 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 67.4216 | FALSE | FALSE | 0.4706 | 1.5345 | 68.353 | 42 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.46569 | Confirmed/Materialized Shift | 69.2844 | -1.0595 | Night | 202602 | 2026-02-09 | 1.0595
2026-02-09 07:11 | 67.577 | FALSE | TRUE | -0.19566 | -0.29038 | -1.5782 | -2.2822 | -0.2826 |  | 2026-02-08 20:44 | none | FALSE | 0 | 67.3813 | FALSE | FALSE | 0.5039 | 1.5351 | 68.2683 | 43 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.44348 | Confirmed/Materialized Shift | 69.1552 | -1.5588 | Day | 202602 | 2026-02-09 | 1.5588
2026-02-09 07:26 | 67.577 | FALSE | TRUE | -0.24945 | -0.37051 | -1.4909 | -2.1586 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 67.3275 | FALSE | FALSE | 0.4951 | 1.5326 | 68.1977 | 44 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.43509 | Confirmed/Materialized Shift | 69.0679 | -1.4267 | Day | 202602 | 2026-02-09 | 1.4267
2026-02-09 07:30 | 67.577 | FALSE | TRUE | -0.27798 | -0.41305 | -1.3783 | -1.9989 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 67.299 | FALSE | FALSE | 0.4886 | 1.5281 | 68.1272 | 45 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.41407 | Confirmed/Materialized Shift | 68.9553 | -1.3287 | Day | 202602 | 2026-02-09 | 1.3287
2026-02-09 07:45 | 67.577 | FALSE | TRUE | -0.32217 | -0.47902 | -1.3096 | -1.9012 | 0 |  | 2026-02-08 20:44 | none | FALSE | 0 | 67.2548 | FALSE | FALSE | 0.4807 | 1.5212 | 68.0707 | 46 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.40795 | Confirmed/Materialized Shift | 68.8866 | -1.2103 | Day | 202602 | 2026-02-09 | 1.2103
2026-02-09 08:00 | 67.8596 | TRUE | FALSE | -0.59451 | -0.88383 | -0.93219 | -1.3551 | 0.2826 |  |  | none | FALSE | 1 | 67.2651 | FALSE | FALSE | 0.0581 |  | 68.0284 | 0 | 0.2826 | -0.0423 | 0.13813 | 2.3521 | 0.38168 | Persistence ends | 68.7918 | -0.44237 | Day | 202602 | 2026-02-09 | 0.44237
2026-02-09 08:15 | 68.1404 | FALSE | FALSE | -0.83696 | -1.2436 | -0.55652 | -0.81011 | 0.2808 |  |  | none | FALSE | 1 | 67.3034 | FALSE | FALSE | 0.0554 |  | 68.0002 | 0 | 0.2808 | -0.02826 | 0.1558 | 1.9837 | 0.34837 | Normal | 68.6969 | 0.4025 | Day | 202602 | 2026-02-09 | 0.4025
2026-02-09 08:30 | 68.423 | FALSE | FALSE | -1.0831 | -1.6084 | -0.20918 | -0.30478 | 0.2826 |  |  | none | FALSE | 1 | 67.3399 | FALSE | FALSE | 0.1187 |  | 67.9861 | 0 | 0.2826 | -0.01413 | 0.17061 | 1.7393 | 0.32306 | Normal | 68.6322 | 1.3525 | Day | 202602 | 2026-02-09 | 1.3525
2026-02-09 08:30 | 68.423 | FALSE | FALSE | -1.0409 | -1.5447 | -0.13869 | -0.20229 | 0 |  |  | none | FALSE | 1 | 67.3821 | FALSE | FALSE | 0.1305 |  | 67.9719 | 0 | 0 | -0.01413 | 0.17061 | 0.082823 | 0.29489 | Normal | 68.5617 | 1.5297 | Day | 202602 | 2026-02-09 | 1.5297
2026-02-09 08:45 | 68.7056 | FALSE | FALSE | -1.3657 | -2.028 | 0.073423 | 0.10698 | 0.2826 | 2026-02-09 12:59 | 2026-02-09 08:45 | upper | TRUE | 1 | 67.3399 | FALSE | FALSE | 0.2342 | 2.2273 | 67.9861 | 1 | 0.2826 | 0.01413 | 0.17061 | 1.5736 | 0.32306 | Extreme triggered | 68.6322 | 2.2273 | Day | 202602 | 2026-02-09 | 2.2273
2026-02-09 09:00 | 68.9882 | FALSE | FALSE | -1.739 | -2.5859 | 0.20881 | 0.30359 | 0.2826 |  | 2026-02-09 08:45 | upper | TRUE | 1 | 67.2492 | FALSE | FALSE | 0.3126 | 2.3866 | 68.0143 | 2 | 0.2826 | 0.02826 | 0.18077 | 1.407 | 0.38254 | Extreme/elevated | 68.7794 | 2.5458 | Day | 202602 | 2026-02-09 | 2.5458
2026-02-09 09:15 | 69.2708 | FALSE | FALSE | -2.1491 | -3.2019 | 0.2508 | 0.36337 | 0.2826 |  | 2026-02-09 08:45 | upper | TRUE | 1 | 67.1217 | FALSE | TRUE | 0.3686 | 2.4339 | 68.0708 | 3 | 0.2826 | 0.05652 | 0.17366 | 1.3019 | 0.47459 | Persistent | 69.02 | 2.5285 | Day | 202602 | 2026-02-09 | 2.5285
2026-02-09 09:30 | 69.5534 | FALSE | FALSE | -2.5702 | -3.8371 | 0.25363 | 0.36599 | 0.2826 |  | 2026-02-09 08:45 | upper | TRUE | 1 | 66.9832 | FALSE | TRUE | 0.4197 | 2.4349 | 68.1415 | 4 | 0.2826 | 0.07065 | 0.18019 | 1.1763 | 0.57914 | Persistent | 69.2998 | 2.4379 | Day | 202602 | 2026-02-09 | 2.4379
2026-02-09 09:45 | 69.836 | FALSE | FALSE | -2.9939 | -4.479 | 0.22559 | 0.32407 | 0.2826 |  | 2026-02-09 08:45 | upper | TRUE | 1 | 66.8421 | FALSE | TRUE | 0.4693 | 2.4131 | 68.2263 | 5 | 0.2826 | 0.08478 | 0.18537 | 1.0672 | 0.69208 | Persistent | 69.6104 | 2.326 | Day | 202602 | 2026-02-09 | 2.326
2026-02-09 10:00 | 70.3994 | TRUE | FALSE | -3.7236 | -5.5847 | 0.36869 | 0.52646 | 0.5634 |  | 2026-02-09 08:45 | upper | TRUE | 2 | 66.6758 | TRUE | TRUE | 0.5626 | 2.4175 | 68.3533 | 6 | 0.5634 | 0.12699 | 0.19367 | 2.2534 | 0.83873 | Persistent | 70.0307 | 2.4396 | Day | 202602 | 2026-02-09 | 2.4396
2026-02-09 10:15 | 70.9646 | FALSE | TRUE | -4.4801 | -6.7386 | 0.43207 | 0.61258 | 0.5652 |  | 2026-02-09 08:45 | upper | TRUE | 1 | 66.4845 | FALSE | TRUE | 0.5904 | 2.4189 | 68.5085 | 7 | 0.5652 | 0.15525 | 0.2143 | 1.913 | 1.012 | Confirmed/Materialized Shift | 70.5325 | 2.4269 | Day | 202602 | 2026-02-09 | 2.4269
2026-02-09 10:29 | 71.5298 | FALSE | TRUE | -5.2436 | -7.9106 | 0.43196 | 0.60756 | 0.5652 |  | 2026-02-09 08:45 | upper | TRUE | 1 | 66.2862 | FALSE | TRUE | 0.5858 | 2.4114 | 68.692 | 8 | 0.5652 | 0.18351 | 0.22948 | 1.6633 | 1.2029 | Confirmed/Materialized Shift | 71.0978 | 2.3591 | Day | 202602 | 2026-02-09 | 2.3591
2026-02-09 10:44 | 71.8124 | FALSE | TRUE | -5.6664 | -8.5665 | 0.17912 | 0.25005 | 0.2826 |  | 2026-02-09 08:45 | upper | TRUE | 1 | 66.146 | FALSE | TRUE | 0.5706 | 2.3802 | 68.8897 | 9 | 0.2826 | 0.19764 | 0.22626 | 0.37549 | 1.3718 | Confirmed/Materialized Shift | 71.6333 | 2.1306 | Day | 202602 | 2026-02-09 | 2.1306
2026-02-09 10:59 | 72.095 | FALSE | TRUE | -6.0396 | -9.1433 | -0.052455 | -0.072706 | 0.2826 |  | 2026-02-09 08:45 | none | FALSE | 1 | 66.0554 | FALSE | FALSE | 0.5596 | 2.3387 | 69.1014 | 10 | 0.2826 | 0.21177 | 0.22206 | 0.31897 | 1.523 | Confirmed/Materialized Shift | 72.1475 | 1.9656 | Day | 202602 | 2026-02-09 | 1.9656
2026-02-09 11:15 | 72.3758 | FALSE | TRUE | -6.3646 | -9.6417 | -0.26747 | -0.3682 | 0.2808 |  | 2026-02-09 08:45 | none | FALSE | 1 | 66.0112 | FALSE | FALSE | 0.5512 | 2.2933 | 69.3272 | 11 | 0.2808 | 0.22581 | 0.21678 | 0.25367 | 1.658 | Confirmed/Materialized Shift | 72.6433 | 1.8387 | Day | 202602 | 2026-02-09 | 1.8387
2026-02-09 11:29 | 72.095 | TRUE | TRUE | -6.0153 | -9.1031 | -0.90328 | -1.2374 | -0.2808 |  | 2026-02-09 08:45 | none | FALSE | 2 | 66.0797 | TRUE | FALSE | 0.5557 | 2.2253 | 69.539 | 12 | -0.2808 | 0.21177 | 0.24002 | -2.0522 | 1.7296 | Confirmed/Materialized Shift | 72.9983 | 1.4778 | Day | 202602 | 2026-02-09 | 1.4778
2026-02-09 11:44 | 72.095 | FALSE | TRUE | -5.8396 | -8.8138 | -1.1794 | -1.6096 | 0 |  | 2026-02-09 08:45 | none | FALSE | 2 | 66.2554 | FALSE | FALSE | 0.5457 | 2.1563 | 69.7649 | 13 | 0 | 0.2259 | 0.21655 | -1.0432 | 1.7548 | Confirmed/Materialized Shift | 73.2744 | 1.3279 | Day | 202602 | 2026-02-09 | 1.3279
2026-02-09 11:59 | 72.3758 | FALSE | TRUE | -5.9067 | -8.8864 | -1.1648 | -1.5839 | 0.2808 |  | 2026-02-09 08:45 | none | FALSE | 2 | 66.4691 | FALSE | FALSE | 0.5466 | 2.098 | 70.0048 | 14 | 0.2808 | 0.23994 | 0.21014 | 0.19444 | 1.7679 | Confirmed/Materialized Shift | 73.5406 | 1.3411 | Day | 202602 | 2026-02-09 | 1.3411
2026-02-09 12:14 | 72.6584 | FALSE | TRUE | -5.931 | -8.8884 | -1.132 | -1.5341 | 0.2826 |  | 2026-02-09 08:45 | none | FALSE | 2 | 66.7274 | FALSE | FALSE | 0.5477 | 2.0488 | 70.2589 | 15 | 0.2826 | 0.25407 | 0.20253 | 0.14087 | 1.7657 | Confirmed/Materialized Shift | 73.7904 | 1.3589 | Day | 202602 | 2026-02-09 | 1.3589
2026-02-09 12:29 | 72.941 | FALSE | TRUE | -5.9023 | -8.8042 | -1.0745 | -1.4517 | 0.2826 |  | 2026-02-09 08:45 | none | FALSE | 1 | 67.0387 | FALSE | FALSE | 0.5208 | 2.0072 | 70.5271 | 16 | 0.2826 | 0.2682 | 0.19352 | 0.074409 | 1.7442 | Confirmed/Materialized Shift | 74.0155 | 1.384 | Day | 202602 | 2026-02-09 | 1.384
2026-02-09 12:44 | 73.2236 | FALSE | TRUE | -5.8777 | -8.7277 | -1.0211 | -1.3754 | 0.2826 |  | 2026-02-09 08:45 | none | FALSE | 1 | 67.3459 | FALSE | FALSE | 0.5224 | 1.972 | 70.7953 | 17 | 0.2826 | 0.2682 | 0.19352 | 0.074409 | 1.7247 | Confirmed/Materialized Shift | 74.2447 | 1.4079 | Day | 202602 | 2026-02-09 | 1.4079
2026-02-09 12:59 | 72.6584 | TRUE | FALSE | -4.9433 | -7.3002 | -1.6689 | -2.2454 | -0.5652 |  |  | none | FALSE | 2 | 67.7151 | TRUE | FALSE | 0.1232 |  | 71.0212 | 0 | -0.5652 | 0.2259 | 0.26854 | -2.9459 | 1.6531 | Persistence ends | 74.3273 | 0.9904 | Day | 202602 | 2026-02-09 | 0.9904
2026-02-09 13:14 | 72.3758 | FALSE | FALSE | -4.2764 | -6.2797 | -1.9625 | -2.64 | -0.2826 |  |  | none | FALSE | 2 | 68.0994 | FALSE | FALSE | 0.1066 |  | 71.2189 | 0 | -0.2826 | 0.19764 | 0.29106 | -1.65 | 1.5597 | Normal | 74.3383 | 0.74176 | Day | 202602 | 2026-02-09 | 0.74176
2026-02-09 13:28 | 72.3758 | FALSE | FALSE | -3.8234 | -5.5773 | -1.9048 | -2.5643 | 0 |  |  | none | FALSE | 2 | 68.5524 | FALSE | FALSE | 0.1018 |  | 71.4165 | 0 | 0 | 0.19764 | 0.29106 | -0.67904 | 1.432 | Normal | 74.2806 | 0.6699 | Day | 202602 | 2026-02-09 | 0.6699
2026-02-09 13:44 | 72.3758 | FALSE | FALSE | -3.3657 | -4.8771 | -1.8141 | -2.4452 | 0 |  |  | none | FALSE | 2 | 69.0101 | FALSE | FALSE | 0.0971 |  | 71.6 | 0 | 0 | 0.18351 | 0.29357 | -0.62511 | 1.295 | Normal | 74.1899 | 0.59909 | Day | 202602 | 2026-02-09 | 0.59909
2026-02-09 13:59 | 72.3758 | FALSE | FALSE | -2.9037 | -4.1797 | -1.6909 | -2.2829 | 0 |  |  | none | FALSE | 1 | 69.4721 | FALSE | FALSE | 0.0638 |  | 71.7694 | 0 | 0 | 0.16938 | 0.29534 | -0.57351 | 1.1486 | Normal | 74.0667 | 0.52795 | Day | 202602 | 2026-02-09 | 0.52795
2026-02-09 14:14 | 72.3758 | FALSE | FALSE | -2.4359 | -3.4828 | -1.5335 | -2.0749 | 0 |  |  | none | FALSE | 1 | 69.9399 | FALSE | FALSE | 0.0589 |  | 71.9246 | 0 | 0 | 0.15525 | 0.2964 | -0.52379 | 0.99236 | Normal | 73.9093 | 0.45464 | Day | 202602 | 2026-02-09 | 0.45464
2026-02-09 14:28 | 72.3758 | FALSE | FALSE | -1.9576 | -2.7799 | -1.3375 | -1.8144 | 0 |  |  | none | FALSE | 1 | 70.4182 | FALSE | FALSE | 0.0537 |  | 72.0657 | 0 | 0 | 0.14112 | 0.29674 | -0.47556 | 0.82377 | Normal | 73.7133 | 0.37638 | Day | 202602 | 2026-02-09 | 0.37638
2026-02-09 14:43 | 72.095 | FALSE | FALSE | -1.1868 | -1.6737 | -1.3542 | -1.8437 | -0.2808 |  |  | none | FALSE | 1 | 70.9082 | FALSE | FALSE | 0.0374 |  | 72.1787 | 0 | -0.2808 | 0.11295 | 0.30909 | -1.2739 | 0.63524 | Normal | 73.4492 | -0.13176 | Day | 202602 | 2026-02-09 | 0.13176
2026-02-09 14:58 | 72.3758 | FALSE | FALSE | -1.0547 | -1.4788 | -0.85811 | -1.1717 | 0.2808 |  |  | none | FALSE | 1 | 71.3211 | FALSE | FALSE | 0.0423 |  | 72.2775 | 0 | 0.2808 | 0.09882 | 0.29348 | 0.62008 | 0.4782 | Normal | 73.2339 | 0.20552 | Day | 202602 | 2026-02-09 | 0.20552
2026-02-09 15:13 | 72.3758 | FALSE | FALSE | -0.7577 | -1.058 | -0.70226 | -0.96097 | 0 |  |  | none | FALSE | 1 | 71.6181 | FALSE | FALSE | 0.0336 |  | 72.3481 | 0 | 0 | 0.07056 | 0.27268 | -0.25876 | 0.36499 | Normal | 73.0781 | 0.075948 | Day | 202602 | 2026-02-09 | 0.075948
2026-02-09 15:28 | 72.3758 | FALSE | FALSE | -0.60552 | -0.8437 | -0.63468 | -0.8693 | 0 |  |  | none | FALSE | 0 | 71.7703 | FALSE | FALSE | 0.0031 |  | 72.3904 | 0 | 0 | 0.0423 | 0.24678 | -0.17141 | 0.31005 | Normal | 73.0105 | -0.047024 | Day | 202602 | 2026-02-09 | 0.047024
2026-02-09 15:43 | 72.3758 | FALSE | FALSE | -0.51484 | -0.71643 | -0.60034 | -0.82265 | 0 |  |  | none | FALSE | 0 | 71.861 | FALSE | FALSE | 0.0102 |  | 72.4185 | 0 | 0 | 0.02817 | 0.2403 | -0.11723 | 0.27879 | Normal | 72.9761 | -0.15334 | Day | 202602 | 2026-02-09 | 0.15334
2026-02-09 15:58 | 72.3758 | FALSE | FALSE | -0.48026 | -0.66799 | -0.59384 | -0.81381 | 0 |  |  | none | FALSE | 0 | 71.8955 | FALSE | FALSE | 0.0141 |  | 72.4326 | 0 | 0 | 0.01404 | 0.23274 | -0.060324 | 0.26852 | Normal | 72.9696 | -0.21149 | Day | 202602 | 2026-02-09 | 0.21149
2026-02-09 16:13 | 72.3758 | FALSE | FALSE | -0.48026 | -0.66799 | -0.59384 | -0.81381 | 0 |  |  | none | FALSE | 0 | 71.8955 | FALSE | FALSE | 0.0141 |  | 72.4326 | 0 | 0 | 0 | 0.22411 | 0 | 0.26852 | Normal | 72.9696 | -0.21149 | Day | 202602 | 2026-02-09 | 0.21149
2026-02-09 16:28 | 72.3758 | FALSE | FALSE | -0.44325 | -0.6162 | -0.58491 | -0.80167 | 0 |  |  | none | FALSE | 0 | 71.9326 | FALSE | FALSE | 0.0184 |  | 72.4466 | 0 | 0 | 0.01404 | 0.21417 | -0.065555 | 0.25704 | Normal | 72.9607 | -0.27556 | Day | 202602 | 2026-02-09 | 0.27556
2026-02-09 16:43 | 72.3758 | FALSE | FALSE | -0.40346 | -0.56058 | -0.5732 | -0.78576 | 0 |  |  | none | FALSE | 0 | 71.9723 | FALSE | FALSE | 0.0232 |  | 72.4607 | 0 | 0 | 0.01404 | 0.21417 | -0.065555 | 0.24417 | Normal | 72.949 | -0.34759 | Day | 202602 | 2026-02-09 | 0.34759
2026-02-09 16:58 | 72.3758 | FALSE | FALSE | -0.40346 | -0.56058 | -0.5732 | -0.78576 | 0 |  |  | none | FALSE | 0 | 71.9723 | FALSE | FALSE | 0.0232 |  | 72.4607 | 0 | 0 | 0 | 0.20476 | 0 | 0.24417 | Normal | 72.949 | -0.34759 | Day | 202602 | 2026-02-09 | 0.34759
2026-02-09 17:13 | 72.3758 | FALSE | FALSE | -0.4098 | -0.56943 | -0.55128 | -0.75593 | 0 |  |  | none | FALSE | 0 | 71.966 | FALSE | FALSE | 0.0196 |  | 72.4465 | 0 | 0 | -0.01413 | 0.19368 | 0.072955 | 0.24027 | Normal | 72.9271 | -0.29442 | Day | 202602 | 2026-02-09 | 0.29442
2026-02-09 17:27 | 72.941 | TRUE | FALSE | -0.975 | -1.3548 | 0.013924 | 0.019093 | 0.5652 | 2026-02-09 19:45 | 2026-02-09 17:27 | upper | TRUE | 1 | 71.966 | FALSE | FALSE | 0.2229 | 2.058 | 72.4465 | 1 | 0.5652 | 0 | 0.22435 | 2.5193 | 0.24027 | Extreme triggered | 72.9271 | 2.058 | Day | 202602 | 2026-02-09 | 2.058
2026-02-09 17:42 | 73.2236 | FALSE | FALSE | -1.2576 | -1.7475 | 0.29652 | 0.4066 | 0.2826 |  | 2026-02-09 17:27 | upper | TRUE | 1 | 71.966 | FALSE | FALSE | 0.3585 | 2.646 | 72.4465 | 2 | 0.2826 | 0 | 0.22435 | 1.2596 | 0.24027 | Extreme/elevated | 72.9271 | 3.2341 | Day | 202602 | 2026-02-09 | 3.2341
2026-02-09 17:57 | 73.2236 | FALSE | FALSE | -1.3364 | -1.859 | 0.16124 | 0.22069 | 0 |  | 2026-02-09 17:27 | upper | TRUE | 1 | 71.8872 | FALSE | TRUE | 0.3699 | 2.6137 | 72.4748 | 3 | 0 | 0.02826 | 0.18077 | -0.15633 | 0.29378 | Persistent | 73.0624 | 2.5489 | Day | 202602 | 2026-02-09 | 2.5489
2026-02-09 18:12 | 73.2236 | FALSE | FALSE | -1.3799 | -1.9207 | 0.032885 | 0.04493 | 0 |  | 2026-02-09 17:27 | upper | TRUE | 1 | 71.8437 | FALSE | TRUE | 0.397 | 2.4847 | 72.5172 | 4 | 0 | 0.04239 | 0.1656 | -0.25597 | 0.33676 | Persistent | 73.1907 | 2.0976 | Night | 202602 | 2026-02-09 | 2.0976
2026-02-09 18:27 | 73.5062 | FALSE | FALSE | -1.7337 | -2.4155 | 0.1313 | 0.17895 | 0.2826 |  | 2026-02-09 17:27 | upper | TRUE | 1 | 71.7725 | FALSE | TRUE | 0.4695 | 2.4533 | 72.5737 | 5 | 0.2826 | 0.05652 | 0.17366 | 1.3019 | 0.40059 | Persistent | 73.3749 | 2.3278 | Night | 202602 | 2026-02-09 | 2.3278
2026-02-09 18:30 | 73.5062 | FALSE | FALSE | -1.7722 | -2.4705 | -0.020281 | -0.027583 | 0 |  | 2026-02-09 17:27 | none | FALSE | 1 | 71.734 | FALSE | FALSE | 0.5017 | 2.3702 | 72.6302 | 6 | 0 | 0.05652 | 0.17366 | -0.32547 | 0.44813 | Persistent | 73.5265 | 1.9547 | Night | 202602 | 2026-02-09 | 1.9547
2026-02-09 18:31 | 73.5062 | FALSE | TRUE | -1.7878 | -2.4928 | -0.14891 | -0.20218 | 0 |  | 2026-02-09 17:27 | none | FALSE | 1 | 71.7184 | FALSE | FALSE | 0.5414 | 2.2734 | 72.6868 | 7 | 0 | 0.05652 | 0.17366 | -0.32547 | 0.48418 | Confirmed/Materialized Shift | 73.6551 | 1.6924 | Night | 202602 | 2026-02-09 | 1.6924
2026-02-09 18:46 | 73.5062 | FALSE | TRUE | -1.7853 | -2.4893 | -0.25946 | -0.35174 | 0 |  | 2026-02-09 17:27 | none | FALSE | 1 | 71.7209 | FALSE | FALSE | 0.5281 | 2.1757 | 72.7433 | 8 | 0 | 0.05652 | 0.17366 | -0.32547 | 0.5112 | Confirmed/Materialized Shift | 73.7657 | 1.4924 | Night | 202602 | 2026-02-09 | 1.4924
2026-02-09 19:01 | 73.5062 | FALSE | TRUE | -1.7675 | -2.4638 | -0.3547 | -0.48022 | 0 |  | 2026-02-09 17:27 | none | FALSE | 1 | 71.7387 | FALSE | FALSE | 0.5173 | 2.0819 | 72.7998 | 9 | 0 | 0.05652 | 0.17366 | -0.32547 | 0.53055 | Confirmed/Materialized Shift | 73.8609 | 1.3315 | Night | 202602 | 2026-02-09 | 1.3315
2026-02-09 19:16 | 73.5062 | FALSE | TRUE | -1.6873 | -2.3493 | -0.41556 | -0.56217 | 0 |  | 2026-02-09 17:27 | none | FALSE | 1 | 71.8189 | FALSE | FALSE | 0.5092 | 1.9947 | 72.8704 | 10 | 0 | 0.07056 | 0.15534 | -0.45424 | 0.52571 | Confirmed/Materialized Shift | 73.9218 | 1.2095 | Night | 202602 | 2026-02-09 | 1.2095
2026-02-09 19:30 | 73.5062 | FALSE | TRUE | -1.6403 | -2.2824 | -0.48163 | -0.65096 | 0 |  | 2026-02-09 17:27 | none | FALSE | 0 | 71.8659 | FALSE | FALSE | 0.4728 | 1.9126 | 72.9269 | 11 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.53048 | Confirmed/Materialized Shift | 73.9878 | 1.0921 | Night | 202602 | 2026-02-09 | 1.0921
2026-02-09 19:45 | 73.5062 | FALSE | FALSE | -1.5806 | -2.1975 | -0.53498 | -0.72254 | 0 |  |  | none | FALSE | 0 | 71.9256 | FALSE | FALSE | 0.0659 |  | 72.9834 | 0 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.52889 | Persistence ends | 74.0412 | 0.9885 | Night | 202602 | 2026-02-09 | 0.9885
2026-02-09 20:00 | 73.5062 | FALSE | FALSE | -1.5081 | -2.0946 | -0.57548 | -0.77682 | 0 |  |  | none | FALSE | 0 | 71.9981 | FALSE | FALSE | 0.0597 |  | 73.0399 | 0 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.52089 | Normal | 74.0817 | 0.89518 | Night | 202602 | 2026-02-09 | 0.89518
2026-02-09 20:15 | 73.2236 | FALSE | FALSE | -1.1373 | -1.5777 | -0.85468 | -1.1538 | -0.2826 |  |  | none | FALSE | 0 | 72.0863 | FALSE | FALSE | 0.0189 |  | 73.0823 | 0 | -0.2826 | 0.04239 | 0.16593 | -1.9586 | 0.49799 | Normal | 74.0783 | 0.28374 | Night | 202602 | 2026-02-09 | 0.28374
2026-02-09 20:29 | 73.2236 | FALSE | FALSE | -1.0389 | -1.4392 | -0.84106 | -1.1356 | 0 |  |  | none | FALSE | 0 | 72.1847 | FALSE | FALSE | 0.014 |  | 73.1247 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.46998 | Normal | 74.0647 | 0.21045 | Night | 202602 | 2026-02-09 | 0.21045
2026-02-09 20:44 | 72.941 | FALSE | FALSE | -0.66509 | -0.92021 | -1.089 | -1.471 | -0.2826 |  |  | none | FALSE | 0 | 72.2759 | FALSE | FALSE | 0.0322 |  | 73.153 | 0 | -0.2826 | 0.02826 | 0.18107 | -1.7168 | 0.43852 | Normal | 74.03 | -0.48333 | Night | 202602 | 2026-02-09 | 0.48333
2026-02-09 20:59 | 72.6584 | FALSE | FALSE | -0.32361 | -0.44738 | -1.341 | -1.8121 | -0.2826 |  |  | none | FALSE | 0 | 72.3348 | FALSE | FALSE | 0.0815 |  | 73.1671 | 0 | -0.2826 | 0.01413 | 0.19396 | -1.5299 | 0.41614 | Normal | 73.9994 | -1.2224 | Night | 202602 | 2026-02-09 | 1.2224
2026-02-09 21:15 | 72.3758 | FALSE | FALSE | -0.041009 | -0.056693 | -1.6236 | -2.194 | -0.2826 |  |  | none | FALSE | 0 | 72.3348 | FALSE | FALSE | 0.1268 |  | 73.1671 | 0 | -0.2826 | 0 | 0.20502 | -1.3784 | 0.41614 | Normal | 73.9994 | -1.9015 | Night | 202602 | 2026-02-09 | 1.9015
2026-02-09 21:29 | 72.3758 | FALSE | FALSE | -0.041009 | -0.056693 | -1.6236 | -2.194 | 0 |  |  | none | FALSE | 0 | 72.3348 | FALSE | FALSE | 0.1268 |  | 73.1671 | 0 | 0 | 0 | 0.20502 | 0 | 0.41614 | Normal | 73.9994 | -1.9015 | Night | 202602 | 2026-02-09 | 1.9015
2026-02-09 21:44 | 72.095 | FALSE | FALSE | 0.16248 | 0.22486 | -1.9536 | -2.6383 | -0.2808 | 2026-02-10 08:00 | 2026-02-09 21:44 | lower | TRUE | 0 | 72.2575 | FALSE | FALSE | 0.2147 | 2.3629 | 73.153 | 1 | -0.2808 | -0.01404 | 0.21442 | -1.2441 | 0.44778 | Extreme triggered | 74.0486 | -2.3629 | Night | 202602 | 2026-02-09 | 2.3629
2026-02-09 21:59 | 72.095 | FALSE | FALSE | 0.0054418 | 0.0075475 | -2.026 | -2.7334 | 0 |  | 2026-02-09 21:44 | lower | TRUE | 0 | 72.1004 | FALSE | FALSE | 0.2483 | 2.1868 | 73.1107 | 2 | 0 | -0.0423 | 0.16579 | 0.25514 | 0.50515 | Extreme/elevated | 74.121 | -2.0108 | Night | 202602 | 2026-02-09 | 2.0108
2026-02-09 22:14 | 72.095 | FALSE | FALSE | -0.14605 | -0.20299 | -2.0647 | -2.7841 | 0 |  | 2026-02-09 21:44 | none | FALSE | 0 | 71.949 | FALSE | FALSE | 0.2871 | 2.0365 | 73.0543 | 3 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.55268 | Persistent | 74.1597 | -1.7357 | Night | 202602 | 2026-02-09 | 1.7357
2026-02-09 22:29 | 72.095 | FALSE | FALSE | -0.2787 | -0.38807 | -2.0845 | -2.81 | 0 |  | 2026-02-09 21:44 | none | FALSE | 0 | 71.8163 | FALSE | FALSE | 0.3305 | 1.9094 | 72.9979 | 4 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.59079 | Persistent | 74.1795 | -1.5283 | Night | 202602 | 2026-02-09 | 1.5283
2026-02-09 22:44 | 71.8124 | FALSE | FALSE | -0.1736 | -0.24233 | -2.4034 | -3.2385 | -0.2826 |  | 2026-02-09 21:44 | none | FALSE | 0 | 71.6388 | FALSE | FALSE | 0.4011 | 1.8736 | 72.9273 | 5 | -0.2826 | -0.07056 | 0.15534 | -1.365 | 0.64426 | Persistent | 74.2158 | -1.7305 | Night | 202602 | 2026-02-09 | 1.7305
2026-02-09 22:59 | 71.8124 | FALSE | FALSE | -0.3193 | -0.44662 | -2.3798 | -3.2076 | 0 |  | 2026-02-09 21:44 | none | FALSE | 0 | 71.4931 | FALSE | FALSE | 0.4446 | 1.8158 | 72.8426 | 6 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.67477 | Persistent | 74.1922 | -1.5268 | Night | 202602 | 2026-02-09 | 1.5268
2026-02-09 23:14 | 71.5298 | FALSE | TRUE | -0.21787 | -0.30551 | -2.6459 | -3.5671 | -0.2826 |  | 2026-02-09 21:44 | none | FALSE | 0 | 71.3119 | FALSE | FALSE | 0.513 | 1.7987 | 72.7438 | 7 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.71594 | Confirmed/Materialized Shift | 74.1757 | -1.6957 | Night | 202602 | 2026-02-09 | 1.6957
2026-02-09 23:28 | 71.5298 | FALSE | TRUE | -0.36706 | -0.5158 | -2.5974 | -3.504 | 0 |  | 2026-02-09 21:44 | none | FALSE | 0 | 71.1627 | FALSE | FALSE | 0.5003 | 1.7619 | 72.645 | 8 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.74113 | Confirmed/Materialized Shift | 74.1272 | -1.5047 | Night | 202602 | 2026-02-09 | 1.5047
2026-02-09 23:44 | 71.5298 | FALSE | TRUE | -0.4875 | -0.68621 | -2.5202 | -3.4034 | 0 |  | 2026-02-09 21:44 | none | FALSE | 0 | 71.0423 | FALSE | FALSE | 0.4901 | 1.7163 | 72.5462 | 9 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.75194 | Confirmed/Materialized Shift | 74.05 | -1.3517 | Night | 202602 | 2026-02-09 | 1.3517
2026-02-09 23:59 | 71.2472 | FALSE | TRUE | -0.35317 | -0.49816 | -2.7252 | -3.6841 | -0.2826 |  | 2026-02-09 21:44 | none | FALSE | 0 | 70.894 | FALSE | FALSE | 0.5027 | 1.6988 | 72.4332 | 10 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.76959 | Confirmed/Materialized Shift | 73.9724 | -1.5411 | Night | 202602 | 2026-02-09 | 1.5411
2026-02-10 00:14 | 70.9646 | FALSE | TRUE | -0.24364 | -0.34451 | -2.9267 | -3.9608 | -0.2826 |  | 2026-02-09 21:44 | none | FALSE | 0 | 70.721 | FALSE | FALSE | 0.5128 | 1.6983 | 72.3061 | 11 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.79259 | Confirmed/Materialized Shift | 73.8913 | -1.6926 | Night | 202602 | 2026-02-10 | 1.6926
2026-02-10 00:28 | 71.2472 | TRUE | TRUE | -0.60061 | -0.85016 | -2.4926 | -3.3803 | 0.2826 |  | 2026-02-09 21:44 | none | FALSE | 1 | 70.6466 | FALSE | FALSE | 0.5101 | 1.6587 | 72.1932 | 12 | 0.2826 | -0.11295 | 0.16897 | 2.341 | 0.7733 | Confirmed/Materialized Shift | 73.7398 | -1.2233 | Night | 202602 | 2026-02-10 | 1.2233
2026-02-10 00:43 | 70.9646 | FALSE | TRUE | -0.40806 | -0.57835 | -2.6111 | -3.5488 | -0.2826 |  | 2026-02-09 21:44 | none | FALSE | 1 | 70.5565 | FALSE | FALSE | 0.5259 | 1.6433 | 72.0661 | 13 | -0.2826 | -0.12708 | 0.17083 | -0.91037 | 0.75479 | Confirmed/Materialized Shift | 73.5757 | -1.4594 | Night | 202602 | 2026-02-10 | 1.4594
2026-02-10 00:58 | 70.9646 | FALSE | TRUE | -0.45022 | -0.63849 | -2.3991 | -3.2701 | 0 |  | 2026-02-09 21:44 | none | FALSE | 1 | 70.5144 | FALSE | FALSE | 0.5198 | 1.6237 | 71.939 | 14 | 0 | -0.12708 | 0.17083 | 0.74389 | 0.71233 | Confirmed/Materialized Shift | 73.3637 | -1.368 | Night | 202602 | 2026-02-10 | 1.368
2026-02-10 01:13 | 70.682 | FALSE | TRUE | -0.26537 | -0.37685 | -2.5253 | -3.4495 | -0.2826 |  | 2026-02-09 21:44 | none | FALSE | 1 | 70.4166 | FALSE | FALSE | 0.5365 | 1.6234 | 71.8119 | 15 | -0.2826 | -0.12708 | 0.17083 | -0.91037 | 0.69766 | Confirmed/Materialized Shift | 73.2073 | -1.6196 | Night | 202602 | 2026-02-10 | 1.6196
2026-02-10 01:28 | 70.682 | FALSE | TRUE | -0.31173 | -0.44299 | -2.3175 | -3.1746 | 0 |  | 2026-02-09 21:44 | none | FALSE | 1 | 70.3703 | FALSE | FALSE | 0.5303 | 1.6173 | 71.6849 | 16 | 0 | -0.12708 | 0.17083 | 0.74389 | 0.6573 | Confirmed/Materialized Shift | 72.9995 | -1.5257 | Night | 202602 | 2026-02-10 | 1.5257
2026-02-10 01:43 | 70.3994 | FALSE | TRUE | -0.13617 | -0.1938 | -2.4529 | -3.367 | -0.2826 |  | 2026-02-09 21:44 | none | FALSE | 1 | 70.2632 | FALSE | FALSE | 0.5479 | 1.6274 | 71.5578 | 17 | -0.2826 | -0.12708 | 0.17083 | -0.91037 | 0.64728 | Confirmed/Materialized Shift | 72.8523 | -1.7896 | Night | 202602 | 2026-02-10 | 1.7896
2026-02-10 01:58 | 70.3994 | FALSE | TRUE | -0.23895 | -0.34057 | -2.3298 | -3.2034 | 0 |  | 2026-02-09 21:44 | none | FALSE | 1 | 70.1605 | FALSE | FALSE | 0.5371 | 1.6275 | 71.4448 | 18 | 0 | -0.11295 | 0.16897 | 0.66847 | 0.64219 | Confirmed/Materialized Shift | 72.7292 | -1.6279 | Night | 202602 | 2026-02-10 | 1.6279
2026-02-10 02:13 | 70.3994 | FALSE | TRUE | -0.3403 | -0.48573 | -2.2335 | -3.0751 | 0 |  | 2026-02-09 21:44 | none | FALSE | 1 | 70.0591 | FALSE | FALSE | 0.5266 | 1.6192 | 71.346 | 19 | 0 | -0.09882 | 0.16582 | 0.59594 | 0.64346 | Confirmed/Materialized Shift | 72.6329 | -1.4711 | Night | 202602 | 2026-02-10 | 1.4711
2026-02-10 02:28 | 70.1168 | FALSE | TRUE | -0.18653 | -0.26674 | -2.4191 | -3.335 | -0.2826 |  | 2026-02-09 21:44 | none | FALSE | 1 | 69.9303 | FALSE | FALSE | 0.5428 | 1.624 | 71.2331 | 20 | -0.2826 | -0.11295 | 0.16897 | -1.004 | 0.6514 | Confirmed/Materialized Shift | 72.5359 | -1.7136 | Night | 202602 | 2026-02-10 | 1.7136
2026-02-10 02:43 | 70.1168 | FALSE | TRUE | -0.31005 | -0.44416 | -2.3448 | -3.2359 | 0 |  | 2026-02-09 21:44 | none | FALSE | 1 | 69.8067 | FALSE | FALSE | 0.5308 | 1.6196 | 71.1342 | 21 | 0 | -0.09891 | 0.16593 | 0.59611 | 0.66371 | Confirmed/Materialized Shift | 72.4616 | -1.5328 | Night | 202602 | 2026-02-10 | 1.5328
2026-02-10 02:58 | 70.1168 | FALSE | TRUE | -0.4023 | -0.57706 | -2.2392 | -3.0947 | 0 |  | 2026-02-09 21:44 | none | FALSE | 0 | 69.7145 | FALSE | FALSE | 0.4927 | 1.6092 | 71.0353 | 22 | 0 | -0.09891 | 0.16593 | 0.59611 | 0.66037 | Confirmed/Materialized Shift | 72.356 | -1.3908 | Night | 202602 | 2026-02-10 | 1.3908
2026-02-10 03:13 | 69.836 | FALSE | TRUE | -0.23922 | -0.34372 | -2.4118 | -3.3383 | -0.2808 |  | 2026-02-09 21:44 | none | FALSE | 0 | 69.5968 | FALSE | FALSE | 0.5093 | 1.6105 | 70.9223 | 23 | -0.2808 | -0.11295 | 0.16897 | -0.99338 | 0.66276 | Confirmed/Materialized Shift | 72.2478 | -1.6391 | Night | 202602 | 2026-02-10 | 1.6391
2026-02-10 03:27 | 69.836 | FALSE | TRUE | -0.31591 | -0.45442 | -2.2626 | -3.1382 | 0 |  | 2026-02-09 21:44 | none | FALSE | 0 | 69.5201 | FALSE | FALSE | 0.5007 | 1.6063 | 70.8093 | 24 | 0 | -0.11295 | 0.16897 | 0.66847 | 0.64463 | Confirmed/Materialized Shift | 72.0986 | -1.5099 | Night | 202602 | 2026-02-10 | 1.5099
2026-02-10 03:42 | 69.836 | FALSE | TRUE | -0.39382 | -0.56712 | -2.1429 | -2.9771 | 0 |  | 2026-02-09 21:44 | none | FALSE | 0 | 69.4422 | FALSE | FALSE | 0.4919 | 1.5972 | 70.7105 | 25 | 0 | -0.09882 | 0.16582 | 0.59594 | 0.63418 | Confirmed/Materialized Shift | 71.9789 | -1.379 | Night | 202602 | 2026-02-10 | 1.379
2026-02-10 03:57 | 69.5534 | FALSE | TRUE | -0.21331 | -0.30763 | -2.3017 | -3.2032 | -0.2826 |  | 2026-02-09 21:44 | none | FALSE | 0 | 69.3401 | FALSE | FALSE | 0.5107 | 1.5997 | 70.5976 | 26 | -0.2826 | -0.11295 | 0.16897 | -1.004 | 0.62874 | Confirmed/Materialized Shift | 71.8551 | -1.6607 | Night | 202602 | 2026-02-10 | 1.6607
2026-02-10 04:12 | 69.5534 | FALSE | TRUE | -0.3143 | -0.45394 | -2.205 | -3.0728 | 0 |  | 2026-02-09 21:44 | none | FALSE | 0 | 69.2391 | FALSE | FALSE | 0.5001 | 1.596 | 70.4988 | 27 | 0 | -0.09882 | 0.16582 | 0.59594 | 0.62983 | Confirmed/Materialized Shift | 71.7584 | -1.501 | Night | 202602 | 2026-02-10 | 1.501
2026-02-10 04:27 | 69.5534 | FALSE | TRUE | -0.38227 | -0.55265 | -2.0754 | -2.8974 | 0 |  | 2026-02-09 21:44 | none | FALSE | 0 | 69.1711 | FALSE | FALSE | 0.4919 | 1.5882 | 70.3999 | 28 | 0 | -0.09882 | 0.16582 | 0.59594 | 0.61441 | Confirmed/Materialized Shift | 71.6288 | -1.3778 | Night | 202602 | 2026-02-10 | 1.3778
2026-02-10 04:42 | 69.2708 | FALSE | TRUE | -0.19043 | -0.27566 | -2.2228 | -3.1091 | -0.2826 |  | 2026-02-09 21:44 | none | FALSE | 0 | 69.0804 | FALSE | FALSE | 0.5123 | 1.5915 | 70.287 | 29 | -0.2826 | -0.11295 | 0.16897 | -1.004 | 0.60331 | Confirmed/Materialized Shift | 71.4936 | -1.6844 | Night | 202602 | 2026-02-10 | 1.6844
2026-02-10 04:57 | 69.2708 | FALSE | TRUE | -0.28184 | -0.40852 | -2.1166 | -2.9649 | 0 |  | 2026-02-09 21:44 | none | FALSE | 0 | 68.989 | FALSE | FALSE | 0.502 | 1.5895 | 70.1882 | 30 | 0 | -0.09882 | 0.16582 | 0.59594 | 0.5996 | Confirmed/Materialized Shift | 71.3874 | -1.53 | Night | 202602 | 2026-02-10 | 1.53
2026-02-10 05:12 | 69.2708 | FALSE | TRUE | -0.37486 | -0.5441 | -2.0402 | -2.861 | 0 |  | 2026-02-09 21:44 | none | FALSE | 0 | 68.8959 | FALSE | FALSE | 0.4919 | 1.5827 | 70.1035 | 31 | 0 | -0.08469 | 0.16132 | 0.52499 | 0.60377 | Confirmed/Materialized Shift | 71.311 | -1.3791 | Night | 202602 | 2026-02-10 | 1.3791
2026-02-10 05:27 | 68.9882 | FALSE | TRUE | -0.17704 | -0.25728 | -2.1817 | -3.0655 | -0.2826 |  | 2026-02-09 21:44 | none | FALSE | 0 | 68.8112 | FALSE | FALSE | 0.5133 | 1.5864 | 69.9905 | 32 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.58968 | Confirmed/Materialized Shift | 71.1699 | -1.6998 | Night | 202602 | 2026-02-10 | 1.6998
2026-02-10 05:42 | 68.9882 | FALSE | TRUE | -0.26335 | -0.38319 | -2.0704 | -2.9136 | 0 |  | 2026-02-09 21:44 | none | FALSE | 0 | 68.7249 | FALSE | FALSE | 0.5032 | 1.5852 | 69.8917 | 33 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.58343 | Confirmed/Materialized Shift | 71.0586 | -1.5486 | Night | 202602 | 2026-02-10 | 1.5486
2026-02-10 05:57 | 68.9882 | FALSE | TRUE | -0.31333 | -0.45624 | -1.9227 | -2.7114 | 0 |  | 2026-02-09 21:44 | none | FALSE | 0 | 68.6749 | FALSE | FALSE | 0.496 | 1.5809 | 69.7929 | 34 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.55901 | Confirmed/Materialized Shift | 70.9109 | -1.4395 | Night | 202602 | 2026-02-10 | 1.4395
2026-02-10 06:12 | 68.9882 | FALSE | TRUE | -0.37071 | -0.54026 | -1.8107 | -2.5575 | 0 |  | 2026-02-09 21:44 | none | FALSE | 0 | 68.6175 | FALSE | FALSE | 0.488 | 1.5735 | 69.7082 | 35 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.54536 | Confirmed/Materialized Shift | 70.7989 | -1.3202 | Night | 202602 | 2026-02-10 | 1.3202
2026-02-10 06:26 | 68.7056 | FALSE | TRUE | -0.1735 | -0.25316 | -1.9811 | -2.8026 | -0.2826 |  | 2026-02-09 21:44 | none | FALSE | 0 | 68.5321 | FALSE | FALSE | 0.5119 | 1.5764 | 69.6094 | 36 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.53864 | Confirmed/Materialized Shift | 70.6867 | -1.6779 | Night | 202602 | 2026-02-10 | 1.6779
2026-02-10 06:41 | 68.7056 | FALSE | TRUE | -0.26299 | -0.38424 | -1.9012 | -2.6926 | 0 |  | 2026-02-09 21:44 | none | FALSE | 0 | 68.4426 | FALSE | FALSE | 0.5009 | 1.5747 | 69.5247 | 37 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.54104 | Confirmed/Materialized Shift | 70.6068 | -1.5139 | Night | 202602 | 2026-02-10 | 1.5139
2026-02-10 06:56 | 68.7056 | FALSE | TRUE | -0.3243 | -0.47426 | -1.7931 | -2.5435 | 0 |  | 2026-02-09 21:44 | none | FALSE | 0 | 68.3813 | FALSE | FALSE | 0.4925 | 1.5698 | 69.44 | 38 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.52935 | Confirmed/Materialized Shift | 70.4987 | -1.3874 | Night | 202602 | 2026-02-10 | 1.3874
2026-02-10 07:11 | 68.7056 | FALSE | TRUE | -0.35549 | -0.5201 | -1.6549 | -2.352 | 0 |  | 2026-02-09 21:44 | none | FALSE | 0 | 68.3501 | FALSE | FALSE | 0.4862 | 1.5627 | 69.3553 | 39 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.5026 | Confirmed/Materialized Shift | 70.3605 | -1.2927 | Day | 202602 | 2026-02-10 | 1.2927
2026-02-10 07:26 | 68.423 | FALSE | TRUE | -0.17274 | -0.2531 | -1.868 | -2.6575 | -0.2826 |  | 2026-02-09 21:44 | none | FALSE | 0 | 68.2503 | FALSE | FALSE | 0.5108 | 1.5651 | 69.2706 | 40 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.51018 | Confirmed/Materialized Shift | 70.291 | -1.6614 | Day | 202602 | 2026-02-10 | 1.6614
2026-02-10 07:30 | 68.7056 | TRUE | TRUE | -0.47334 | -0.69372 | -1.4623 | -2.0839 | 0.2826 |  | 2026-02-09 21:44 | none | FALSE | 1 | 68.2323 | FALSE | FALSE | 0.4967 | 1.5519 | 69.2001 | 41 | 0.2826 | -0.07056 | 0.15534 | 2.2735 | 0.4839 | Confirmed/Materialized Shift | 70.1679 | -1.0218 | Day | 202602 | 2026-02-10 | 1.0218
2026-02-10 07:45 | 68.423 | FALSE | TRUE | -0.23317 | -0.34195 | -1.6179 | -2.31 | -0.2826 |  | 2026-02-09 21:44 | none | FALSE | 1 | 68.1898 | FALSE | FALSE | 0.5283 | 1.5506 | 69.1154 | 42 | -0.2826 | -0.08469 | 0.16132 | -1.2268 | 0.46277 | Confirmed/Materialized Shift | 70.0409 | -1.4961 | Day | 202602 | 2026-02-10 | 1.4961
2026-02-10 08:00 | 68.7056 | FALSE | FALSE | -0.52379 | -0.76823 | -1.2303 | -1.7592 | 0.2826 |  |  | none | FALSE | 1 | 68.1818 | FALSE | FALSE | 0.0823 |  | 69.0589 | 0 | 0.2826 | -0.05652 | 0.17396 | 1.9494 | 0.43852 | Persistence ends | 69.9359 | -0.80555 | Day | 202602 | 2026-02-10 | 0.80555
2026-02-10 08:16 | 68.7056 | FALSE | FALSE | -0.51251 | -0.75156 | -1.106 | -1.5842 | 0 |  |  | none | FALSE | 1 | 68.1931 | FALSE | FALSE | 0.0775 |  | 69.0023 | 0 | 0 | -0.05652 | 0.17396 | 0.32489 | 0.40462 | Normal | 69.8116 | -0.73335 | Day | 202602 | 2026-02-10 | 0.73335
2026-02-10 08:30 | 68.9882 | FALSE | FALSE | -0.7361 | -1.0785 | -0.67958 | -0.97545 | 0.2826 |  |  | none | FALSE | 1 | 68.2521 | FALSE | FALSE | 0.0339 |  | 68.9599 | 0 | 0.2826 | -0.04239 | 0.18957 | 1.7143 | 0.35392 | Normal | 69.6678 | 0.079849 | Day | 202602 | 2026-02-10 | 0.079849
2026-02-10 08:30 | 68.9882 | FALSE | FALSE | -0.70744 | -1.0361 | -0.5944 | -0.85423 | 0 |  |  | none | FALSE | 1 | 68.2808 | FALSE | FALSE | 0.0401 |  | 68.9317 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.32546 | Normal | 69.5826 | 0.17366 | Day | 202602 | 2026-02-10 | 0.17366
2026-02-10 08:45 | 68.9882 | FALSE | FALSE | -0.66756 | -0.97709 | -0.498 | -0.71668 | 0 |  |  | none | FALSE | 1 | 68.3206 | FALSE | FALSE | 0.048 |  | 68.9034 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.29139 | Normal | 69.4862 | 0.29095 | Day | 202602 | 2026-02-10 | 0.29095
2026-02-10 09:00 | 69.2708 | FALSE | FALSE | -0.90901 | -1.3297 | -0.14599 | -0.21031 | 0.2826 |  |  | none | FALSE | 1 | 68.3618 | FALSE | FALSE | 0.125 |  | 68.8893 | 0 | 0.2826 | -0.01413 | 0.19396 | 1.5299 | 0.26375 | Normal | 69.4168 | 1.4465 | Day | 202602 | 2026-02-10 | 1.4465
2026-02-10 09:15 | 69.5534 | FALSE | FALSE | -1.2328 | -1.8044 | 0.067205 | 0.096717 | 0.2826 | 2026-02-10 12:59 | 2026-02-10 09:15 | upper | TRUE | 1 | 68.3206 | FALSE | FALSE | 0.2344 | 2.2306 | 68.9034 | 1 | 0.2826 | 0.01413 | 0.19396 | 1.3842 | 0.29139 | Extreme triggered | 69.4862 | 2.2306 | Day | 202602 | 2026-02-10 | 2.2306
2026-02-10 09:30 | 69.836 | FALSE | FALSE | -1.605 | -2.3523 | 0.20364 | 0.29246 | 0.2826 |  | 2026-02-10 09:15 | upper | TRUE | 1 | 68.231 | FALSE | FALSE | 0.3149 | 2.406 | 68.9317 | 2 | 0.2826 | 0.02826 | 0.20296 | 1.2532 | 0.35034 | Extreme/elevated | 69.6324 | 2.5813 | Day | 202602 | 2026-02-10 | 2.5813
2026-02-10 09:45 | 70.1168 | FALSE | FALSE | -2.0117 | -2.9538 | 0.27398 | 0.39228 | 0.2808 |  | 2026-02-10 09:15 | upper | TRUE | 0 | 68.1051 | FALSE | TRUE | 0.3468 | 2.4809 | 68.974 | 3 | 0.2808 | 0.0423 | 0.21047 | 1.1332 | 0.43442 | Persistent | 69.8428 | 2.6307 | Day | 202602 | 2026-02-10 | 2.6307
2026-02-10 10:00 | 70.3994 | FALSE | FALSE | -2.4327 | -3.5792 | 0.27707 | 0.39512 | 0.2826 |  | 2026-02-10 09:15 | upper | TRUE | 0 | 67.9667 | FALSE | TRUE | 0.3962 | 2.4892 | 69.0445 | 4 | 0.2826 | 0.07056 | 0.20234 | 1.0479 | 0.5389 | Persistent | 70.1223 | 2.5141 | Day | 202602 | 2026-02-10 | 2.5141
2026-02-10 10:15 | 70.682 | FALSE | FALSE | -2.8548 | -4.2089 | 0.25075 | 0.35603 | 0.2826 |  | 2026-02-10 09:15 | upper | TRUE | 0 | 67.8272 | FALSE | TRUE | 0.4447 | 2.4684 | 69.1292 | 5 | 0.2826 | 0.08469 | 0.20697 | 0.95623 | 0.65101 | Persistent | 70.4312 | 2.3852 | Day | 202602 | 2026-02-10 | 2.3852
2026-02-10 10:29 | 70.9646 | FALSE | FALSE | -3.2725 | -4.8344 | 0.20061 | 0.28349 | 0.2826 |  | 2026-02-10 09:15 | upper | TRUE | 0 | 67.6921 | FALSE | TRUE | 0.4936 | 2.4339 | 69.228 | 6 | 0.2826 | 0.09882 | 0.2105 | 0.87306 | 0.76797 | Persistent | 70.764 | 2.2612 | Day | 202602 | 2026-02-10 | 2.2612
2026-02-10 10:44 | 71.8124 | TRUE | TRUE | -4.3586 | -6.4617 | 0.52764 | 0.74019 | 0.8478 |  | 2026-02-10 09:15 | upper | TRUE | 1 | 67.4538 | FALSE | TRUE | 0.5986 | 2.4506 | 69.3693 | 7 | 0.8478 | 0.14121 | 0.26726 | 2.6438 | 0.95775 | Confirmed/Materialized Shift | 71.2848 | 2.5509 | Day | 202602 | 2026-02-10 | 2.5509
2026-02-10 10:59 | 72.095 | FALSE | TRUE | -4.7967 | -7.1275 | 0.31582 | 0.43999 | 0.2826 |  | 2026-02-10 09:15 | upper | TRUE | 1 | 67.2983 | FALSE | TRUE | 0.5807 | 2.4295 | 69.5387 | 8 | 0.2826 | 0.16947 | 0.24937 | 0.45366 | 1.1202 | Confirmed/Materialized Shift | 71.7792 | 2.2819 | Day | 202602 | 2026-02-10 | 2.2819
2026-02-10 11:15 | 72.3758 | FALSE | TRUE | -5.1886 | -7.7225 | 0.11856 | 0.16409 | 0.2808 |  | 2026-02-10 09:15 | upper | TRUE | 1 | 67.1872 | FALSE | TRUE | 0.5681 | 2.3922 | 69.7222 | 9 | 0.2808 | 0.18351 | 0.24723 | 0.39353 | 1.2675 | Confirmed/Materialized Shift | 72.2572 | 2.0935 | Day | 202602 | 2026-02-10 | 2.0935
2026-02-10 11:29 | 72.3758 | FALSE | TRUE | -5.2176 | -7.7692 | -0.27753 | -0.382 | 0 |  | 2026-02-10 09:15 | none | FALSE | 1 | 67.1582 | FALSE | FALSE | 0.5484 | 2.3328 | 69.9057 | 10 | 0 | 0.18351 | 0.24723 | -0.74228 | 1.3738 | Confirmed/Materialized Shift | 72.6533 | 1.798 | Day | 202602 | 2026-02-10 | 1.798
2026-02-10 11:44 | 72.941 | FALSE | TRUE | -5.8229 | -8.6756 | -0.17597 | -0.24067 | 0.5652 |  | 2026-02-10 09:15 | none | FALSE | 1 | 67.1181 | FALSE | FALSE | 0.5541 | 2.2918 | 70.1175 | 11 | 0.5652 | 0.21177 | 0.25725 | 1.3739 | 1.4997 | Confirmed/Materialized Shift | 73.117 | 1.8827 | Day | 202602 | 2026-02-10 | 1.8827
2026-02-10 11:59 | 73.2236 | FALSE | TRUE | -6.0568 | -9.0175 | -0.32467 | -0.44144 | 0.2826 |  | 2026-02-10 09:15 | none | FALSE | 1 | 67.1668 | FALSE | FALSE | 0.5483 | 2.2506 | 70.3576 | 12 | 0.2826 | 0.24003 | 0.22964 | 0.18538 | 1.5954 | Confirmed/Materialized Shift | 73.5483 | 1.7965 | Day | 202602 | 2026-02-10 | 1.7965
2026-02-10 12:14 | 72.941 | FALSE | TRUE | -5.6614 | -8.4148 | -0.91807 | -1.243 | -0.2826 |  | 2026-02-10 09:15 | none | FALSE | 1 | 67.2796 | FALSE | FALSE | 0.5247 | 2.1883 | 70.5693 | 13 | -0.2826 | 0.21177 | 0.25725 | -1.9218 | 1.6449 | Confirmed/Materialized Shift | 73.8591 | 1.4419 | Day | 202602 | 2026-02-10 | 1.4419
2026-02-10 12:29 | 72.6584 | FALSE | TRUE | -5.1304 | -7.5974 | -1.3758 | -1.8583 | -0.2826 |  | 2026-02-10 09:15 | none | FALSE | 1 | 67.528 | FALSE | FALSE | 0.5055 | 2.1145 | 70.7811 | 14 | -0.2826 | 0.21177 | 0.25725 | -1.9218 | 1.6265 | Confirmed/Materialized Shift | 74.0342 | 1.1542 | Day | 202602 | 2026-02-10 | 1.1542
2026-02-10 12:44 | 72.6584 | FALSE | TRUE | -4.8817 | -7.2027 | -1.5224 | -2.0523 | 0 |  | 2026-02-10 09:15 | none | FALSE | 1 | 67.7767 | FALSE | FALSE | 0.4985 | 2.0435 | 70.9787 | 15 | 0 | 0.19764 | 0.26089 | -0.75757 | 1.601 | Confirmed/Materialized Shift | 74.1808 | 1.0491 | Day | 202602 | 2026-02-10 | 1.0491
2026-02-10 12:59 | 72.6584 | FALSE | FALSE | -4.5796 | -6.7269 | -1.6155 | -2.1751 | 0 |  |  | none | FALSE | 1 | 68.0788 | FALSE | FALSE | 0.0924 |  | 71.1764 | 0 | 0 | 0.19764 | 0.26089 | -0.75757 | 1.5488 | Persistence ends | 74.2739 | 0.9569 | Day | 202602 | 2026-02-10 | 0.9569
2026-02-10 13:14 | 72.6584 | FALSE | FALSE | -4.2831 | -6.264 | -1.686 | -2.2678 | 0 |  |  | none | FALSE | 0 | 68.3753 | FALSE | FALSE | 0.058 |  | 71.3599 | 0 | 0 | 0.18351 | 0.26368 | -0.69596 | 1.4923 | Normal | 74.3444 | 0.87017 | Day | 202602 | 2026-02-10 | 0.87017
2026-02-10 13:28 | 72.941 | FALSE | FALSE | -4.2269 | -6.1514 | -1.46 | -1.9623 | 0.2826 |  |  | none | FALSE | 0 | 68.7141 | FALSE | FALSE | 0.0649 |  | 71.5575 | 0 | 0.2826 | 0.19764 | 0.26089 | 0.32566 | 1.4217 | Normal | 74.401 | 0.97311 | Day | 202602 | 2026-02-10 | 0.97311
2026-02-10 13:43 | 72.941 | FALSE | FALSE | -3.8191 | -5.5251 | -1.4474 | -1.9457 | 0 |  |  | none | FALSE | 0 | 69.1219 | FALSE | FALSE | 0.06 |  | 71.7552 | 0 | 0 | 0.19764 | 0.26089 | -0.75757 | 1.3166 | Normal | 74.3884 | 0.90068 | Day | 202602 | 2026-02-10 | 0.90068
2026-02-10 13:59 | 72.941 | FALSE | FALSE | -3.4083 | -4.9017 | -1.4036 | -1.888 | 0 |  |  | none | FALSE | 0 | 69.5327 | FALSE | FALSE | 0.0555 |  | 71.9387 | 0 | 0 | 0.18351 | 0.26368 | -0.69596 | 1.203 | Normal | 74.3446 | 0.8332 | Day | 202602 | 2026-02-10 | 0.8332
2026-02-10 14:14 | 73.2236 | FALSE | FALSE | -3.2916 | -4.7068 | -1.0887 | -1.4651 | 0.2826 |  |  | none | FALSE | 0 | 69.932 | FALSE | FALSE | 0.0671 |  | 72.1222 | 0 | 0.2826 | 0.18351 | 0.26368 | 0.3758 | 1.0951 | Normal | 74.3123 | 1.0058 | Day | 202602 | 2026-02-10 | 1.0058
2026-02-10 14:28 | 73.2236 | FALSE | FALSE | -2.8893 | -4.108 | -1.0252 | -1.3808 | 0 |  |  | none | FALSE | 0 | 70.3343 | FALSE | FALSE | 0.0635 |  | 72.2916 | 0 | 0 | 0.16938 | 0.26566 | -0.63759 | 0.97864 | Normal | 74.2488 | 0.95238 | Day | 202602 | 2026-02-10 | 0.95238
2026-02-10 14:43 | 73.2236 | FALSE | FALSE | -2.4845 | -3.5122 | -0.93109 | -1.2556 | 0 |  |  | none | FALSE | 0 | 70.7391 | FALSE | FALSE | 0.0606 |  | 72.4469 | 0 | 0 | 0.15534 | 0.26687 | -0.58207 | 0.85389 | Normal | 74.1547 | 0.9096 | Day | 202602 | 2026-02-10 | 0.9096
2026-02-10 14:58 | 73.2236 | FALSE | FALSE | -2.0767 | -2.9188 | -0.80569 | -1.0883 | 0 |  |  | none | FALSE | 0 | 71.1469 | FALSE | FALSE | 0.0588 |  | 72.5881 | 0 | 0 | 0.14121 | 0.26726 | -0.52836 | 0.72059 | Normal | 74.0293 | 0.8819 | Day | 202602 | 2026-02-10 | 0.8819
2026-02-10 15:13 | 73.2236 | FALSE | FALSE | -1.6613 | -2.3215 | -0.64447 | -0.87246 | 0 |  |  | none | FALSE | 0 | 71.5623 | FALSE | FALSE | 0.0588 |  | 72.7152 | 0 | 0 | 0.12708 | 0.26686 | -0.4762 | 0.57644 | Normal | 73.8681 | 0.88199 | Day | 202602 | 2026-02-10 | 0.88199
2026-02-10 15:28 | 73.2236 | FALSE | FALSE | -1.2229 | -1.6985 | -0.43198 | -0.58648 | 0 |  |  | none | FALSE | 0 | 72.0007 | FALSE | FALSE | 0.0637 |  | 72.8281 | 0 | 0 | 0.11295 | 0.26568 | -0.42514 | 0.41372 | Normal | 73.6556 | 0.95587 | Day | 202602 | 2026-02-10 | 0.95587
2026-02-10 15:43 | 73.2236 | FALSE | FALSE | -1.0173 | -1.4089 | -0.36749 | -0.49937 | 0 |  |  | none | FALSE | 0 | 72.2063 | FALSE | FALSE | 0.0626 |  | 72.8987 | 0 | 0 | 0.07056 | 0.20234 | -0.34872 | 0.3462 | Normal | 73.5911 | 0.93848 | Day | 202602 | 2026-02-10 | 0.93848
2026-02-10 15:58 | 73.5062 | FALSE | FALSE | -1.1695 | -1.6168 | -0.095638 | -0.12994 | 0.2826 |  |  | none | FALSE | 0 | 72.3367 | FALSE | FALSE | 0.1132 |  | 72.9693 | 0 | 0.2826 | 0.07056 | 0.20234 | 1.0479 | 0.31629 | Normal | 73.6018 | 1.6976 | Day | 202602 | 2026-02-10 | 1.6976
2026-02-10 16:13 | 73.2236 | FALSE | FALSE | -0.7882 | -1.0881 | -0.3643 | -0.49505 | -0.2826 |  |  | none | FALSE | 0 | 72.4354 | FALSE | FALSE | 0.049 |  | 73.0117 | 0 | -0.2826 | 0.04239 | 0.21058 | -1.5433 | 0.28812 | Normal | 73.5879 | 0.73562 | Day | 202602 | 2026-02-10 | 0.73562
2026-02-10 16:28 | 73.2236 | FALSE | FALSE | -0.66839 | -0.92122 | -0.32927 | -0.44767 | 0 |  |  | none | FALSE | 0 | 72.5552 | FALSE | FALSE | 0.0453 |  | 73.054 | 0 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.24942 | Normal | 73.5529 | 0.67983 | Day | 202602 | 2026-02-10 | 0.67983
2026-02-10 16:43 | 73.2236 | FALSE | FALSE | -0.65679 | -0.90508 | -0.34593 | -0.4702 | 0 |  |  | none | FALSE | 0 | 72.5668 | FALSE | FALSE | 0.0413 |  | 73.0682 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.25068 | Normal | 73.5695 | 0.62004 | Day | 202602 | 2026-02-10 | 0.62004
2026-02-10 16:58 | 73.2236 | FALSE | FALSE | -0.65679 | -0.90508 | -0.34593 | -0.4702 | 0 |  |  | none | FALSE | 0 | 72.5668 | FALSE | FALSE | 0.0413 |  | 73.0682 | 0 | 0 | 0 | 0.15881 | 0 | 0.25068 | Normal | 73.5695 | 0.62004 | Day | 202602 | 2026-02-10 | 0.62004
2026-02-10 17:13 | 73.2236 | FALSE | FALSE | -0.64349 | -0.8866 | -0.36089 | -0.49045 | 0 |  |  | none | FALSE | 0 | 72.5801 | FALSE | FALSE | 0.0375 |  | 73.0823 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.2511 | Normal | 73.5845 | 0.56273 | Day | 202602 | 2026-02-10 | 0.56273
2026-02-10 17:27 | 72.941 | TRUE | FALSE | -0.31119 | -0.42846 | -0.62205 | -0.8456 | -0.2826 |  |  | none | FALSE | 1 | 72.6298 | FALSE | FALSE | 0.073 |  | 73.0964 | 0 | -0.2826 | 0.01413 | 0.14424 | -2.0571 | 0.23331 | Normal | 73.563 | -0.6662 | Day | 202602 | 2026-02-10 | 0.6662
2026-02-10 17:42 | 72.941 | FALSE | FALSE | -0.25657 | -0.35299 | -0.59569 | -0.81005 | 0 |  |  | none | FALSE | 1 | 72.6844 | FALSE | FALSE | 0.0816 |  | 73.1106 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.21306 | Normal | 73.5367 | -0.79582 | Day | 202602 | 2026-02-10 | 0.79582
2026-02-10 17:57 | 72.941 | FALSE | FALSE | -0.19546 | -0.26869 | -0.56284 | -0.76573 | 0 |  |  | none | FALSE | 1 | 72.7455 | FALSE | FALSE | 0.0932 |  | 73.1247 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.18957 | Normal | 73.5038 | -0.96896 | Day | 202602 | 2026-02-10 | 0.96896
2026-02-10 18:12 | 72.941 | FALSE | FALSE | -0.12505 | -0.17173 | -0.52069 | -0.70878 | 0 |  |  | none | FALSE | 1 | 72.816 | FALSE | FALSE | 0.1103 |  | 73.1388 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.16143 | Normal | 73.4617 | -1.2254 | Night | 202602 | 2026-02-10 | 1.2254
2026-02-10 18:27 | 72.6584 | FALSE | FALSE | 0.087142 | 0.11979 | -0.84544 | -1.1502 | -0.2826 | 2026-02-10 19:01 | 2026-02-10 18:27 | lower | TRUE | 1 | 72.7455 | FALSE | FALSE | 0.2497 | 2.4597 | 73.1247 | 1 | -0.2826 | -0.01413 | 0.14424 | -1.8612 | 0.18957 | Extreme triggered | 73.5038 | -2.4597 | Night | 202602 | 2026-02-10 | 2.4597
2026-02-10 18:30 | 72.6584 | FALSE | FALSE | 0.026035 | 0.035819 | -0.87829 | -1.1943 | 0 |  | 2026-02-10 18:27 | lower | TRUE | 1 | 72.6844 | FALSE | FALSE | 0.2843 | 2.2909 | 73.1106 | 2 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.21306 | Extreme/elevated | 73.5367 | -2.1222 | Night | 202602 | 2026-02-10 | 2.1222
2026-02-10 18:31 | 72.6584 | FALSE | FALSE | -0.028587 | -0.039359 | -0.90465 | -1.2298 | 0 |  | 2026-02-10 18:27 | none | FALSE | 1 | 72.6298 | FALSE | FALSE | 0.3252 | 2.1531 | 73.0964 | 3 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.23331 | Persistent | 73.563 | -1.8775 | Night | 202602 | 2026-02-10 | 1.8775
2026-02-10 18:46 | 72.6584 | FALSE | FALSE | -0.091586 | -0.12621 | -0.91113 | -1.2385 | 0 |  | 2026-02-10 18:27 | none | FALSE | 1 | 72.5668 | FALSE | FALSE | 0.3661 | 2.0235 | 73.0682 | 4 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.25068 | Persistent | 73.5695 | -1.6346 | Night | 202602 | 2026-02-10 | 1.6346
2026-02-10 19:01 | 72.941 | TRUE | FALSE | -0.38579 | -0.53173 | -0.61187 | -0.83188 | 0.2826 |  |  | none | FALSE | 2 | 72.5552 | TRUE | FALSE | 0.0874 |  | 73.054 | 0 | 0.2826 | -0.01413 | 0.14424 | 2.0571 | 0.24942 | Persistence ends | 73.5529 | -0.45322 | Night | 202602 | 2026-02-10 | 0.45322
2026-02-10 19:16 | 73.2236 | FALSE | FALSE | -0.66839 | -0.92122 | -0.32927 | -0.44767 | 0.2826 |  |  | none | FALSE | 2 | 72.5552 | FALSE | FALSE | 0.1025 |  | 73.054 | 0 | 0.2826 | 0 | 0.15881 | 1.7795 | 0.24942 | Normal | 73.5529 | 0.67983 | Night | 202602 | 2026-02-10 | 0.67983
2026-02-10 19:30 | 73.2236 | FALSE | FALSE | -0.66839 | -0.92122 | -0.32927 | -0.44767 | 0 |  |  | none | FALSE | 1 | 72.5552 | FALSE | FALSE | 0.0739 |  | 73.054 | 0 | 0 | 0 | 0.15881 | 0 | 0.24942 | Normal | 73.5529 | 0.67983 | Night | 202602 | 2026-02-10 | 0.67983
2026-02-10 19:45 | 73.2236 | FALSE | FALSE | -0.66839 | -0.92122 | -0.32927 | -0.44767 | 0 |  |  | none | FALSE | 1 | 72.5552 | FALSE | FALSE | 0.0739 |  | 73.054 | 0 | 0 | 0 | 0.15881 | 0 | 0.24942 | Normal | 73.5529 | 0.67983 | Night | 202602 | 2026-02-10 | 0.67983
2026-02-10 20:00 | 73.2236 | FALSE | FALSE | -0.66839 | -0.92122 | -0.32927 | -0.44767 | 0 |  |  | none | FALSE | 1 | 72.5552 | FALSE | FALSE | 0.0739 |  | 73.054 | 0 | 0 | 0 | 0.15881 | 0 | 0.24942 | Normal | 73.5529 | 0.67983 | Night | 202602 | 2026-02-10 | 0.67983
2026-02-10 20:15 | 73.2236 | FALSE | FALSE | -0.66839 | -0.92122 | -0.32927 | -0.44767 | 0 |  |  | none | FALSE | 1 | 72.5552 | FALSE | FALSE | 0.0739 |  | 73.054 | 0 | 0 | 0 | 0.15881 | 0 | 0.24942 | Normal | 73.5529 | 0.67983 | Night | 202602 | 2026-02-10 | 0.67983
2026-02-10 20:29 | 72.941 | FALSE | FALSE | -0.36812 | -0.50725 | -0.53768 | -0.73175 | -0.2826 |  |  | none | FALSE | 1 | 72.5729 | FALSE | FALSE | 0.0535 |  | 73.0258 | 0 | -0.2826 | -0.02826 | 0.15614 | -1.6289 | 0.22645 | Normal | 73.4787 | -0.37438 | Night | 202602 | 2026-02-10 | 0.37438
2026-02-10 20:44 | 72.941 | FALSE | FALSE | -0.37382 | -0.51514 | -0.51512 | -0.70126 | 0 |  |  | none | FALSE | 1 | 72.5672 | FALSE | FALSE | 0.0498 |  | 73.0117 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.22224 | Normal | 73.4561 | -0.31791 | Night | 202602 | 2026-02-10 | 0.31791
2026-02-10 20:59 | 72.941 | FALSE | FALSE | -0.37742 | -0.52013 | -0.49046 | -0.66792 | 0 |  |  | none | FALSE | 1 | 72.5636 | FALSE | FALSE | 0.0459 |  | 72.9975 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.21697 | Normal | 73.4315 | -0.26049 | Night | 202602 | 2026-02-10 | 0.26049
2026-02-10 21:14 | 72.6584 | FALSE | FALSE | -0.13456 | -0.18553 | -0.75628 | -1.0301 | -0.2826 |  |  | none | FALSE | 1 | 72.5238 | FALSE | FALSE | 0.1216 |  | 72.9693 | 0 | -0.2826 | -0.02826 | 0.15614 | -1.6289 | 0.22271 | Normal | 73.4147 | -1.3958 | Night | 202602 | 2026-02-10 | 1.3958
2026-02-10 21:29 | 72.6584 | FALSE | FALSE | -0.16658 | -0.22979 | -0.73178 | -0.9971 | 0 |  |  | none | FALSE | 0 | 72.4918 | FALSE | FALSE | 0.0839 |  | 72.941 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.22459 | Normal | 73.3902 | -1.2583 | Night | 202602 | 2026-02-10 | 1.2583
2026-02-10 21:44 | 72.3758 | FALSE | FALSE | 0.028207 | 0.038958 | -1.0174 | -1.3862 | -0.2826 | 2026-02-11 08:41 | 2026-02-10 21:44 | lower | TRUE | 0 | 72.404 | FALSE | FALSE | 0.1981 | 2.1141 | 72.8986 | 1 | -0.2826 | -0.04239 | 0.16593 | -1.4477 | 0.2473 | Extreme triggered | 73.3932 | -2.1141 | Night | 202602 | 2026-02-10 | 2.1141
2026-02-10 21:59 | 72.3758 | FALSE | FALSE | -0.051742 | -0.071541 | -1.0408 | -1.4177 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 72.3241 | FALSE | FALSE | 0.235 | 1.9623 | 72.8704 | 2 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.27315 | Extreme/elevated | 73.4166 | -1.8106 | Night | 202602 | 2026-02-10 | 1.8106
2026-02-10 22:14 | 72.3758 | FALSE | FALSE | -0.12151 | -0.16817 | -1.0541 | -1.4355 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 72.2543 | FALSE | FALSE | 0.2772 | 1.8371 | 72.8421 | 3 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.2939 | Persistent | 73.4299 | -1.5866 | Night | 202602 | 2026-02-10 | 1.5866
2026-02-10 22:29 | 72.3758 | FALSE | FALSE | -0.18315 | -0.25369 | -1.0592 | -1.4424 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 72.1927 | FALSE | FALSE | 0.3226 | 1.7304 | 72.8138 | 4 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.31059 | Persistent | 73.435 | -1.4103 | Night | 202602 | 2026-02-10 | 1.4103
2026-02-10 22:44 | 72.095 | FALSE | FALSE | -0.018961 | -0.026306 | -1.372 | -1.8675 | -0.2808 |  | 2026-02-10 21:44 | none | FALSE | 0 | 72.076 | FALSE | FALSE | 0.4154 | 1.7734 | 72.7715 | 5 | -0.2808 | -0.0423 | 0.16579 | -1.4386 | 0.34775 | Persistent | 73.467 | -1.9455 | Night | 202602 | 2026-02-10 | 1.9455
2026-02-10 22:59 | 72.095 | FALSE | FALSE | -0.10929 | -0.15182 | -1.406 | -1.9129 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 71.9857 | FALSE | FALSE | 0.457 | 1.7631 | 72.7434 | 6 | 0 | -0.02817 | 0.15598 | 0.18059 | 0.37882 | Persistent | 73.501 | -1.7115 | Night | 202602 | 2026-02-10 | 1.7115
2026-02-10 23:14 | 72.095 | FALSE | TRUE | -0.19078 | -0.26532 | -1.4312 | -1.9465 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 71.9042 | FALSE | FALSE | 0.502 | 1.7297 | 72.7152 | 7 | 0 | -0.02817 | 0.15598 | 0.18059 | 0.40548 | Confirmed/Materialized Shift | 73.5262 | -1.5295 | Night | 202602 | 2026-02-10 | 1.5295
2026-02-10 23:28 | 71.8124 | FALSE | TRUE | -0.045622 | -0.063569 | -1.7666 | -2.401 | -0.2826 |  | 2026-02-10 21:44 | none | FALSE | 0 | 71.7668 | FALSE | FALSE | 0.5266 | 1.7509 | 72.6729 | 8 | -0.2826 | -0.0423 | 0.16579 | -1.4494 | 0.45306 | Confirmed/Materialized Shift | 73.579 | -1.8993 | Night | 202602 | 2026-02-10 | 1.8993
2026-02-10 23:43 | 71.8124 | FALSE | TRUE | -0.16636 | -0.2322 | -1.8027 | -2.4489 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 71.646 | FALSE | FALSE | 0.5108 | 1.741 | 72.6306 | 9 | 0 | -0.0423 | 0.16579 | 0.25514 | 0.49228 | Confirmed/Materialized Shift | 73.6151 | -1.6621 | Night | 202602 | 2026-02-10 | 1.6621
2026-02-10 23:58 | 71.8124 | FALSE | TRUE | -0.27583 | -0.38557 | -1.7993 | -2.4444 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 71.5366 | FALSE | FALSE | 0.4979 | 1.7138 | 72.5742 | 10 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.51879 | Confirmed/Materialized Shift | 73.6117 | -1.4683 | Night | 202602 | 2026-02-10 | 1.4683
2026-02-11 00:14 | 71.8124 | FALSE | TRUE | -0.35235 | -0.49307 | -1.7347 | -2.3587 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 71.4601 | FALSE | FALSE | 0.4883 | 1.6784 | 72.5036 | 11 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.52177 | Confirmed/Materialized Shift | 73.5471 | -1.3247 | Night | 202602 | 2026-02-11 | 1.3247
2026-02-11 00:28 | 71.5298 | FALSE | TRUE | -0.18294 | -0.25641 | -1.9612 | -2.6686 | -0.2826 |  | 2026-02-10 21:44 | none | FALSE | 0 | 71.3469 | FALSE | FALSE | 0.5106 | 1.6768 | 72.4189 | 12 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.53603 | Confirmed/Materialized Shift | 73.491 | -1.6587 | Night | 202602 | 2026-02-11 | 1.6587
2026-02-11 00:43 | 71.5298 | FALSE | TRUE | -0.26759 | -0.3755 | -1.8764 | -2.5562 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 71.2622 | FALSE | FALSE | 0.5001 | 1.6632 | 72.3342 | 13 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.536 | Confirmed/Materialized Shift | 73.4062 | -1.5008 | Night | 202602 | 2026-02-11 | 1.5008
2026-02-11 00:58 | 71.5298 | FALSE | TRUE | -0.32368 | -0.45457 | -1.7631 | -2.4056 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 71.2061 | FALSE | FALSE | 0.492 | 1.643 | 72.2495 | 14 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.5217 | Confirmed/Materialized Shift | 73.2929 | -1.3796 | Night | 202602 | 2026-02-11 | 1.3796
2026-02-11 01:13 | 71.5298 | FALSE | TRUE | -0.34873 | -0.48992 | -1.6188 | -2.213 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 71.1811 | FALSE | FALSE | 0.4861 | 1.6195 | 72.1648 | 15 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.49189 | Confirmed/Materialized Shift | 73.1486 | -1.291 | Night | 202602 | 2026-02-11 | 1.291
2026-02-11 01:28 | 71.5298 | FALSE | TRUE | -0.38679 | -0.54368 | -1.5158 | -2.0751 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 71.143 | FALSE | FALSE | 0.4791 | 1.5925 | 72.0943 | 16 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.47564 | Confirmed/Materialized Shift | 73.0456 | -1.1868 | Night | 202602 | 2026-02-11 | 1.1868
2026-02-11 01:43 | 71.2472 | FALSE | TRUE | -0.17294 | -0.24333 | -1.6977 | -2.3274 | -0.2826 |  | 2026-02-10 21:44 | none | FALSE | 0 | 71.0743 | FALSE | FALSE | 0.5087 | 1.5947 | 72.0096 | 17 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.46767 | Confirmed/Materialized Shift | 72.9449 | -1.6302 | Night | 202602 | 2026-02-11 | 1.6302
2026-02-11 01:58 | 71.2472 | FALSE | TRUE | -0.20795 | -0.29273 | -1.5634 | -2.1471 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 71.0392 | FALSE | FALSE | 0.502 | 1.5911 | 71.9249 | 18 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.44283 | Confirmed/Materialized Shift | 72.8106 | -1.5304 | Night | 202602 | 2026-02-11 | 1.5304
2026-02-11 02:13 | 70.9646 | FALSE | TRUE | -0.038202 | -0.053861 | -1.7894 | -2.4596 | -0.2826 |  | 2026-02-10 21:44 | none | FALSE | 0 | 70.9264 | FALSE | FALSE | 0.5278 | 1.6082 | 71.8402 | 19 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.45691 | Confirmed/Materialized Shift | 72.754 | -1.9164 | Night | 202602 | 2026-02-11 | 1.9164
2026-02-11 02:27 | 70.9646 | FALSE | TRUE | -0.11756 | -0.16593 | -1.6994 | -2.3387 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 70.847 | FALSE | FALSE | 0.5161 | 1.6149 | 71.7555 | 20 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.45424 | Confirmed/Materialized Shift | 72.664 | -1.7412 | Night | 202602 | 2026-02-11 | 1.7412
2026-02-11 02:43 | 70.9646 | FALSE | TRUE | -0.20433 | -0.28877 | -1.6451 | -2.2656 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 70.7603 | FALSE | FALSE | 0.5039 | 1.6122 | 71.685 | 21 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.46235 | Confirmed/Materialized Shift | 72.6097 | -1.558 | Night | 202602 | 2026-02-11 | 1.558
2026-02-11 02:58 | 70.682 | FALSE | TRUE | -0.049284 | -0.069774 | -1.8858 | -2.5987 | -0.2826 |  | 2026-02-10 21:44 | none | FALSE | 0 | 70.6327 | FALSE | FALSE | 0.5265 | 1.6252 | 71.6003 | 22 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.48378 | Confirmed/Materialized Shift | 72.5678 | -1.8981 | Night | 202602 | 2026-02-11 | 1.8981
2026-02-11 03:13 | 70.682 | FALSE | TRUE | -0.14461 | -0.20501 | -1.8118 | -2.4992 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 70.5374 | FALSE | FALSE | 0.5136 | 1.6286 | 71.5156 | 23 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.4891 | Confirmed/Materialized Shift | 72.4938 | -1.7043 | Night | 202602 | 2026-02-11 | 1.7043
2026-02-11 03:27 | 70.682 | FALSE | TRUE | -0.2088 | -0.29628 | -1.7066 | -2.3575 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 70.4732 | FALSE | FALSE | 0.5043 | 1.6259 | 71.4309 | 24 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.47884 | Confirmed/Materialized Shift | 72.3886 | -1.564 | Night | 202602 | 2026-02-11 | 1.564
2026-02-11 03:42 | 70.3994 | FALSE | TRUE | -0.06227 | -0.08853 | -1.9557 | -2.7029 | -0.2826 |  | 2026-02-10 21:44 | none | FALSE | 0 | 70.3371 | FALSE | FALSE | 0.5251 | 1.6359 | 71.3461 | 25 | -0.2826 | -0.08478 | 0.13287 | -1.4888 | 0.50449 | Confirmed/Materialized Shift | 72.3551 | -1.8766 | Night | 202602 | 2026-02-11 | 1.8766
2026-02-11 03:57 | 70.3994 | FALSE | TRUE | -0.16685 | -0.23757 | -1.8907 | -2.6154 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 70.2325 | FALSE | FALSE | 0.5117 | 1.6375 | 71.2613 | 26 | 0 | -0.08478 | 0.13287 | 0.63808 | 0.51439 | Confirmed/Materialized Shift | 72.2901 | -1.6756 | Night | 202602 | 2026-02-11 | 1.6756
2026-02-11 04:12 | 70.3994 | FALSE | TRUE | -0.24178 | -0.34462 | -1.7961 | -2.4878 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 70.1576 | FALSE | FALSE | 0.5017 | 1.6333 | 71.1766 | 27 | 0 | -0.08478 | 0.13287 | 0.63808 | 0.50946 | Confirmed/Materialized Shift | 72.1955 | -1.5254 | Night | 202602 | 2026-02-11 | 1.5254
2026-02-11 04:27 | 70.3994 | FALSE | TRUE | -0.32269 | -0.46048 | -1.7357 | -2.4062 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 70.0767 | FALSE | FALSE | 0.4915 | 1.624 | 71.1059 | 28 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.5146 | Confirmed/Materialized Shift | 72.1351 | -1.3729 | Night | 202602 | 2026-02-11 | 1.3729
2026-02-11 04:42 | 70.3994 | FALSE | TRUE | -0.38308 | -0.54713 | -1.6548 | -2.2966 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 70.0163 | FALSE | FALSE | 0.4832 | 1.6111 | 71.0353 | 29 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.50946 | Confirmed/Materialized Shift | 72.0542 | -1.2481 | Night | 202602 | 2026-02-11 | 1.2481
2026-02-11 04:57 | 70.1168 | FALSE | TRUE | -0.19511 | -0.27904 | -1.8625 | -2.5875 | -0.2826 |  | 2026-02-10 21:44 | none | FALSE | 0 | 69.9217 | FALSE | FALSE | 0.508 | 1.6114 | 70.9505 | 30 | -0.2826 | -0.08478 | 0.13287 | -1.4888 | 0.51439 | Confirmed/Materialized Shift | 71.9793 | -1.6207 | Night | 202602 | 2026-02-11 | 1.6207
2026-02-11 05:12 | 70.1168 | FALSE | TRUE | -0.26009 | -0.37232 | -1.7579 | -2.4457 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 69.8567 | FALSE | FALSE | 0.499 | 1.6073 | 70.8657 | 31 | 0 | -0.08478 | 0.13287 | 0.63808 | 0.50449 | Confirmed/Materialized Shift | 71.8747 | -1.4845 | Night | 202602 | 2026-02-11 | 1.4845
2026-02-11 05:27 | 70.1168 | FALSE | TRUE | -0.33282 | -0.47693 | -1.6893 | -2.3526 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 69.784 | FALSE | FALSE | 0.4894 | 1.599 | 70.795 | 32 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.50553 | Confirmed/Materialized Shift | 71.8061 | -1.3416 | Night | 202602 | 2026-02-11 | 1.3416
2026-02-11 05:42 | 70.1168 | FALSE | TRUE | -0.38459 | -0.55152 | -1.5998 | -2.2307 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 69.7322 | FALSE | FALSE | 0.4817 | 1.5876 | 70.7244 | 33 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.49609 | Confirmed/Materialized Shift | 71.7166 | -1.2248 | Night | 202602 | 2026-02-11 | 1.2248
2026-02-11 05:57 | 69.836 | FALSE | TRUE | -0.18817 | -0.27017 | -1.7956 | -2.5067 | -0.2808 |  | 2026-02-10 21:44 | none | FALSE | 0 | 69.6478 | FALSE | FALSE | 0.508 | 1.5886 | 70.6397 | 34 | -0.2808 | -0.08469 | 0.13273 | -1.4775 | 0.49593 | Confirmed/Materialized Shift | 71.6316 | -1.6206 | Night | 202602 | 2026-02-11 | 1.6206
2026-02-11 06:12 | 69.836 | FALSE | TRUE | -0.24161 | -0.34717 | -1.6796 | -2.3486 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 69.5944 | FALSE | FALSE | 0.4998 | 1.586 | 70.555 | 35 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.48031 | Confirmed/Materialized Shift | 71.5156 | -1.497 | Night | 202602 | 2026-02-11 | 1.497
2026-02-11 06:26 | 69.836 | FALSE | TRUE | -0.26088 | -0.37496 | -1.5295 | -2.1432 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 69.5751 | FALSE | FALSE | 0.4945 | 1.5813 | 70.4703 | 36 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.4476 | Confirmed/Materialized Shift | 71.3655 | -1.4172 | Night | 202602 | 2026-02-11 | 1.4172
2026-02-11 06:41 | 69.836 | FALSE | TRUE | -0.29535 | -0.42472 | -1.4229 | -1.9968 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 69.5406 | FALSE | FALSE | 0.4875 | 1.574 | 70.3998 | 37 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.42956 | Confirmed/Materialized Shift | 71.2589 | -1.3124 | Night | 202602 | 2026-02-11 | 1.3124
2026-02-11 06:56 | 69.5534 | FALSE | TRUE | -0.079452 | -0.11436 | -1.6028 | -2.2525 | -0.2826 |  | 2026-02-10 21:44 | none | FALSE | 0 | 69.4739 | FALSE | FALSE | 0.5207 | 1.5803 | 70.3151 | 38 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.42056 | Confirmed/Materialized Shift | 71.1562 | -1.8111 | Night | 202602 | 2026-02-11 | 1.8111
2026-02-11 07:11 | 69.5534 | FALSE | TRUE | -0.15732 | -0.2267 | -1.5395 | -2.1655 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 69.3961 | FALSE | FALSE | 0.5086 | 1.5815 | 70.2445 | 39 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.42422 | Confirmed/Materialized Shift | 71.0929 | -1.6291 | Day | 202602 | 2026-02-11 | 1.6291
2026-02-11 07:26 | 69.5534 | FALSE | TRUE | -0.21027 | -0.30323 | -1.4514 | -2.044 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 69.3431 | FALSE | FALSE | 0.4996 | 1.5793 | 70.174 | 40 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.41541 | Confirmed/Materialized Shift | 71.0048 | -1.4938 | Day | 202602 | 2026-02-11 | 1.4938
2026-02-11 07:41 | 69.5534 | FALSE | TRUE | -0.23663 | -0.34137 | -1.3366 | -1.8855 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 69.3168 | FALSE | FALSE | 0.4932 | 1.5749 | 70.1034 | 41 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.39331 | Confirmed/Materialized Shift | 70.89 | -1.3984 | Day | 202602 | 2026-02-11 | 1.3984
2026-02-11 07:41 | 69.5534 | FALSE | TRUE | -0.28011 | -0.40435 | -1.2672 | -1.7893 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 69.2733 | FALSE | FALSE | 0.4851 | 1.5678 | 70.047 | 42 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.38683 | Confirmed/Materialized Shift | 70.8206 | -1.2759 | Day | 202602 | 2026-02-11 | 1.2759
2026-02-11 07:56 | 69.5534 | FALSE | TRUE | -0.30552 | -0.4412 | -1.1798 | -1.6679 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 69.2479 | FALSE | FALSE | 0.4785 | 1.5587 | 69.9905 | 43 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.37133 | Confirmed/Materialized Shift | 70.7332 | -1.1772 | Day | 202602 | 2026-02-11 | 1.1772
2026-02-11 08:11 | 69.5534 | FALSE | TRUE | -0.31046 | -0.44836 | -1.0719 | -1.5177 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 69.2429 | FALSE | FALSE | 0.4734 | 1.5483 | 69.9341 | 44 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.34558 | Confirmed/Materialized Shift | 70.6253 | -1.1016 | Day | 202602 | 2026-02-11 | 1.1016
2026-02-11 08:27 | 69.5534 | FALSE | TRUE | -0.33621 | -0.48573 | -1.013 | -1.4355 | 0 |  | 2026-02-10 21:44 | none | FALSE | 0 | 69.2172 | FALSE | FALSE | 0.4669 | 1.5362 | 69.8918 | 45 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.3373 | Confirmed/Materialized Shift | 70.5664 | -1.0033 | Day | 202602 | 2026-02-11 | 1.0033
2026-02-11 08:41 | 69.836 | TRUE | FALSE | -0.60337 | -0.87152 | -0.65863 | -0.9343 | 0.2826 |  |  | none | FALSE | 1 | 69.2326 | FALSE | FALSE | 0.0344 |  | 69.8636 | 0 | 0.2826 | -0.02817 | 0.12619 | 2.4627 | 0.3155 | Persistence ends | 70.4946 | -0.087575 | Day | 202602 | 2026-02-11 | 0.087575
2026-02-11 08:41 | 69.836 | FALSE | FALSE | -0.57895 | -0.83594 | -0.57787 | -0.82067 | 0 |  |  | none | FALSE | 1 | 69.2571 | FALSE | FALSE | 0.0287 |  | 69.8355 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.2892 | Normal | 70.4139 | 0.0018672 | Day | 202602 | 2026-02-11 | 0.0018672
2026-02-11 08:56 | 70.1168 | TRUE | FALSE | -0.82785 | -1.1948 | -0.23691 | -0.33673 | 0.2808 |  |  | none | FALSE | 2 | 69.289 | TRUE | FALSE | 0.1311 |  | 69.8213 | 0 | 0.2808 | -0.01413 | 0.14387 | 2.0499 | 0.26619 | Normal | 70.3537 | 1.11 | Day | 202602 | 2026-02-11 | 1.11
2026-02-11 09:11 | 70.3994 | FALSE | FALSE | -1.1104 | -1.6026 | 0.045695 | 0.06495 | 0.2826 | 2026-02-11 12:39 | 2026-02-11 09:11 | upper | TRUE | 2 | 69.289 | FALSE | FALSE | 0.2591 | 2.1717 | 69.8213 | 1 | 0.2826 | 0 | 0.15847 | 1.7833 | 0.26619 | Extreme triggered | 70.3537 | 2.1717 | Day | 202602 | 2026-02-11 | 2.1717
2026-02-11 09:26 | 70.3994 | FALSE | FALSE | -1.1423 | -1.6494 | -0.014466 | -0.020544 | 0 |  | 2026-02-11 09:11 | none | FALSE | 2 | 69.2571 | FALSE | FALSE | 0.3014 | 2.0608 | 69.8355 | 2 | 0 | 0.01413 | 0.14387 | -0.098211 | 0.2892 | Extreme/elevated | 70.4139 | 1.95 | Day | 202602 | 2026-02-11 | 1.95
2026-02-11 09:40 | 70.9646 | TRUE | FALSE | -1.8475 | -2.673 | 0.326 | 0.46151 | 0.5652 |  | 2026-02-11 09:11 | upper | TRUE | 3 | 69.1171 | TRUE | TRUE | 0.4476 | 2.3262 | 69.8778 | 3 | 0.5652 | 0.04239 | 0.18929 | 2.7619 | 0.38037 | Persistent | 70.6386 | 2.8571 | Day | 202602 | 2026-02-11 | 2.8571
2026-02-11 09:55 | 71.5298 | TRUE | FALSE | -2.6397 | -3.8318 | 0.5229 | 0.73641 | 0.5652 |  | 2026-02-11 09:11 | upper | TRUE | 4 | 68.8901 | TRUE | TRUE | 0.5421 | 2.4917 | 69.9485 | 4 | 0.5652 | 0.07065 | 0.222 | 2.2277 | 0.5292 | Persistent | 71.0069 | 2.9881 | Day | 202602 | 2026-02-11 | 2.9881
2026-02-11 10:10 | 71.5298 | FALSE | FALSE | -2.7833 | -4.0487 | 0.23799 | 0.33383 | 0 |  | 2026-02-11 09:11 | upper | TRUE | 4 | 68.7465 | FALSE | TRUE | 0.5583 | 2.4682 | 70.0191 | 5 | 0 | 0.07065 | 0.222 | -0.31825 | 0.63633 | Persistent | 71.2918 | 2.374 | Day | 202602 | 2026-02-11 | 2.374
2026-02-11 10:25 | 72.095 | FALSE | FALSE | -3.5333 | -5.1534 | 0.39253 | 0.54744 | 0.5652 |  | 2026-02-11 09:11 | upper | TRUE | 4 | 68.5617 | FALSE | TRUE | 0.6238 | 2.4735 | 70.1321 | 6 | 0.5652 | 0.11295 | 0.23188 | 1.9503 | 0.78519 | Persistent | 71.7025 | 2.4999 | Day | 202602 | 2026-02-11 | 2.4999
2026-02-11 10:40 | 72.3758 | FALSE | TRUE | -3.9713 | -5.8056 | 0.26211 | 0.36347 | 0.2808 |  | 2026-02-11 09:11 | upper | TRUE | 4 | 68.4045 | FALSE | TRUE | 0.6665 | 2.4462 | 70.2591 | 7 | 0.2808 | 0.12699 | 0.23318 | 0.65961 | 0.9273 | Confirmed/Materialized Shift | 72.1137 | 2.2827 | Day | 202602 | 2026-02-11 | 2.2827
2026-02-11 10:55 | 72.6584 | FALSE | TRUE | -4.3866 | -6.4251 | 0.12983 | 0.179 | 0.2826 |  | 2026-02-11 09:11 | upper | TRUE | 3 | 68.2718 | FALSE | TRUE | 0.6272 | 2.4057 | 70.4002 | 8 | 0.2826 | 0.14112 | 0.23364 | 0.60554 | 1.0642 | Confirmed/Materialized Shift | 72.5286 | 2.122 | Day | 202602 | 2026-02-11 | 2.122
2026-02-11 11:10 | 73.2236 | FALSE | TRUE | -5.1076 | -7.4985 | 0.20037 | 0.2744 | 0.5652 |  | 2026-02-11 09:11 | upper | TRUE | 3 | 68.116 | FALSE | TRUE | 0.6299 | 2.3787 | 70.5696 | 9 | 0.5652 | 0.16938 | 0.24933 | 1.5875 | 1.2268 | Confirmed/Materialized Shift | 73.0232 | 2.1633 | Day | 202602 | 2026-02-11 | 2.1633
2026-02-11 11:25 | 73.2236 | FALSE | TRUE | -5.1433 | -7.5548 | -0.20233 | -0.27556 | 0 |  | 2026-02-11 09:11 | none | FALSE | 2 | 68.0803 | FALSE | FALSE | 0.5804 | 2.3257 | 70.7531 | 10 | 0 | 0.18351 | 0.2296 | -0.79927 | 1.3364 | Confirmed/Materialized Shift | 73.4259 | 1.8486 | Day | 202602 | 2026-02-11 | 1.8486
2026-02-11 11:40 | 73.2236 | FALSE | TRUE | -5.1126 | -7.5063 | -0.53864 | -0.73023 | 0 |  | 2026-02-11 09:11 | none | FALSE | 2 | 68.111 | FALSE | FALSE | 0.5651 | 2.2615 | 70.9366 | 11 | 0 | 0.18351 | 0.2296 | -0.79927 | 1.4128 | Confirmed/Materialized Shift | 73.7622 | 1.6187 | Day | 202602 | 2026-02-11 | 1.6187
2026-02-11 11:55 | 72.941 | FALSE | TRUE | -4.7171 | -6.9141 | -1.0471 | -1.4152 | -0.2826 |  | 2026-02-11 09:11 | none | FALSE | 2 | 68.2239 | FALSE | FALSE | 0.542 | 2.1791 | 71.106 | 12 | -0.2826 | 0.16938 | 0.24933 | -1.8128 | 1.441 | Confirmed/Materialized Shift | 73.9881 | 1.2734 | Day | 202602 | 2026-02-11 | 1.2734
2026-02-11 12:10 | 72.941 | FALSE | TRUE | -4.5617 | -6.6711 | -1.2304 | -1.6589 | 0 |  | 2026-02-11 09:11 | none | FALSE | 1 | 68.3793 | FALSE | FALSE | 0.5053 | 2.1 | 71.2754 | 13 | 0 | 0.16938 | 0.24933 | -0.67934 | 1.448 | Confirmed/Materialized Shift | 74.1714 | 1.1503 | Day | 202602 | 2026-02-11 | 1.1503
2026-02-11 12:25 | 72.941 | FALSE | TRUE | -4.3644 | -6.3642 | -1.3719 | -1.8461 | 0 |  | 2026-02-11 09:11 | none | FALSE | 0 | 68.5766 | FALSE | FALSE | 0.4696 | 2.0245 | 71.4447 | 14 | 0 | 0.16938 | 0.24933 | -0.67934 | 1.4341 | Confirmed/Materialized Shift | 74.3129 | 1.0434 | Day | 202602 | 2026-02-11 | 1.0434
2026-02-11 12:39 | 72.941 | FALSE | FALSE | -4.1239 | -5.9926 | -1.4702 | -1.9757 | 0 |  |  | none | FALSE | 0 | 68.8171 | FALSE | FALSE | 0.0633 |  | 71.6141 | 0 | 0 | 0.16938 | 0.24933 | -0.67934 | 1.3985 | Persistence ends | 74.4112 | 0.94877 | Day | 202602 | 2026-02-11 | 0.94877
2026-02-11 12:54 | 72.941 | FALSE | FALSE | -3.8369 | -5.5524 | -1.5219 | -2.0439 | 0 |  |  | none | FALSE | 0 | 69.1041 | FALSE | FALSE | 0.0576 |  | 71.7835 | 0 | 0 | 0.16938 | 0.24933 | -0.67934 | 1.3397 | Normal | 74.4629 | 0.86399 | Day | 202602 | 2026-02-11 | 0.86399
2026-02-11 13:10 | 72.941 | FALSE | FALSE | -3.4968 | -5.0354 | -1.5206 | -2.0421 | 0 |  |  | none | FALSE | 0 | 69.4442 | FALSE | FALSE | 0.0525 |  | 71.9529 | 0 | 0 | 0.16938 | 0.24933 | -0.67934 | 1.2543 | Normal | 74.4616 | 0.78775 | Day | 202602 | 2026-02-11 | 0.78775
2026-02-11 13:25 | 72.941 | FALSE | FALSE | -3.1683 | -4.5408 | -1.5026 | -2.0184 | 0 |  |  | none | FALSE | 0 | 69.7727 | FALSE | FALSE | 0.0475 |  | 72.1081 | 0 | 0 | 0.15525 | 0.25058 | -0.61956 | 1.1677 | Normal | 74.4436 | 0.71324 | Day | 202602 | 2026-02-11 | 0.71324
2026-02-11 13:39 | 72.6584 | FALSE | FALSE | -2.4941 | -3.5547 | -1.6758 | -2.2545 | -0.2826 |  |  | none | FALSE | 0 | 70.1643 | FALSE | FALSE | 0.0262 |  | 72.2493 | 0 | -0.2826 | 0.14112 | 0.26721 | -1.5857 | 1.0425 | Normal | 74.3342 | 0.39246 | Day | 202602 | 2026-02-11 | 0.39246
2026-02-11 13:54 | 72.6584 | FALSE | FALSE | -2.1143 | -2.9971 | -1.5502 | -2.0889 | 0 |  |  | none | FALSE | 0 | 70.5441 | FALSE | FALSE | 0.0205 |  | 72.3763 | 0 | 0 | 0.12708 | 0.26686 | -0.4762 | 0.91612 | Normal | 74.2086 | 0.30789 | Day | 202602 | 2026-02-11 | 0.30789
2026-02-11 14:09 | 72.6584 | FALSE | FALSE | -1.7494 | -2.4671 | -1.4112 | -1.9052 | 0 |  |  | none | FALSE | 0 | 70.909 | FALSE | FALSE | 0.0143 |  | 72.4893 | 0 | 0 | 0.11295 | 0.26568 | -0.42514 | 0.79014 | Normal | 74.0696 | 0.21402 | Day | 202602 | 2026-02-11 | 0.21402
2026-02-11 14:24 | 72.941 | FALSE | FALSE | -1.5707 | -2.2008 | -0.92147 | -1.2475 | 0.2826 |  |  | none | FALSE | 0 | 71.3703 | FALSE | FALSE | 0.0347 |  | 72.6164 | 0 | 0.2826 | 0.12708 | 0.26686 | 0.58277 | 0.62305 | Normal | 73.8625 | 0.52103 | Day | 202602 | 2026-02-11 | 0.52103
2026-02-11 14:39 | 72.941 | FALSE | FALSE | -1.2053 | -1.6802 | -0.7537 | -1.0227 | 0 |  |  | none | FALSE | 0 | 71.7357 | FALSE | FALSE | 0.0307 |  | 72.7152 | 0 | 0 | 0.09882 | 0.24723 | -0.39971 | 0.48976 | Normal | 73.6947 | 0.46107 | Day | 202602 | 2026-02-11 | 0.46107
2026-02-11 14:54 | 72.941 | FALSE | FALSE | -0.96358 | -1.3387 | -0.65308 | -0.88741 | 0 |  |  | none | FALSE | 0 | 71.9774 | FALSE | FALSE | 0.0256 |  | 72.7857 | 0 | 0 | 0.07056 | 0.22215 | -0.31763 | 0.40417 | Normal | 73.5941 | 0.38413 | Day | 202602 | 2026-02-11 | 0.38413
2026-02-11 15:09 | 72.941 | FALSE | FALSE | -0.63734 | -0.88148 | -0.46796 | -0.63747 | 0 |  |  | none | FALSE | 0 | 72.3037 | FALSE | FALSE | 0.0204 |  | 72.8563 | 0 | 0 | 0.07056 | 0.22215 | -0.31763 | 0.27633 | Normal | 73.409 | 0.30649 | Day | 202602 | 2026-02-11 | 0.30649
2026-02-11 15:24 | 72.941 | FALSE | FALSE | -0.46355 | -0.63958 | -0.37877 | -0.51661 | 0 |  |  | none | FALSE | 0 | 72.4774 | FALSE | FALSE | 0.0134 |  | 72.8986 | 0 | 0 | 0.0423 | 0.18945 | -0.22327 | 0.21058 | Normal | 73.3198 | 0.2013 | Day | 202602 | 2026-02-11 | 0.2013
2026-02-11 15:38 | 72.941 | FALSE | FALSE | -0.35597 | -0.49041 | -0.32771 | -0.44727 | 0 |  |  | none | FALSE | 0 | 72.585 | FALSE | FALSE | 0.0055 |  | 72.9269 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.17092 | Normal | 73.2687 | 0.082671 | Day | 202602 | 2026-02-11 | 0.082671
2026-02-11 15:54 | 72.941 | FALSE | FALSE | -0.31761 | -0.43735 | -0.31761 | -0.43355 | 0 |  |  | none | FALSE | 0 | 72.6234 | FALSE | FALSE | 0 |  | 72.941 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.15881 | Normal | 73.2586 | 0 | Day | 202602 | 2026-02-11 | 0
2026-02-11 16:09 | 72.941 | FALSE | FALSE | -0.30262 | -0.41661 | -0.27436 | -0.37473 | 0 |  |  | none | FALSE | 0 | 72.6384 | FALSE | FALSE | 0.0065 |  | 72.9269 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14424 | Normal | 73.2154 | 0.097959 | Day | 202602 | 2026-02-11 | 0.097959
2026-02-11 16:24 | 72.6584 | TRUE | FALSE | -0.036377 | -0.05009 | -0.5168 | -0.70625 | -0.2826 |  |  | none | FALSE | 1 | 72.622 | FALSE | FALSE | 0.1444 |  | 72.8986 | 0 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.13829 | Normal | 73.1752 | -1.737 | Day | 202602 | 2026-02-11 | 1.737
2026-02-11 16:38 | 72.941 | TRUE | FALSE | -0.28847 | -0.39706 | -0.17543 | -0.23994 | 0.2826 |  |  | none | FALSE | 2 | 72.6525 | TRUE | FALSE | 0.0896 |  | 72.8845 | 0 | 0.2826 | -0.01413 | 0.14424 | 2.0571 | 0.11598 | Normal | 73.1164 | 0.48734 | Day | 202602 | 2026-02-11 | 0.48734
2026-02-11 16:53 | 72.6584 | FALSE | FALSE | -0.039147 | -0.053907 | -0.46305 | -0.63326 | -0.2826 |  |  | none | FALSE | 2 | 72.6193 | FALSE | FALSE | 0.1697 |  | 72.8704 | 0 | -0.2826 | -0.01413 | 0.14424 | -1.8612 | 0.12555 | Normal | 73.1214 | -1.6882 | Day | 202602 | 2026-02-11 | 1.6882
2026-02-11 17:08 | 72.6584 | FALSE | FALSE | -0.067916 | -0.09356 | -0.46356 | -0.63395 | 0 |  |  | none | FALSE | 2 | 72.5905 | FALSE | FALSE | 0.1564 |  | 72.8562 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.13287 | Normal | 73.122 | -1.4888 | Day | 202602 | 2026-02-11 | 1.4888
2026-02-11 17:23 | 72.3758 | FALSE | FALSE | 0.11403 | 0.15731 | -0.79029 | -1.0801 | -0.2826 | 2026-02-11 17:38 | 2026-02-11 17:23 | lower | TRUE | 2 | 72.4898 | FALSE | FALSE | 0.2926 | 2.6745 | 72.828 | 1 | -0.2826 | -0.02826 | 0.15614 | -1.6289 | 0.16906 | Extreme triggered | 73.1661 | -2.6745 | Day | 202602 | 2026-02-11 | 2.6745
2026-02-11 17:38 | 72.6584 | FALSE | FALSE | -0.18641 | -0.25721 | -0.49727 | -0.67974 | 0.2826 |  |  | none | FALSE | 2 | 72.472 | FALSE | FALSE | 0.1178 |  | 72.8138 | 0 | 0.2826 | -0.01413 | 0.17092 | 1.7361 | 0.17092 | Persistence ends | 73.1557 | -0.90938 | Day | 202602 | 2026-02-11 | 0.90938
2026-02-11 17:53 | 72.6584 | FALSE | FALSE | -0.20176 | -0.27846 | -0.48436 | -0.66222 | 0 |  |  | none | FALSE | 2 | 72.4566 | FALSE | FALSE | 0.1121 |  | 72.7997 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.17153 | Normal | 73.1428 | -0.82375 | Day | 202602 | 2026-02-11 | 0.82375
2026-02-11 18:08 | 72.3758 | FALSE | FALSE | 0.010989 | 0.015181 | -0.78029 | -1.0666 | -0.2826 | 2026-02-11 18:23 | 2026-02-11 18:08 | lower | TRUE | 2 | 72.3868 | FALSE | FALSE | 0.2514 | 2.0571 | 72.7714 | 1 | -0.2826 | -0.02826 | 0.18107 | -1.4047 | 0.19233 | Extreme triggered | 73.1561 | -2.0571 | Day | 202602 | 2026-02-11 | 2.0571
2026-02-11 18:23 | 72.941 | TRUE | FALSE | -0.55421 | -0.76562 | -0.21509 | -0.29402 | 0.5652 |  |  | none | FALSE | 3 | 72.3868 | TRUE | FALSE | 0.1445 |  | 72.7714 | 0 | 0.5652 | 0 | 0.22459 | 2.5166 | 0.19233 | Persistence ends | 73.1561 | 0.88163 | Night | 202602 | 2026-02-11 | 0.88163
2026-02-11 18:38 | 73.2236 | FALSE | FALSE | -0.85395 | -1.18 | -0.0061527 | -0.0084019 | 0.2826 |  |  | none | FALSE | 3 | 72.3696 | FALSE | FALSE | 0.2171 |  | 72.7997 | 0 | 0.2826 | 0.02826 | 0.22271 | 1.142 | 0.21503 | Normal | 73.2298 | 1.9714 | Night | 202602 | 2026-02-11 | 1.9714
2026-02-11 18:38 | 73.2236 | FALSE | FALSE | -0.85955 | -1.1878 | -0.068266 | -0.093143 | 0 |  |  | none | FALSE | 2 | 72.3641 | FALSE | FALSE | 0.1709 |  | 72.828 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.23195 | Normal | 73.2919 | 1.7057 | Night | 202602 | 2026-02-11 | 1.7057
2026-02-11 18:53 | 73.2236 | FALSE | FALSE | -0.856 | -1.1828 | -0.12124 | -0.1653 | 0 |  |  | none | FALSE | 1 | 72.3676 | FALSE | FALSE | 0.1288 |  | 72.8562 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.24431 | Normal | 73.3448 | 1.5038 | Night | 202602 | 2026-02-11 | 1.5038
2026-02-11 19:08 | 73.2236 | FALSE | FALSE | -0.86785 | -1.1994 | -0.16135 | -0.21986 | 0 |  |  | none | FALSE | 1 | 72.3558 | FALSE | FALSE | 0.1201 |  | 72.8704 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.2573 | Normal | 73.3849 | 1.3729 | Night | 202602 | 2026-02-11 | 1.3729
2026-02-11 19:23 | 73.5062 | FALSE | FALSE | -1.1954 | -1.6531 | 0.019788 | 0.026927 | 0.2826 | 2026-02-11 20:07 | 2026-02-11 19:23 | upper | TRUE | 1 | 72.3108 | FALSE | FALSE | 0.2235 | 2.0673 | 72.8986 | 1 | 0.2826 | 0.02826 | 0.22271 | 1.142 | 0.2939 | Extreme triggered | 73.4864 | 2.0673 | Night | 202602 | 2026-02-11 | 2.0673
2026-02-11 19:37 | 73.5062 | FALSE | FALSE | -1.227 | -1.6976 | -0.06835 | -0.092899 | 0 |  | 2026-02-11 19:23 | none | FALSE | 1 | 72.2792 | FALSE | FALSE | 0.2621 | 1.9281 | 72.9269 | 2 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.32384 | Extreme/elevated | 73.5746 | 1.7889 | Night | 202602 | 2026-02-11 | 1.7889
2026-02-11 19:52 | 73.5062 | FALSE | FALSE | -1.2487 | -1.7282 | -0.1466 | -0.19904 | 0 |  | 2026-02-11 19:23 | none | FALSE | 1 | 72.2575 | FALSE | FALSE | 0.3053 | 1.812 | 72.9551 | 3 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.34883 | Persistent | 73.6528 | 1.5797 | Night | 202602 | 2026-02-11 | 1.5797
2026-02-11 20:07 | 73.2236 | FALSE | FALSE | -0.96218 | -1.3315 | -0.4535 | -0.61552 | -0.2826 |  |  | none | FALSE | 1 | 72.2614 | FALSE | FALSE | 0.0765 |  | 72.9693 | 0 | -0.2826 | 0.01413 | 0.23331 | -1.2718 | 0.35392 | Persistence ends | 73.6771 | 0.71864 | Night | 202602 | 2026-02-11 | 0.71864
2026-02-11 20:22 | 73.2236 | FALSE | FALSE | -0.9569 | -1.3241 | -0.47648 | -0.64651 | 0 |  |  | none | FALSE | 1 | 72.2667 | FALSE | FALSE | 0.0733 |  | 72.9834 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.35834 | Normal | 73.7001 | 0.67033 | Night | 202602 | 2026-02-11 | 0.67033
2026-02-11 20:37 | 73.2236 | FALSE | FALSE | -0.95035 | -1.3149 | -0.49819 | -0.67578 | 0 |  |  | none | FALSE | 0 | 72.2732 | FALSE | FALSE | 0.0416 |  | 72.9975 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.36214 | Normal | 73.7218 | 0.62429 | Night | 202602 | 2026-02-11 | 0.62429
2026-02-11 20:52 | 72.941 | FALSE | FALSE | -0.66775 | -0.92393 | -0.78079 | -1.0591 | -0.2826 |  |  | none | FALSE | 0 | 72.2732 | FALSE | FALSE | 0.0104 |  | 72.9975 | 0 | -0.2826 | 0 | 0.24258 | -1.165 | 0.36214 | Normal | 73.7218 | -0.15607 | Night | 202602 | 2026-02-11 | 0.15607
2026-02-11 21:07 | 72.941 | FALSE | FALSE | -0.63659 | -0.88043 | -0.77789 | -1.0552 | 0 |  |  | none | FALSE | 0 | 72.3044 | FALSE | FALSE | 0.0133 |  | 73.0117 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.35362 | Normal | 73.7189 | -0.19979 | Night | 202602 | 2026-02-11 | 0.19979
2026-02-11 21:22 | 72.941 | FALSE | FALSE | -0.63659 | -0.88043 | -0.77789 | -1.0552 | 0 |  |  | none | FALSE | 0 | 72.3044 | FALSE | FALSE | 0.0133 |  | 73.0117 | 0 | 0 | 0 | 0.22459 | 0 | 0.35362 | Normal | 73.7189 | -0.19979 | Night | 202602 | 2026-02-11 | 0.19979
2026-02-11 21:37 | 72.6584 | FALSE | FALSE | -0.35399 | -0.48959 | -1.0605 | -1.4386 | -0.2826 |  |  | none | FALSE | 0 | 72.3044 | FALSE | FALSE | 0.0666 |  | 73.0117 | 0 | -0.2826 | 0 | 0.22459 | -1.2583 | 0.35362 | Normal | 73.7189 | -0.99895 | Night | 202602 | 2026-02-11 | 0.99895
2026-02-11 21:52 | 72.6584 | FALSE | FALSE | -0.35399 | -0.48959 | -1.0605 | -1.4386 | 0 |  |  | none | FALSE | 0 | 72.3044 | FALSE | FALSE | 0.0666 |  | 73.0117 | 0 | 0 | 0 | 0.22459 | 0 | 0.35362 | Normal | 73.7189 | -0.99895 | Night | 202602 | 2026-02-11 | 0.99895
2026-02-11 22:07 | 72.3758 | FALSE | FALSE | -0.071393 | -0.09874 | -1.3431 | -1.8219 | -0.2826 |  |  | none | FALSE | 0 | 72.3044 | FALSE | FALSE | 0.1199 |  | 73.0117 | 0 | -0.2826 | 0 | 0.22459 | -1.2583 | 0.35362 | Normal | 73.7189 | -1.7981 | Night | 202602 | 2026-02-11 | 1.7981
2026-02-11 22:22 | 72.3758 | FALSE | FALSE | -0.12541 | -0.17357 | -1.3688 | -1.8562 | 0 |  |  | none | FALSE | 0 | 72.2504 | FALSE | FALSE | 0.111 |  | 72.9975 | 0 | 0 | -0.01413 | 0.21454 | 0.065863 | 0.37356 | Normal | 73.7446 | -1.6643 | Night | 202602 | 2026-02-11 | 1.6643
2026-02-11 22:36 | 72.3758 | FALSE | FALSE | -0.17633 | -0.24422 | -1.3915 | -1.8863 | 0 |  |  | none | FALSE | 0 | 72.1995 | FALSE | FALSE | 0.1033 |  | 72.9834 | 0 | 0 | -0.01413 | 0.21454 | 0.065863 | 0.39196 | Normal | 73.7673 | -1.5501 | Night | 202602 | 2026-02-11 | 1.5501
2026-02-11 22:51 | 72.3758 | FALSE | FALSE | -0.17633 | -0.24422 | -1.3915 | -1.8863 | 0 |  |  | none | FALSE | 0 | 72.1995 | FALSE | FALSE | 0.1033 |  | 72.9834 | 0 | 0 | 0 | 0.20502 | 0 | 0.39196 | Normal | 73.7673 | -1.5501 | Night | 202602 | 2026-02-11 | 1.5501
2026-02-11 23:06 | 72.3758 | FALSE | FALSE | -0.25043 | -0.34721 | -1.4091 | -1.9097 | 0 |  |  | none | FALSE | 0 | 72.1254 | FALSE | FALSE | 0.0931 |  | 72.9551 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.41488 | Normal | 73.7849 | -1.3964 | Night | 202602 | 2026-02-11 | 1.3964
2026-02-11 23:22 | 72.3758 | FALSE | FALSE | -0.32121 | -0.44578 | -1.3951 | -1.8911 | 0 |  |  | none | FALSE | 0 | 72.0546 | FALSE | FALSE | 0.0834 |  | 72.9127 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.42907 | Normal | 73.7709 | -1.2514 | Night | 202602 | 2026-02-11 | 1.2514
2026-02-11 23:36 | 72.095 | FALSE | FALSE | -0.15708 | -0.21836 | -1.6797 | -2.2768 | -0.2808 |  |  | none | FALSE | 0 | 71.9379 | FALSE | FALSE | 0.1105 |  | 72.8563 | 0 | -0.2808 | -0.05643 | 0.1477 | -1.5191 | 0.4592 | Normal | 73.7747 | -1.6579 | Night | 202602 | 2026-02-11 | 1.6579
2026-02-11 23:51 | 72.095 | FALSE | FALSE | -0.25619 | -0.35662 | -1.666 | -2.2586 | 0 |  |  | none | FALSE | 0 | 71.8388 | FALSE | FALSE | 0.0978 |  | 72.7999 | 0 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.48054 | Normal | 73.761 | -1.4669 | Night | 202602 | 2026-02-11 | 1.4669
2026-02-12 00:06 | 72.095 | FALSE | FALSE | -0.34001 | -0.47385 | -1.6369 | -2.2201 | 0 |  |  | none | FALSE | 0 | 71.755 | FALSE | FALSE | 0.0875 |  | 72.7434 | 0 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.49423 | Normal | 73.7319 | -1.312 | Night | 202602 | 2026-02-12 | 1.312
2026-02-12 00:21 | 72.095 | FALSE | FALSE | -0.38239 | -0.53322 | -1.5382 | -2.089 | 0 |  |  | none | FALSE | 0 | 71.7126 | FALSE | FALSE | 0.0802 |  | 72.6729 | 0 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.48014 | Normal | 73.6332 | -1.2036 | Night | 202602 | 2026-02-12 | 1.2036
2026-02-12 00:36 | 71.8124 | FALSE | FALSE | -0.17374 | -0.24252 | -1.7253 | -2.3462 | -0.2826 |  |  | none | FALSE | 0 | 71.6387 | FALSE | FALSE | 0.1089 |  | 72.5882 | 0 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.47477 | Normal | 73.5377 | -1.6341 | Night | 202602 | 2026-02-12 | 1.6341
2026-02-12 00:51 | 71.8124 | FALSE | FALSE | -0.21482 | -0.30004 | -1.597 | -2.1755 | 0 |  |  | none | FALSE | 0 | 71.5976 | FALSE | FALSE | 0.1017 |  | 72.5035 | 0 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.45297 | Normal | 73.4094 | -1.5257 | Night | 202602 | 2026-02-12 | 1.5257
2026-02-12 01:06 | 71.8124 | FALSE | FALSE | -0.26891 | -0.37587 | -1.51 | -2.0594 | 0 |  |  | none | FALSE | 0 | 71.5435 | FALSE | FALSE | 0.093 |  | 72.433 | 0 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.44473 | Normal | 73.3224 | -1.3953 | Night | 202602 | 2026-02-12 | 1.3953
2026-02-12 01:21 | 71.5298 | FALSE | FALSE | -0.076561 | -0.10715 | -1.7135 | -2.3394 | -0.2826 |  |  | none | FALSE | 0 | 71.4532 | FALSE | FALSE | 0.1219 |  | 72.3483 | 0 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.44751 | Normal | 73.2433 | -1.8289 | Night | 202602 | 2026-02-12 | 1.8289
2026-02-12 01:35 | 71.5298 | FALSE | FALSE | -0.13259 | -0.18571 | -1.6001 | -2.1881 | 0 |  |  | none | FALSE | 0 | 71.3972 | FALSE | FALSE | 0.1129 |  | 72.2636 | 0 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.43318 | Normal | 73.1299 | -1.6939 | Night | 202602 | 2026-02-12 | 1.6939
2026-02-12 01:50 | 71.5298 | FALSE | FALSE | -0.20071 | -0.28138 | -1.5271 | -2.0903 | 0 |  |  | none | FALSE | 0 | 71.3291 | FALSE | FALSE | 0.1024 |  | 72.193 | 0 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.43196 | Normal | 73.0569 | -1.5354 | Night | 202602 | 2026-02-12 | 1.5354
2026-02-12 02:06 | 71.2472 | FALSE | FALSE | -0.025839 | -0.036279 | -1.7481 | -2.3948 | -0.2826 |  |  | none | FALSE | 0 | 71.2214 | FALSE | FALSE | 0.1294 |  | 72.1083 | 0 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.44348 | Normal | 72.9953 | -1.9417 | Night | 202602 | 2026-02-12 | 1.9417
2026-02-12 02:21 | 71.2472 | FALSE | FALSE | -0.099148 | -0.13936 | -1.652 | -2.2662 | 0 |  |  | none | FALSE | 0 | 71.1481 | FALSE | FALSE | 0.1182 |  | 72.0236 | 0 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.43779 | Normal | 72.8992 | -1.7735 | Night | 202602 | 2026-02-12 | 1.7735
2026-02-12 02:35 | 70.9646 | FALSE | FALSE | 0.032149 | 0.045282 | -1.9165 | -2.6297 | -0.2826 | 2026-02-12 08:04 | 2026-02-12 02:35 | lower | TRUE | 0 | 70.9967 | FALSE | FALSE | 0.195 | 2.0682 | 71.9389 | 1 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.4711 | Extreme triggered | 72.8811 | -2.0682 | Night | 202602 | 2026-02-12 | 2.0682
2026-02-12 02:50 | 70.9646 | FALSE | FALSE | -0.084215 | -0.11881 | -1.8635 | -2.5588 | 0 |  | 2026-02-12 02:35 | none | FALSE | 0 | 70.8804 | FALSE | FALSE | 0.2361 | 1.9476 | 71.8542 | 2 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.48693 | Extreme/elevated | 72.8281 | -1.8271 | Night | 202602 | 2026-02-12 | 1.8271
2026-02-12 03:05 | 70.9646 | FALSE | FALSE | -0.19915 | -0.28142 | -1.8373 | -2.5237 | 0 |  | 2026-02-12 02:35 | none | FALSE | 0 | 70.7655 | FALSE | FALSE | 0.2787 | 1.8347 | 71.7837 | 3 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.50912 | Persistent | 72.8019 | -1.6088 | Night | 202602 | 2026-02-12 | 1.6088
2026-02-12 03:20 | 70.682 | FALSE | FALSE | -0.073102 | -0.10353 | -2.1071 | -2.8948 | -0.2826 |  | 2026-02-12 02:35 | none | FALSE | 0 | 70.6089 | FALSE | FALSE | 0.353 | 1.8425 | 71.699 | 4 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.54505 | Persistent | 72.7891 | -1.8659 | Night | 202602 | 2026-02-12 | 1.8659
2026-02-12 03:35 | 70.682 | FALSE | FALSE | -0.19881 | -0.28207 | -2.0634 | -2.8365 | 0 |  | 2026-02-12 02:35 | none | FALSE | 0 | 70.4832 | FALSE | FALSE | 0.3956 | 1.8037 | 71.6143 | 5 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.56556 | Persistent | 72.7454 | -1.6485 | Night | 202602 | 2026-02-12 | 1.6485
2026-02-12 03:50 | 70.682 | FALSE | FALSE | -0.297 | -0.42196 | -1.9922 | -2.7413 | 0 |  | 2026-02-12 02:35 | none | FALSE | 0 | 70.385 | FALSE | FALSE | 0.4416 | 1.7499 | 71.5296 | 6 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.57231 | Persistent | 72.6742 | -1.4811 | Night | 202602 | 2026-02-12 | 1.4811
2026-02-12 04:05 | 70.3994 | FALSE | TRUE | -0.1464 | -0.20839 | -2.2092 | -3.0426 | -0.2826 |  | 2026-02-12 02:35 | none | FALSE | 0 | 70.253 | FALSE | FALSE | 0.5168 | 1.7501 | 71.4308 | 7 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.5889 | Confirmed/Materialized Shift | 72.6086 | -1.7514 | Night | 202602 | 2026-02-12 | 1.7514
2026-02-12 04:20 | 70.3994 | FALSE | TRUE | -0.24302 | -0.3464 | -2.1082 | -2.9075 | 0 |  | 2026-02-12 02:35 | none | FALSE | 0 | 70.1564 | FALSE | FALSE | 0.5058 | 1.7297 | 71.332 | 8 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.5878 | Confirmed/Materialized Shift | 72.5076 | -1.5866 | Night | 202602 | 2026-02-12 | 1.5866
2026-02-12 04:35 | 70.3994 | FALSE | TRUE | -0.34061 | -0.48617 | -2.0362 | -2.8111 | 0 |  | 2026-02-12 02:35 | none | FALSE | 0 | 70.0588 | FALSE | FALSE | 0.4951 | 1.696 | 71.2472 | 9 | 0 | -0.08478 | 0.13287 | 0.63808 | 0.5942 | Confirmed/Materialized Shift | 72.4356 | -1.4268 | Night | 202602 | 2026-02-12 | 1.4268
2026-02-12 04:50 | 70.1168 | FALSE | TRUE | -0.18868 | -0.26982 | -2.2517 | -3.1114 | -0.2826 |  | 2026-02-12 02:35 | none | FALSE | 0 | 69.9281 | FALSE | FALSE | 0.5127 | 1.6955 | 71.1483 | 10 | -0.2826 | -0.09891 | 0.13829 | -1.3283 | 0.61008 | Confirmed/Materialized Shift | 72.3685 | -1.6907 | Night | 202602 | 2026-02-12 | 1.6907
2026-02-12 05:05 | 70.1168 | FALSE | TRUE | -0.28517 | -0.40837 | -2.1503 | -2.9755 | 0 |  | 2026-02-12 02:35 | none | FALSE | 0 | 69.8316 | FALSE | FALSE | 0.5021 | 1.6806 | 71.0494 | 11 | 0 | -0.09891 | 0.13829 | 0.71522 | 0.60888 | Confirmed/Materialized Shift | 72.2671 | -1.5316 | Night | 202602 | 2026-02-12 | 1.5316
2026-02-12 05:20 | 70.1168 | FALSE | TRUE | -0.34729 | -0.49776 | -2.0146 | -2.793 | 0 |  | 2026-02-12 02:35 | none | FALSE | 0 | 69.7695 | FALSE | FALSE | 0.4941 | 1.6582 | 70.9505 | 12 | 0 | -0.09891 | 0.13829 | 0.71522 | 0.59048 | Confirmed/Materialized Shift | 72.1314 | -1.4119 | Night | 202602 | 2026-02-12 | 1.4119
2026-02-12 05:34 | 70.1168 | FALSE | TRUE | -0.41486 | -0.59519 | -1.9126 | -2.6554 | 0 |  | 2026-02-12 02:35 | none | FALSE | 0 | 69.7019 | FALSE | FALSE | 0.4858 | 1.6297 | 70.8657 | 13 | 0 | -0.08478 | 0.13287 | 0.63808 | 0.58187 | Confirmed/Materialized Shift | 72.0294 | -1.287 | Night | 202602 | 2026-02-12 | 1.287
2026-02-12 05:49 | 70.1168 | FALSE | TRUE | -0.45545 | -0.65381 | -1.7837 | -2.4808 | 0 |  | 2026-02-12 02:35 | none | FALSE | 0 | 69.6613 | FALSE | FALSE | 0.4791 | 1.598 | 70.7809 | 14 | 0 | -0.08478 | 0.13287 | 0.63808 | 0.55978 | Confirmed/Materialized Shift | 71.9005 | -1.1864 | Night | 202602 | 2026-02-12 | 1.1864
2026-02-12 06:04 | 69.836 | FALSE | TRUE | -0.23848 | -0.34265 | -1.9307 | -2.6902 | -0.2808 |  | 2026-02-12 02:35 | none | FALSE | 0 | 69.5975 | FALSE | FALSE | 0.504 | 1.5955 | 70.6821 | 15 | -0.2808 | -0.09882 | 0.13817 | -1.3171 | 0.54228 | Confirmed/Materialized Shift | 71.7667 | -1.5602 | Night | 202602 | 2026-02-12 | 1.5602
2026-02-12 06:19 | 69.836 | FALSE | TRUE | -0.30888 | -0.44426 | -1.8317 | -2.5558 | 0 |  | 2026-02-12 02:35 | none | FALSE | 0 | 69.5271 | FALSE | FALSE | 0.4949 | 1.5847 | 70.5974 | 16 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.53514 | Confirmed/Materialized Shift | 71.6677 | -1.4228 | Night | 202602 | 2026-02-12 | 1.4228
2026-02-12 06:34 | 69.836 | FALSE | TRUE | -0.3501 | -0.50384 | -1.7035 | -2.3812 | 0 |  | 2026-02-12 02:35 | none | FALSE | 0 | 69.4859 | FALSE | FALSE | 0.4879 | 1.569 | 70.5127 | 17 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.5134 | Confirmed/Materialized Shift | 71.5395 | -1.3181 | Night | 202602 | 2026-02-12 | 1.3181
2026-02-12 06:49 | 69.836 | FALSE | TRUE | -0.35811 | -0.51544 | -1.5422 | -2.1605 | 0 |  | 2026-02-12 02:35 | none | FALSE | 0 | 69.4779 | FALSE | FALSE | 0.4831 | 1.5511 | 70.428 | 18 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.47507 | Confirmed/Materialized Shift | 71.3782 | -1.2462 | Night | 202602 | 2026-02-12 | 1.2462
2026-02-12 07:04 | 69.5534 | FALSE | TRUE | -0.1547 | -0.22291 | -1.7346 | -2.4332 | -0.2826 |  | 2026-02-12 02:35 | none | FALSE | 0 | 69.3987 | FALSE | FALSE | 0.5115 | 1.5575 | 70.3433 | 19 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.47231 | Confirmed/Materialized Shift | 71.288 | -1.6725 | Day | 202602 | 2026-02-12 | 1.6725
2026-02-12 07:19 | 69.5534 | FALSE | TRUE | -0.20112 | -0.29 | -1.6116 | -2.2646 | 0 |  | 2026-02-12 02:35 | none | FALSE | 0 | 69.3523 | FALSE | FALSE | 0.5037 | 1.5574 | 70.2586 | 20 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.45318 | Confirmed/Materialized Shift | 71.165 | -1.5562 | Day | 202602 | 2026-02-12 | 1.5562
2026-02-12 07:34 | 69.5534 | FALSE | TRUE | -0.25992 | -0.37511 | -1.5293 | -2.1514 | 0 |  | 2026-02-12 02:35 | none | FALSE | 0 | 69.2935 | FALSE | FALSE | 0.4946 | 1.5508 | 70.1881 | 21 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.4473 | Confirmed/Materialized Shift | 71.0827 | -1.4189 | Day | 202602 | 2026-02-12 | 1.4189
2026-02-12 07:49 | 69.5534 | FALSE | TRUE | -0.29449 | -0.4252 | -1.4227 | -2.0045 | 0 |  | 2026-02-12 02:35 | none | FALSE | 0 | 69.2589 | FALSE | FALSE | 0.4876 | 1.54 | 70.1175 | 22 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.42931 | Confirmed/Materialized Shift | 70.9761 | -1.314 | Day | 202602 | 2026-02-12 | 1.314
2026-02-12 07:49 | 69.5534 | FALSE | TRUE | -0.30154 | -0.43543 | -1.2887 | -1.8191 | 0 |  | 2026-02-12 02:35 | none | FALSE | 0 | 69.2519 | FALSE | FALSE | 0.4828 | 1.5271 | 70.047 | 23 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.39755 | Confirmed/Materialized Shift | 70.8421 | -1.2415 | Day | 202602 | 2026-02-12 | 1.2415
2026-02-12 08:04 | 69.836 | TRUE | FALSE | -0.57237 | -0.82636 | -0.90969 | -1.2859 | 0.2826 |  |  | none | FALSE | 1 | 69.2636 | FALSE | FALSE | 0.0589 |  | 70.0047 | 0 | 0.2826 | -0.0423 | 0.13813 | 2.3521 | 0.37051 | Persistence ends | 70.7457 | -0.45521 | Day | 202602 | 2026-02-12 | 0.45521
2026-02-12 08:19 | 69.836 | FALSE | FALSE | -0.5452 | -0.78682 | -0.79792 | -1.1297 | 0 |  |  | none | FALSE | 1 | 69.2908 | FALSE | FALSE | 0.0537 |  | 69.9624 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.33578 | Normal | 70.6339 | -0.37632 | Day | 202602 | 2026-02-12 | 0.37632
2026-02-12 08:34 | 69.836 | FALSE | FALSE | -0.49714 | -0.71697 | -0.66526 | -0.94361 | 0 |  |  | none | FALSE | 1 | 69.3389 | FALSE | FALSE | 0.0479 |  | 69.9201 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.2906 | Normal | 70.5013 | -0.28927 | Day | 202602 | 2026-02-12 | 0.28927
2026-02-12 08:48 | 69.836 | FALSE | FALSE | -0.48036 | -0.6926 | -0.59214 | -0.84077 | 0 |  |  | none | FALSE | 1 | 69.3556 | FALSE | FALSE | 0.0425 |  | 69.8919 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.26812 | Normal | 70.4281 | -0.20845 | Day | 202602 | 2026-02-12 | 0.20845
2026-02-12 08:48 | 69.836 | FALSE | FALSE | -0.45254 | -0.65224 | -0.50798 | -0.72214 | 0 |  |  | none | FALSE | 1 | 69.3835 | FALSE | FALSE | 0.0363 |  | 69.8637 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.24013 | Normal | 70.344 | -0.11544 | Day | 202602 | 2026-02-12 | 0.11544
2026-02-12 09:04 | 70.1168 | TRUE | FALSE | -0.69486 | -1.0009 | -0.16044 | -0.2283 | 0.2808 |  |  | none | FALSE | 2 | 69.4219 | TRUE | FALSE | 0.1405 |  | 69.8496 | 0 | 0.2808 | -0.01413 | 0.14387 | 2.0499 | 0.21383 | Normal | 70.2772 | 1.2497 | Day | 202602 | 2026-02-12 | 1.2497
2026-02-12 09:19 | 70.3994 | FALSE | FALSE | -1.0159 | -1.4642 | 0.055415 | 0.078777 | 0.2826 | 2026-02-12 13:02 | 2026-02-12 09:19 | upper | TRUE | 2 | 69.3835 | FALSE | FALSE | 0.263 | 2.2308 | 69.8637 | 1 | 0.2826 | 0.01413 | 0.14387 | 1.866 | 0.24013 | Extreme triggered | 70.344 | 2.2308 | Day | 202602 | 2026-02-12 | 2.2308
2026-02-12 09:34 | 70.3994 | FALSE | FALSE | -1.0476 | -1.5106 | -0.0045116 | -0.0064082 | 0 |  | 2026-02-12 09:19 | none | FALSE | 2 | 69.3518 | FALSE | FALSE | 0.3036 | 2.1068 | 69.8778 | 2 | 0 | 0.01413 | 0.14387 | -0.098211 | 0.26303 | Extreme/elevated | 70.4039 | 1.9828 | Day | 202602 | 2026-02-12 | 1.9828
2026-02-12 09:48 | 70.9646 | TRUE | FALSE | -1.7556 | -2.5366 | 0.33317 | 0.4717 | 0.5652 |  | 2026-02-12 09:19 | upper | TRUE | 3 | 69.209 | TRUE | TRUE | 0.4529 | 2.3835 | 69.9202 | 3 | 0.5652 | 0.04239 | 0.18929 | 2.7619 | 0.3556 | Persistent | 70.6314 | 2.9369 | Day | 202602 | 2026-02-12 | 2.9369
2026-02-12 10:03 | 71.2472 | FALSE | FALSE | -2.1951 | -3.1788 | 0.34583 | 0.48776 | 0.2826 |  | 2026-02-12 09:19 | upper | TRUE | 3 | 69.0521 | FALSE | TRUE | 0.4975 | 2.4747 | 69.9768 | 4 | 0.2826 | 0.05652 | 0.19638 | 1.1513 | 0.46231 | Persistent | 70.9014 | 2.7481 | Day | 202602 | 2026-02-12 | 2.7481
2026-02-12 10:18 | 71.8124 | TRUE | FALSE | -2.9878 | -4.3411 | 0.51397 | 0.72087 | 0.5652 |  | 2026-02-12 09:19 | upper | TRUE | 3 | 68.8246 | TRUE | TRUE | 0.5602 | 2.5459 | 70.0615 | 5 | 0.5652 | 0.08478 | 0.22622 | 2.1237 | 0.61845 | Persistent | 71.2984 | 2.8311 | Day | 202602 | 2026-02-12 | 2.8311
2026-02-12 10:33 | 72.095 | FALSE | FALSE | -3.4489 | -5.0242 | 0.39212 | 0.54686 | 0.2826 |  | 2026-02-12 09:19 | upper | TRUE | 3 | 68.6461 | FALSE | TRUE | 0.5961 | 2.5405 | 70.1745 | 6 | 0.2826 | 0.11295 | 0.21299 | 0.79653 | 0.7642 | Persistent | 71.7029 | 2.5131 | Day | 202602 | 2026-02-12 | 2.5131
2026-02-12 10:48 | 72.3758 | FALSE | TRUE | -3.881 | -5.6661 | 0.26763 | 0.37115 | 0.2808 |  | 2026-02-12 09:19 | upper | TRUE | 3 | 68.4948 | FALSE | TRUE | 0.6388 | 2.5056 | 70.3015 | 7 | 0.2808 | 0.12699 | 0.2144 | 0.7174 | 0.90335 | Confirmed/Materialized Shift | 72.1082 | 2.2963 | Day | 202602 | 2026-02-12 | 2.2963
2026-02-12 11:03 | 72.6584 | FALSE | TRUE | -4.2904 | -6.2755 | 0.14116 | 0.19465 | 0.2826 |  | 2026-02-12 09:19 | upper | TRUE | 3 | 68.368 | FALSE | TRUE | 0.6281 | 2.4594 | 70.4426 | 8 | 0.2826 | 0.14112 | 0.2149 | 0.65834 | 1.0373 | Confirmed/Materialized Shift | 72.5172 | 2.1361 | Day | 202602 | 2026-02-12 | 2.1361
2026-02-12 11:18 | 72.941 | FALSE | TRUE | -4.6754 | -6.8488 | 0.010918 | 0.01497 | 0.2826 |  | 2026-02-12 09:19 | upper | TRUE | 3 | 68.2656 | FALSE | TRUE | 0.6197 | 2.4094 | 70.5978 | 9 | 0.2826 | 0.15525 | 0.21443 | 0.59391 | 1.1661 | Confirmed/Materialized Shift | 72.9301 | 2.0094 | Day | 202602 | 2026-02-12 | 2.0094
2026-02-12 11:33 | 73.2236 | FALSE | TRUE | -4.9955 | -7.3218 | -0.11106 | -0.15144 | 0.2826 |  | 2026-02-12 09:19 | none | FALSE | 2 | 68.2281 | FALSE | FALSE | 0.5847 | 2.3597 | 70.7814 | 10 | 0.2826 | 0.18351 | 0.18948 | 0.52297 | 1.2767 | Confirmed/Materialized Shift | 73.3347 | 1.913 | Day | 202602 | 2026-02-12 | 1.913
2026-02-12 11:47 | 73.5062 | FALSE | TRUE | -5.2841 | -7.7454 | -0.22971 | -0.31152 | 0.2826 |  | 2026-02-12 09:19 | none | FALSE | 2 | 68.2221 | FALSE | FALSE | 0.5794 | 2.3119 | 70.979 | 11 | 0.2826 | 0.19764 | 0.18557 | 0.45784 | 1.3785 | Confirmed/Materialized Shift | 73.7359 | 1.8334 | Day | 202602 | 2026-02-12 | 1.8334
2026-02-12 12:02 | 73.2236 | TRUE | TRUE | -4.9057 | -7.1806 | -0.78348 | -1.0586 | -0.2826 |  | 2026-02-12 09:19 | none | FALSE | 3 | 68.3179 | TRUE | FALSE | 0.5823 | 2.24 | 71.1625 | 12 | -0.2826 | 0.18351 | 0.21049 | -2.2144 | 1.4223 | Confirmed/Materialized Shift | 74.0071 | 1.4491 | Day | 202602 | 2026-02-12 | 1.4491
2026-02-12 12:17 | 73.2236 | FALSE | TRUE | -4.7584 | -6.9501 | -1.0032 | -1.3516 | 0 |  | 2026-02-12 09:19 | none | FALSE | 2 | 68.4652 | FALSE | FALSE | 0.544 | 2.168 | 71.346 | 13 | 0 | 0.18351 | 0.21049 | -0.87181 | 1.4404 | Confirmed/Materialized Shift | 74.2268 | 1.3035 | Day | 202602 | 2026-02-12 | 1.3035
2026-02-12 12:33 | 72.941 | FALSE | TRUE | -4.2606 | -6.2035 | -1.4094 | -1.8956 | -0.2826 |  | 2026-02-12 09:19 | none | FALSE | 2 | 68.6804 | FALSE | FALSE | 0.5242 | 2.0849 | 71.5154 | 14 | -0.2826 | 0.16938 | 0.23186 | -1.9494 | 1.4175 | Confirmed/Materialized Shift | 74.3504 | 1.0057 | Day | 202602 | 2026-02-12 | 1.0057
2026-02-12 12:47 | 73.2236 | FALSE | TRUE | -4.3561 | -6.3253 | -1.2784 | -1.716 | 0.2826 |  | 2026-02-12 09:19 | none | FALSE | 1 | 68.8675 | FALSE | FALSE | 0.5014 | 2.0188 | 71.6848 | 15 | 0.2826 | 0.16938 | 0.23186 | 0.48831 | 1.4086 | Confirmed/Materialized Shift | 74.502 | 1.0924 | Day | 202602 | 2026-02-12 | 1.0924
2026-02-12 13:02 | 73.2236 | FALSE | FALSE | -4.1254 | -5.9703 | -1.3865 | -1.8583 | 0 |  |  | none | FALSE | 1 | 69.0982 | FALSE | FALSE | 0.0948 |  | 71.8542 | 0 | 0 | 0.16938 | 0.23186 | -0.73052 | 1.378 | Persistence ends | 74.6101 | 0.99381 | Day | 202602 | 2026-02-12 | 0.99381
2026-02-12 13:17 | 73.5062 | FALSE | FALSE | -4.1463 | -5.9779 | -1.2092 | -1.6185 | 0.2826 |  |  | none | FALSE | 1 | 69.3599 | FALSE | FALSE | 0.1017 |  | 72.0377 | 0 | 0.2826 | 0.18351 | 0.2296 | 0.43158 | 1.3389 | Normal | 74.7154 | 1.0968 | Day | 202602 | 2026-02-12 | 1.0968
2026-02-12 13:32 | 73.5062 | FALSE | FALSE | -3.8271 | -5.4925 | -1.2571 | -1.6814 | 0 |  |  | none | FALSE | 1 | 69.6791 | FALSE | FALSE | 0.096 |  | 72.2212 | 0 | 0 | 0.18351 | 0.2296 | -0.79927 | 1.271 | Normal | 74.7633 | 1.011 | Day | 202602 | 2026-02-12 | 1.011
2026-02-12 13:47 | 73.5062 | FALSE | FALSE | -3.4404 | -4.9102 | -1.2374 | -1.6555 | 0 |  |  | none | FALSE | 1 | 70.0658 | FALSE | FALSE | 0.0914 |  | 72.4047 | 0 | 0 | 0.18351 | 0.2296 | -0.79927 | 1.1694 | Normal | 74.7436 | 0.94192 | Day | 202602 | 2026-02-12 | 0.94192
2026-02-12 14:02 | 73.2236 | FALSE | FALSE | -2.7631 | -3.9214 | -1.4359 | -1.9233 | -0.2826 |  |  | none | FALSE | 1 | 70.4605 | FALSE | FALSE | 0.0707 |  | 72.56 | 0 | -0.2826 | 0.15534 | 0.25063 | -1.7474 | 1.0498 | Normal | 74.6595 | 0.63212 | Day | 202602 | 2026-02-12 | 0.63212
2026-02-12 14:17 | 73.2236 | FALSE | FALSE | -2.3754 | -3.3528 | -1.3307 | -1.7849 | 0 |  |  | none | FALSE | 1 | 70.8482 | FALSE | FALSE | 0.0662 |  | 72.7012 | 0 | 0 | 0.14121 | 0.25104 | -0.56249 | 0.92653 | Normal | 74.5543 | 0.56378 | Day | 202602 | 2026-02-12 | 0.56378
2026-02-12 14:32 | 73.2236 | FALSE | FALSE | -1.895 | -2.6568 | -1.1327 | -1.5234 | 0 |  |  | none | FALSE | 0 | 71.3286 | FALSE | FALSE | 0.0336 |  | 72.8424 | 0 | 0 | 0.14121 | 0.25104 | -0.56249 | 0.75694 | Normal | 74.3563 | 0.50354 | Day | 202602 | 2026-02-12 | 0.50354
2026-02-12 14:46 | 73.2236 | FALSE | FALSE | -1.5037 | -2.0966 | -0.96725 | -1.3037 | 0 |  |  | none | FALSE | 0 | 71.7199 | FALSE | FALSE | 0.0289 |  | 72.9554 | 0 | 0 | 0.11295 | 0.23188 | -0.4871 | 0.61773 | Normal | 74.1909 | 0.43417 | Day | 202602 | 2026-02-12 | 0.43417
2026-02-12 15:02 | 73.2236 | FALSE | FALSE | -1.1107 | -1.5402 | -0.77193 | -1.0432 | 0 |  |  | none | FALSE | 0 | 72.1129 | FALSE | FALSE | 0.024 |  | 73.0542 | 0 | 0 | 0.09882 | 0.2296 | -0.4304 | 0.47066 | Normal | 73.9955 | 0.35988 | Day | 202602 | 2026-02-12 | 0.35988
2026-02-12 15:17 | 73.2236 | FALSE | FALSE | -0.83807 | -1.1578 | -0.64043 | -0.86704 | 0 |  |  | none | FALSE | 0 | 72.3855 | FALSE | FALSE | 0.0178 |  | 73.1248 | 0 | 0 | 0.07056 | 0.20234 | -0.34872 | 0.36962 | Normal | 73.864 | 0.26735 | Day | 202602 | 2026-02-12 | 0.26735
2026-02-12 15:32 | 73.2236 | FALSE | FALSE | -0.60086 | -0.82737 | -0.51608 | -0.69986 | 0 |  |  | none | FALSE | 0 | 72.6227 | FALSE | FALSE | 0.0101 |  | 73.1812 | 0 | 0 | 0.05643 | 0.19654 | -0.28712 | 0.27923 | Normal | 73.7397 | 0.15181 | Day | 202602 | 2026-02-12 | 0.15181
2026-02-12 15:46 | 73.2236 | FALSE | FALSE | -0.41004 | -0.56314 | -0.41004 | -0.55686 | 0 |  |  | none | FALSE | 0 | 72.8136 | FALSE | FALSE | 0 |  | 73.2236 | 0 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.20502 | Normal | 73.6336 | 0 | Day | 202602 | 2026-02-12 | 0
2026-02-12 16:01 | 73.2236 | FALSE | FALSE | -0.28402 | -0.38939 | -0.34054 | -0.46291 | 0 |  |  | none | FALSE | 0 | 72.9396 | FALSE | FALSE | 0.0121 |  | 73.2519 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.15614 | Normal | 73.5641 | -0.18099 | Day | 202602 | 2026-02-12 | 0.18099
2026-02-12 16:16 | 73.2236 | FALSE | FALSE | -0.2342 | -0.32086 | -0.31898 | -0.43373 | 0 |  |  | none | FALSE | 0 | 72.9894 | FALSE | FALSE | 0.0204 |  | 73.266 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.13829 | Normal | 73.5426 | -0.30652 | Day | 202602 | 2026-02-12 | 0.30652
2026-02-12 16:31 | 73.2236 | FALSE | FALSE | -0.2342 | -0.32086 | -0.31898 | -0.43373 | 0 |  |  | none | FALSE | 0 | 72.9894 | FALSE | FALSE | 0.0204 |  | 73.266 | 0 | 0 | 0 | 0.15881 | 0 | 0.13829 | Normal | 73.5426 | -0.30652 | Day | 202602 | 2026-02-12 | 0.30652
2026-02-12 16:46 | 73.2236 | FALSE | FALSE | -0.22451 | -0.30755 | -0.28103 | -0.38232 | 0 |  |  | none | FALSE | 0 | 72.9991 | FALSE | FALSE | 0.0149 |  | 73.2519 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.12638 | Normal | 73.5046 | -0.22361 | Day | 202602 | 2026-02-12 | 0.22361
2026-02-12 17:01 | 73.2236 | FALSE | FALSE | -0.22451 | -0.30755 | -0.28103 | -0.38232 | 0 |  |  | none | FALSE | 0 | 72.9991 | FALSE | FALSE | 0.0149 |  | 73.2519 | 0 | 0 | 0 | 0.12967 | 0 | 0.12638 | Normal | 73.5046 | -0.22361 | Day | 202602 | 2026-02-12 | 0.22361
2026-02-12 17:16 | 72.941 | FALSE | FALSE | 0.0082419 | 0.011298 | -0.58522 | -0.79593 | -0.2826 | 2026-02-12 19:01 | 2026-02-12 17:16 | lower | TRUE | 0 | 72.9492 | FALSE | FALSE | 0.1943 | 2.0571 | 73.2377 | 1 | -0.2826 | -0.01413 | 0.14424 | -1.8612 | 0.14424 | Extreme triggered | 73.5262 | -2.0571 | Day | 202602 | 2026-02-12 | 2.0571
2026-02-12 17:31 | 72.941 | FALSE | FALSE | 0.0082419 | 0.011298 | -0.58522 | -0.79593 | 0 |  | 2026-02-12 17:16 | lower | TRUE | 0 | 72.9492 | FALSE | FALSE | 0.2514 | 2.0571 | 73.2377 | 2 | 0 | 0 | 0.12967 | 0 | 0.14424 | Extreme/elevated | 73.5262 | -2.0571 | Day | 202602 | 2026-02-12 | 2.0571
2026-02-12 17:46 | 72.941 | FALSE | FALSE | -0.035015 | -0.048028 | -0.60021 | -0.81616 | 0 |  | 2026-02-12 17:16 | none | FALSE | 0 | 72.906 | FALSE | FALSE | 0.2901 | 1.9646 | 73.2236 | 3 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.15881 | Persistent | 73.5412 | -1.7795 | Day | 202602 | 2026-02-12 | 1.7795
2026-02-12 18:01 | 72.941 | FALSE | FALSE | -0.073366 | -0.10068 | -0.61031 | -0.82977 | 0 |  | 2026-02-12 17:16 | none | FALSE | 0 | 72.8676 | FALSE | FALSE | 0.3333 | 1.8661 | 73.2095 | 4 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.17092 | Persistent | 73.5513 | -1.5708 | Day | 202602 | 2026-02-12 | 1.5708
2026-02-12 18:16 | 72.6584 | TRUE | FALSE | 0.11538 | 0.15855 | -0.90198 | -1.2262 | -0.2826 |  | 2026-02-12 17:16 | lower | TRUE | 1 | 72.7738 | FALSE | TRUE | 0.4867 | 2.0103 | 73.1671 | 5 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.19665 | Persistent | 73.5604 | -2.5868 | Night | 202602 | 2026-02-12 | 2.5868
2026-02-12 18:30 | 72.6584 | FALSE | FALSE | 0.045126 | 0.062068 | -0.88745 | -1.2067 | 0 |  | 2026-02-12 17:16 | lower | TRUE | 1 | 72.7035 | FALSE | TRUE | 0.519 | 2.0443 | 73.1247 | 6 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.21058 | Persistent | 73.5459 | -2.2143 | Night | 202602 | 2026-02-12 | 2.2143
2026-02-12 18:31 | 72.6584 | FALSE | TRUE | -0.0061527 | -0.0084687 | -0.85395 | -1.1616 | 0 |  | 2026-02-12 17:16 | none | FALSE | 1 | 72.6522 | FALSE | FALSE | 0.56 | 2.0339 | 73.0823 | 7 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.21503 | Confirmed/Materialized Shift | 73.5124 | -1.9714 | Night | 202602 | 2026-02-12 | 1.9714
2026-02-12 18:46 | 72.6584 | FALSE | TRUE | -0.068266 | -0.094044 | -0.85955 | -1.1692 | 0 |  | 2026-02-12 17:16 | none | FALSE | 1 | 72.5901 | FALSE | FALSE | 0.5423 | 1.9928 | 73.054 | 8 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.23195 | Confirmed/Materialized Shift | 73.5179 | -1.7057 | Night | 202602 | 2026-02-12 | 1.7057
2026-02-12 19:01 | 72.941 | TRUE | FALSE | -0.36044 | -0.49661 | -0.55826 | -0.75955 | 0.2826 |  |  | none | FALSE | 2 | 72.5806 | TRUE | FALSE | 0.0859 |  | 73.0399 | 0 | 0.2826 | -0.01413 | 0.11135 | 2.6647 | 0.22968 | Persistence ends | 73.4993 | -0.43065 | Night | 202602 | 2026-02-12 | 0.43065
2026-02-12 19:16 | 73.2236 | TRUE | FALSE | -0.64304 | -0.88597 | -0.27566 | -0.37506 | 0.2826 |  |  | none | FALSE | 3 | 72.5806 | TRUE | FALSE | 0.139 |  | 73.0399 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.22968 | Normal | 73.4993 | 0.79978 | Night | 202602 | 2026-02-12 | 0.79978
2026-02-12 19:30 | 73.2236 | FALSE | FALSE | -0.64304 | -0.88597 | -0.27566 | -0.37506 | 0 |  |  | none | FALSE | 3 | 72.5806 | FALSE | FALSE | 0.139 |  | 73.0399 | 0 | 0 | 0 | 0.12967 | 0 | 0.22968 | Normal | 73.4993 | 0.79978 | Night | 202602 | 2026-02-12 | 0.79978
2026-02-12 19:45 | 73.2236 | FALSE | FALSE | -0.64304 | -0.88597 | -0.27566 | -0.37506 | 0 |  |  | none | FALSE | 3 | 72.5806 | FALSE | FALSE | 0.139 |  | 73.0399 | 0 | 0 | 0 | 0.12967 | 0 | 0.22968 | Normal | 73.4993 | 0.79978 | Night | 202602 | 2026-02-12 | 0.79978
2026-02-12 20:00 | 73.2236 | FALSE | FALSE | -0.64304 | -0.88597 | -0.27566 | -0.37506 | 0 |  |  | none | FALSE | 3 | 72.5806 | FALSE | FALSE | 0.139 |  | 73.0399 | 0 | 0 | 0 | 0.12967 | 0 | 0.22968 | Normal | 73.4993 | 0.79978 | Night | 202602 | 2026-02-12 | 0.79978
2026-02-12 20:15 | 73.2236 | FALSE | FALSE | -0.64304 | -0.88597 | -0.27566 | -0.37506 | 0 |  |  | none | FALSE | 3 | 72.5806 | FALSE | FALSE | 0.139 |  | 73.0399 | 0 | 0 | 0 | 0.12967 | 0 | 0.22968 | Normal | 73.4993 | 0.79978 | Night | 202602 | 2026-02-12 | 0.79978
2026-02-12 20:29 | 72.941 | FALSE | FALSE | -0.36812 | -0.50725 | -0.53768 | -0.73175 | -0.2826 |  |  | none | FALSE | 2 | 72.5729 | FALSE | FALSE | 0.0821 |  | 73.0258 | 0 | -0.2826 | -0.01413 | 0.14424 | -1.8612 | 0.22645 | Normal | 73.4787 | -0.37438 | Night | 202602 | 2026-02-12 | 0.37438
2026-02-12 20:44 | 72.941 | FALSE | FALSE | -0.37382 | -0.51514 | -0.51512 | -0.70126 | 0 |  |  | none | FALSE | 2 | 72.5672 | FALSE | FALSE | 0.0783 |  | 73.0117 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.22224 | Normal | 73.4561 | -0.31791 | Night | 202602 | 2026-02-12 | 0.31791
2026-02-12 20:59 | 72.941 | FALSE | FALSE | -0.37742 | -0.52013 | -0.49046 | -0.66792 | 0 |  |  | none | FALSE | 2 | 72.5636 | FALSE | FALSE | 0.0745 |  | 72.9975 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.21697 | Normal | 73.4315 | -0.26049 | Night | 202602 | 2026-02-12 | 0.26049
2026-02-12 21:14 | 72.941 | FALSE | FALSE | -0.37877 | -0.522 | -0.46355 | -0.63151 | 0 |  |  | none | FALSE | 2 | 72.5622 | FALSE | FALSE | 0.0706 |  | 72.9834 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.21058 | Normal | 73.4046 | -0.2013 | Night | 202602 | 2026-02-12 | 0.2013
2026-02-12 21:29 | 72.941 | FALSE | FALSE | -0.37766 | -0.52045 | -0.43418 | -0.59172 | 0 |  |  | none | FALSE | 1 | 72.5633 | FALSE | FALSE | 0.0379 |  | 72.9693 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.20296 | Normal | 73.3752 | -0.13924 | Night | 202602 | 2026-02-12 | 0.13924
2026-02-12 21:44 | 72.6584 | FALSE | FALSE | -0.12744 | -0.1757 | -0.69264 | -0.94428 | -0.2826 |  |  | none | FALSE | 0 | 72.531 | FALSE | FALSE | 0.0919 |  | 72.941 | 0 | -0.2826 | -0.02826 | 0.15614 | -1.6289 | 0.20502 | Normal | 73.351 | -1.3784 | Night | 202602 | 2026-02-12 | 1.3784
2026-02-12 21:59 | 72.6584 | FALSE | FALSE | -0.1606 | -0.22153 | -0.69754 | -0.9509 | 0 |  |  | none | FALSE | 0 | 72.4978 | FALSE | FALSE | 0.0834 |  | 72.9269 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.21454 | Normal | 73.3559 | -1.2514 | Night | 202602 | 2026-02-12 | 1.2514
2026-02-12 22:14 | 72.6584 | FALSE | FALSE | -0.19108 | -0.26367 | -0.69976 | -0.95389 | 0 |  |  | none | FALSE | 0 | 72.4673 | FALSE | FALSE | 0.0761 |  | 72.9127 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.22271 | Normal | 73.3582 | -1.142 | Night | 202602 | 2026-02-12 | 1.142
2026-02-12 22:29 | 72.6584 | FALSE | FALSE | -0.21914 | -0.30252 | -0.69956 | -0.95363 | 0 |  |  | none | FALSE | 0 | 72.4393 | FALSE | FALSE | 0.0697 |  | 72.8986 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.22968 | Normal | 73.358 | -1.0459 | Night | 202602 | 2026-02-12 | 1.0459
2026-02-12 22:44 | 72.3758 | FALSE | FALSE | -0.020045 | -0.027704 | -1.0091 | -1.3751 | -0.2826 |  |  | none | FALSE | 0 | 72.3558 | FALSE | FALSE | 0.1281 |  | 72.8704 | 0 | -0.2826 | -0.02826 | 0.15614 | -1.6289 | 0.2573 | Normal | 73.3849 | -1.9221 | Night | 202602 | 2026-02-12 | 1.9221
2026-02-12 22:59 | 72.3758 | FALSE | FALSE | -0.072753 | -0.10062 | -1.0336 | -1.408 | 0 |  |  | none | FALSE | 0 | 72.303 | FALSE | FALSE | 0.1158 |  | 72.8562 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.27659 | Normal | 73.4094 | -1.737 | Night | 202602 | 2026-02-12 | 1.737
2026-02-12 23:14 | 72.3758 | FALSE | FALSE | -0.12151 | -0.16817 | -1.0541 | -1.4355 | 0 |  |  | none | FALSE | 0 | 72.2543 | FALSE | FALSE | 0.1058 |  | 72.8421 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.2939 | Normal | 73.4299 | -1.5866 | Night | 202602 | 2026-02-12 | 1.5866
2026-02-12 23:28 | 72.3758 | FALSE | FALSE | -0.16699 | -0.23125 | -1.0713 | -1.4586 | 0 |  |  | none | FALSE | 0 | 72.2088 | FALSE | FALSE | 0.0974 |  | 72.828 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.30957 | Normal | 73.4471 | -1.4606 | Night | 202602 | 2026-02-12 | 1.4606
2026-02-12 23:43 | 72.3758 | FALSE | FALSE | -0.20965 | -0.29051 | -1.0857 | -1.4779 | 0 |  |  | none | FALSE | 0 | 72.1661 | FALSE | FALSE | 0.0902 |  | 72.8138 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.32384 | Normal | 73.4615 | -1.3526 | Night | 202602 | 2026-02-12 | 1.3526
2026-02-12 23:58 | 72.3758 | FALSE | FALSE | -0.26337 | -0.36522 | -1.0829 | -1.4742 | 0 |  |  | none | FALSE | 0 | 72.1124 | FALSE | FALSE | 0.0812 |  | 72.7856 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.33657 | Normal | 73.4587 | -1.2175 | Night | 202602 | 2026-02-12 | 1.2175
2026-02-13 00:14 | 72.095 | FALSE | FALSE | -0.072763 | -0.10103 | -1.341 | -1.8261 | -0.2808 |  |  | none | FALSE | 0 | 72.0222 | FALSE | FALSE | 0.1196 |  | 72.7291 | 0 | -0.2808 | -0.05643 | 0.11579 | -1.9377 | 0.35345 | Normal | 73.436 | -1.7941 | Night | 202602 | 2026-02-13 | 1.7941
2026-02-13 00:28 | 72.095 | FALSE | FALSE | -0.14305 | -0.19881 | -1.2985 | -1.7692 | 0 |  |  | none | FALSE | 0 | 71.952 | FALSE | FALSE | 0.1069 |  | 72.6727 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.36038 | Normal | 73.3935 | -1.6031 | Night | 202602 | 2026-02-13 | 1.6031
2026-02-13 00:43 | 72.095 | FALSE | FALSE | -0.19458 | -0.27063 | -1.2371 | -1.687 | 0 |  |  | none | FALSE | 0 | 71.9004 | FALSE | FALSE | 0.0971 |  | 72.6163 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.35793 | Normal | 73.3321 | -1.4564 | Night | 202602 | 2026-02-13 | 1.4564
2026-02-13 00:58 | 72.095 | FALSE | FALSE | -0.22696 | -0.31581 | -1.1567 | -1.579 | 0 |  |  | none | FALSE | 0 | 71.868 | FALSE | FALSE | 0.0896 |  | 72.5598 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.34591 | Normal | 73.2517 | -1.3439 | Night | 202602 | 2026-02-13 | 1.3439
2026-02-13 01:13 | 72.095 | FALSE | FALSE | -0.23806 | -0.3313 | -1.0549 | -1.4421 | 0 |  |  | none | FALSE | 0 | 71.8569 | FALSE | FALSE | 0.0842 |  | 72.5034 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.32324 | Normal | 73.1499 | -1.2635 | Night | 202602 | 2026-02-13 | 1.2635
2026-02-13 01:28 | 71.8124 | FALSE | FALSE | -0.047135 | -0.065679 | -1.3163 | -1.8 | -0.2826 |  |  | none | FALSE | 0 | 71.7653 | FALSE | FALSE | 0.1241 |  | 72.447 | 0 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.34086 | Normal | 73.1287 | -1.8617 | Night | 202602 | 2026-02-13 | 1.8617
2026-02-13 01:43 | 71.8124 | FALSE | FALSE | -0.11807 | -0.16469 | -1.2744 | -1.7437 | 0 |  |  | none | FALSE | 0 | 71.6943 | FALSE | FALSE | 0.1107 |  | 72.3906 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.34812 | Normal | 73.0868 | -1.6608 | Night | 202602 | 2026-02-13 | 1.6608
2026-02-13 01:58 | 71.8124 | FALSE | FALSE | -0.16959 | -0.23671 | -1.213 | -1.6611 | 0 |  |  | none | FALSE | 0 | 71.6428 | FALSE | FALSE | 0.1006 |  | 72.3341 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.34566 | Normal | 73.0254 | -1.5094 | Night | 202602 | 2026-02-13 | 1.5094
2026-02-13 02:13 | 71.8124 | FALSE | FALSE | -0.20125 | -0.28103 | -1.1318 | -1.5517 | 0 |  |  | none | FALSE | 0 | 71.6112 | FALSE | FALSE | 0.0931 |  | 72.2777 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.33327 | Normal | 72.9442 | -1.3962 | Night | 202602 | 2026-02-13 | 1.3962
2026-02-13 02:27 | 71.8124 | FALSE | FALSE | -0.21067 | -0.29423 | -1.0284 | -1.4119 | 0 |  |  | none | FALSE | 0 | 71.6017 | FALSE | FALSE | 0.088 |  | 72.2213 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.30977 | Normal | 72.8408 | -1.3199 | Night | 202602 | 2026-02-13 | 1.3199
2026-02-13 02:43 | 71.5298 | FALSE | FALSE | -0.021356 | -0.029865 | -1.2914 | -1.7734 | -0.2826 |  |  | none | FALSE | 0 | 71.5084 | FALSE | FALSE | 0.129 |  | 72.1648 | 0 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.3282 | Normal | 72.8212 | -1.9349 | Night | 202602 | 2026-02-13 | 1.9349
2026-02-13 02:58 | 71.5298 | FALSE | FALSE | -0.093002 | -0.13019 | -1.2502 | -1.7178 | 0 |  |  | none | FALSE | 0 | 71.4368 | FALSE | FALSE | 0.1149 |  | 72.1084 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.33581 | Normal | 72.78 | -1.723 | Night | 202602 | 2026-02-13 | 1.723
2026-02-13 03:13 | 71.5298 | FALSE | FALSE | -0.1445 | -0.20242 | -1.1889 | -1.6349 | 0 |  |  | none | FALSE | 0 | 71.3853 | FALSE | FALSE | 0.1044 |  | 72.052 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.33334 | Normal | 72.7187 | -1.5665 | Night | 202602 | 2026-02-13 | 1.5665
2026-02-13 03:27 | 71.5298 | FALSE | FALSE | -0.17537 | -0.24577 | -1.1069 | -1.5238 | 0 |  |  | none | FALSE | 0 | 71.3544 | FALSE | FALSE | 0.0969 |  | 71.9955 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.32056 | Normal | 72.6367 | -1.4529 | Night | 202602 | 2026-02-13 | 1.4529
2026-02-13 03:42 | 71.5298 | FALSE | FALSE | -0.22364 | -0.31363 | -1.0705 | -1.4746 | 0 |  |  | none | FALSE | 0 | 71.3062 | FALSE | FALSE | 0.0873 |  | 71.9532 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.32355 | Normal | 72.6003 | -1.3088 | Night | 202602 | 2026-02-13 | 1.3088
2026-02-13 03:57 | 71.5298 | FALSE | FALSE | -0.26022 | -0.36512 | -1.0225 | -1.4094 | 0 |  |  | none | FALSE | 0 | 71.2696 | FALSE | FALSE | 0.0792 |  | 71.9109 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.32068 | Normal | 72.5523 | -1.1886 | Night | 202602 | 2026-02-13 | 1.1886
2026-02-13 04:12 | 71.5298 | FALSE | FALSE | -0.28478 | -0.39972 | -0.96248 | -1.3277 | 0 |  |  | none | FALSE | 0 | 71.245 | FALSE | FALSE | 0.0724 |  | 71.8687 | 0 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.31181 | Normal | 72.4923 | -1.0867 | Night | 202602 | 2026-02-13 | 1.0867
2026-02-13 04:27 | 71.2472 | FALSE | FALSE | -0.069536 | -0.097694 | -1.1996 | -1.6558 | -0.2826 |  |  | none | FALSE | 0 | 71.1777 | FALSE | FALSE | 0.1187 |  | 71.8122 | 0 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.31728 | Normal | 72.4468 | -1.7808 | Night | 202602 | 2026-02-13 | 1.7808
2026-02-13 04:42 | 71.2472 | FALSE | FALSE | -0.11559 | -0.1625 | -1.1328 | -1.565 | 0 |  |  | none | FALSE | 0 | 71.1316 | FALSE | FALSE | 0.1086 |  | 71.7558 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.31209 | Normal | 72.38 | -1.6296 | Night | 202602 | 2026-02-13 | 1.6296
2026-02-13 04:57 | 71.2472 | FALSE | FALSE | -0.13921 | -0.19577 | -1.0435 | -1.4435 | 0 |  |  | none | FALSE | 0 | 71.108 | FALSE | FALSE | 0.1019 |  | 71.6994 | 0 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.29568 | Normal | 72.2907 | -1.5292 | Night | 202602 | 2026-02-13 | 1.5292
2026-02-13 05:12 | 70.9646 | FALSE | FALSE | 0.03251 | 0.04579 | -1.324 | -1.8315 | -0.2826 | 2026-02-13 07:45 | 2026-02-13 05:12 | lower | TRUE | 0 | 70.9971 | FALSE | FALSE | 0.1972 | 2.1007 | 71.6428 | 1 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.32287 | Extreme triggered | 72.2886 | -2.1007 | Night | 202602 | 2026-02-13 | 2.1007
2026-02-13 05:27 | 70.9646 | FALSE | FALSE | -0.054534 | -0.076906 | -1.298 | -1.7962 | 0 |  | 2026-02-13 05:12 | none | FALSE | 0 | 70.9101 | FALSE | FALSE | 0.2369 | 1.9697 | 71.5863 | 2 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.33813 | Extreme/elevated | 72.2626 | -1.8387 | Night | 202602 | 2026-02-13 | 1.8387
2026-02-13 05:42 | 70.9646 | FALSE | FALSE | -0.12093 | -0.1707 | -1.2513 | -1.7328 | 0 |  | 2026-02-13 05:12 | none | FALSE | 0 | 70.8437 | FALSE | FALSE | 0.2813 | 1.8623 | 71.5298 | 3 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.34306 | Persistent | 72.2159 | -1.6475 | Night | 202602 | 2026-02-13 | 1.6475
2026-02-13 05:57 | 70.9646 | FALSE | FALSE | -0.16757 | -0.2367 | -1.1849 | -1.6423 | 0 |  | 2026-02-13 05:12 | none | FALSE | 0 | 70.797 | FALSE | FALSE | 0.3289 | 1.7728 | 71.4733 | 4 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.33813 | Persistent | 72.1495 | -1.5044 | Night | 202602 | 2026-02-13 | 1.5044
2026-02-13 06:12 | 70.682 | FALSE | FALSE | 0.022961 | 0.032474 | -1.4183 | -1.9671 | -0.2826 |  | 2026-02-13 05:12 | lower | TRUE | 0 | 70.705 | FALSE | TRUE | 0.4234 | 1.8314 | 71.4026 | 5 | -0.2826 | -0.07065 | 0.12555 | -1.6882 | 0.34883 | Persistent | 72.1003 | -2.0658 | Night | 202602 | 2026-02-13 | 2.0658
2026-02-13 06:26 | 70.682 | FALSE | FALSE | -0.075667 | -0.10717 | -1.4039 | -1.9475 | 0 |  | 2026-02-13 05:12 | none | FALSE | 0 | 70.6063 | FALSE | FALSE | 0.4626 | 1.8254 | 71.3461 | 6 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.36989 | Persistent | 72.0859 | -1.7954 | Night | 202602 | 2026-02-13 | 1.7954
2026-02-13 06:41 | 70.682 | FALSE | TRUE | -0.15458 | -0.21917 | -1.3698 | -1.9011 | 0 |  | 2026-02-13 05:12 | none | FALSE | 0 | 70.5274 | FALSE | FALSE | 0.5063 | 1.7924 | 71.2896 | 7 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.38108 | Confirmed/Materialized Shift | 72.0518 | -1.5944 | Night | 202602 | 2026-02-13 | 1.5944
2026-02-13 06:56 | 70.682 | FALSE | TRUE | -0.21549 | -0.30581 | -1.3176 | -1.8301 | 0 |  | 2026-02-13 05:12 | none | FALSE | 0 | 70.4665 | FALSE | FALSE | 0.4959 | 1.7481 | 71.2331 | 8 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.38328 | Confirmed/Materialized Shift | 71.9996 | -1.4378 | Night | 202602 | 2026-02-13 | 1.4378
2026-02-13 07:11 | 70.682 | FALSE | TRUE | -0.25874 | -0.36741 | -1.2478 | -1.7348 | 0 |  | 2026-02-13 05:12 | none | FALSE | 0 | 70.4233 | FALSE | FALSE | 0.4875 | 1.6998 | 71.1766 | 9 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.37665 | Confirmed/Materialized Shift | 71.9298 | -1.313 | Day | 202602 | 2026-02-13 | 1.313
2026-02-13 07:26 | 70.3994 | FALSE | TRUE | -0.060613 | -0.086173 | -1.4736 | -2.0503 | -0.2826 |  | 2026-02-13 05:12 | none | FALSE | 0 | 70.3388 | FALSE | FALSE | 0.5228 | 1.714 | 71.1059 | 10 | -0.2826 | -0.07065 | 0.12555 | -1.6882 | 0.38356 | Confirmed/Materialized Shift | 71.873 | -1.842 | Day | 202602 | 2026-02-13 | 1.842
2026-02-13 07:30 | 70.3994 | FALSE | TRUE | -0.15143 | -0.21557 | -1.4514 | -2.02 | 0 |  | 2026-02-13 05:12 | none | FALSE | 0 | 70.248 | FALSE | FALSE | 0.5081 | 1.7056 | 71.0494 | 11 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.40071 | Confirmed/Materialized Shift | 71.8508 | -1.6221 | Day | 202602 | 2026-02-13 | 1.6221
2026-02-13 07:45 | 70.682 | TRUE | FALSE | -0.45893 | -0.65352 | -1.1089 | -1.5446 | 0.2826 |  |  | none | FALSE | 1 | 70.2231 | FALSE | FALSE | 0.0838 |  | 71.007 | 0 | 0.2826 | -0.04239 | 0.13829 | 2.35 | 0.39196 | Persistence ends | 71.7909 | -0.82915 | Day | 202602 | 2026-02-13 | 0.82915
2026-02-13 08:00 | 70.682 | FALSE | FALSE | -0.47347 | -0.67438 | -1.0387 | -1.4482 | 0 |  |  | none | FALSE | 1 | 70.2085 | FALSE | FALSE | 0.0784 |  | 70.9646 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.37804 | Normal | 71.7207 | -0.74755 | Day | 202602 | 2026-02-13 | 0.74755
2026-02-13 08:15 | 70.682 | FALSE | FALSE | -0.47648 | -0.67869 | -0.9569 | -1.3357 | 0 |  |  | none | FALSE | 1 | 70.2055 | FALSE | FALSE | 0.0733 |  | 70.9222 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.35834 | Normal | 71.6389 | -0.67033 | Day | 202602 | 2026-02-13 | 0.67033
2026-02-13 08:30 | 70.9646 | FALSE | FALSE | -0.72863 | -1.0374 | -0.58733 | -0.82085 | 0.2826 |  |  | none | FALSE | 1 | 70.236 | FALSE | FALSE | 0.0429 |  | 70.894 | 0 | 0.2826 | -0.02826 | 0.15614 | 1.9909 | 0.32899 | Normal | 71.5519 | 0.21475 | Day | 202602 | 2026-02-13 | 0.21475
2026-02-13 08:30 | 70.9646 | FALSE | FALSE | -0.68671 | -0.97714 | -0.48889 | -0.68421 | 0 |  |  | none | FALSE | 1 | 70.2779 | FALSE | FALSE | 0.051 |  | 70.8657 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.2939 | Normal | 71.4535 | 0.33654 | Day | 202602 | 2026-02-13 | 0.33654
2026-02-13 08:45 | 71.2472 | FALSE | FALSE | -0.92711 | -1.3184 | -0.13583 | -0.19029 | 0.2826 |  |  | none | FALSE | 1 | 70.3201 | FALSE | FALSE | 0.1278 |  | 70.8516 | 0 | 0.2826 | -0.01413 | 0.17092 | 1.7361 | 0.26574 | Normal | 71.383 | 1.4888 | Day | 202602 | 2026-02-13 | 1.4888
2026-02-13 09:00 | 71.5298 | FALSE | FALSE | -1.2519 | -1.7814 | 0.076308 | 0.10679 | 0.2826 | 2026-02-13 13:22 | 2026-02-13 09:00 | upper | TRUE | 1 | 70.2779 | FALSE | FALSE | 0.2364 | 2.2596 | 70.8657 | 1 | 0.2826 | 0.01413 | 0.17092 | 1.5708 | 0.2939 | Extreme triggered | 71.4535 | 2.2596 | Day | 202602 | 2026-02-13 | 2.2596
2026-02-13 09:15 | 71.5298 | FALSE | FALSE | -1.2879 | -1.8335 | 0.012109 | 0.016931 | 0 |  | 2026-02-13 09:00 | upper | TRUE | 1 | 70.2419 | FALSE | FALSE | 0.2787 | 2.1488 | 70.8798 | 2 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.31894 | Extreme/elevated | 71.5177 | 2.038 | Day | 202602 | 2026-02-13 | 2.038
2026-02-13 09:30 | 71.8124 | FALSE | FALSE | -1.6514 | -2.3538 | 0.15719 | 0.21937 | 0.2826 |  | 2026-02-13 09:00 | upper | TRUE | 1 | 70.161 | FALSE | TRUE | 0.3614 | 2.2395 | 70.9081 | 3 | 0.2826 | 0.02826 | 0.18107 | 1.4047 | 0.37356 | Persistent | 71.6552 | 2.4208 | Day | 202602 | 2026-02-13 | 2.4208
2026-02-13 09:45 | 72.095 | FALSE | FALSE | -2.0473 | -2.9227 | 0.21352 | 0.29705 | 0.2826 |  | 2026-02-13 09:00 | upper | TRUE | 1 | 70.0477 | FALSE | TRUE | 0.4215 | 2.296 | 70.9646 | 4 | 0.2826 | 0.05652 | 0.17396 | 1.2996 | 0.45844 | Persistent | 71.8815 | 2.4658 | Day | 202602 | 2026-02-13 | 2.4658
2026-02-13 10:00 | 72.3758 | FALSE | FALSE | -2.4537 | -3.5092 | 0.22756 | 0.3154 | 0.2808 |  | 2026-02-13 09:00 | upper | TRUE | 0 | 69.9221 | FALSE | TRUE | 0.4463 | 2.3186 | 71.0352 | 5 | 0.2808 | 0.07056 | 0.18038 | 1.1656 | 0.55654 | Persistent | 72.1482 | 2.4089 | Day | 202602 | 2026-02-13 | 2.4089
2026-02-13 10:15 | 72.941 | TRUE | FALSE | -3.2075 | -4.5997 | 0.40649 | 0.56042 | 0.5652 |  | 2026-02-13 09:00 | upper | TRUE | 1 | 69.7335 | FALSE | TRUE | 0.5435 | 2.3623 | 71.134 | 6 | 0.5652 | 0.09882 | 0.2105 | 2.2156 | 0.70026 | Persistent | 72.5345 | 2.5805 | Day | 202602 | 2026-02-13 | 2.5805
2026-02-13 10:29 | 72.941 | FALSE | TRUE | -3.3212 | -4.7705 | 0.095206 | 0.1307 | 0 |  | 2026-02-13 09:00 | upper | TRUE | 1 | 69.6198 | FALSE | TRUE | 0.5698 | 2.3274 | 71.2328 | 7 | 0 | 0.09882 | 0.2105 | -0.46945 | 0.8065 | Confirmed/Materialized Shift | 72.8458 | 2.118 | Day | 202602 | 2026-02-13 | 2.118
2026-02-13 10:44 | 72.941 | FALSE | TRUE | -3.3555 | -4.8221 | -0.165 | -0.2257 | 0 |  | 2026-02-13 09:00 | none | FALSE | 1 | 69.5855 | FALSE | FALSE | 0.5494 | 2.263 | 71.3457 | 8 | 0 | 0.11295 | 0.19224 | -0.58754 | 0.88012 | Confirmed/Materialized Shift | 73.106 | 1.8125 | Day | 202602 | 2026-02-13 | 1.8125
2026-02-13 10:59 | 72.941 | FALSE | TRUE | -3.3499 | -4.8136 | -0.38525 | -0.5254 | 0 |  | 2026-02-13 09:00 | none | FALSE | 1 | 69.5911 | FALSE | FALSE | 0.5344 | 2.1879 | 71.4587 | 9 | 0 | 0.11295 | 0.19224 | -0.58754 | 0.93378 | Confirmed/Materialized Shift | 73.3263 | 1.5874 | Day | 202602 | 2026-02-13 | 1.5874
2026-02-13 11:15 | 73.2236 | FALSE | TRUE | -3.6249 | -5.2083 | -0.34927 | -0.47472 | 0.2826 |  | 2026-02-13 09:00 | none | FALSE | 1 | 69.5987 | FALSE | FALSE | 0.5385 | 2.134 | 71.5858 | 10 | 0.2826 | 0.12708 | 0.19388 | 0.80214 | 0.99354 | Confirmed/Materialized Shift | 73.5729 | 1.6485 | Day | 202602 | 2026-02-13 | 1.6485
2026-02-13 11:29 | 73.2236 | FALSE | TRUE | -3.5779 | -5.1373 | -0.55645 | -0.7542 | 0 |  | 2026-02-13 09:00 | none | FALSE | 1 | 69.6457 | FALSE | FALSE | 0.526 | 2.0729 | 71.7129 | 11 | 0 | 0.12708 | 0.19388 | -0.65545 | 1.0336 | Confirmed/Materialized Shift | 73.7801 | 1.4616 | Day | 202602 | 2026-02-13 | 1.4616
2026-02-13 11:44 | 73.2236 | FALSE | TRUE | -3.496 | -5.0138 | -0.7287 | -0.98536 | 0 |  | 2026-02-13 09:00 | none | FALSE | 1 | 69.7276 | FALSE | FALSE | 0.5159 | 2.0093 | 71.8399 | 12 | 0 | 0.12708 | 0.19388 | -0.65545 | 1.0562 | Confirmed/Materialized Shift | 73.9523 | 1.3101 | Day | 202602 | 2026-02-13 | 1.3101
2026-02-13 11:59 | 73.5062 | FALSE | TRUE | -3.6341 | -5.2011 | -0.61231 | -0.82612 | 0.2826 |  | 2026-02-13 09:00 | none | FALSE | 1 | 69.8721 | FALSE | FALSE | 0.5235 | 1.9642 | 71.9953 | 13 | 0.2826 | 0.15534 | 0.17085 | 0.74487 | 1.0616 | Confirmed/Materialized Shift | 74.1185 | 1.4232 | Day | 202602 | 2026-02-13 | 1.4232
2026-02-13 12:14 | 73.5062 | FALSE | TRUE | -3.4415 | -4.9118 | -0.73031 | -0.98376 | 0 |  | 2026-02-13 09:00 | none | FALSE | 1 | 70.0647 | FALSE | FALSE | 0.5152 | 1.9168 | 72.1506 | 14 | 0 | 0.15534 | 0.17085 | -0.90923 | 1.0429 | Confirmed/Materialized Shift | 74.2365 | 1.2998 | Day | 202602 | 2026-02-13 | 1.2998
2026-02-13 12:29 | 73.5062 | FALSE | TRUE | -3.2637 | -4.6463 | -0.83496 | -1.1231 | 0 |  | 2026-02-13 09:00 | none | FALSE | 1 | 70.2425 | FALSE | FALSE | 0.5076 | 1.868 | 72.2918 | 15 | 0 | 0.14121 | 0.17145 | -0.8236 | 1.0247 | Confirmed/Materialized Shift | 74.3412 | 1.1851 | Day | 202602 | 2026-02-13 | 1.1851
2026-02-13 12:44 | 73.5062 | FALSE | TRUE | -3.0431 | -4.3187 | -0.89678 | -1.2053 | 0 |  | 2026-02-13 09:00 | none | FALSE | 0 | 70.4631 | FALSE | FALSE | 0.4726 | 1.8193 | 72.433 | 16 | 0 | 0.14121 | 0.17145 | -0.8236 | 0.98497 | Confirmed/Materialized Shift | 74.403 | 1.0895 | Day | 202602 | 2026-02-13 | 1.0895
2026-02-13 12:59 | 73.7888 | FALSE | TRUE | -3.0767 | -4.3511 | -0.67589 | -0.90766 | 0.2826 |  | 2026-02-13 09:00 | none | FALSE | 0 | 70.7121 | FALSE | FALSE | 0.4853 | 1.7876 | 72.5884 | 17 | 0.2826 | 0.15534 | 0.17085 | 0.74487 | 0.93815 | Confirmed/Materialized Shift | 74.4647 | 1.2796 | Day | 202602 | 2026-02-13 | 1.2796
2026-02-13 13:04 | 74.0714 | FALSE | TRUE | -3.1516 | -4.444 | -0.49629 | -0.66555 | 0.2826 |  | 2026-02-13 09:00 | none | FALSE | 0 | 70.9198 | FALSE | FALSE | 0.4971 | 1.7692 | 72.7437 | 18 | 0.2826 | 0.15534 | 0.17085 | 0.74487 | 0.91198 | Confirmed/Materialized Shift | 74.5677 | 1.4558 | Day | 202602 | 2026-02-13 | 1.4558
2026-02-13 13:07 | 74.0714 | FALSE | TRUE | -2.8841 | -4.0514 | -0.53938 | -0.72292 | 0 |  | 2026-02-13 09:00 | none | FALSE | 0 | 71.1873 | FALSE | FALSE | 0.4913 | 1.7481 | 72.8991 | 19 | 0 | 0.15534 | 0.17085 | -0.90923 | 0.85586 | Confirmed/Materialized Shift | 74.6108 | 1.3698 | Day | 202602 | 2026-02-13 | 1.3698
2026-02-13 13:22 | 73.7888 | TRUE | FALSE | -2.3292 | -3.2595 | -0.80393 | -1.0778 | -0.2826 |  |  | none | FALSE | 1 | 71.4596 | FALSE | FALSE | 0.0935 |  | 73.0261 | 0 | -0.2826 | 0.12708 | 0.19388 | -2.113 | 0.78329 | Persistence ends | 74.5927 | 0.97366 | Day | 202602 | 2026-02-13 | 0.97366
2026-02-13 13:28 | 73.5062 | FALSE | FALSE | -1.792 | -2.4988 | -1.0295 | -1.3812 | -0.2826 |  |  | none | FALSE | 1 | 71.7142 | FALSE | FALSE | 0.0646 |  | 73.125 | 0 | -0.2826 | 0.09882 | 0.2105 | -1.812 | 0.70538 | Normal | 74.5357 | 0.54048 | Day | 202602 | 2026-02-13 | 0.54048
2026-02-13 13:44 | 73.2236 | FALSE | FALSE | -1.2083 | -1.6778 | -1.1804 | -1.5864 | -0.2826 |  |  | none | FALSE | 1 | 72.0153 | FALSE | FALSE | 0.0301 |  | 73.2096 | 0 | -0.2826 | 0.08469 | 0.22637 | -1.6225 | 0.59716 | Normal | 74.404 | 0.023361 | Day | 202602 | 2026-02-13 | 0.023361
2026-02-13 13:59 | 73.2236 | FALSE | FALSE | -0.94061 | -1.3013 | -1.0538 | -1.4188 | 0 |  |  | none | FALSE | 1 | 72.283 | FALSE | FALSE | 0.0361 |  | 73.2802 | 0 | 0 | 0.07056 | 0.22215 | -0.31763 | 0.49861 | Normal | 74.2774 | -0.11354 | Day | 202602 | 2026-02-13 | 0.11354
2026-02-13 14:14 | 72.6584 | TRUE | FALSE | -0.23137 | -0.31945 | -1.5313 | -2.0641 | -0.5652 |  |  | none | FALSE | 2 | 72.427 | TRUE | FALSE | 0.1555 |  | 73.3084 | 0 | -0.5652 | 0.02817 | 0.25761 | -2.3033 | 0.44067 | Normal | 74.1897 | -1.475 | Day | 202602 | 2026-02-13 | 1.475
2026-02-13 14:28 | 72.6584 | FALSE | FALSE | -0.16159 | -0.22289 | -1.4898 | -2.0092 | 0 |  |  | none | FALSE | 2 | 72.4968 | FALSE | FALSE | 0.1644 |  | 73.3225 | 0 | 0 | 0.01413 | 0.25068 | -0.056367 | 0.41285 | Normal | 74.1482 | -1.6086 | Day | 202602 | 2026-02-13 | 1.6086
2026-02-13 14:43 | 72.3758 | FALSE | FALSE | 0.0038696 | 0.0053462 | -1.833 | -2.4701 | -0.2826 | 2026-02-13 15:58 | 2026-02-13 14:43 | lower | TRUE | 2 | 72.3797 | FALSE | FALSE | 0.2482 | 2.0085 | 73.2943 | 1 | -0.2826 | -0.02826 | 0.22271 | -1.142 | 0.45729 | Extreme triggered | 74.2088 | -2.0085 | Day | 202602 | 2026-02-13 | 2.0085
2026-02-13 14:58 | 72.3758 | FALSE | FALSE | -0.10199 | -0.14111 | -1.8824 | -2.5349 | 0 |  | 2026-02-13 14:43 | none | FALSE | 2 | 72.2738 | FALSE | FALSE | 0.2911 | 1.9014 | 73.266 | 2 | 0 | -0.02826 | 0.22271 | 0.12689 | 0.49609 | Extreme/elevated | 74.2582 | -1.7944 | Day | 202602 | 2026-02-13 | 1.7944
2026-02-13 15:13 | 72.3758 | FALSE | FALSE | -0.19903 | -0.27576 | -1.9229 | -2.5881 | 0 |  | 2026-02-13 14:43 | none | FALSE | 2 | 72.1768 | FALSE | FALSE | 0.3369 | 1.8092 | 73.2377 | 3 | 0 | -0.02826 | 0.22271 | 0.12689 | 0.53048 | Persistent | 74.2987 | -1.6248 | Day | 202602 | 2026-02-13 | 1.6248
2026-02-13 15:28 | 72.3758 | FALSE | FALSE | -0.28889 | -0.40076 | -1.9562 | -2.6318 | 0 |  | 2026-02-13 14:43 | none | FALSE | 2 | 72.0869 | FALSE | FALSE | 0.3847 | 1.7282 | 73.2095 | 4 | 0 | -0.02826 | 0.22271 | 0.12689 | 0.56128 | Persistent | 74.332 | -1.4853 | Day | 202602 | 2026-02-13 | 1.4853
2026-02-13 15:43 | 72.3758 | FALSE | FALSE | -0.39145 | -0.5438 | -1.974 | -2.655 | 0 |  | 2026-02-13 14:43 | none | FALSE | 1 | 71.9843 | FALSE | FALSE | 0.4035 | 1.6502 | 73.1671 | 5 | 0 | -0.04239 | 0.21058 | 0.2013 | 0.59137 | Persistent | 74.3498 | -1.3381 | Day | 202602 | 2026-02-13 | 1.3381
2026-02-13 15:58 | 72.6584 | FALSE | FALSE | -0.72345 | -1.0057 | -1.6843 | -2.2656 | 0.2826 |  |  | none | FALSE | 1 | 71.935 | FALSE | FALSE | 0.0818 |  | 73.1388 | 0 | 0.2826 | -0.02826 | 0.22271 | 1.3958 | 0.60193 | Persistence ends | 74.3427 | -0.79813 | Day | 202602 | 2026-02-13 | 0.79813
2026-02-13 16:13 | 72.941 | FALSE | FALSE | -1.0226 | -1.4219 | -1.39 | -1.87 | 0.2826 |  |  | none | FALSE | 1 | 71.9184 | FALSE | FALSE | 0.0489 |  | 73.1247 | 0 | 0.2826 | -0.01413 | 0.23331 | 1.2718 | 0.60315 | Normal | 74.331 | -0.30455 | Day | 202602 | 2026-02-13 | 0.30455
2026-02-13 16:28 | 72.941 | FALSE | FALSE | -1.0397 | -1.446 | -1.3505 | -1.8179 | 0 |  |  | none | FALSE | 1 | 71.9013 | FALSE | FALSE | 0.0459 |  | 73.0964 | 0 | 0 | -0.02826 | 0.22271 | 0.12689 | 0.59755 | Normal | 74.2915 | -0.26011 | Day | 202602 | 2026-02-13 | 0.26011
2026-02-13 16:43 | 73.2236 | FALSE | FALSE | -1.3226 | -1.8395 | -1.04 | -1.4004 | 0.2826 |  |  | none | FALSE | 0 | 71.901 | FALSE | FALSE | 0.0159 |  | 73.0823 | 0 | 0.2826 | -0.01413 | 0.23331 | 1.2718 | 0.59066 | Normal | 74.2636 | 0.23923 | Day | 202602 | 2026-02-13 | 0.23923
2026-02-13 16:58 | 73.2236 | FALSE | FALSE | -1.3221 | -1.8387 | -1.0112 | -1.3622 | 0 |  |  | none | FALSE | 0 | 71.9015 | FALSE | FALSE | 0.0178 |  | 73.0682 | 0 | 0 | -0.01413 | 0.23331 | 0.060564 | 0.58332 | Normal | 74.2348 | 0.26646 | Day | 202602 | 2026-02-13 | 0.26646
2026-02-13 17:13 | 72.941 | FALSE | FALSE | -1.0503 | -1.461 | -1.2481 | -1.6823 | -0.2826 |  |  | none | FALSE | 0 | 71.8907 | FALSE | FALSE | 0.0115 |  | 73.0399 | 0 | -0.2826 | -0.02826 | 0.24084 | -1.056 | 0.5746 | Normal | 74.1891 | -0.17214 | Day | 202602 | 2026-02-13 | 0.17214
2026-02-13 17:27 | 72.941 | FALSE | FALSE | -1.0376 | -1.443 | -1.1506 | -1.553 | 0 |  |  | none | FALSE | 0 | 71.9034 | FALSE | FALSE | 0.0069 |  | 72.9975 | 0 | 0 | -0.04239 | 0.22968 | 0.18456 | 0.54706 | Normal | 74.0916 | -0.10332 | Day | 202602 | 2026-02-13 | 0.10332
2026-02-13 17:42 | 72.941 | FALSE | FALSE | -0.97033 | -1.3482 | -0.97033 | -1.3128 | 0 |  |  | none | FALSE | 0 | 71.9707 | FALSE | FALSE | 0 |  | 72.941 | 0 | 0 | -0.05652 | 0.21697 | 0.26049 | 0.48516 | Normal | 73.9113 | 0 | Day | 202602 | 2026-02-13 | 0
2026-02-13 17:57 | 72.6584 | FALSE | FALSE | -0.60556 | -0.84044 | -1.0295 | -1.3971 | -0.2826 |  |  | none | FALSE | 0 | 72.0528 | FALSE | FALSE | 0.0346 |  | 72.8704 | 0 | -0.2826 | -0.07065 | 0.22224 | -0.95372 | 0.40876 | Normal | 73.6879 | -0.51852 | Day | 202602 | 2026-02-13 | 0.51852
2026-02-13 18:12 | 72.6584 | FALSE | FALSE | -0.54224 | -0.7519 | -0.8531 | -1.1605 | 0 |  |  | none | FALSE | 0 | 72.1162 | FALSE | FALSE | 0.0297 |  | 72.8138 | 0 | 0 | -0.05652 | 0.21697 | 0.26049 | 0.34883 | Normal | 73.5115 | -0.44557 | Day | 202602 | 2026-02-13 | 0.44557
2026-02-13 18:27 | 72.6584 | FALSE | FALSE | -0.50611 | -0.70144 | -0.73219 | -0.99766 | 0 |  |  | none | FALSE | 0 | 72.1523 | FALSE | FALSE | 0.0243 |  | 72.7714 | 0 | 0 | -0.04239 | 0.21058 | 0.2013 | 0.30957 | Normal | 73.3906 | -0.36515 | Night | 202602 | 2026-02-13 | 0.36515
2026-02-13 18:42 | 72.3758 | FALSE | FALSE | -0.25147 | -0.34866 | -0.95797 | -1.3063 | -0.2826 |  |  | none | FALSE | 0 | 72.1243 | FALSE | FALSE | 0.0779 |  | 72.7291 | 0 | -0.2826 | -0.04239 | 0.21058 | -1.1407 | 0.30236 | Normal | 73.3338 | -1.1683 | Night | 202602 | 2026-02-13 | 1.1683
2026-02-13 18:42 | 72.3758 | FALSE | FALSE | -0.26612 | -0.36904 | -0.88784 | -1.2118 | 0 |  |  | none | FALSE | 0 | 72.1097 | FALSE | FALSE | 0.0718 |  | 72.6867 | 0 | 0 | -0.04239 | 0.21058 | 0.2013 | 0.28849 | Normal | 73.2636 | -1.0775 | Night | 202602 | 2026-02-13 | 1.0775
2026-02-13 18:43 | 72.3758 | FALSE | FALSE | -0.29677 | -0.41172 | -0.89023 | -1.2151 | 0 |  |  | none | FALSE | 0 | 72.079 | FALSE | FALSE | 0.0667 |  | 72.6725 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.29675 | Normal | 73.266 | -0.99994 | Night | 202602 | 2026-02-13 | 0.99994
2026-02-13 18:58 | 72.941 | TRUE | FALSE | -0.85976 | -1.1928 | -0.35108 | -0.47901 | 0.5652 |  |  | none | FALSE | 1 | 72.0812 | FALSE | FALSE | 0.0846 |  | 72.6867 | 0 | 0.5652 | 0.01413 | 0.21454 | 2.5686 | 0.30271 | Normal | 73.2921 | 0.84022 | Night | 202602 | 2026-02-13 | 0.84022
2026-02-13 19:13 | 72.941 | FALSE | FALSE | -0.82311 | -1.1413 | -0.37095 | -0.50598 | 0 |  |  | none | FALSE | 1 | 72.1179 | FALSE | FALSE | 0.0791 |  | 72.7149 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.29851 | Normal | 73.3119 | 0.75735 | Night | 202602 | 2026-02-13 | 0.75735
2026-02-13 19:28 | 72.941 | FALSE | FALSE | -0.7806 | -1.0817 | -0.38496 | -0.52499 | 0 |  |  | none | FALSE | 1 | 72.1604 | FALSE | FALSE | 0.0738 |  | 72.7432 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.29139 | Normal | 73.326 | 0.67889 | Night | 202602 | 2026-02-13 | 0.67889
2026-02-13 19:42 | 72.941 | FALSE | FALSE | -0.73178 | -1.0134 | -0.39266 | -0.53544 | 0 |  |  | none | FALSE | 1 | 72.2092 | FALSE | FALSE | 0.0688 |  | 72.7714 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.28111 | Normal | 73.3337 | 0.60318 | Night | 202602 | 2026-02-13 | 0.60318
2026-02-13 19:57 | 72.941 | FALSE | FALSE | -0.67593 | -0.93534 | -0.39333 | -0.53635 | 0 |  |  | none | FALSE | 1 | 72.2651 | FALSE | FALSE | 0.0638 |  | 72.7997 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.26731 | Normal | 73.3343 | 0.52859 | Night | 202602 | 2026-02-13 | 0.52859
2026-02-13 20:12 | 72.941 | FALSE | FALSE | -0.61187 | -0.84596 | -0.38579 | -0.52613 | 0 |  |  | none | FALSE | 1 | 72.3291 | FALSE | FALSE | 0.0588 |  | 72.828 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.24942 | Normal | 73.3268 | 0.45322 | Night | 202602 | 2026-02-13 | 0.45322
2026-02-13 20:27 | 72.941 | FALSE | FALSE | -0.59351 | -0.82036 | -0.39569 | -0.53956 | 0 |  |  | none | FALSE | 1 | 72.3475 | FALSE | FALSE | 0.0552 |  | 72.8421 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.2473 | Normal | 73.3367 | 0.39996 | Night | 202602 | 2026-02-13 | 0.39996
2026-02-13 20:41 | 72.941 | FALSE | FALSE | -0.59351 | -0.82036 | -0.39569 | -0.53956 | 0 |  |  | none | FALSE | 1 | 72.3475 | FALSE | FALSE | 0.0552 |  | 72.8421 | 0 | 0 | 0 | 0.18338 | 0 | 0.2473 | Normal | 73.3367 | 0.39996 | Night | 202602 | 2026-02-13 | 0.39996
2026-02-13 20:56 | 72.941 | FALSE | FALSE | -0.59351 | -0.82036 | -0.39569 | -0.53956 | 0 |  |  | none | FALSE | 1 | 72.3475 | FALSE | FALSE | 0.0552 |  | 72.8421 | 0 | 0 | 0 | 0.18338 | 0 | 0.2473 | Normal | 73.3367 | 0.39996 | Night | 202602 | 2026-02-13 | 0.39996
2026-02-13 21:11 | 72.941 | FALSE | FALSE | -0.57695 | -0.79728 | -0.35087 | -0.47872 | 0 |  |  | none | FALSE | 1 | 72.3641 | FALSE | FALSE | 0.0611 |  | 72.828 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.23195 | Normal | 73.2919 | 0.48734 | Night | 202602 | 2026-02-13 | 0.48734
2026-02-13 21:27 | 72.941 | FALSE | FALSE | -0.55624 | -0.76845 | -0.3019 | -0.4122 | 0 |  |  | none | FALSE | 0 | 72.3848 | FALSE | FALSE | 0.0395 |  | 72.8138 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.21454 | Normal | 73.2429 | 0.59276 | Night | 202602 | 2026-02-13 | 0.59276
2026-02-13 21:41 | 72.6584 | FALSE | FALSE | -0.28875 | -0.399 | -0.57135 | -0.78022 | -0.2826 |  |  | none | FALSE | 0 | 72.3696 | FALSE | FALSE | 0.0438 |  | 72.7997 | 0 | -0.2826 | -0.01413 | 0.17092 | -1.5708 | 0.21503 | Normal | 73.2298 | -0.65713 | Night | 202602 | 2026-02-13 | 0.65713
2026-02-13 21:56 | 72.6584 | FALSE | FALSE | -0.3019 | -0.41725 | -0.55624 | -0.75974 | 0 |  |  | none | FALSE | 0 | 72.3565 | FALSE | FALSE | 0.0395 |  | 72.7856 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.21454 | Normal | 73.2146 | -0.59276 | Night | 202602 | 2026-02-13 | 0.59276
2026-02-13 22:11 | 72.6584 | FALSE | FALSE | -0.31309 | -0.43277 | -0.53917 | -0.73659 | 0 |  |  | none | FALSE | 0 | 72.3453 | FALSE | FALSE | 0.0354 |  | 72.7714 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.21306 | Normal | 73.1976 | -0.53055 | Night | 202602 | 2026-02-13 | 0.53055
2026-02-13 22:26 | 72.6584 | FALSE | FALSE | -0.31309 | -0.43277 | -0.53917 | -0.73659 | 0 |  |  | none | FALSE | 0 | 72.3453 | FALSE | FALSE | 0.0354 |  | 72.7714 | 0 | 0 | 0 | 0.15881 | 0 | 0.21306 | Normal | 73.1976 | -0.53055 | Night | 202602 | 2026-02-13 | 0.53055
2026-02-13 22:41 | 72.3758 | FALSE | FALSE | -0.077844 | -0.10767 | -0.84086 | -1.1485 | -0.2826 |  |  | none | FALSE | 0 | 72.298 | FALSE | FALSE | 0.1107 |  | 72.7573 | 0 | -0.2826 | -0.01413 | 0.17092 | -1.5708 | 0.22968 | Normal | 73.2167 | -1.6611 | Night | 202602 | 2026-02-13 | 1.6611
2026-02-13 22:56 | 72.3758 | FALSE | FALSE | -0.12124 | -0.16779 | -0.856 | -1.1689 | 0 |  |  | none | FALSE | 0 | 72.2546 | FALSE | FALSE | 0.1003 |  | 72.7432 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.24431 | Normal | 73.2318 | -1.5038 | Night | 202602 | 2026-02-13 | 1.5038
2026-02-13 23:11 | 72.3758 | FALSE | FALSE | -0.12124 | -0.16779 | -0.856 | -1.1689 | 0 |  |  | none | FALSE | 0 | 72.2546 | FALSE | FALSE | 0.1003 |  | 72.7432 | 0 | 0 | 0 | 0.15881 | 0 | 0.24431 | Normal | 73.2318 | -1.5038 | Night | 202602 | 2026-02-13 | 1.5038
2026-02-13 23:26 | 72.3758 | FALSE | FALSE | -0.12124 | -0.16779 | -0.856 | -1.1689 | 0 |  |  | none | FALSE | 0 | 72.2546 | FALSE | FALSE | 0.1003 |  | 72.7432 | 0 | 0 | 0 | 0.15881 | 0 | 0.24431 | Normal | 73.2318 | -1.5038 | Night | 202602 | 2026-02-13 | 1.5038
2026-02-13 23:40 | 72.3758 | FALSE | FALSE | -0.12124 | -0.16779 | -0.856 | -1.1689 | 0 |  |  | none | FALSE | 0 | 72.2546 | FALSE | FALSE | 0.1003 |  | 72.7432 | 0 | 0 | 0 | 0.15881 | 0 | 0.24431 | Normal | 73.2318 | -1.5038 | Night | 202602 | 2026-02-13 | 1.5038
2026-02-13 23:56 | 72.095 | TRUE | FALSE | 0.047825 | 0.066292 | -1.1639 | -1.5888 | -0.2808 | 2026-02-14 08:30 | 2026-02-13 23:56 | lower | TRUE | 1 | 72.1428 | FALSE | FALSE | 0.2305 | 2.1714 | 72.7009 | 1 | -0.2808 | -0.0423 | 0.10331 | -2.3086 | 0.27903 | Extreme triggered | 73.2589 | -2.1714 | Night | 202602 | 2026-02-13 | 2.1714
2026-02-14 00:11 | 72.095 | FALSE | FALSE | -0.043903 | -0.060933 | -1.1711 | -1.5984 | 0 |  | 2026-02-13 23:56 | none | FALSE | 1 | 72.0511 | FALSE | FALSE | 0.2666 | 2.0134 | 72.6586 | 2 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.30374 | Extreme/elevated | 73.2661 | -1.8555 | Night | 202602 | 2026-02-14 | 1.8555
2026-02-14 00:26 | 72.095 | FALSE | FALSE | -0.12026 | -0.16709 | -1.1628 | -1.5873 | 0 |  | 2026-02-13 23:56 | none | FALSE | 1 | 71.9747 | FALSE | FALSE | 0.3083 | 1.884 | 72.6163 | 3 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.32077 | Persistent | 73.2578 | -1.6251 | Night | 202602 | 2026-02-14 | 1.6251
2026-02-14 00:40 | 72.095 | FALSE | FALSE | -0.18363 | -0.25536 | -1.1416 | -1.5588 | 0 |  | 2026-02-13 23:56 | none | FALSE | 1 | 71.9114 | FALSE | FALSE | 0.3535 | 1.7744 | 72.574 | 4 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.3313 | Persistent | 73.2366 | -1.4457 | Night | 202602 | 2026-02-14 | 1.4457
2026-02-14 00:55 | 72.095 | FALSE | FALSE | -0.23523 | -0.32734 | -1.1086 | -1.5144 | 0 |  | 2026-02-13 23:56 | none | FALSE | 1 | 71.8598 | FALSE | FALSE | 0.4009 | 1.6795 | 72.5317 | 5 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.33595 | Persistent | 73.2036 | -1.2998 | Night | 202602 | 2026-02-14 | 1.2998
2026-02-14 01:10 | 72.095 | FALSE | FALSE | -0.27554 | -0.38366 | -1.0643 | -1.4548 | 0 |  | 2026-02-13 23:56 | none | FALSE | 1 | 71.8195 | FALSE | FALSE | 0.4499 | 1.5958 | 72.4894 | 6 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.33496 | Persistent | 73.1593 | -1.1774 | Night | 202602 | 2026-02-14 | 1.1774
2026-02-14 01:25 | 71.8124 | FALSE | TRUE | -0.078689 | -0.1097 | -1.3198 | -1.8047 | -0.2826 |  | 2026-02-13 23:56 | none | FALSE | 1 | 71.7337 | FALSE | FALSE | 0.5469 | 1.6214 | 72.433 | 7 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.34962 | Confirmed/Materialized Shift | 73.1322 | -1.7749 | Night | 202602 | 2026-02-14 | 1.7749
2026-02-14 01:40 | 71.8124 | FALSE | TRUE | -0.14458 | -0.20174 | -1.2728 | -1.7416 | 0 |  | 2026-02-13 23:56 | none | FALSE | 1 | 71.6678 | FALSE | FALSE | 0.5347 | 1.6177 | 72.3765 | 8 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.35435 | Confirmed/Materialized Shift | 73.0852 | -1.592 | Night | 202602 | 2026-02-14 | 1.592
2026-02-14 01:55 | 71.8124 | FALSE | TRUE | -0.19143 | -0.26728 | -1.2068 | -1.6527 | 0 |  | 2026-02-13 23:56 | none | FALSE | 1 | 71.621 | FALSE | FALSE | 0.5254 | 1.5994 | 72.3201 | 9 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.34956 | Confirmed/Materialized Shift | 73.0192 | -1.4524 | Night | 202602 | 2026-02-14 | 1.4524
2026-02-14 02:10 | 71.8124 | FALSE | TRUE | -0.21841 | -0.30507 | -1.1209 | -1.5369 | 0 |  | 2026-02-13 23:56 | none | FALSE | 1 | 71.594 | FALSE | FALSE | 0.5184 | 1.5742 | 72.2637 | 10 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.33483 | Confirmed/Materialized Shift | 72.9333 | -1.3477 | Night | 202602 | 2026-02-14 | 1.3477
2026-02-14 02:25 | 71.8124 | FALSE | TRUE | -0.22269 | -0.31106 | -1.0124 | -1.3901 | 0 |  | 2026-02-13 23:56 | none | FALSE | 0 | 71.5897 | FALSE | FALSE | 0.4853 | 1.5473 | 72.2072 | 11 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.30876 | Confirmed/Materialized Shift | 72.8248 | -1.2788 | Night | 202602 | 2026-02-14 | 1.2788
2026-02-14 02:40 | 71.5298 | FALSE | TRUE | -0.028371 | -0.039679 | -1.2704 | -1.745 | -0.2826 |  | 2026-02-13 23:56 | none | FALSE | 0 | 71.5014 | FALSE | FALSE | 0.5275 | 1.5778 | 72.1508 | 12 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.32469 | Confirmed/Materialized Shift | 72.8002 | -1.9126 | Night | 202602 | 2026-02-14 | 1.9126
2026-02-14 02:55 | 71.5298 | FALSE | TRUE | -0.095141 | -0.13319 | -1.2243 | -1.6828 | 0 |  | 2026-02-13 23:56 | none | FALSE | 0 | 71.4347 | FALSE | FALSE | 0.5141 | 1.5881 | 72.0944 | 13 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.32986 | Confirmed/Materialized Shift | 72.7541 | -1.7116 | Night | 202602 | 2026-02-14 | 1.7116
2026-02-14 03:10 | 71.5298 | FALSE | TRUE | -0.14143 | -0.19811 | -1.1577 | -1.5927 | 0 |  | 2026-02-13 23:56 | none | FALSE | 0 | 71.3884 | FALSE | FALSE | 0.5043 | 1.5864 | 72.0379 | 14 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.32478 | Confirmed/Materialized Shift | 72.6875 | -1.5645 | Night | 202602 | 2026-02-14 | 1.5645
2026-02-14 03:25 | 71.5298 | FALSE | TRUE | -0.16623 | -0.23293 | -1.0696 | -1.4734 | 0 |  | 2026-02-13 23:56 | none | FALSE | 0 | 71.3636 | FALSE | FALSE | 0.4975 | 1.5781 | 71.9815 | 15 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.30897 | Confirmed/Materialized Shift | 72.5994 | -1.462 | Night | 202602 | 2026-02-14 | 1.462
2026-02-14 03:39 | 71.2472 | FALSE | TRUE | 0.0076371 | 0.010718 | -1.3481 | -1.857 | -0.2826 |  | 2026-02-13 23:56 | lower | TRUE | 0 | 71.2548 | FALSE | TRUE | 0.5349 | 1.6059 | 71.9251 | 16 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.33512 | Confirmed/Materialized Shift | 72.5953 | -2.0228 | Night | 202602 | 2026-02-14 | 2.0228
2026-02-14 03:54 | 71.2472 | FALSE | TRUE | -0.078401 | -0.11016 | -1.3213 | -1.8208 | 0 |  | 2026-02-13 23:56 | none | FALSE | 0 | 71.1688 | FALSE | FALSE | 0.5184 | 1.6159 | 71.8687 | 17 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.34993 | Confirmed/Materialized Shift | 72.5685 | -1.776 | Night | 202602 | 2026-02-14 | 1.776
2026-02-14 04:09 | 71.2472 | FALSE | TRUE | -0.14459 | -0.20335 | -1.2746 | -1.7576 | 0 |  | 2026-02-13 23:56 | none | FALSE | 0 | 71.1026 | FALSE | FALSE | 0.5062 | 1.6146 | 71.8122 | 18 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.3548 | Confirmed/Materialized Shift | 72.5218 | -1.5925 | Night | 202602 | 2026-02-14 | 1.5925
2026-02-14 04:24 | 71.2472 | FALSE | TRUE | -0.19175 | -0.26986 | -1.2089 | -1.6685 | 0 |  | 2026-02-13 23:56 | none | FALSE | 0 | 71.0555 | FALSE | FALSE | 0.4968 | 1.6061 | 71.7558 | 19 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.35017 | Confirmed/Materialized Shift | 72.4561 | -1.4524 | Night | 202602 | 2026-02-14 | 1.4524
2026-02-14 04:39 | 70.9646 | FALSE | TRUE | -0.00073602 | -0.0010372 | -1.442 | -1.9915 | -0.2826 |  | 2026-02-13 23:56 | none | FALSE | 0 | 70.9639 | FALSE | FALSE | 0.5332 | 1.6256 | 71.6852 | 20 | -0.2826 | -0.07056 | 0.12539 | -1.6911 | 0.36068 | Confirmed/Materialized Shift | 72.4066 | -1.998 | Night | 202602 | 2026-02-14 | 1.998
2026-02-14 04:54 | 70.9646 | FALSE | TRUE | -0.098056 | -0.13837 | -1.4263 | -1.9702 | 0 |  | 2026-02-13 23:56 | none | FALSE | 0 | 70.8665 | FALSE | FALSE | 0.5162 | 1.6312 | 71.6287 | 21 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.38108 | Confirmed/Materialized Shift | 72.3909 | -1.7427 | Night | 202602 | 2026-02-14 | 1.7427
2026-02-14 05:09 | 70.9646 | FALSE | TRUE | -0.17633 | -0.24909 | -1.3915 | -1.9231 | 0 |  | 2026-02-13 23:56 | none | FALSE | 0 | 70.7883 | FALSE | FALSE | 0.5033 | 1.6275 | 71.5722 | 22 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.39196 | Confirmed/Materialized Shift | 72.3561 | -1.5501 | Night | 202602 | 2026-02-14 | 1.5501
2026-02-14 05:24 | 70.9646 | FALSE | TRUE | -0.23712 | -0.33526 | -1.3393 | -1.8523 | 0 |  | 2026-02-13 23:56 | none | FALSE | 0 | 70.7275 | FALSE | FALSE | 0.4932 | 1.6176 | 71.5157 | 23 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.3941 | Confirmed/Materialized Shift | 72.3039 | -1.3983 | Night | 202602 | 2026-02-14 | 1.3983
2026-02-14 05:39 | 70.682 | FALSE | TRUE | -0.059106 | -0.083692 | -1.5851 | -2.1935 | -0.2826 |  | 2026-02-13 23:56 | none | FALSE | 0 | 70.6229 | FALSE | FALSE | 0.5237 | 1.6275 | 71.445 | 24 | -0.2826 | -0.07065 | 0.12555 | -1.6882 | 0.41106 | Confirmed/Materialized Shift | 72.2671 | -1.8562 | Night | 202602 | 2026-02-14 | 1.8562
2026-02-14 05:54 | 70.682 | FALSE | TRUE | -0.13739 | -0.19476 | -1.5221 | -2.1081 | 0 |  | 2026-02-13 23:56 | none | FALSE | 0 | 70.5446 | FALSE | FALSE | 0.5113 | 1.6292 | 71.3744 | 25 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.41488 | Confirmed/Materialized Shift | 72.2041 | -1.6688 | Night | 202602 | 2026-02-14 | 1.6688
2026-02-14 06:09 | 70.682 | FALSE | TRUE | -0.19012 | -0.2697 | -1.4336 | -1.9879 | 0 |  | 2026-02-13 23:56 | none | FALSE | 0 | 70.4919 | FALSE | FALSE | 0.5021 | 1.6254 | 71.3037 | 26 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.40592 | Confirmed/Materialized Shift | 72.1156 | -1.5316 | Night | 202602 | 2026-02-14 | 1.5316
2026-02-14 06:24 | 70.682 | FALSE | TRUE | -0.25488 | -0.3619 | -1.3853 | -1.9222 | 0 |  | 2026-02-13 23:56 | none | FALSE | 0 | 70.4271 | FALSE | FALSE | 0.4919 | 1.6163 | 71.2472 | 27 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.41004 | Confirmed/Materialized Shift | 72.0673 | -1.3784 | Night | 202602 | 2026-02-14 | 1.3784
2026-02-14 06:38 | 70.682 | FALSE | TRUE | -0.30316 | -0.43075 | -1.3205 | -1.834 | 0 |  | 2026-02-13 23:56 | none | FALSE | 0 | 70.3788 | FALSE | FALSE | 0.4835 | 1.6033 | 71.1907 | 28 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.40592 | Confirmed/Materialized Shift | 72.0025 | -1.2532 | Night | 202602 | 2026-02-14 | 1.2532
2026-02-14 06:53 | 70.3994 | FALSE | TRUE | -0.10913 | -0.15526 | -1.5504 | -2.1548 | -0.2826 |  | 2026-02-13 23:56 | none | FALSE | 0 | 70.2903 | FALSE | FALSE | 0.5158 | 1.6079 | 71.12 | 29 | -0.2826 | -0.07065 | 0.12555 | -1.6882 | 0.41488 | Confirmed/Materialized Shift | 71.9498 | -1.737 | Night | 202602 | 2026-02-14 | 1.737
2026-02-14 07:08 | 70.3994 | FALSE | TRUE | -0.17215 | -0.24513 | -1.4721 | -2.0482 | 0 |  | 2026-02-13 23:56 | none | FALSE | 0 | 70.2273 | FALSE | FALSE | 0.5054 | 1.607 | 71.0494 | 30 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.41106 | Confirmed/Materialized Shift | 71.8715 | -1.5812 | Day | 202602 | 2026-02-14 | 1.5812
2026-02-14 07:23 | 70.3994 | FALSE | TRUE | -0.20886 | -0.29757 | -1.3675 | -1.9055 | 0 |  | 2026-02-13 23:56 | none | FALSE | 0 | 70.1905 | FALSE | FALSE | 0.498 | 1.6026 | 70.9787 | 31 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.3941 | Confirmed/Materialized Shift | 71.7669 | -1.47 | Day | 202602 | 2026-02-14 | 1.47
2026-02-14 07:30 | 70.3994 | FALSE | TRUE | -0.26111 | -0.37227 | -1.3067 | -1.8223 | 0 |  | 2026-02-13 23:56 | none | FALSE | 0 | 70.1383 | FALSE | FALSE | 0.4889 | 1.5942 | 70.9222 | 32 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.39196 | Confirmed/Materialized Shift | 71.7061 | -1.3338 | Day | 202602 | 2026-02-14 | 1.3338
2026-02-14 07:45 | 70.3994 | FALSE | TRUE | -0.29588 | -0.42206 | -1.2285 | -1.7151 | 0 |  | 2026-02-13 23:56 | none | FALSE | 0 | 70.1035 | FALSE | FALSE | 0.4816 | 1.583 | 70.8657 | 33 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.38108 | Confirmed/Materialized Shift | 71.6279 | -1.2236 | Day | 202602 | 2026-02-14 | 1.2236
2026-02-14 08:00 | 70.3994 | FALSE | TRUE | -0.3116 | -0.44458 | -1.1311 | -1.5813 | 0 |  | 2026-02-13 23:56 | none | FALSE | 0 | 70.0878 | FALSE | FALSE | 0.4757 | 1.5698 | 70.8092 | 34 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.36068 | Confirmed/Materialized Shift | 71.5305 | -1.1361 | Day | 202602 | 2026-02-14 | 1.1361
2026-02-14 08:16 | 70.3994 | FALSE | TRUE | -0.30473 | -0.43474 | -1.0112 | -1.4161 | 0 |  | 2026-02-13 23:56 | none | FALSE | 0 | 70.0947 | FALSE | FALSE | 0.4716 | 1.5557 | 70.7527 | 35 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.32899 | Confirmed/Materialized Shift | 71.4106 | -1.0737 | Day | 202602 | 2026-02-14 | 1.0737
2026-02-14 08:30 | 70.682 | TRUE | FALSE | -0.57335 | -0.8178 | -0.65813 | -0.92253 | 0.2826 |  |  | none | FALSE | 1 | 70.1086 | FALSE | FALSE | 0.0378 |  | 70.7244 | 0 | 0.2826 | -0.02826 | 0.12638 | 2.4597 | 0.30787 | Persistence ends | 71.3401 | -0.13769 | Day | 202602 | 2026-02-14 | 0.13769
2026-02-14 08:30 | 70.682 | FALSE | FALSE | -0.55033 | -0.7847 | -0.57859 | -0.81193 | 0 |  |  | none | FALSE | 1 | 70.1317 | FALSE | FALSE | 0.0319 |  | 70.6961 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.28223 | Normal | 71.2606 | -0.050066 | Day | 202602 | 2026-02-14 | 0.050066
2026-02-14 08:45 | 70.9646 | TRUE | FALSE | -0.80126 | -1.142 | -0.23606 | -0.33155 | 0.2826 |  |  | none | FALSE | 2 | 70.1633 | TRUE | FALSE | 0.1298 |  | 70.682 | 0 | 0.2826 | -0.01413 | 0.14424 | 2.0571 | 0.25933 | Normal | 71.2007 | 1.0897 | Day | 202602 | 2026-02-14 | 1.0897
2026-02-14 09:00 | 71.2472 | FALSE | FALSE | -1.0839 | -1.5448 | 0.046537 | 0.06536 | 0.2826 | 2026-02-14 11:59 | 2026-02-14 09:00 | upper | TRUE | 2 | 70.1633 | FALSE | FALSE | 0.2596 | 2.1794 | 70.682 | 1 | 0.2826 | 0 | 0.15881 | 1.7795 | 0.25933 | Extreme triggered | 71.2007 | 2.1794 | Day | 202602 | 2026-02-14 | 2.1794
2026-02-14 09:15 | 71.5298 | FALSE | FALSE | -1.4521 | -2.0722 | 0.18696 | 0.26206 | 0.2826 |  | 2026-02-14 09:00 | upper | TRUE | 2 | 70.0777 | FALSE | FALSE | 0.3442 | 2.3853 | 70.7103 | 2 | 0.2826 | 0.02826 | 0.15614 | 1.6289 | 0.31629 | Extreme/elevated | 71.3428 | 2.5911 | Day | 202602 | 2026-02-14 | 2.5911
2026-02-14 09:30 | 71.8124 | FALSE | FALSE | -1.8564 | -2.6537 | 0.26307 | 0.36768 | 0.2826 |  | 2026-02-14 09:00 | upper | TRUE | 2 | 69.956 | FALSE | TRUE | 0.4059 | 2.477 | 70.7527 | 3 | 0.2826 | 0.04239 | 0.16593 | 1.4477 | 0.39834 | Persistent | 71.5493 | 2.6604 | Day | 202602 | 2026-02-14 | 2.6604
2026-02-14 09:45 | 72.095 | FALSE | FALSE | -2.2814 | -3.2678 | 0.29027 | 0.40425 | 0.2826 |  | 2026-02-14 09:00 | upper | TRUE | 2 | 69.8136 | FALSE | TRUE | 0.4579 | 2.5035 | 70.8092 | 4 | 0.2826 | 0.05652 | 0.17396 | 1.2996 | 0.49778 | Persistent | 71.8047 | 2.5831 | Day | 202602 | 2026-02-14 | 2.5831
2026-02-14 10:00 | 72.6584 | TRUE | FALSE | -3.0591 | -4.3952 | 0.47002 | 0.6511 | 0.5634 |  | 2026-02-14 09:00 | upper | TRUE | 3 | 69.5993 | TRUE | TRUE | 0.5532 | 2.5481 | 70.8939 | 5 | 0.5634 | 0.08469 | 0.20684 | 2.3144 | 0.64726 | Persistent | 72.1884 | 2.7262 | Day | 202602 | 2026-02-14 | 2.7262
2026-02-14 10:15 | 72.941 | FALSE | FALSE | -3.5137 | -5.061 | 0.35467 | 0.48862 | 0.2826 |  | 2026-02-14 09:00 | upper | TRUE | 3 | 69.4273 | FALSE | TRUE | 0.5918 | 2.5316 | 71.0068 | 6 | 0.2826 | 0.11295 | 0.1921 | 0.88312 | 0.78976 | Persistent | 72.5863 | 2.4491 | Day | 202602 | 2026-02-14 | 2.4491
2026-02-14 10:29 | 73.2236 | FALSE | TRUE | -3.9442 | -5.6932 | 0.23519 | 0.32223 | 0.2826 |  | 2026-02-14 09:00 | upper | TRUE | 3 | 69.2794 | FALSE | TRUE | 0.636 | 2.4919 | 71.1339 | 7 | 0.2826 | 0.12708 | 0.19374 | 0.80271 | 0.92726 | Confirmed/Materialized Shift | 72.9884 | 2.2536 | Day | 202602 | 2026-02-14 | 2.2536
2026-02-14 10:44 | 73.5062 | FALSE | TRUE | -4.3517 | -6.2928 | 0.11046 | 0.1505 | 0.2826 |  | 2026-02-14 09:00 | upper | TRUE | 2 | 69.1545 | FALSE | TRUE | 0.5974 | 2.4434 | 71.2751 | 8 | 0.2826 | 0.14121 | 0.19429 | 0.72772 | 1.0603 | Confirmed/Materialized Shift | 73.3957 | 2.1042 | Day | 202602 | 2026-02-14 | 2.1042
2026-02-14 10:59 | 73.2236 | FALSE | TRUE | -4.0917 | -5.9187 | -0.4489 | -0.60931 | -0.2826 |  | 2026-02-14 09:00 | none | FALSE | 2 | 69.1319 | FALSE | FALSE | 0.5641 | 2.3502 | 71.4022 | 9 | -0.2826 | 0.12708 | 0.21434 | -1.9113 | 1.1352 | Confirmed/Materialized Shift | 73.6725 | 1.6046 | Day | 202602 | 2026-02-14 | 1.6046
2026-02-14 11:14 | 73.2236 | FALSE | TRUE | -4.0767 | -5.8957 | -0.68801 | -0.93085 | 0 |  | 2026-02-14 09:00 | none | FALSE | 1 | 69.1469 | FALSE | FALSE | 0.5234 | 2.2574 | 71.5293 | 10 | 0 | 0.12708 | 0.21434 | -0.59288 | 1.1912 | Confirmed/Materialized Shift | 73.9116 | 1.4224 | Day | 202602 | 2026-02-14 | 1.4224
2026-02-14 11:29 | 72.941 | FALSE | TRUE | -3.6843 | -5.3198 | -1.115 | -1.5056 | -0.2826 |  | 2026-02-14 09:00 | none | FALSE | 1 | 69.2567 | FALSE | FALSE | 0.5 | 2.1495 | 71.6563 | 11 | -0.2826 | 0.12708 | 0.21434 | -1.9113 | 1.1998 | Confirmed/Materialized Shift | 74.056 | 1.0707 | Day | 202602 | 2026-02-14 | 1.0707
2026-02-14 11:44 | 73.2236 | FALSE | TRUE | -3.8466 | -5.5445 | -0.99448 | -1.3399 | 0.2826 |  | 2026-02-14 09:00 | none | FALSE | 1 | 69.377 | FALSE | FALSE | 0.5071 | 2.0686 | 71.7976 | 12 | 0.2826 | 0.14121 | 0.21484 | 0.65812 | 1.2103 | Confirmed/Materialized Shift | 74.2181 | 1.1783 | Day | 202602 | 2026-02-14 | 1.1783
2026-02-14 11:59 | 72.941 | FALSE | FALSE | -3.3943 | -4.8806 | -1.3616 | -1.8325 | -0.2826 |  |  | none | FALSE | 1 | 69.5467 | FALSE | FALSE | 0.0856 |  | 71.9246 | 0 | -0.2826 | 0.12708 | 0.23313 | -1.7573 | 1.189 | Persistence ends | 74.3026 | 0.85483 | Day | 202602 | 2026-02-14 | 0.85483
2026-02-14 12:14 | 72.941 | FALSE | FALSE | -3.1946 | -4.5803 | -1.416 | -1.9043 | 0 |  |  | none | FALSE | 1 | 69.7464 | FALSE | FALSE | 0.08 |  | 72.0517 | 0 | 0 | 0.12708 | 0.23313 | -0.5451 | 1.1527 | Normal | 74.357 | 0.77152 | Day | 202602 | 2026-02-14 | 0.77152
2026-02-14 12:29 | 72.941 | FALSE | FALSE | -2.9618 | -4.2324 | -1.4374 | -1.9325 | 0 |  |  | none | FALSE | 0 | 69.9792 | FALSE | FALSE | 0.0462 |  | 72.1788 | 0 | 0 | 0.12708 | 0.23313 | -0.5451 | 1.0998 | Normal | 74.3784 | 0.69305 | Day | 202602 | 2026-02-14 | 0.69305
2026-02-14 12:44 | 72.941 | FALSE | FALSE | -2.6908 | -3.8303 | -1.4206 | -1.9103 | 0 |  |  | none | FALSE | 0 | 70.2502 | FALSE | FALSE | 0.0412 |  | 72.3059 | 0 | 0 | 0.12708 | 0.23313 | -0.5451 | 1.0278 | Normal | 74.3616 | 0.61792 | Day | 202602 | 2026-02-14 | 0.61792
2026-02-14 12:59 | 72.941 | FALSE | FALSE | -2.3729 | -3.3625 | -1.3568 | -1.8261 | 0 |  |  | none | FALSE | 0 | 70.5681 | FALSE | FALSE | 0.0363 |  | 72.433 | 0 | 0 | 0.12708 | 0.23313 | -0.5451 | 0.93242 | Normal | 74.2978 | 0.54487 | Day | 202602 | 2026-02-14 | 0.54487
2026-02-14 13:14 | 73.2236 | FALSE | FALSE | -2.3653 | -3.338 | -1.0381 | -1.3979 | 0.2826 |  |  | none | FALSE | 0 | 70.8583 | FALSE | FALSE | 0.052 |  | 72.56 | 0 | 0.2826 | 0.12708 | 0.23313 | 0.66709 | 0.85085 | Normal | 74.2617 | 0.77989 | Day | 202602 | 2026-02-14 | 0.77989
2026-02-14 13:28 | 73.2236 | FALSE | FALSE | -2.0123 | -2.8258 | -0.9393 | -1.2665 | 0 |  |  | none | FALSE | 0 | 71.2113 | FALSE | FALSE | 0.0485 |  | 72.6871 | 0 | 0 | 0.12708 | 0.23313 | -0.5451 | 0.7379 | Normal | 74.1629 | 0.72705 | Day | 202602 | 2026-02-14 | 0.72705
2026-02-14 13:43 | 73.2236 | FALSE | FALSE | -1.6726 | -2.3377 | -0.82554 | -1.1149 | 0 |  |  | none | FALSE | 0 | 71.551 | FALSE | FALSE | 0.0452 |  | 72.8001 | 0 | 0 | 0.11295 | 0.23177 | -0.48734 | 0.62454 | Normal | 74.0491 | 0.67816 | Day | 202602 | 2026-02-14 | 0.67816
2026-02-14 13:59 | 73.5062 | FALSE | FALSE | -1.6438 | -2.2874 | -0.45743 | -0.61845 | 0.2826 |  |  | none | FALSE | 0 | 71.8624 | FALSE | FALSE | 0.0753 |  | 72.913 | 0 | 0.2826 | 0.11295 | 0.23177 | 0.73198 | 0.52531 | Normal | 73.9636 | 1.1292 | Day | 202602 | 2026-02-14 | 1.1292
2026-02-14 14:14 | 73.7888 | FALSE | FALSE | -1.6622 | -2.3045 | -0.13648 | -0.18461 | 0.2826 |  |  | none | FALSE | 0 | 72.1266 | FALSE | FALSE | 0.1131 |  | 73.026 | 0 | 0.2826 | 0.11295 | 0.23177 | 0.73198 | 0.44966 | Normal | 73.9253 | 1.6965 | Day | 202602 | 2026-02-14 | 1.6965
2026-02-14 14:28 | 73.7888 | FALSE | FALSE | -1.4257 | -1.9702 | -0.097633 | -0.13214 | 0 |  |  | none | FALSE | 0 | 72.3631 | FALSE | FALSE | 0.1162 |  | 73.1248 | 0 | 0 | 0.09882 | 0.22948 | -0.43062 | 0.38083 | Normal | 73.8864 | 1.7436 | Day | 202602 | 2026-02-14 | 1.7436
2026-02-14 14:43 | 73.7888 | FALSE | FALSE | -1.227 | -1.691 | -0.06835 | -0.092544 | 0 |  |  | none | FALSE | 0 | 72.5618 | FALSE | FALSE | 0.1193 |  | 73.2095 | 0 | 0 | 0.08469 | 0.22625 | -0.37432 | 0.32384 | Normal | 73.8572 | 1.7889 | Day | 202602 | 2026-02-14 | 1.7889
2026-02-14 14:54 | 74.0714 | FALSE | FALSE | -1.492 | -2.0556 | 0.090605 | 0.12247 | 0.2826 | 2026-02-14 15:12 | 2026-02-14 14:54 | upper | TRUE | 0 | 72.5794 | FALSE | FALSE | 0.2077 | 2.2586 | 73.2801 | 1 | 0.2826 | 0.07065 | 0.20244 | 1.047 | 0.35034 | Extreme triggered | 73.9808 | 2.2586 | Day | 202602 | 2026-02-14 | 2.2586
2026-02-14 14:57 | 73.7888 | FALSE | FALSE | -1.183 | -1.6293 | -0.2504 | -0.3382 | -0.2826 |  | 2026-02-14 14:54 | none | FALSE | 0 | 72.6058 | FALSE | FALSE | 0.201 | 1.7799 | 73.3225 | 2 | -0.2826 | 0.04239 | 0.21058 | -1.5433 | 0.35834 | Extreme/elevated | 74.0392 | 1.3012 | Day | 202602 | 2026-02-14 | 1.3012
2026-02-14 15:12 | 73.5062 | FALSE | FALSE | -0.88918 | -1.2245 | -0.55006 | -0.74275 | -0.2826 |  |  | none | FALSE | 0 | 72.617 | FALSE | FALSE | 0.0314 |  | 73.3366 | 0 | -0.2826 | 0.01413 | 0.21454 | -1.3831 | 0.35981 | Persistence ends | 74.0563 | 0.47125 | Day | 202602 | 2026-02-14 | 0.47125
2026-02-14 15:27 | 73.2236 | FALSE | FALSE | -0.61778 | -0.85087 | -0.8156 | -1.1016 | -0.2826 |  |  | none | FALSE | 0 | 72.6058 | FALSE | FALSE | 0.0184 |  | 73.3225 | 0 | -0.2826 | -0.01413 | 0.21454 | -1.2514 | 0.35834 | Normal | 74.0392 | -0.27602 | Day | 202602 | 2026-02-14 | 0.27602
2026-02-14 15:28 | 73.2236 | FALSE | FALSE | -0.61778 | -0.85087 | -0.8156 | -1.1016 | 0 |  |  | none | FALSE | 0 | 72.6058 | FALSE | FALSE | 0.0184 |  | 73.3225 | 0 | 0 | 0 | 0.20502 | 0 | 0.35834 | Normal | 74.0392 | -0.27602 | Day | 202602 | 2026-02-14 | 0.27602
2026-02-14 15:43 | 73.2236 | FALSE | FALSE | -0.61778 | -0.85087 | -0.8156 | -1.1016 | 0 |  |  | none | FALSE | 0 | 72.6058 | FALSE | FALSE | 0.0184 |  | 73.3225 | 0 | 0 | 0 | 0.20502 | 0 | 0.35834 | Normal | 74.0392 | -0.27602 | Day | 202602 | 2026-02-14 | 0.27602
2026-02-14 15:58 | 72.941 | FALSE | FALSE | -0.33518 | -0.46164 | -1.0982 | -1.4833 | -0.2826 |  |  | none | FALSE | 0 | 72.6058 | FALSE | FALSE | 0.071 |  | 73.3225 | 0 | -0.2826 | 0 | 0.20502 | -1.3784 | 0.35834 | Normal | 74.0392 | -1.0646 | Day | 202602 | 2026-02-14 | 1.0646
2026-02-14 16:13 | 72.941 | FALSE | FALSE | -0.36841 | -0.50764 | -1.1032 | -1.4899 | 0 |  |  | none | FALSE | 0 | 72.5726 | FALSE | FALSE | 0.0666 |  | 73.3084 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.36789 | Normal | 74.0442 | -0.9986 | Day | 202602 | 2026-02-14 | 0.9986
2026-02-14 16:27 | 72.6584 | FALSE | FALSE | -0.13944 | -0.19228 | -1.4111 | -1.9052 | -0.2826 |  |  | none | FALSE | 0 | 72.519 | FALSE | FALSE | 0.1094 |  | 73.2943 | 0 | -0.2826 | -0.01413 | 0.19396 | -1.3842 | 0.38764 | Normal | 74.0695 | -1.6403 | Day | 202602 | 2026-02-14 | 1.6403
2026-02-14 16:43 | 72.3758 | FALSE | FALSE | 0.024726 | 0.034151 | -1.7557 | -2.3683 | -0.2826 | 2026-02-14 17:13 | 2026-02-14 16:43 | lower | TRUE | 0 | 72.4005 | FALSE | FALSE | 0.1943 | 2.0571 | 73.266 | 1 | -0.2826 | -0.02826 | 0.20296 | -1.2532 | 0.43273 | Extreme triggered | 74.1315 | -2.0571 | Day | 202602 | 2026-02-14 | 2.0571
2026-02-14 16:58 | 72.6584 | FALSE | FALSE | -0.30302 | -0.41879 | -1.4899 | -2.0094 | 0.2826 |  | 2026-02-14 16:43 | none | FALSE | 0 | 72.3554 | FALSE | FALSE | 0.2026 | 1.6906 | 73.2519 | 2 | 0.2826 | -0.01413 | 0.21454 | 1.3831 | 0.44824 | Extreme/elevated | 74.1483 | -1.324 | Day | 202602 | 2026-02-14 | 1.324
2026-02-14 17:13 | 72.941 | FALSE | FALSE | -0.58562 | -0.80936 | -1.2073 | -1.6283 | 0.2826 |  |  | none | FALSE | 0 | 72.3554 | FALSE | FALSE | 0.0462 |  | 73.2519 | 0 | 0.2826 | 0 | 0.22459 | 1.2583 | 0.44824 | Persistence ends | 74.1483 | -0.69351 | Day | 202602 | 2026-02-14 | 0.69351
2026-02-14 17:27 | 73.2236 | FALSE | FALSE | -0.84229 | -1.1637 | -0.92707 | -1.2502 | 0.2826 |  |  | none | FALSE | 0 | 72.3813 | FALSE | FALSE | 0.0064 |  | 73.266 | 0 | 0.2826 | 0.01413 | 0.23331 | 1.1507 | 0.44234 | Normal | 74.1507 | -0.095831 | Day | 202602 | 2026-02-14 | 0.095831
2026-02-14 17:42 | 72.941 | FALSE | FALSE | -0.58562 | -0.80936 | -1.2073 | -1.6283 | -0.2826 |  |  | none | FALSE | 0 | 72.3554 | FALSE | FALSE | 0.0462 |  | 73.2519 | 0 | -0.2826 | -0.01413 | 0.23331 | -1.1507 | 0.44824 | Normal | 74.1483 | -0.69351 | Day | 202602 | 2026-02-14 | 0.69351
2026-02-14 17:42 | 72.941 | FALSE | FALSE | -0.61047 | -0.844 | -1.2039 | -1.6237 | 0 |  |  | none | FALSE | 0 | 72.3305 | FALSE | FALSE | 0.0436 |  | 73.2377 | 0 | 0 | -0.01413 | 0.23331 | 0.060564 | 0.4536 | Normal | 74.1449 | -0.65417 | Day | 202602 | 2026-02-14 | 0.65417
2026-02-14 17:43 | 73.2236 | FALSE | FALSE | -0.89307 | -1.2347 | -0.92133 | -1.2426 | 0.2826 |  |  | none | FALSE | 0 | 72.3305 | FALSE | FALSE | 0.0021 |  | 73.2377 | 0 | 0.2826 | 0 | 0.24258 | 1.165 | 0.4536 | Normal | 74.1449 | -0.031151 | Day | 202602 | 2026-02-14 | 0.031151
2026-02-14 17:58 | 73.5062 | FALSE | FALSE | -1.1757 | -1.6254 | -0.63873 | -0.86146 | 0.2826 |  |  | none | FALSE | 0 | 72.3305 | FALSE | FALSE | 0.0395 |  | 73.2377 | 0 | 0.2826 | 0 | 0.24258 | 1.165 | 0.4536 | Normal | 74.1449 | 0.59187 | Day | 202602 | 2026-02-14 | 0.59187
2026-02-14 18:13 | 73.5062 | FALSE | FALSE | -1.162 | -1.6063 | -0.59684 | -0.80541 | 0 |  |  | none | FALSE | 0 | 72.3442 | FALSE | FALSE | 0.0428 |  | 73.2236 | 0 | 0 | -0.01413 | 0.23331 | 0.060564 | 0.43972 | Normal | 74.103 | 0.64268 | Day | 202602 | 2026-02-14 | 0.64268
2026-02-14 18:28 | 73.5062 | FALSE | FALSE | -1.1465 | -1.5845 | -0.55305 | -0.74677 | 0 |  |  | none | FALSE | 0 | 72.3597 | FALSE | FALSE | 0.0466 |  | 73.2095 | 0 | 0 | -0.01413 | 0.23331 | 0.060564 | 0.42489 | Normal | 74.0593 | 0.69837 | Night | 202602 | 2026-02-14 | 0.69837
2026-02-14 18:42 | 73.7888 | FALSE | FALSE | -1.4291 | -1.975 | -0.27045 | -0.36518 | 0.2826 |  |  | none | FALSE | 0 | 72.3597 | FALSE | FALSE | 0.0909 |  | 73.2095 | 0 | 0.2826 | 0 | 0.24258 | 1.165 | 0.42489 | Normal | 74.0593 | 1.3635 | Night | 202602 | 2026-02-14 | 1.3635
2026-02-14 18:57 | 73.7888 | FALSE | FALSE | -1.3907 | -1.9209 | -0.20375 | -0.27536 | 0 |  |  | none | FALSE | 0 | 72.3981 | FALSE | FALSE | 0.0993 |  | 73.1953 | 0 | 0 | -0.01413 | 0.23331 | 0.060564 | 0.3986 | Normal | 73.9925 | 1.4888 | Night | 202602 | 2026-02-14 | 1.4888
2026-02-14 19:12 | 74.0714 | FALSE | FALSE | -1.7117 | -2.3656 | 0.012149 | 0.016405 | 0.2826 | 2026-02-14 20:12 | 2026-02-14 19:12 | upper | TRUE | 0 | 72.3597 | FALSE | FALSE | 0.1924 | 2.0286 | 73.2095 | 1 | 0.2826 | 0.01413 | 0.23331 | 1.1507 | 0.42489 | Extreme triggered | 74.0593 | 2.0286 | Night | 202602 | 2026-02-14 | 2.0286
2026-02-14 19:27 | 74.0714 | FALSE | FALSE | -1.7592 | -2.4328 | -0.091875 | -0.12388 | 0 |  | 2026-02-14 19:12 | none | FALSE | 0 | 72.3122 | FALSE | FALSE | 0.2344 | 1.915 | 73.2377 | 2 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.46277 | Extreme/elevated | 74.1633 | 1.8015 | Night | 202602 | 2026-02-14 | 1.8015
2026-02-14 19:42 | 73.7888 | FALSE | FALSE | -1.4805 | -2.0475 | -0.43488 | -0.5859 | -0.2826 |  | 2026-02-14 19:12 | none | FALSE | 0 | 72.3083 | FALSE | FALSE | 0.2442 | 1.6406 | 73.266 | 3 | -0.2826 | 0.02826 | 0.22271 | -1.3958 | 0.47884 | Persistent | 74.2237 | 1.0918 | Night | 202602 | 2026-02-14 | 1.0918
2026-02-14 19:57 | 73.7888 | FALSE | FALSE | -1.4799 | -2.0467 | -0.49082 | -0.66078 | 0 |  | 2026-02-14 19:12 | none | FALSE | 0 | 72.3089 | FALSE | FALSE | 0.2955 | 1.4814 | 73.2943 | 4 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.49269 | Persistent | 74.2796 | 1.0038 | Night | 202602 | 2026-02-14 | 1.0038
2026-02-14 20:12 | 73.7888 | FALSE | FALSE | -1.4753 | -2.0401 | -0.54269 | -0.73009 | 0 |  |  | none | FALSE | 0 | 72.3135 | FALSE | FALSE | 0.0616 |  | 73.3225 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.50449 | Persistence ends | 74.3315 | 0.92428 | Night | 202602 | 2026-02-14 | 0.92428
2026-02-14 20:27 | 73.7888 | FALSE | FALSE | -1.4366 | -1.9856 | -0.58882 | -0.79167 | 0 |  |  | none | FALSE | 0 | 72.3522 | FALSE | FALSE | 0.0558 |  | 73.3649 | 0 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.50636 | Normal | 74.3776 | 0.83715 | Night | 202602 | 2026-02-14 | 0.83715
2026-02-14 20:41 | 73.7888 | FALSE | FALSE | -1.3905 | -1.9206 | -0.62747 | -0.84319 | 0 |  |  | none | FALSE | 0 | 72.3983 | FALSE | FALSE | 0.0504 |  | 73.4073 | 0 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.50449 | Normal | 74.4163 | 0.75623 | Night | 202602 | 2026-02-14 | 0.75623
2026-02-14 20:56 | 73.7888 | FALSE | FALSE | -1.2827 | -1.7691 | -0.6327 | -0.85015 | 0 |  |  | none | FALSE | 0 | 72.5061 | FALSE | FALSE | 0.0452 |  | 73.4638 | 0 | 0 | 0.05652 | 0.19665 | -0.28742 | 0.47884 | Normal | 74.4215 | 0.6787 | Night | 202602 | 2026-02-14 | 0.6787
2026-02-14 21:11 | 73.7888 | FALSE | FALSE | -1.0724 | -1.4747 | -0.56369 | -0.75813 | 0 |  |  | none | FALSE | 0 | 72.7164 | FALSE | FALSE | 0.0415 |  | 73.5345 | 0 | 0 | 0.07065 | 0.18049 | -0.39144 | 0.40901 | Normal | 74.3525 | 0.62184 | Night | 202602 | 2026-02-14 | 0.62184
2026-02-14 21:26 | 73.5062 | FALSE | FALSE | -0.63659 | -0.87361 | -0.77789 | -1.0472 | -0.2826 |  |  | none | FALSE | 0 | 72.8696 | FALSE | FALSE | 0.0133 |  | 73.5768 | 0 | -0.2826 | 0.04239 | 0.18957 | -1.7143 | 0.35362 | Normal | 74.2841 | -0.19979 | Night | 202602 | 2026-02-14 | 0.19979
2026-02-14 21:41 | 73.5062 | FALSE | FALSE | -0.54356 | -0.74498 | -0.74138 | -0.99852 | 0 |  |  | none | FALSE | 0 | 72.9626 | FALSE | FALSE | 0.0205 |  | 73.6051 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.32123 | Normal | 74.2476 | -0.30791 | Night | 202602 | 2026-02-14 | 0.30791
2026-02-14 21:56 | 73.5062 | FALSE | FALSE | -0.50611 | -0.69329 | -0.73219 | -0.98626 | 0 |  |  | none | FALSE | 0 | 73.0001 | FALSE | FALSE | 0.0243 |  | 73.6192 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.30957 | Normal | 74.2384 | -0.36515 | Night | 202602 | 2026-02-14 | 0.36515
2026-02-14 22:11 | 73.5062 | FALSE | FALSE | -0.39333 | -0.53797 | -0.67593 | -0.91117 | 0 |  |  | none | FALSE | 0 | 73.1129 | FALSE | FALSE | 0.0352 |  | 73.6475 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.26731 | Normal | 74.1821 | -0.52859 | Night | 202602 | 2026-02-14 | 0.52859
2026-02-14 22:26 | 73.5062 | FALSE | FALSE | -0.25657 | -0.35026 | -0.59569 | -0.80387 | 0 |  |  | none | FALSE | 0 | 73.2496 | FALSE | FALSE | 0.0531 |  | 73.6758 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.21306 | Normal | 74.1019 | -0.79582 | Night | 202602 | 2026-02-14 | 0.79582
2026-02-14 22:41 | 73.2236 | FALSE | FALSE | 0.026035 | 0.035543 | -0.87829 | -1.1852 | -0.2826 | 2026-02-15 00:55 | 2026-02-14 22:41 | lower | TRUE | 0 | 73.2496 | FALSE | FALSE | 0.1986 | 2.1222 | 73.6758 | 1 | -0.2826 | 0 | 0.15881 | -1.7795 | 0.21306 | Extreme triggered | 74.1019 | -2.1222 | Night | 202602 | 2026-02-14 | 2.1222
2026-02-14 22:56 | 73.2236 | FALSE | FALSE | -0.028587 | -0.039055 | -0.90465 | -1.2204 | 0 |  | 2026-02-14 22:41 | none | FALSE | 0 | 73.195 | FALSE | FALSE | 0.2395 | 1.9998 | 73.6616 | 2 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.23331 | Extreme/elevated | 74.1282 | -1.8775 | Night | 202602 | 2026-02-14 | 1.8775
2026-02-14 23:11 | 73.2236 | FALSE | FALSE | -0.078293 | -0.10704 | -0.92609 | -1.249 | 0 |  | 2026-02-14 22:41 | none | FALSE | 0 | 73.1453 | FALSE | FALSE | 0.284 | 1.896 | 73.6475 | 3 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.2511 | Persistent | 74.1497 | -1.6882 | Night | 202602 | 2026-02-14 | 1.6882
2026-02-14 23:26 | 73.2236 | FALSE | FALSE | -0.12407 | -0.16973 | -0.94361 | -1.2723 | 0 |  | 2026-02-14 22:41 | none | FALSE | 0 | 73.0995 | FALSE | FALSE | 0.3309 | 1.8058 | 73.6334 | 4 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.26692 | Persistent | 74.1672 | -1.5352 | Night | 202602 | 2026-02-14 | 1.5352
2026-02-14 23:40 | 73.2236 | FALSE | FALSE | -0.17696 | -0.24225 | -0.93998 | -1.2674 | 0 |  | 2026-02-14 22:41 | none | FALSE | 0 | 73.0466 | FALSE | FALSE | 0.3768 | 1.7179 | 73.6051 | 5 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.27923 | Persistent | 74.1636 | -1.3663 | Night | 202602 | 2026-02-14 | 1.3663
2026-02-14 23:55 | 73.2236 | FALSE | FALSE | -0.223 | -0.30547 | -0.9295 | -1.2535 | 0 |  | 2026-02-14 22:41 | none | FALSE | 0 | 73.0006 | FALSE | FALSE | 0.4246 | 1.6359 | 73.5768 | 6 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.28812 | Persistent | 74.1531 | -1.226 | Night | 202602 | 2026-02-14 | 1.226
2026-02-15 00:10 | 73.2236 | FALSE | TRUE | -0.2362 | -0.32362 | -0.85792 | -1.1581 | 0 |  | 2026-02-14 22:41 | none | FALSE | 0 | 72.9874 | FALSE | FALSE | 0.4758 | 1.5645 | 73.5345 | 7 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27353 | Confirmed/Materialized Shift | 74.0815 | -1.1365 | Night | 202602 | 2026-02-15 | 1.1365
2026-02-15 00:26 | 73.2236 | FALSE | TRUE | -0.23289 | -0.31906 | -0.76983 | -1.0404 | 0 |  | 2026-02-14 22:41 | none | FALSE | 0 | 72.9907 | FALSE | FALSE | 0.4714 | 1.5029 | 73.4921 | 8 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.25068 | Confirmed/Materialized Shift | 73.9934 | -1.071 | Night | 202602 | 2026-02-15 | 1.071
2026-02-15 00:40 | 72.941 | TRUE | TRUE | -0.029081 | -0.039886 | -1.0464 | -1.4143 | -0.2826 |  | 2026-02-14 22:41 | none | FALSE | 1 | 72.9119 | FALSE | FALSE | 0.5547 | 1.5461 | 73.4497 | 9 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.26888 | Confirmed/Materialized Shift | 73.9874 | -1.8918 | Night | 202602 | 2026-02-15 | 1.8918
2026-02-15 00:55 | 73.2236 | TRUE | FALSE | -0.32407 | -0.44455 | -0.71971 | -0.97333 | 0.2826 |  |  | none | FALSE | 2 | 72.8995 | TRUE | FALSE | 0.1077 |  | 73.4214 | 0 | 0.2826 | -0.02826 | 0.12638 | 2.4597 | 0.26095 | Persistence ends | 73.9433 | -0.75808 | Night | 202602 | 2026-02-15 | 0.75808
2026-02-15 01:10 | 73.2236 | FALSE | FALSE | -0.32927 | -0.45171 | -0.66839 | -0.90456 | 0 |  |  | none | FALSE | 2 | 72.8943 | FALSE | FALSE | 0.1025 |  | 73.3932 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.24942 | Normal | 73.892 | -0.67983 | Night | 202602 | 2026-02-15 | 0.67983
2026-02-15 01:25 | 72.941 | FALSE | FALSE | -0.091586 | -0.12572 | -0.91113 | -1.2337 | -0.2826 |  |  | none | FALSE | 2 | 72.8494 | FALSE | FALSE | 0.1661 |  | 73.3508 | 0 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.25068 | Normal | 73.8521 | -1.6346 | Night | 202602 | 2026-02-15 | 1.6346
2026-02-15 01:40 | 72.941 | FALSE | FALSE | -0.12124 | -0.16649 | -0.856 | -1.1599 | 0 |  |  | none | FALSE | 2 | 72.8198 | FALSE | FALSE | 0.1574 |  | 73.3084 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.24431 | Normal | 73.797 | -1.5038 | Night | 202602 | 2026-02-15 | 1.5038
2026-02-15 01:55 | 72.941 | FALSE | FALSE | -0.13436 | -0.18455 | -0.78434 | -1.0639 | 0 |  |  | none | FALSE | 2 | 72.8066 | FALSE | FALSE | 0.1515 |  | 73.266 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.22968 | Normal | 73.7253 | -1.415 | Night | 202602 | 2026-02-15 | 1.415
2026-02-15 02:10 | 72.941 | FALSE | FALSE | -0.12744 | -0.17502 | -0.69264 | -0.94066 | 0 |  |  | none | FALSE | 2 | 72.8136 | FALSE | FALSE | 0.149 |  | 73.2236 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.20502 | Normal | 73.6336 | -1.3784 | Night | 202602 | 2026-02-15 | 1.3784
2026-02-15 02:25 | 72.941 | FALSE | FALSE | -0.15158 | -0.20824 | -0.66026 | -0.89707 | 0 |  |  | none | FALSE | 2 | 72.7894 | FALSE | FALSE | 0.1407 |  | 73.1953 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.20296 | Normal | 73.6013 | -1.2532 | Night | 202602 | 2026-02-15 | 1.2532
2026-02-15 02:39 | 72.941 | FALSE | FALSE | -0.16722 | -0.22977 | -0.61938 | -0.842 | 0 |  |  | none | FALSE | 2 | 72.7738 | FALSE | FALSE | 0.1338 |  | 73.1671 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.19665 | Normal | 73.5604 | -1.1497 | Night | 202602 | 2026-02-15 | 1.1497
2026-02-15 02:54 | 72.941 | FALSE | FALSE | -0.17349 | -0.23841 | -0.56913 | -0.77421 | 0 |  |  | none | FALSE | 2 | 72.7675 | FALSE | FALSE | 0.1282 |  | 73.1388 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.18565 | Normal | 73.5101 | -1.0655 | Night | 202602 | 2026-02-15 | 1.0655
2026-02-15 03:10 | 72.6584 | FALSE | FALSE | 0.050115 | 0.068926 | -0.82595 | -1.124 | -0.2826 | 2026-02-15 04:54 | 2026-02-15 03:10 | lower | TRUE | 1 | 72.7085 | FALSE | FALSE | 0.2363 | 2.2584 | 73.0964 | 1 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.19396 | Extreme triggered | 73.4843 | -2.2584 | Night | 202602 | 2026-02-15 | 2.2584
2026-02-15 03:25 | 72.6584 | FALSE | FALSE | 0.010989 | 0.015122 | -0.78029 | -1.0625 | 0 |  | 2026-02-15 03:10 | lower | TRUE | 0 | 72.6694 | FALSE | FALSE | 0.2514 | 2.1578 | 73.054 | 2 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.19233 | Extreme/elevated | 73.4387 | -2.0571 | Night | 202602 | 2026-02-15 | 2.0571
2026-02-15 03:39 | 72.6584 | FALSE | FALSE | -0.046739 | -0.064369 | -0.7815 | -1.0641 | 0 |  | 2026-02-15 03:10 | none | FALSE | 0 | 72.6117 | FALSE | FALSE | 0.2897 | 2.0299 | 73.0258 | 3 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.20706 | Persistent | 73.4399 | -1.7743 | Night | 202602 | 2026-02-15 | 1.7743
2026-02-15 03:54 | 72.6584 | FALSE | FALSE | -0.094825 | -0.13068 | -0.77306 | -1.0528 | 0 |  | 2026-02-15 03:10 | none | FALSE | 0 | 72.5636 | FALSE | FALSE | 0.3328 | 1.9132 | 72.9975 | 4 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21697 | Persistent | 73.4315 | -1.563 | Night | 202602 | 2026-02-15 | 1.563
2026-02-15 04:09 | 72.6584 | FALSE | FALSE | -0.13456 | -0.18553 | -0.75628 | -1.0301 | 0 |  | 2026-02-15 03:10 | none | FALSE | 0 | 72.5238 | FALSE | FALSE | 0.3788 | 1.8097 | 72.9693 | 5 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.22271 | Persistent | 73.4147 | -1.3958 | Night | 202602 | 2026-02-15 | 1.3958
2026-02-15 04:24 | 72.6584 | FALSE | FALSE | -0.16658 | -0.22979 | -0.73178 | -0.9971 | 0 |  | 2026-02-15 03:10 | none | FALSE | 0 | 72.4918 | FALSE | FALSE | 0.4267 | 1.7178 | 72.941 | 6 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.22459 | Persistent | 73.3902 | -1.2583 | Night | 202602 | 2026-02-15 | 1.2583
2026-02-15 04:39 | 72.3758 | FALSE | TRUE | 0.028207 | 0.038958 | -1.0174 | -1.3862 | -0.2826 |  | 2026-02-15 03:10 | lower | TRUE | 0 | 72.404 | FALSE | TRUE | 0.5409 | 1.7744 | 72.8986 | 7 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.2473 | Confirmed/Materialized Shift | 73.3932 | -2.1141 | Night | 202602 | 2026-02-15 | 2.1141
2026-02-15 04:54 | 72.6584 | FALSE | FALSE | -0.26886 | -0.37141 | -0.69276 | -0.94445 | 0.2826 |  |  | none | FALSE | 0 | 72.3895 | FALSE | FALSE | 0.0588 |  | 72.8704 | 0 | 0.2826 | -0.02826 | 0.15614 | 1.9909 | 0.24041 | Persistence ends | 73.3512 | -0.88163 | Night | 202602 | 2026-02-15 | 0.88163
2026-02-15 05:09 | 72.6584 | FALSE | FALSE | -0.27566 | -0.38084 | -0.64304 | -0.87726 | 0 |  |  | none | FALSE | 0 | 72.3827 | FALSE | FALSE | 0.0533 |  | 72.8421 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.22968 | Normal | 73.3014 | -0.79978 | Night | 202602 | 2026-02-15 | 0.79978
2026-02-15 05:24 | 72.3758 | FALSE | FALSE | -0.043617 | -0.0603 | -0.89142 | -1.2167 | -0.2826 |  |  | none | FALSE | 0 | 72.3322 | FALSE | FALSE | 0.1209 |  | 72.7997 | 0 | -0.2826 | -0.04239 | 0.16593 | -1.4477 | 0.23376 | Normal | 73.2672 | -1.8134 | Night | 202602 | 2026-02-15 | 1.8134
2026-02-15 05:39 | 72.3758 | FALSE | FALSE | -0.10319 | -0.14278 | -0.89447 | -1.2208 | 0 |  |  | none | FALSE | 0 | 72.2726 | FALSE | FALSE | 0.1058 |  | 72.7714 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.24942 | Normal | 73.2703 | -1.5863 | Night | 202602 | 2026-02-15 | 1.5863
2026-02-15 05:54 | 72.3758 | FALSE | FALSE | -0.12756 | -0.17656 | -0.83406 | -1.1393 | 0 |  |  | none | FALSE | 0 | 72.2482 | FALSE | FALSE | 0.098 |  | 72.7291 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.24041 | Normal | 73.2099 | -1.4694 | Night | 202602 | 2026-02-15 | 1.4694
2026-02-15 06:09 | 72.3758 | FALSE | FALSE | -0.13456 | -0.18626 | -0.75628 | -1.0341 | 0 |  |  | none | FALSE | 0 | 72.2412 | FALSE | FALSE | 0.0931 |  | 72.6867 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.22271 | Normal | 73.1321 | -1.3958 | Night | 202602 | 2026-02-15 | 1.3958
2026-02-15 06:24 | 72.3758 | FALSE | FALSE | -0.16658 | -0.23068 | -0.73178 | -1.001 | 0 |  |  | none | FALSE | 0 | 72.2092 | FALSE | FALSE | 0.0839 |  | 72.6584 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.22459 | Normal | 73.1076 | -1.2583 | Night | 202602 | 2026-02-15 | 1.2583
2026-02-15 06:38 | 72.3758 | FALSE | FALSE | -0.19108 | -0.2647 | -0.69976 | -0.95758 | 0 |  |  | none | FALSE | 0 | 72.1847 | FALSE | FALSE | 0.0761 |  | 72.6301 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.22271 | Normal | 73.0756 | -1.142 | Night | 202602 | 2026-02-15 | 1.142
2026-02-15 06:53 | 72.3758 | FALSE | FALSE | -0.20786 | -0.28803 | -0.66002 | -0.9037 | 0 |  |  | none | FALSE | 0 | 72.1679 | FALSE | FALSE | 0.0695 |  | 72.6019 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21697 | Normal | 73.0358 | -1.042 | Night | 202602 | 2026-02-15 | 1.042
2026-02-15 07:08 | 72.095 | FALSE | FALSE | 0.0056104 | 0.0077814 | -0.92355 | -1.2648 | -0.2808 | 2026-02-15 07:23 | 2026-02-15 07:08 | lower | TRUE | 0 | 72.1006 | FALSE | FALSE | 0.1921 | 2.0244 | 72.5596 | 1 | -0.2808 | -0.0423 | 0.13813 | -1.7266 | 0.22948 | Extreme triggered | 73.0185 | -2.0244 | Day | 202602 | 2026-02-15 | 2.0244
2026-02-15 07:23 | 72.3758 | FALSE | FALSE | -0.27317 | -0.37886 | -0.58421 | -0.80072 | 0.2808 |  |  | none | FALSE | 0 | 72.1026 | FALSE | FALSE | 0.0484 |  | 72.5313 | 0 | 0.2808 | -0.02826 | 0.1558 | 1.9837 | 0.21434 | Persistence ends | 72.96 | -0.72556 | Day | 202602 | 2026-02-15 | 0.72556
2026-02-15 07:38 | 72.095 | FALSE | FALSE | -0.031402 | -0.043576 | -0.81944 | -1.1238 | -0.2808 |  |  | none | FALSE | 0 | 72.0636 | FALSE | FALSE | 0.1235 |  | 72.489 | 0 | -0.2808 | -0.0423 | 0.16547 | -1.4414 | 0.21271 | Normal | 72.9144 | -1.8524 | Day | 202602 | 2026-02-15 | 1.8524
2026-02-15 07:53 | 72.3758 | FALSE | FALSE | -0.2856 | -0.39617 | -0.45552 | -0.62544 | 0.2808 |  |  | none | FALSE | 0 | 72.0902 | FALSE | FALSE | 0.0306 |  | 72.4608 | 0 | 0.2808 | -0.02826 | 0.18048 | 1.7125 | 0.18528 | Normal | 72.8313 | -0.45855 | Day | 202602 | 2026-02-15 | 0.45855
2026-02-15 08:08 | 72.3758 | FALSE | FALSE | -0.2894 | -0.40147 | -0.43106 | -0.59206 | 0 |  |  | none | FALSE | 0 | 72.0864 | FALSE | FALSE | 0.0262 |  | 72.4466 | 0 | 0 | -0.01413 | 0.17029 | 0.082975 | 0.18012 | Normal | 72.8069 | -0.39324 | Day | 202602 | 2026-02-15 | 0.39324
2026-02-15 08:23 | 72.6584 | FALSE | FALSE | -0.572 | -0.7935 | -0.14846 | -0.20391 | 0.2826 |  |  | none | FALSE | 0 | 72.0864 | FALSE | FALSE | 0.0784 |  | 72.4466 | 0 | 0.2826 | 0 | 0.18279 | 1.546 | 0.18012 | Normal | 72.8069 | 1.1757 | Day | 202602 | 2026-02-15 | 1.1757
2026-02-15 08:30 | 72.941 | FALSE | FALSE | -0.89369 | -1.2404 | 0.066792 | 0.091654 | 0.2826 | 2026-02-15 10:15 | 2026-02-15 08:30 | upper | TRUE | 0 | 72.0473 | FALSE | FALSE | 0.212 | 2.3231 | 72.4608 | 1 | 0.2826 | 0.01413 | 0.19341 | 1.3881 | 0.20672 | Extreme triggered | 72.8742 | 2.3231 | Day | 202602 | 2026-02-15 | 2.3231
2026-02-15 08:45 | 72.941 | FALSE | FALSE | -0.92484 | -1.2842 | 0.0073849 | 0.010125 | 0 |  | 2026-02-15 08:30 | upper | TRUE | 0 | 72.0162 | FALSE | FALSE | 0.2498 | 2.1776 | 72.4749 | 2 | 0 | 0.01413 | 0.19341 | -0.073059 | 0.22936 | Extreme/elevated | 72.9336 | 2.0322 | Day | 202602 | 2026-02-15 | 2.0322
2026-02-15 09:00 | 73.2236 | FALSE | FALSE | -1.2844 | -1.7853 | 0.15654 | 0.21425 | 0.2826 |  | 2026-02-15 08:30 | upper | TRUE | 0 | 71.9392 | FALSE | TRUE | 0.3418 | 2.3035 | 72.5032 | 3 | 0.2826 | 0.02826 | 0.20243 | 1.2564 | 0.28195 | Persistent | 73.0671 | 2.5552 | Day | 202602 | 2026-02-15 | 2.5552
2026-02-15 09:16 | 73.2236 | FALSE | FALSE | -1.3394 | -1.8632 | 0.045022 | 0.061523 | 0 |  | 2026-02-15 08:30 | upper | TRUE | 0 | 71.8842 | FALSE | TRUE | 0.3712 | 2.2624 | 72.5314 | 4 | 0 | 0.02826 | 0.20243 | -0.1396 | 0.32358 | Persistent | 73.1786 | 2.1391 | Day | 202602 | 2026-02-15 | 2.1391
2026-02-15 09:30 | 73.5062 | FALSE | FALSE | -1.6931 | -2.3576 | 0.14346 | 0.19555 | 0.2826 |  | 2026-02-15 08:30 | upper | TRUE | 0 | 71.8131 | FALSE | TRUE | 0.4437 | 2.284 | 72.5879 | 5 | 0.2826 | 0.05652 | 0.1961 | 1.1529 | 0.3874 | Persistent | 73.3627 | 2.3703 | Day | 202602 | 2026-02-15 | 2.3703
2026-02-15 09:45 | 73.5062 | FALSE | FALSE | -1.7529 | -2.443 | -0.001179 | -0.0016039 | 0 |  | 2026-02-15 08:30 | none | FALSE | 0 | 71.7533 | FALSE | FALSE | 0.476 | 2.2362 | 72.6303 | 6 | 0 | 0.04239 | 0.18901 | -0.22427 | 0.43853 | Persistent | 73.5074 | 1.9973 | Day | 202602 | 2026-02-15 | 1.9973
2026-02-15 09:45 | 73.5062 | FALSE | TRUE | -1.7942 | -2.502 | -0.12724 | -0.17281 | 0 |  | 2026-02-15 08:30 | none | FALSE | 0 | 71.712 | FALSE | FALSE | 0.5157 | 2.1646 | 72.6727 | 7 | 0 | 0.04239 | 0.18901 | -0.22427 | 0.48037 | Confirmed/Materialized Shift | 73.6334 | 1.7351 | Day | 202602 | 2026-02-15 | 1.7351
2026-02-15 10:00 | 73.5062 | FALSE | TRUE | -1.7954 | -2.5037 | -0.24149 | -0.32745 | 0 |  | 2026-02-15 08:30 | none | FALSE | 0 | 71.7108 | FALSE | FALSE | 0.5017 | 2.0848 | 72.7292 | 8 | 0 | 0.05652 | 0.17335 | -0.32605 | 0.50923 | Confirmed/Materialized Shift | 73.7477 | 1.5258 | Day | 202602 | 2026-02-15 | 1.5258
2026-02-15 10:15 | 73.2236 | FALSE | FALSE | -1.479 | -2.0615 | -0.57508 | -0.77925 | -0.2826 |  |  | none | FALSE | 0 | 71.7446 | FALSE | FALSE | 0.0587 |  | 72.7716 | 0 | -0.2826 | 0.04239 | 0.18901 | -1.7194 | 0.51353 | Persistence ends | 73.7987 | 0.88015 | Day | 202602 | 2026-02-15 | 0.88015
2026-02-15 10:30 | 73.2236 | FALSE | FALSE | -1.4378 | -2.003 | -0.61866 | -0.83781 | 0 |  |  | none | FALSE | 0 | 71.7858 | FALSE | FALSE | 0.0531 |  | 72.814 | 0 | 0 | 0.04239 | 0.18901 | -0.22427 | 0.51413 | Normal | 73.8423 | 0.79667 | Day | 202602 | 2026-02-15 | 0.79667
2026-02-15 10:44 | 73.5062 | FALSE | FALSE | -1.6865 | -2.3483 | -0.41518 | -0.56165 | 0.2826 |  |  | none | FALSE | 0 | 71.8197 | FALSE | FALSE | 0.0807 |  | 72.8705 | 0 | 0.2826 | 0.05652 | 0.1961 | 1.1529 | 0.52543 | Normal | 73.9214 | 1.2098 | Day | 202602 | 2026-02-15 | 1.2098
2026-02-15 10:59 | 73.7888 | FALSE | FALSE | -1.9473 | -2.7105 | -0.25205 | -0.34042 | 0.2826 |  |  | none | FALSE | 0 | 71.8415 | FALSE | FALSE | 0.1028 |  | 72.9412 | 0 | 0.2826 | 0.07065 | 0.20191 | 1.0497 | 0.54983 | Normal | 74.0408 | 1.5416 | Day | 202602 | 2026-02-15 | 1.5416
2026-02-15 11:09 | 74.0714 | FALSE | FALSE | -2.2204 | -3.0903 | -0.12956 | -0.17461 | 0.2826 |  |  | none | FALSE | 0 | 71.851 | FALSE | FALSE | 0.1186 |  | 73.026 | 0 | 0.2826 | 0.08478 | 0.20654 | 0.95776 | 0.5875 | Normal | 74.201 | 1.7795 | Day | 202602 | 2026-02-15 | 1.7795
2026-02-15 11:12 | 73.7888 | FALSE | FALSE | -1.8725 | -2.6037 | -0.48812 | -0.65717 | -0.2826 |  |  | none | FALSE | 0 | 71.9163 | FALSE | FALSE | 0.0782 |  | 73.0966 | 0 | -0.2826 | 0.07065 | 0.22176 | -1.593 | 0.59016 | Normal | 74.2769 | 1.1729 | Day | 202602 | 2026-02-15 | 1.1729
2026-02-15 11:27 | 73.7888 | FALSE | FALSE | -1.7267 | -2.3961 | -0.5117 | -0.68869 | 0 |  |  | none | FALSE | 0 | 72.0621 | FALSE | FALSE | 0.0724 |  | 73.1813 | 0 | 0 | 0.08469 | 0.20671 | -0.4097 | 0.5596 | Normal | 74.3005 | 1.0856 | Day | 202602 | 2026-02-15 | 1.0856
2026-02-15 11:42 | 73.2236 | TRUE | FALSE | -1.0529 | -1.4589 | -1.0531 | -1.4178 | -0.5652 |  |  | none | FALSE | 1 | 72.1707 | FALSE | FALSE | 0.0286 |  | 73.2237 | 0 | -0.5652 | 0.04239 | 0.24709 | -2.459 | 0.5265 | Normal | 74.2767 | -0.00017094 | Day | 202602 | 2026-02-15 | 0.00017094
2026-02-15 11:44 | 73.2236 | FALSE | FALSE | -0.85299 | -1.1786 | -0.96603 | -1.3021 | 0 |  |  | none | FALSE | 1 | 72.3706 | FALSE | FALSE | 0.0369 |  | 73.2801 | 0 | 0 | 0.05643 | 0.23546 | -0.23966 | 0.45476 | Normal | 74.1896 | -0.12429 | Day | 202602 | 2026-02-15 | 0.12429
2026-02-15 11:59 | 73.2236 | FALSE | FALSE | -0.70617 | -0.97379 | -0.90399 | -1.2195 | 0 |  |  | none | FALSE | 1 | 72.5174 | FALSE | FALSE | 0.045 |  | 73.3225 | 0 | 0 | 0.04239 | 0.22968 | -0.18456 | 0.40254 | Normal | 74.1276 | -0.24572 | Day | 202602 | 2026-02-15 | 0.24572
2026-02-15 12:14 | 72.941 | FALSE | FALSE | -0.2879 | -0.39627 | -1.1074 | -1.4956 | -0.2826 |  |  | none | FALSE | 1 | 72.6531 | FALSE | FALSE | 0.1069 |  | 73.3508 | 0 | -0.2826 | 0.02826 | 0.24084 | -1.2907 | 0.34883 | Normal | 74.0484 | -1.1747 | Day | 202602 | 2026-02-15 | 1.1747
2026-02-15 12:29 | 73.2236 | FALSE | FALSE | -0.46575 | -0.64014 | -0.77661 | -1.0495 | 0.2826 |  |  | none | FALSE | 1 | 72.7579 | FALSE | FALSE | 0.0619 |  | 73.379 | 0 | 0.2826 | 0.02826 | 0.24084 | 1.056 | 0.31059 | Normal | 74.0002 | -0.50044 | Day | 202602 | 2026-02-15 | 0.50044
2026-02-15 12:44 | 72.941 | FALSE | FALSE | -0.18315 | -0.25172 | -1.0592 | -1.4314 | -0.2826 |  |  | none | FALSE | 1 | 72.7579 | FALSE | FALSE | 0.1226 |  | 73.379 | 0 | -0.2826 | 0 | 0.24258 | -1.165 | 0.31059 | Normal | 74.0002 | -1.4103 | Day | 202602 | 2026-02-15 | 1.4103
2026-02-15 12:59 | 72.941 | FALSE | FALSE | -0.18315 | -0.25172 | -1.0592 | -1.4314 | 0 |  |  | none | FALSE | 1 | 72.7579 | FALSE | FALSE | 0.1226 |  | 73.379 | 0 | 0 | 0 | 0.24258 | 0 | 0.31059 | Normal | 74.0002 | -1.4103 | Day | 202602 | 2026-02-15 | 1.4103
2026-02-15 13:14 | 72.941 | FALSE | FALSE | -0.22443 | -0.30864 | -1.0722 | -1.4487 | 0 |  |  | none | FALSE | 1 | 72.7166 | FALSE | FALSE | 0.1157 |  | 73.3649 | 0 | 0 | -0.01413 | 0.23331 | 0.060564 | 0.32416 | Normal | 74.0132 | -1.3077 | Day | 202602 | 2026-02-15 | 1.3077
2026-02-15 13:29 | 72.941 | FALSE | FALSE | -0.26337 | -0.36238 | -1.0829 | -1.4629 | 0 |  |  | none | FALSE | 1 | 72.6776 | FALSE | FALSE | 0.1097 |  | 73.3508 | 0 | 0 | -0.01413 | 0.23331 | 0.060564 | 0.33657 | Normal | 74.0239 | -1.2175 | Day | 202602 | 2026-02-15 | 1.2175
2026-02-15 13:43 | 72.941 | FALSE | FALSE | -0.31132 | -0.42864 | -1.0743 | -1.4515 | 0 |  |  | none | FALSE | 1 | 72.6297 | FALSE | FALSE | 0.102 |  | 73.3225 | 0 | 0 | -0.02826 | 0.22271 | 0.12689 | 0.34642 | Normal | 74.0153 | -1.1013 | Day | 202602 | 2026-02-15 | 1.1013
2026-02-15 13:59 | 72.941 | FALSE | FALSE | -0.35399 | -0.48768 | -1.0605 | -1.4331 | 0 |  |  | none | FALSE | 0 | 72.587 | FALSE | FALSE | 0.0666 |  | 73.2943 | 0 | 0 | -0.02826 | 0.22271 | 0.12689 | 0.35362 | Normal | 74.0015 | -0.99895 | Day | 202602 | 2026-02-15 | 0.99895
2026-02-15 14:14 | 72.6584 | FALSE | FALSE | -0.16039 | -0.22123 | -1.3473 | -1.8205 | -0.2826 |  |  | none | FALSE | 0 | 72.498 | FALSE | FALSE | 0.105 |  | 73.2519 | 0 | -0.2826 | -0.04239 | 0.22968 | -1.0459 | 0.37692 | Normal | 74.0057 | -1.5745 | Day | 202602 | 2026-02-15 | 1.5745
2026-02-15 14:29 | 72.6584 | FALSE | FALSE | -0.23712 | -0.32742 | -1.3393 | -1.8099 | 0 |  |  | none | FALSE | 0 | 72.4213 | FALSE | FALSE | 0.0932 |  | 73.2095 | 0 | 0 | -0.04239 | 0.22968 | 0.18456 | 0.3941 | Normal | 73.9977 | -1.3983 | Day | 202602 | 2026-02-15 | 1.3983
2026-02-15 14:43 | 73.2236 | TRUE | FALSE | -0.80232 | -1.1079 | -0.77406 | -1.0461 | 0.5652 |  |  | none | FALSE | 1 | 72.4213 | FALSE | FALSE | 0.031 |  | 73.2095 | 0 | 0.5652 | 0 | 0.25933 | 2.1794 | 0.3941 | Normal | 73.9977 | 0.035854 | Day | 202602 | 2026-02-15 | 0.035854
2026-02-15 14:58 | 72.941 | FALSE | FALSE | -0.54287 | -0.74984 | -1.0515 | -1.4212 | -0.2826 |  |  | none | FALSE | 1 | 72.3981 | FALSE | FALSE | 0.0711 |  | 73.1953 | 0 | -0.2826 | -0.01413 | 0.26692 | -1.0058 | 0.3986 | Normal | 73.9925 | -0.63808 | Day | 202602 | 2026-02-15 | 0.63808
2026-02-15 15:13 | 72.941 | FALSE | FALSE | -0.56477 | -0.78033 | -1.0169 | -1.375 | 0 |  |  | none | FALSE | 1 | 72.3762 | FALSE | FALSE | 0.0667 |  | 73.1671 | 0 | 0 | -0.02826 | 0.25771 | 0.10966 | 0.39543 | Normal | 73.9579 | -0.57174 | Day | 202602 | 2026-02-15 | 0.57174
2026-02-15 15:28 | 72.6584 | FALSE | FALSE | -0.31276 | -0.43231 | -1.2171 | -1.6475 | -0.2826 |  |  | none | FALSE | 1 | 72.3456 | FALSE | FALSE | 0.1074 |  | 73.1106 | 0 | -0.2826 | -0.05652 | 0.25277 | -0.89443 | 0.38246 | Normal | 73.8755 | -1.1822 | Day | 202602 | 2026-02-15 | 1.1822
2026-02-15 15:43 | 72.3758 | FALSE | FALSE | -0.038593 | -0.053351 | -1.3386 | -1.8159 | -0.2826 |  |  | none | FALSE | 1 | 72.3372 | FALSE | FALSE | 0.1544 |  | 73.0258 | 0 | -0.2826 | -0.08478 | 0.24431 | -0.80971 | 0.34429 | Normal | 73.7144 | -1.8879 | Day | 202602 | 2026-02-15 | 1.8879
2026-02-15 15:58 | 72.6584 | FALSE | FALSE | -0.29456 | -0.40705 | -0.91628 | -1.2454 | 0.2826 |  |  | none | FALSE | 1 | 72.3638 | FALSE | FALSE | 0.097 |  | 72.9693 | 0 | 0.2826 | -0.05652 | 0.25277 | 1.3416 | 0.30271 | Normal | 73.5747 | -1.0269 | Day | 202602 | 2026-02-15 | 1.0269
2026-02-15 16:13 | 72.6584 | FALSE | FALSE | -0.22735 | -0.31388 | -0.73603 | -1.0028 | 0 |  |  | none | FALSE | 1 | 72.4311 | FALSE | FALSE | 0.099 |  | 72.9127 | 0 | 0 | -0.05652 | 0.25277 | 0.22361 | 0.24084 | Normal | 73.3944 | -1.056 | Day | 202602 | 2026-02-15 | 1.056
2026-02-15 16:28 | 72.3758 | FALSE | FALSE | -0.020045 | -0.027704 | -1.0091 | -1.3751 | -0.2826 |  |  | none | FALSE | 1 | 72.3558 | FALSE | FALSE | 0.1567 |  | 72.8704 | 0 | -0.2826 | -0.04239 | 0.22968 | -1.0459 | 0.2573 | Normal | 73.3849 | -1.9221 | Day | 202602 | 2026-02-15 | 1.9221
2026-02-15 16:43 | 72.3758 | FALSE | FALSE | -0.079312 | -0.1097 | -0.98363 | -1.3408 | 0 |  |  | none | FALSE | 1 | 72.2965 | FALSE | FALSE | 0.142 |  | 72.828 | 0 | 0 | -0.04239 | 0.22968 | 0.18456 | 0.26574 | Normal | 73.3594 | -1.7015 | Day | 202602 | 2026-02-15 | 1.7015
2026-02-15 16:58 | 72.3758 | FALSE | FALSE | -0.12407 | -0.17172 | -0.94361 | -1.287 | 0 |  |  | none | FALSE | 1 | 72.2517 | FALSE | FALSE | 0.1309 |  | 72.7856 | 0 | 0 | -0.04239 | 0.22968 | 0.18456 | 0.26692 | Normal | 73.3194 | -1.5352 | Day | 202602 | 2026-02-15 | 1.5352
2026-02-15 17:13 | 72.941 | TRUE | FALSE | -0.68927 | -0.95398 | -0.37841 | -0.51611 | 0.5652 |  |  | none | FALSE | 1 | 72.2517 | FALSE | FALSE | 0.0674 |  | 72.7856 | 0 | 0.5652 | 0 | 0.25933 | 2.1794 | 0.26692 | Normal | 73.3194 | 0.58231 | Day | 202602 | 2026-02-15 | 0.58231
2026-02-15 17:28 | 72.941 | FALSE | FALSE | -0.66839 | -0.92482 | -0.32927 | -0.4494 | 0 |  |  | none | FALSE | 1 | 72.2726 | FALSE | FALSE | 0.0739 |  | 72.7714 | 0 | 0 | -0.01413 | 0.25068 | 0.056367 | 0.24942 | Normal | 73.2703 | 0.67983 | Day | 202602 | 2026-02-15 | 0.67983
2026-02-15 17:42 | 73.2236 | FALSE | FALSE | -0.97187 | -1.3451 | -0.095809 | -0.13067 | 0.2826 |  |  | none | FALSE | 1 | 72.2517 | FALSE | FALSE | 0.138 |  | 72.7856 | 0 | 0.2826 | 0.01413 | 0.25068 | 1.071 | 0.26692 | Normal | 73.3194 | 1.6411 | Day | 202602 | 2026-02-15 | 1.6411
2026-02-15 17:42 | 73.2236 | FALSE | FALSE | -0.9891 | -1.3693 | -0.1413 | -0.1926 | 0 |  |  | none | FALSE | 1 | 72.2345 | FALSE | FALSE | 0.1286 |  | 72.7997 | 0 | 0 | 0.01413 | 0.25068 | -0.056367 | 0.2826 | Normal | 73.3649 | 1.5 | Day | 202602 | 2026-02-15 | 1.5
2026-02-15 17:43 | 73.2236 | FALSE | FALSE | -1.0033 | -1.3892 | -0.18373 | -0.25028 | 0 |  |  | none | FALSE | 1 | 72.2203 | FALSE | FALSE | 0.1206 |  | 72.8138 | 0 | 0 | 0.01413 | 0.25068 | -0.056367 | 0.29675 | Normal | 73.4073 | 1.3809 | Day | 202602 | 2026-02-15 | 1.3809
2026-02-15 17:58 | 73.5062 | FALSE | FALSE | -1.3322 | -1.8459 | -0.0040148 | -0.0054616 | 0.2826 |  |  | none | FALSE | 1 | 72.174 | FALSE | FALSE | 0.1611 |  | 72.8421 | 0 | 0.2826 | 0.02826 | 0.25771 | 0.98694 | 0.33406 | Normal | 73.5102 | 1.988 | Day | 202602 | 2026-02-15 | 1.988
2026-02-15 18:13 | 73.5062 | FALSE | FALSE | -1.3665 | -1.8942 | -0.09478 | -0.12877 | 0 |  |  | none | FALSE | 1 | 72.1397 | FALSE | FALSE | 0.1446 |  | 72.8704 | 0 | 0 | 0.02826 | 0.25771 | -0.10966 | 0.36531 | Normal | 73.601 | 1.7406 | Day | 202602 | 2026-02-15 | 1.7406
2026-02-15 18:28 | 73.7888 | FALSE | FALSE | -1.7144 | -2.3786 | 0.037733 | 0.051163 | 0.2826 | 2026-02-15 20:12 | 2026-02-15 18:28 | upper | TRUE | 1 | 72.0744 | FALSE | FALSE | 0.225 | 2.09 | 72.9127 | 1 | 0.2826 | 0.04239 | 0.26375 | 0.91074 | 0.41916 | Extreme triggered | 73.7511 | 2.09 | Night | 202602 | 2026-02-15 | 2.09
2026-02-15 18:42 | 73.7888 | FALSE | FALSE | -1.7346 | -2.4073 | -0.0955 | -0.12926 | 0 |  | 2026-02-15 18:28 | none | FALSE | 1 | 72.0542 | FALSE | FALSE | 0.2623 | 1.9406 | 72.9693 | 2 | 0 | 0.05652 | 0.25277 | -0.22361 | 0.45752 | Extreme/elevated | 73.8843 | 1.7913 | Night | 202602 | 2026-02-15 | 1.7913
2026-02-15 18:57 | 73.7888 | FALSE | FALSE | -1.7351 | -2.408 | -0.20904 | -0.2825 | 0 |  | 2026-02-15 18:28 | none | FALSE | 1 | 72.0537 | FALSE | FALSE | 0.3047 | 1.8171 | 73.0258 | 3 | 0 | 0.05652 | 0.25277 | -0.22361 | 0.48603 | Persistent | 73.9978 | 1.5699 | Night | 202602 | 2026-02-15 | 1.5699
2026-02-15 19:12 | 73.7888 | FALSE | FALSE | -1.7623 | -2.4468 | -0.2928 | -0.39523 | 0 |  | 2026-02-15 18:28 | none | FALSE | 0 | 72.0265 | FALSE | FALSE | 0.3239 | 1.7203 | 73.054 | 4 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.51378 | Persistent | 74.0816 | 1.4301 | Night | 202602 | 2026-02-15 | 1.4301
2026-02-15 19:27 | 73.7888 | FALSE | FALSE | -1.7691 | -2.4564 | -0.38432 | -0.51815 | 0 |  | 2026-02-15 18:28 | none | FALSE | 0 | 72.0197 | FALSE | FALSE | 0.3715 | 1.6335 | 73.0964 | 5 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.53835 | Persistent | 74.1731 | 1.2861 | Night | 202602 | 2026-02-15 | 1.2861
2026-02-15 19:42 | 73.7888 | FALSE | FALSE | -1.7669 | -2.4533 | -0.46695 | -0.62884 | 0 |  | 2026-02-15 18:28 | none | FALSE | 0 | 72.0219 | FALSE | FALSE | 0.4204 | 1.5552 | 73.1388 | 6 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.55847 | Persistent | 74.2558 | 1.1639 | Night | 202602 | 2026-02-15 | 1.1639
2026-02-15 19:57 | 73.7888 | FALSE | TRUE | -1.7224 | -2.39 | -0.53545 | -0.72043 | 0 |  | 2026-02-15 18:28 | none | FALSE | 0 | 72.0664 | FALSE | FALSE | 0.4701 | 1.4832 | 73.1953 | 7 | 0 | 0.05652 | 0.19665 | -0.28742 | 0.56446 | Confirmed/Materialized Shift | 74.3243 | 1.0514 | Night | 202602 | 2026-02-15 | 1.0514
2026-02-15 20:12 | 73.7888 | FALSE | FALSE | -1.6119 | -2.2333 | -0.56631 | -0.76162 | 0 |  |  | none | FALSE | 0 | 72.1769 | FALSE | FALSE | 0.064 |  | 73.266 | 0 | 0 | 0.07065 | 0.18049 | -0.39144 | 0.54456 | Persistence ends | 74.3551 | 0.96006 | Night | 202602 | 2026-02-15 | 0.96006
2026-02-15 20:27 | 73.7888 | FALSE | FALSE | -1.5399 | -2.1313 | -0.60728 | -0.81628 | 0 |  |  | none | FALSE | 0 | 72.2489 | FALSE | FALSE | 0.0579 |  | 73.3225 | 0 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.53678 | Normal | 74.3961 | 0.86867 | Night | 202602 | 2026-02-15 | 0.86867
2026-02-15 20:41 | 73.7888 | FALSE | FALSE | -1.4548 | -2.0112 | -0.63523 | -0.85352 | 0 |  |  | none | FALSE | 0 | 72.334 | FALSE | FALSE | 0.0523 |  | 73.379 | 0 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.5225 | Normal | 74.424 | 0.78425 | Night | 202602 | 2026-02-15 | 0.78425
2026-02-15 20:56 | 73.7888 | FALSE | FALSE | -1.2849 | -1.7722 | -0.60664 | -0.81543 | 0 |  |  | none | FALSE | 0 | 72.5039 | FALSE | FALSE | 0.0478 |  | 73.4497 | 0 | 0 | 0.07065 | 0.15546 | -0.45445 | 0.47288 | Normal | 74.3954 | 0.71714 | Night | 202602 | 2026-02-15 | 0.71714
2026-02-15 21:11 | 73.7888 | FALSE | FALSE | -1.0777 | -1.4822 | -0.54077 | -0.72753 | 0 |  |  | none | FALSE | 0 | 72.7111 | FALSE | FALSE | 0.0442 |  | 73.5203 | 0 | 0 | 0.07065 | 0.15546 | -0.45445 | 0.40462 | Normal | 74.3296 | 0.66351 | Night | 202602 | 2026-02-15 | 0.66351
2026-02-15 21:26 | 73.7888 | FALSE | FALSE | -0.80876 | -1.1082 | -0.41312 | -0.55676 | 0 |  |  | none | FALSE | 0 | 72.98 | FALSE | FALSE | 0.0432 |  | 73.591 | 0 | 0 | 0.07065 | 0.15546 | -0.45445 | 0.30547 | Normal | 74.2019 | 0.64759 | Night | 202602 | 2026-02-15 | 0.64759
2026-02-15 21:41 | 73.7888 | FALSE | FALSE | -0.68927 | -0.94292 | -0.37841 | -0.51021 | 0 |  |  | none | FALSE | 0 | 73.0995 | FALSE | FALSE | 0.0388 |  | 73.6334 | 0 | 0 | 0.04239 | 0.10353 | -0.40945 | 0.26692 | Normal | 74.1672 | 0.58231 | Night | 202602 | 2026-02-15 | 0.58231
2026-02-15 21:56 | 73.7888 | FALSE | FALSE | -0.53917 | -0.73607 | -0.31309 | -0.42251 | 0 |  |  | none | FALSE | 0 | 73.2496 | FALSE | FALSE | 0.0354 |  | 73.6758 | 0 | 0 | 0.04239 | 0.10353 | -0.40945 | 0.21306 | Normal | 74.1019 | 0.53055 | Night | 202602 | 2026-02-15 | 0.53055
2026-02-15 22:11 | 73.7888 | FALSE | FALSE | -0.45609 | -0.62194 | -0.28653 | -0.3868 | 0 |  |  | none | FALSE | 0 | 73.3327 | FALSE | FALSE | 0.0304 |  | 73.704 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.18565 | Normal | 74.0753 | 0.45666 | Night | 202602 | 2026-02-15 | 0.45666
2026-02-15 22:26 | 73.7888 | FALSE | FALSE | -0.3522 | -0.4796 | -0.23916 | -0.32307 | 0 |  |  | none | FALSE | 0 | 73.4366 | FALSE | FALSE | 0.0255 |  | 73.7323 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.14784 | Normal | 74.028 | 0.3823 | Night | 202602 | 2026-02-15 | 0.3823
2026-02-15 22:41 | 73.7888 | FALSE | FALSE | -0.20222 | -0.27481 | -0.1457 | -0.19707 | 0 |  |  | none | FALSE | 0 | 73.5866 | FALSE | FALSE | 0.0217 |  | 73.7605 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.086982 | Normal | 73.9345 | 0.32489 | Night | 202602 | 2026-02-15 | 0.32489
2026-02-15 22:56 | 73.5062 | TRUE | FALSE | 0.080375 | 0.10923 | -0.4283 | -0.5793 | -0.2826 | 2026-02-16 02:40 | 2026-02-15 22:56 | lower | TRUE | 1 | 73.5866 | FALSE | FALSE | 0.2807 | 2.924 | 73.7605 | 1 | -0.2826 | 0 | 0.091688 | -3.0822 | 0.086982 | Extreme triggered | 73.9345 | -2.924 | Night | 202602 | 2026-02-15 | 2.924
2026-02-15 23:11 | 73.5062 | FALSE | FALSE | 0.080375 | 0.10923 | -0.4283 | -0.5793 | 0 |  | 2026-02-15 22:56 | lower | TRUE | 1 | 73.5866 | FALSE | FALSE | 0.3378 | 2.924 | 73.7605 | 2 | 0 | 0 | 0.091688 | 0 | 0.086982 | Extreme/elevated | 73.9345 | -2.924 | Night | 202602 | 2026-02-15 | 2.924
2026-02-15 23:26 | 73.5062 | FALSE | FALSE | 0.03315 | 0.045078 | -0.44727 | -0.6048 | 0 |  | 2026-02-15 22:56 | lower | TRUE | 1 | 73.5394 | FALSE | TRUE | 0.3547 | 2.7228 | 73.7464 | 3 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.10353 | Persistent | 73.9535 | -2.3202 | Night | 202602 | 2026-02-15 | 2.3202
2026-02-15 23:40 | 73.5062 | FALSE | FALSE | -0.0058732 | -0.0079907 | -0.45803 | -0.61926 | 0 |  | 2026-02-15 22:56 | none | FALSE | 1 | 73.5003 | FALSE | FALSE | 0.3871 | 2.5294 | 73.7323 | 4 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.11598 | Persistent | 73.9642 | -1.9494 | Night | 202602 | 2026-02-15 | 1.9494
2026-02-15 23:55 | 73.5062 | FALSE | FALSE | -0.039147 | -0.053285 | -0.46305 | -0.626 | 0 |  | 2026-02-15 22:56 | none | FALSE | 1 | 73.4671 | FALSE | FALSE | 0.4268 | 2.3612 | 73.7181 | 5 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.12555 | Persistent | 73.9692 | -1.6882 | Night | 202602 | 2026-02-15 | 1.6882
2026-02-16 00:11 | 73.5062 | FALSE | FALSE | -0.067916 | -0.09248 | -0.46356 | -0.62668 | 0 |  | 2026-02-15 22:56 | none | FALSE | 1 | 73.4383 | FALSE | FALSE | 0.4707 | 2.2158 | 73.704 | 6 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.13287 | Persistent | 73.9698 | -1.4888 | Night | 202602 | 2026-02-16 | 1.4888
2026-02-16 00:26 | 73.2236 | TRUE | TRUE | 0.11403 | 0.15549 | -0.79029 | -1.0678 | -0.2826 |  | 2026-02-15 22:56 | lower | TRUE | 2 | 73.3376 | TRUE | TRUE | 0.6354 | 2.2813 | 73.6758 | 7 | -0.2826 | -0.02826 | 0.086982 | -2.924 | 0.16906 | Confirmed/Materialized Shift | 74.0139 | -2.6745 | Night | 202602 | 2026-02-16 | 2.6745
2026-02-16 00:40 | 73.2236 | FALSE | TRUE | 0.034903 | 0.047643 | -0.8129 | -1.098 | 0 |  | 2026-02-15 22:56 | lower | TRUE | 2 | 73.2585 | FALSE | TRUE | 0.6024 | 2.2686 | 73.6475 | 8 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.1945 | Confirmed/Materialized Shift | 74.0365 | -2.1794 | Night | 202602 | 2026-02-16 | 2.1794
2026-02-16 00:55 | 73.2236 | FALSE | TRUE | -0.030485 | -0.04165 | -0.82177 | -1.1098 | 0 |  | 2026-02-15 22:56 | none | FALSE | 2 | 73.1931 | FALSE | FALSE | 0.5809 | 2.2228 | 73.6192 | 9 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21306 | Confirmed/Materialized Shift | 74.0454 | -1.8569 | Night | 202602 | 2026-02-16 | 1.8569
2026-02-16 01:10 | 73.2236 | FALSE | TRUE | -0.085523 | -0.11693 | -0.82028 | -1.1078 | 0 |  | 2026-02-15 22:56 | none | FALSE | 2 | 73.1381 | FALSE | FALSE | 0.5653 | 2.1628 | 73.591 | 10 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22645 | Confirmed/Materialized Shift | 74.0439 | -1.6223 | Night | 202602 | 2026-02-16 | 1.6223
2026-02-16 01:25 | 73.2236 | FALSE | TRUE | -0.13198 | -0.18057 | -0.81022 | -1.0944 | 0 |  | 2026-02-15 22:56 | none | FALSE | 1 | 73.0916 | FALSE | FALSE | 0.5246 | 2.0971 | 73.5627 | 11 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.23555 | Confirmed/Materialized Shift | 74.0338 | -1.4397 | Night | 202602 | 2026-02-16 | 1.4397
2026-02-16 01:40 | 73.2236 | FALSE | TRUE | -0.17083 | -0.23384 | -0.79255 | -1.0708 | 0 |  | 2026-02-15 22:56 | none | FALSE | 1 | 73.0528 | FALSE | FALSE | 0.5146 | 2.0299 | 73.5345 | 12 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.24084 | Confirmed/Materialized Shift | 74.0161 | -1.2907 | Night | 202602 | 2026-02-16 | 1.2907
2026-02-16 01:55 | 73.2236 | FALSE | TRUE | -0.20256 | -0.27741 | -0.76776 | -1.0376 | 0 |  | 2026-02-15 22:56 | none | FALSE | 1 | 73.021 | FALSE | FALSE | 0.5062 | 1.9633 | 73.5062 | 13 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.24258 | Confirmed/Materialized Shift | 73.9914 | -1.165 | Night | 202602 | 2026-02-16 | 1.165
2026-02-16 02:10 | 73.2236 | FALSE | TRUE | -0.22735 | -0.31145 | -0.73603 | -0.99517 | 0 |  | 2026-02-15 22:56 | none | FALSE | 1 | 72.9963 | FALSE | FALSE | 0.499 | 1.8985 | 73.4779 | 14 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.24084 | Confirmed/Materialized Shift | 73.9596 | -1.056 | Night | 202602 | 2026-02-16 | 1.056
2026-02-16 02:25 | 72.941 | TRUE | TRUE | -0.020045 | -0.027489 | -1.0091 | -1.3646 | -0.2826 |  | 2026-02-15 22:56 | none | FALSE | 2 | 72.921 | TRUE | FALSE | 0.5853 | 1.9001 | 73.4356 | 15 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.2573 | Confirmed/Materialized Shift | 73.9501 | -1.9221 | Night | 202602 | 2026-02-16 | 1.9221
2026-02-16 02:40 | 73.2236 | TRUE | FALSE | -0.31091 | -0.42642 | -0.67829 | -0.91783 | 0.2826 |  |  | none | FALSE | 3 | 72.9127 | TRUE | FALSE | 0.1352 |  | 73.4073 | 0 | 0.2826 | -0.02826 | 0.12638 | 2.4597 | 0.2473 | Persistence ends | 73.9019 | -0.74278 | Night | 202602 | 2026-02-16 | 0.74278
2026-02-16 02:55 | 72.941 | FALSE | FALSE | -0.078293 | -0.10745 | -0.92609 | -1.2537 | -0.2826 |  |  | none | FALSE | 2 | 72.8627 | FALSE | FALSE | 0.1697 |  | 73.3649 | 0 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.2511 | Normal | 73.8671 | -1.6882 | Night | 202602 | 2026-02-16 | 1.6882
2026-02-16 03:10 | 72.941 | FALSE | FALSE | -0.11309 | -0.15529 | -0.87611 | -1.1869 | 0 |  |  | none | FALSE | 2 | 72.8279 | FALSE | FALSE | 0.16 |  | 73.3225 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.2473 | Normal | 73.8171 | -1.5427 | Night | 202602 | 2026-02-16 | 1.5427
2026-02-16 03:25 | 72.941 | FALSE | FALSE | -0.13198 | -0.18127 | -0.81022 | -1.0986 | 0 |  |  | none | FALSE | 2 | 72.809 | FALSE | FALSE | 0.1531 |  | 73.2801 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.23555 | Normal | 73.7512 | -1.4397 | Night | 202602 | 2026-02-16 | 1.4397
2026-02-16 03:39 | 72.941 | FALSE | FALSE | -0.13234 | -0.18177 | -0.7258 | -0.98525 | 0 |  |  | none | FALSE | 2 | 72.8087 | FALSE | FALSE | 0.1494 |  | 73.2377 | 0 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.21454 | Normal | 73.6668 | -1.3831 | Night | 202602 | 2026-02-16 | 1.3831
2026-02-16 03:54 | 72.941 | FALSE | FALSE | -0.1606 | -0.22067 | -0.69754 | -0.94725 | 0 |  |  | none | FALSE | 2 | 72.7804 | FALSE | FALSE | 0.1406 |  | 73.2095 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21454 | Normal | 73.6385 | -1.2514 | Night | 202602 | 2026-02-16 | 1.2514
2026-02-16 04:09 | 72.941 | FALSE | FALSE | -0.18095 | -0.2487 | -0.66137 | -0.89858 | 0 |  |  | none | FALSE | 2 | 72.76 | FALSE | FALSE | 0.1332 |  | 73.1812 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21058 | Normal | 73.6024 | -1.1407 | Night | 202602 | 2026-02-16 | 1.1407
2026-02-16 04:24 | 72.941 | FALSE | FALSE | -0.19293 | -0.2652 | -0.61683 | -0.83857 | 0 |  |  | none | FALSE | 2 | 72.7481 | FALSE | FALSE | 0.1269 |  | 73.153 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.20244 | Normal | 73.5578 | -1.047 | Night | 202602 | 2026-02-16 | 1.047
2026-02-16 04:39 | 72.941 | FALSE | FALSE | -0.19546 | -0.26869 | -0.56284 | -0.76573 | 0 |  |  | none | FALSE | 2 | 72.7455 | FALSE | FALSE | 0.1217 |  | 73.1247 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.18957 | Normal | 73.5038 | -0.96896 | Night | 202602 | 2026-02-16 | 0.96896
2026-02-16 04:54 | 72.941 | FALSE | FALSE | -0.18641 | -0.25621 | -0.49727 | -0.67712 | 0 |  |  | none | FALSE | 1 | 72.7546 | FALSE | FALSE | 0.0892 |  | 73.0964 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.17092 | Normal | 73.4383 | -0.90938 | Night | 202602 | 2026-02-16 | 0.90938
2026-02-16 05:09 | 72.941 | FALSE | FALSE | -0.16132 | -0.22165 | -0.41566 | -0.56663 | 0 |  |  | none | FALSE | 0 | 72.7797 | FALSE | FALSE | 0.0588 |  | 73.0682 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.14424 | Normal | 73.3567 | -0.88163 | Night | 202602 | 2026-02-16 | 0.88163
2026-02-16 05:24 | 72.941 | FALSE | FALSE | -0.17104 | -0.23505 | -0.39712 | -0.5415 | 0 |  |  | none | FALSE | 0 | 72.77 | FALSE | FALSE | 0.0531 |  | 73.054 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14204 | Normal | 73.3381 | -0.79582 | Night | 202602 | 2026-02-16 | 0.79582
2026-02-16 05:39 | 72.941 | FALSE | FALSE | -0.17768 | -0.24418 | -0.3755 | -0.51216 | 0 |  |  | none | FALSE | 0 | 72.7633 | FALSE | FALSE | 0.0477 |  | 73.0399 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.13829 | Normal | 73.3165 | -0.71522 | Night | 202602 | 2026-02-16 | 0.71522
2026-02-16 05:54 | 72.6584 | TRUE | FALSE | 0.042322 | 0.058215 | -0.66418 | -0.90583 | -0.2826 | 2026-02-16 08:00 | 2026-02-16 05:54 | lower | TRUE | 1 | 72.7007 | FALSE | FALSE | 0.2372 | 2.2722 | 73.0117 | 1 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.15546 | Extreme triggered | 73.3226 | -2.2722 | Night | 202602 | 2026-02-16 | 2.2722
2026-02-16 06:09 | 72.6584 | FALSE | FALSE | -0.0068632 | -0.0094467 | -0.65684 | -0.89592 | 0 |  | 2026-02-16 05:54 | none | FALSE | 1 | 72.6515 | FALSE | FALSE | 0.2734 | 2.1154 | 72.9834 | 2 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.16593 | Extreme/elevated | 73.3152 | -1.9586 | Night | 202602 | 2026-02-16 | 1.9586
2026-02-16 06:24 | 72.6584 | FALSE | FALSE | -0.045106 | -0.062118 | -0.63857 | -0.8712 | 0 |  | 2026-02-16 05:54 | none | FALSE | 1 | 72.6133 | FALSE | FALSE | 0.3157 | 1.989 | 72.9551 | 3 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.17092 | Persistent | 73.297 | -1.7361 | Night | 202602 | 2026-02-16 | 1.7361
2026-02-16 06:38 | 72.6584 | FALSE | FALSE | -0.073366 | -0.10108 | -0.61031 | -0.83297 | 0 |  | 2026-02-16 05:54 | none | FALSE | 1 | 72.585 | FALSE | FALSE | 0.3619 | 1.8844 | 72.9269 | 4 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.17092 | Persistent | 73.2687 | -1.5708 | Night | 202602 | 2026-02-16 | 1.5708
2026-02-16 06:53 | 72.6584 | FALSE | FALSE | -0.091643 | -0.12629 | -0.57206 | -0.78118 | 0 |  | 2026-02-16 05:54 | none | FALSE | 1 | 72.5668 | FALSE | FALSE | 0.4108 | 1.7971 | 72.8986 | 5 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.16593 | Persistent | 73.2305 | -1.4477 | Night | 202602 | 2026-02-16 | 1.4477
2026-02-16 07:08 | 72.6584 | FALSE | FALSE | -0.098978 | -0.13641 | -0.52288 | -0.7145 | 0 |  | 2026-02-16 05:54 | none | FALSE | 1 | 72.5594 | FALSE | FALSE | 0.4623 | 1.7248 | 72.8704 | 6 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.15546 | Persistent | 73.1813 | -1.3633 | Day | 202602 | 2026-02-16 | 1.3633
2026-02-16 07:23 | 72.6584 | FALSE | TRUE | -0.12505 | -0.1724 | -0.52069 | -0.71152 | 0 |  | 2026-02-16 05:54 | none | FALSE | 1 | 72.5334 | FALSE | FALSE | 0.5103 | 1.6535 | 72.8562 | 7 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.16143 | Confirmed/Materialized Shift | 73.1791 | -1.2254 | Day | 202602 | 2026-02-16 | 1.2254
2026-02-16 07:30 | 72.6584 | FALSE | TRUE | -0.11452 | -0.15787 | -0.45364 | -0.62048 | 0 |  | 2026-02-16 05:54 | none | FALSE | 1 | 72.5439 | FALSE | FALSE | 0.5082 | 1.596 | 72.828 | 8 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.14204 | Confirmed/Materialized Shift | 73.112 | -1.1937 | Day | 202602 | 2026-02-16 | 1.1937
2026-02-16 07:45 | 72.6584 | FALSE | TRUE | -0.13306 | -0.18346 | -0.44392 | -0.60726 | 0 |  | 2026-02-16 05:54 | none | FALSE | 1 | 72.5253 | FALSE | FALSE | 0.5004 | 1.5384 | 72.8138 | 9 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14424 | Confirmed/Materialized Shift | 73.1023 | -1.0775 | Day | 202602 | 2026-02-16 | 1.0775
2026-02-16 08:00 | 72.6584 | FALSE | FALSE | -0.14864 | -0.205 | -0.43124 | -0.59002 | 0 |  |  | none | FALSE | 1 | 72.5098 | FALSE | FALSE | 0.0936 |  | 72.7997 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14497 | Persistence ends | 73.0896 | -0.97468 | Day | 202602 | 2026-02-16 | 0.97468
2026-02-16 08:16 | 72.6584 | FALSE | FALSE | -0.16132 | -0.22252 | -0.41566 | -0.56882 | 0 |  |  | none | FALSE | 0 | 72.4971 | FALSE | FALSE | 0.0588 |  | 72.7856 | 0 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.14424 | Normal | 73.0741 | -0.88163 | Day | 202602 | 2026-02-16 | 0.88163
2026-02-16 08:30 | 72.941 | TRUE | FALSE | -0.44392 | -0.61233 | -0.13306 | -0.18209 | 0.2826 |  |  | none | FALSE | 1 | 72.4971 | FALSE | FALSE | 0.1004 |  | 72.7856 | 0 | 0.2826 | 0 | 0.091688 | 3.0822 | 0.14424 | Normal | 73.0741 | 1.0775 | Day | 202602 | 2026-02-16 | 1.0775
2026-02-16 08:45 | 72.941 | FALSE | FALSE | -0.44392 | -0.61233 | -0.13306 | -0.18209 | 0 |  |  | none | FALSE | 1 | 72.4971 | FALSE | FALSE | 0.1004 |  | 72.7856 | 0 | 0 | 0 | 0.091688 | 0 | 0.14424 | Normal | 73.0741 | 1.0775 | Day | 202602 | 2026-02-16 | 1.0775
2026-02-16 08:45 | 72.941 | FALSE | FALSE | -0.44392 | -0.61233 | -0.13306 | -0.18209 | 0 |  |  | none | FALSE | 1 | 72.4971 | FALSE | FALSE | 0.1004 |  | 72.7856 | 0 | 0 | 0 | 0.091688 | 0 | 0.14424 | Normal | 73.0741 | 1.0775 | Day | 202602 | 2026-02-16 | 1.0775
2026-02-16 09:00 | 73.2236 | TRUE | FALSE | -0.76696 | -1.0585 | 0.080837 | 0.11052 | 0.2826 | 2026-02-16 11:30 | 2026-02-16 09:00 | upper | TRUE | 2 | 72.4566 | TRUE | FALSE | 0.279 | 2.4713 | 72.7997 | 1 | 0.2826 | 0.01413 | 0.11135 | 2.411 | 0.17153 | Extreme triggered | 73.1428 | 2.4713 | Day | 202602 | 2026-02-16 | 2.4713
2026-02-16 09:15 | 73.5062 | TRUE | FALSE | -1.1421 | -1.5783 | 0.21433 | 0.29244 | 0.2826 |  | 2026-02-16 09:00 | upper | TRUE | 3 | 72.3641 | TRUE | FALSE | 0.3949 | 2.6977 | 72.828 | 2 | 0.2826 | 0.02826 | 0.12638 | 2.0125 | 0.23195 | Extreme/elevated | 73.2919 | 2.924 | Day | 202602 | 2026-02-16 | 2.924
2026-02-16 09:30 | 73.2236 | TRUE | FALSE | -0.87611 | -1.211 | -0.11309 | -0.15421 | -0.2826 |  | 2026-02-16 09:00 | none | FALSE | 4 | 72.3475 | TRUE | FALSE | 0.3886 | 2.3127 | 72.8421 | 3 | -0.2826 | 0.01413 | 0.14424 | -2.0571 | 0.2473 | Persistent | 73.3367 | 1.5427 | Day | 202602 | 2026-02-16 | 1.5427
2026-02-16 09:44 | 73.2236 | FALSE | FALSE | -0.88927 | -1.2294 | -0.15451 | -0.21057 | 0 |  | 2026-02-16 09:00 | none | FALSE | 4 | 72.3343 | FALSE | FALSE | 0.4367 | 2.0865 | 72.8562 | 4 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.26095 | Persistent | 73.3781 | 1.4079 | Day | 202602 | 2026-02-16 | 1.4079
2026-02-16 09:59 | 73.2236 | FALSE | FALSE | -0.89954 | -1.2438 | -0.19304 | -0.26294 | 0 |  | 2026-02-16 09:00 | none | FALSE | 4 | 72.3241 | FALSE | FALSE | 0.4862 | 1.9278 | 72.8704 | 5 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.27315 | Persistent | 73.4166 | 1.2933 | Day | 202602 | 2026-02-16 | 1.2933
2026-02-16 10:14 | 73.2236 | FALSE | FALSE | -0.90729 | -1.2546 | -0.22905 | -0.31183 | 0 |  | 2026-02-16 09:00 | none | FALSE | 4 | 72.3163 | FALSE | FALSE | 0.5367 | 1.8055 | 72.8845 | 6 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.28408 | Persistent | 73.4526 | 1.1937 | Day | 202602 | 2026-02-16 | 1.1937
2026-02-16 10:30 | 73.5062 | FALSE | TRUE | -1.2005 | -1.6603 | -0.041849 | -0.0569 | 0.2826 |  | 2026-02-16 09:00 | none | FALSE | 4 | 72.3057 | FALSE | FALSE | 0.6386 | 1.814 | 72.9269 | 7 | 0.2826 | 0.04239 | 0.13829 | 1.737 | 0.31059 | Confirmed/Materialized Shift | 73.548 | 1.8653 | Day | 202602 | 2026-02-16 | 1.8653
2026-02-16 10:44 | 73.5062 | FALSE | TRUE | -1.1956 | -1.6534 | -0.12168 | -0.16526 | 0 |  | 2026-02-16 09:00 | none | FALSE | 3 | 72.3106 | FALSE | FALSE | 0.5944 | 1.7911 | 72.9693 | 8 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.32931 | Confirmed/Materialized Shift | 73.6279 | 1.6305 | Day | 202602 | 2026-02-16 | 1.6305
2026-02-16 10:57 | 74.0714 | TRUE | TRUE | -1.8366 | -2.5425 | 0.22641 | 0.30661 | 0.5652 |  | 2026-02-16 09:00 | upper | TRUE | 4 | 72.2348 | TRUE | TRUE | 0.6851 | 1.8768 | 73.0399 | 9 | 0.5652 | 0.07065 | 0.18049 | 2.7401 | 0.40254 | Confirmed/Materialized Shift | 73.845 | 2.5625 | Day | 202602 | 2026-02-16 | 2.5625
2026-02-16 11:00 | 74.0714 | FALSE | TRUE | -1.8666 | -2.5852 | 0.055034 | 0.074354 | 0 |  | 2026-02-16 09:00 | upper | TRUE | 4 | 72.2048 | FALSE | TRUE | 0.6557 | 1.9013 | 73.1106 | 10 | 0 | 0.07065 | 0.18049 | -0.39144 | 0.4529 | Confirmed/Materialized Shift | 74.0164 | 2.1215 | Day | 202602 | 2026-02-16 | 2.1215
2026-02-16 11:15 | 73.7888 | FALSE | TRUE | -1.5495 | -2.145 | -0.30609 | -0.41311 | -0.2826 |  | 2026-02-16 09:00 | none | FALSE | 3 | 72.2393 | FALSE | FALSE | 0.5751 | 1.8503 | 73.1671 | 11 | -0.2826 | 0.05652 | 0.19665 | -1.7245 | 0.46391 | Confirmed/Materialized Shift | 74.0949 | 1.3402 | Day | 202602 | 2026-02-16 | 1.3402
2026-02-16 11:30 | 73.5062 | FALSE | FALSE | -1.2039 | -1.6651 | -0.61047 | -0.82366 | -0.2826 |  |  | none | FALSE | 2 | 72.3023 | FALSE | FALSE | 0.1008 |  | 73.2095 | 0 | -0.2826 | 0.04239 | 0.21058 | -1.5433 | 0.4536 | Persistence ends | 74.1167 | 0.65417 | Day | 202602 | 2026-02-16 | 0.65417
2026-02-16 11:44 | 73.5062 | FALSE | FALSE | -1.1319 | -1.5639 | -0.62318 | -0.84067 | 0 |  |  | none | FALSE | 1 | 72.3743 | FALSE | FALSE | 0.0672 |  | 73.2519 | 0 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.43876 | Normal | 74.1294 | 0.57968 | Day | 202602 | 2026-02-16 | 0.57968
2026-02-16 11:59 | 73.5062 | FALSE | FALSE | -1.0498 | -1.4488 | -0.62588 | -0.84427 | 0 |  |  | none | FALSE | 1 | 72.4564 | FALSE | FALSE | 0.0623 |  | 73.2943 | 0 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.41891 | Normal | 74.1321 | 0.50595 | Day | 202602 | 2026-02-16 | 0.50595
2026-02-16 12:14 | 73.2236 | FALSE | FALSE | -0.68501 | -0.94433 | -0.88283 | -1.1913 | -0.2826 |  |  | none | FALSE | 1 | 72.5386 | FALSE | FALSE | 0.0454 |  | 73.3225 | 0 | -0.2826 | 0.02826 | 0.22271 | -1.3958 | 0.39196 | Normal | 74.1064 | -0.25235 | Day | 202602 | 2026-02-16 | 0.25235
2026-02-16 12:29 | 73.2236 | FALSE | FALSE | -0.5942 | -0.81812 | -0.84854 | -1.1456 | 0 |  |  | none | FALSE | 1 | 72.6294 | FALSE | FALSE | 0.0521 |  | 73.3508 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.36068 | Normal | 74.0721 | -0.35258 | Day | 202602 | 2026-02-16 | 0.35258
2026-02-16 12:43 | 73.2236 | FALSE | FALSE | -0.49225 | -0.67681 | -0.80311 | -1.0849 | 0 |  |  | none | FALSE | 1 | 72.7313 | FALSE | FALSE | 0.0606 |  | 73.379 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.32384 | Normal | 74.0267 | -0.47996 | Day | 202602 | 2026-02-16 | 0.47996
2026-02-16 12:58 | 73.2236 | FALSE | FALSE | -0.44959 | -0.61778 | -0.78871 | -1.0656 | 0 |  |  | none | FALSE | 1 | 72.774 | FALSE | FALSE | 0.0651 |  | 73.3932 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.30957 | Normal | 74.0123 | -0.54772 | Day | 202602 | 2026-02-16 | 0.54772
2026-02-16 13:14 | 73.2236 | FALSE | FALSE | -0.40411 | -0.55495 | -0.77149 | -1.0426 | 0 |  |  | none | FALSE | 0 | 72.8195 | FALSE | FALSE | 0.0417 |  | 73.4073 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.2939 | Normal | 73.9951 | -0.62501 | Day | 202602 | 2026-02-16 | 0.62501
2026-02-16 13:29 | 73.2236 | FALSE | FALSE | -0.35535 | -0.48767 | -0.75099 | -1.0152 | 0 |  |  | none | FALSE | 0 | 72.8682 | FALSE | FALSE | 0.0477 |  | 73.4214 | 0 | 0 | 0.01413 | 0.21454 | -0.065863 | 0.27659 | Normal | 73.9746 | -0.71522 | Day | 202602 | 2026-02-16 | 0.71522
2026-02-16 13:43 | 73.2236 | FALSE | FALSE | -0.35535 | -0.48767 | -0.75099 | -1.0152 | 0 |  |  | none | FALSE | 0 | 72.8682 | FALSE | FALSE | 0.0477 |  | 73.4214 | 0 | 0 | 0 | 0.20502 | 0 | 0.27659 | Normal | 73.9746 | -0.71522 | Day | 202602 | 2026-02-16 | 0.71522
2026-02-16 13:58 | 72.941 | FALSE | FALSE | -0.13921 | -0.19121 | -1.0435 | -1.4105 | -0.2826 |  |  | none | FALSE | 0 | 72.8018 | FALSE | FALSE | 0.1019 |  | 73.3932 | 0 | -0.2826 | -0.02826 | 0.20296 | -1.2532 | 0.29568 | Normal | 73.9845 | -1.5292 | Day | 202602 | 2026-02-16 | 1.5292
2026-02-16 14:13 | 72.941 | FALSE | FALSE | -0.18315 | -0.25172 | -1.0592 | -1.4314 | 0 |  |  | none | FALSE | 0 | 72.7579 | FALSE | FALSE | 0.094 |  | 73.379 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.31059 | Normal | 74.0002 | -1.4103 | Day | 202602 | 2026-02-16 | 1.4103
2026-02-16 14:28 | 72.941 | FALSE | FALSE | -0.22443 | -0.30864 | -1.0722 | -1.4487 | 0 |  |  | none | FALSE | 0 | 72.7166 | FALSE | FALSE | 0.0872 |  | 73.3649 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.32416 | Normal | 74.0132 | -1.3077 | Day | 202602 | 2026-02-16 | 1.3077
2026-02-16 14:43 | 72.941 | FALSE | FALSE | -0.26337 | -0.36238 | -1.0829 | -1.4629 | 0 |  |  | none | FALSE | 0 | 72.6776 | FALSE | FALSE | 0.0812 |  | 73.3508 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.33657 | Normal | 74.0239 | -1.2175 | Day | 202602 | 2026-02-16 | 1.2175
2026-02-16 14:58 | 72.941 | FALSE | FALSE | -0.30022 | -0.41329 | -1.0915 | -1.4744 | 0 |  |  | none | FALSE | 0 | 72.6408 | FALSE | FALSE | 0.0758 |  | 73.3366 | 0 | 0 | -0.01413 | 0.19396 | 0.072851 | 0.34793 | Normal | 74.0325 | -1.1371 | Day | 202602 | 2026-02-16 | 1.1371
2026-02-16 15:13 | 72.941 | FALSE | FALSE | -0.34519 | -0.4755 | -1.08 | -1.459 | 0 |  |  | none | FALSE | 0 | 72.5958 | FALSE | FALSE | 0.0687 |  | 73.3084 | 0 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.35629 | Normal | 74.021 | -1.0311 | Day | 202602 | 2026-02-16 | 1.0311
2026-02-16 15:28 | 72.6584 | FALSE | FALSE | -0.15458 | -0.2132 | -1.3698 | -1.8503 | -0.2826 |  |  | none | FALSE | 0 | 72.5038 | FALSE | FALSE | 0.1063 |  | 73.266 | 0 | -0.2826 | -0.04239 | 0.18957 | -1.2671 | 0.38108 | Normal | 74.0282 | -1.5944 | Day | 202602 | 2026-02-16 | 1.5944
2026-02-16 15:43 | 72.6584 | FALSE | FALSE | -0.1709 | -0.23576 | -1.2448 | -1.6843 | 0 |  |  | none | FALSE | 0 | 72.4875 | FALSE | FALSE | 0.1011 |  | 73.1953 | 0 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.35392 | Normal | 73.9032 | -1.5171 | Day | 202602 | 2026-02-16 | 1.5171
2026-02-16 15:58 | 72.6584 | FALSE | FALSE | -0.14945 | -0.20611 | -1.082 | -1.4674 | 0 |  |  | none | FALSE | 0 | 72.5089 | FALSE | FALSE | 0.101 |  | 73.1247 | 0 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.30787 | Normal | 73.7404 | -1.5146 | Day | 202602 | 2026-02-16 | 1.5146
2026-02-16 16:13 | 72.3758 | FALSE | FALSE | 0.059094 | 0.081583 | -1.2974 | -1.761 | -0.2826 | 2026-02-16 16:57 | 2026-02-16 16:13 | lower | TRUE | 0 | 72.4349 | FALSE | FALSE | 0.2032 | 2.1909 | 73.054 | 1 | -0.2826 | -0.07065 | 0.12555 | -1.6882 | 0.30957 | Extreme triggered | 73.6732 | -2.1909 | Day | 202602 | 2026-02-16 | 2.1909
2026-02-16 16:28 | 72.3758 | FALSE | FALSE | -0.029197 | -0.040357 | -1.2726 | -1.728 | 0 |  | 2026-02-16 16:13 | none | FALSE | 0 | 72.3466 | FALSE | FALSE | 0.2416 | 2.0506 | 72.9975 | 2 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.32546 | Extreme/elevated | 73.6484 | -1.9103 | Day | 202602 | 2026-02-16 | 1.9103
2026-02-16 16:42 | 72.3758 | FALSE | FALSE | -0.095968 | -0.13277 | -1.2264 | -1.6662 | 0 |  | 2026-02-16 16:13 | none | FALSE | 0 | 72.2798 | FALSE | FALSE | 0.2854 | 1.937 | 72.941 | 3 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.33058 | Persistent | 73.6022 | -1.7097 | Day | 202602 | 2026-02-16 | 1.7097
2026-02-16 16:57 | 72.6584 | TRUE | FALSE | -0.37553 | -0.51953 | -0.85595 | -1.1643 | 0.2826 |  |  | none | FALSE | 1 | 72.2829 | FALSE | FALSE | 0.0806 |  | 72.8986 | 0 | 0.2826 | -0.04239 | 0.13829 | 2.35 | 0.30787 | Persistence ends | 73.5144 | -0.78023 | Day | 202602 | 2026-02-16 | 0.78023
2026-02-16 17:12 | 72.941 | TRUE | FALSE | -0.65355 | -0.90409 | -0.54051 | -0.73557 | 0.2826 |  |  | none | FALSE | 2 | 72.2875 | TRUE | FALSE | 0.0698 |  | 72.8845 | 0 | 0.2826 | -0.01413 | 0.14424 | 2.0571 | 0.29851 | Normal | 73.4815 | 0.18934 | Day | 202602 | 2026-02-16 | 0.18934
2026-02-16 17:27 | 72.941 | FALSE | FALSE | -0.6469 | -0.89481 | -0.5056 | -0.68839 | 0 |  |  | none | FALSE | 2 | 72.2941 | FALSE | FALSE | 0.0735 |  | 72.8704 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.28812 | Normal | 73.4466 | 0.24521 | Day | 202602 | 2026-02-16 | 0.24521
2026-02-16 17:42 | 72.941 | FALSE | FALSE | -0.63795 | -0.88233 | -0.46839 | -0.63806 | 0 |  |  | none | FALSE | 2 | 72.303 | FALSE | FALSE | 0.0776 |  | 72.8562 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.27659 | Normal | 73.4094 | 0.30652 | Day | 202602 | 2026-02-16 | 0.30652
2026-02-16 17:57 | 72.941 | FALSE | FALSE | -0.62641 | -0.86623 | -0.42859 | -0.58416 | 0 |  |  | none | FALSE | 2 | 72.3146 | FALSE | FALSE | 0.0821 |  | 72.8421 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.26375 | Normal | 73.3696 | 0.37501 | Day | 202602 | 2026-02-16 | 0.37501
2026-02-16 18:12 | 72.6584 | FALSE | FALSE | -0.34593 | -0.47838 | -0.65679 | -0.89584 | -0.2826 |  |  | none | FALSE | 2 | 72.3125 | FALSE | FALSE | 0.0985 |  | 72.8138 | 0 | -0.2826 | -0.02826 | 0.15614 | -1.6289 | 0.25068 | Normal | 73.3152 | -0.62004 | Day | 202602 | 2026-02-16 | 0.62004
2026-02-16 18:27 | 72.6584 | FALSE | FALSE | -0.33945 | -0.46937 | -0.59379 | -0.81061 | 0 |  |  | none | FALSE | 2 | 72.319 | FALSE | FALSE | 0.0935 |  | 72.7856 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.23331 | Normal | 73.2522 | -0.54507 | Night | 202602 | 2026-02-16 | 0.54507
2026-02-16 18:30 | 72.6584 | FALSE | FALSE | -0.32225 | -0.4455 | -0.52007 | -0.71069 | 0 |  |  | none | FALSE | 2 | 72.3361 | FALSE | FALSE | 0.0885 |  | 72.7573 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.21058 | Normal | 73.1785 | -0.4697 | Night | 202602 | 2026-02-16 | 0.4697
2026-02-16 18:31 | 72.3758 | FALSE | FALSE | -0.091222 | -0.1262 | -0.79772 | -1.0902 | -0.2826 |  |  | none | FALSE | 2 | 72.2846 | FALSE | FALSE | 0.1631 |  | 72.7291 | 0 | -0.2826 | -0.02826 | 0.15614 | -1.6289 | 0.22224 | Normal | 73.1735 | -1.5895 | Night | 202602 | 2026-02-16 | 1.5895
2026-02-16 18:46 | 73.2236 | TRUE | FALSE | -0.96904 | -1.3411 | -0.0081981 | -0.011195 | 0.8478 |  |  | none | FALSE | 3 | 72.2546 | TRUE | FALSE | 0.2168 |  | 72.7432 | 0 | 0.8478 | 0.01413 | 0.25068 | 3.3257 | 0.24431 | Normal | 73.2318 | 1.9664 | Night | 202602 | 2026-02-16 | 1.9664
2026-02-16 19:01 | 73.2236 | FALSE | FALSE | -0.99379 | -1.3759 | -0.061212 | -0.083527 | 0 |  |  | none | FALSE | 2 | 72.2298 | FALSE | FALSE | 0.175 |  | 72.7573 | 0 | 0 | 0.01413 | 0.25068 | -0.056367 | 0.26375 | Normal | 73.2848 | 1.7679 | Night | 202602 | 2026-02-16 | 1.7679
2026-02-16 19:16 | 73.2236 | FALSE | FALSE | -1.0144 | -1.4048 | -0.11006 | -0.15008 | 0 |  |  | none | FALSE | 1 | 72.2092 | FALSE | FALSE | 0.1358 |  | 72.7714 | 0 | 0 | 0.01413 | 0.25068 | -0.056367 | 0.28111 | Normal | 73.3337 | 1.6085 | Night | 202602 | 2026-02-16 | 1.6085
2026-02-16 19:30 | 73.2236 | FALSE | FALSE | -1.0315 | -1.4289 | -0.15547 | -0.21187 | 0 |  |  | none | FALSE | 1 | 72.1921 | FALSE | FALSE | 0.127 |  | 72.7856 | 0 | 0 | 0.01413 | 0.25068 | -0.056367 | 0.29675 | Normal | 73.3791 | 1.4761 | Night | 202602 | 2026-02-16 | 1.4761
2026-02-16 19:45 | 73.2236 | FALSE | FALSE | -1.0458 | -1.4489 | -0.19796 | -0.26961 | 0 |  |  | none | FALSE | 1 | 72.1778 | FALSE | FALSE | 0.1195 |  | 72.7997 | 0 | 0 | 0.01413 | 0.25068 | -0.056367 | 0.31093 | Normal | 73.4216 | 1.3633 | Night | 202602 | 2026-02-16 | 1.3633
2026-02-16 20:00 | 73.2236 | FALSE | FALSE | -1.0414 | -1.4427 | -0.25009 | -0.34038 | 0 |  |  | none | FALSE | 1 | 72.1822 | FALSE | FALSE | 0.1103 |  | 72.828 | 0 | 0 | 0.02826 | 0.24084 | -0.11734 | 0.32287 | Normal | 73.4737 | 1.2254 | Night | 202602 | 2026-02-16 | 1.2254
2026-02-16 20:15 | 73.2236 | FALSE | FALSE | -1.0311 | -1.4282 | -0.29633 | -0.40306 | 0 |  |  | none | FALSE | 1 | 72.1925 | FALSE | FALSE | 0.1024 |  | 72.8562 | 0 | 0 | 0.02826 | 0.24084 | -0.11734 | 0.33185 | Normal | 73.5199 | 1.1071 | Night | 202602 | 2026-02-16 | 1.1071
2026-02-16 20:29 | 73.2236 | FALSE | FALSE | -1.0154 | -1.4062 | -0.33713 | -0.45831 | 0 |  |  | none | FALSE | 1 | 72.2082 | FALSE | FALSE | 0.0954 |  | 72.8845 | 0 | 0 | 0.02826 | 0.24084 | -0.11734 | 0.33813 | Normal | 73.5607 | 1.0029 | Night | 202602 | 2026-02-16 | 1.0029
2026-02-16 20:44 | 73.2236 | FALSE | FALSE | -0.94441 | -1.3066 | -0.35095 | -0.477 | 0 |  |  | none | FALSE | 1 | 72.2792 | FALSE | FALSE | 0.0897 |  | 72.9269 | 0 | 0 | 0.04239 | 0.22968 | -0.18456 | 0.32384 | Normal | 73.5746 | 0.91629 | Night | 202602 | 2026-02-16 | 0.91629
2026-02-16 20:59 | 73.2236 | FALSE | FALSE | -0.85976 | -1.1881 | -0.35108 | -0.47717 | 0 |  |  | none | FALSE | 1 | 72.3638 | FALSE | FALSE | 0.0846 |  | 72.9693 | 0 | 0 | 0.04239 | 0.22968 | -0.18456 | 0.30271 | Normal | 73.5747 | 0.84022 | Night | 202602 | 2026-02-16 | 0.84022
2026-02-16 21:14 | 72.941 | FALSE | FALSE | -0.48124 | -0.66415 | -0.59428 | -0.80816 | -0.2826 |  |  | none | FALSE | 0 | 72.4598 | FALSE | FALSE | 0.014 |  | 72.9975 | 0 | -0.2826 | 0.02826 | 0.24084 | -1.2907 | 0.26888 | Normal | 73.5353 | -0.2102 | Night | 202602 | 2026-02-16 | 0.2102
2026-02-16 21:29 | 72.941 | FALSE | FALSE | -0.44395 | -0.61236 | -0.58525 | -0.79597 | 0 |  |  | none | FALSE | 0 | 72.4971 | FALSE | FALSE | 0.0183 |  | 73.0117 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.2573 | Normal | 73.5262 | -0.27458 | Night | 202602 | 2026-02-16 | 0.27458
2026-02-16 21:44 | 73.2236 | FALSE | FALSE | -0.71971 | -0.99266 | -0.32407 | -0.44063 | 0.2826 |  |  | none | FALSE | 0 | 72.5039 | FALSE | FALSE | 0.0505 |  | 73.0258 | 0 | 0.2826 | 0.01413 | 0.23331 | 1.1507 | 0.26095 | Normal | 73.5477 | 0.75808 | Night | 202602 | 2026-02-16 | 0.75808
2026-02-16 21:59 | 72.941 | FALSE | FALSE | -0.43711 | -0.60288 | -0.60667 | -0.82487 | -0.2826 |  |  | none | FALSE | 0 | 72.5039 | FALSE | FALSE | 0.0217 |  | 73.0258 | 0 | -0.2826 | 0 | 0.24258 | -1.165 | 0.26095 | Normal | 73.5477 | -0.32489 | Night | 202602 | 2026-02-16 | 0.32489
2026-02-16 22:14 | 72.941 | FALSE | FALSE | -0.43711 | -0.60288 | -0.60667 | -0.82487 | 0 |  |  | none | FALSE | 0 | 72.5039 | FALSE | FALSE | 0.0217 |  | 73.0258 | 0 | 0 | 0 | 0.24258 | 0 | 0.26095 | Normal | 73.5477 | -0.32489 | Night | 202602 | 2026-02-16 | 0.32489
2026-02-16 22:29 | 72.941 | FALSE | FALSE | -0.43711 | -0.60288 | -0.60667 | -0.82487 | 0 |  |  | none | FALSE | 0 | 72.5039 | FALSE | FALSE | 0.0217 |  | 73.0258 | 0 | 0 | 0 | 0.24258 | 0 | 0.26095 | Normal | 73.5477 | -0.32489 | Night | 202602 | 2026-02-16 | 0.32489
2026-02-16 22:44 | 72.941 | FALSE | FALSE | -0.39569 | -0.54544 | -0.59351 | -0.80712 | 0 |  |  | none | FALSE | 0 | 72.5453 | FALSE | FALSE | 0.0267 |  | 73.0399 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.2473 | Normal | 73.5345 | -0.39996 | Night | 202602 | 2026-02-16 | 0.39996
2026-02-16 22:59 | 72.941 | FALSE | FALSE | -0.35087 | -0.48335 | -0.57695 | -0.78477 | 0 |  |  | none | FALSE | 0 | 72.5901 | FALSE | FALSE | 0.0325 |  | 73.054 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.23195 | Normal | 73.5179 | -0.48734 | Night | 202602 | 2026-02-16 | 0.48734
2026-02-16 23:14 | 72.941 | FALSE | FALSE | -0.3019 | -0.41562 | -0.55624 | -0.75682 | 0 |  |  | none | FALSE | 0 | 72.6391 | FALSE | FALSE | 0.0395 |  | 73.0682 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.21454 | Normal | 73.4972 | -0.59276 | Night | 202602 | 2026-02-16 | 0.59276
2026-02-16 23:28 | 72.941 | FALSE | FALSE | -0.13306 | -0.18275 | -0.44392 | -0.60492 | 0 |  |  | none | FALSE | 0 | 72.8079 | FALSE | FALSE | 0.0718 |  | 73.0964 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.14424 | Normal | 73.3849 | -1.0775 | Night | 202602 | 2026-02-16 | 1.0775
2026-02-16 23:43 | 72.941 | FALSE | FALSE | -0.14864 | -0.2042 | -0.43124 | -0.58774 | 0 |  |  | none | FALSE | 0 | 72.7924 | FALSE | FALSE | 0.065 |  | 73.0823 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14497 | Normal | 73.3722 | -0.97468 | Night | 202602 | 2026-02-16 | 0.97468
2026-02-16 23:58 | 72.941 | FALSE | FALSE | -0.16132 | -0.22165 | -0.41566 | -0.56663 | 0 |  |  | none | FALSE | 0 | 72.7797 | FALSE | FALSE | 0.0588 |  | 73.0682 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14424 | Normal | 73.3567 | -0.88163 | Night | 202602 | 2026-02-16 | 0.88163
2026-02-17 00:14 | 72.941 | FALSE | FALSE | -0.17104 | -0.23505 | -0.39712 | -0.5415 | 0 |  |  | none | FALSE | 0 | 72.77 | FALSE | FALSE | 0.0531 |  | 73.054 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.14204 | Normal | 73.3381 | -0.79582 | Night | 202602 | 2026-02-17 | 0.79582
2026-02-17 00:28 | 72.6584 | TRUE | FALSE | 0.044515 | 0.061228 | -0.69025 | -0.94105 | -0.2826 | 2026-02-17 08:15 | 2026-02-17 00:28 | lower | TRUE | 1 | 72.7029 | FALSE | FALSE | 0.2374 | 2.2757 | 73.0258 | 1 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.16143 | Extreme triggered | 73.3486 | -2.2757 | Night | 202602 | 2026-02-17 | 2.2757
2026-02-17 00:43 | 72.6584 | FALSE | FALSE | -0.0088098 | -0.012126 | -0.68705 | -0.93673 | 0 |  | 2026-02-17 00:28 | none | FALSE | 1 | 72.6496 | FALSE | FALSE | 0.2728 | 2.1126 | 72.9975 | 2 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.17396 | Extreme/elevated | 73.3454 | -1.9494 | Night | 202602 | 2026-02-17 | 1.9494
2026-02-17 00:58 | 72.6584 | FALSE | FALSE | -0.051277 | -0.070622 | -0.673 | -0.91775 | 0 |  | 2026-02-17 00:28 | none | FALSE | 1 | 72.6071 | FALSE | FALSE | 0.3145 | 1.9806 | 72.9693 | 3 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.18107 | Persistent | 73.3314 | -1.7168 | Night | 202602 | 2026-02-17 | 1.7168
2026-02-17 01:13 | 72.6584 | FALSE | FALSE | -0.08415 | -0.11595 | -0.64935 | -0.88579 | 0 |  | 2026-02-17 00:28 | none | FALSE | 1 | 72.5742 | FALSE | FALSE | 0.3599 | 1.8708 | 72.941 | 4 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.18338 | Persistent | 73.3078 | -1.5411 | Night | 202602 | 2026-02-17 | 1.5411
2026-02-17 01:28 | 72.6584 | FALSE | FALSE | -0.1078 | -0.14858 | -0.61648 | -0.84132 | 0 |  | 2026-02-17 00:28 | none | FALSE | 1 | 72.5506 | FALSE | FALSE | 0.4079 | 1.7775 | 72.9127 | 5 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.18107 | Persistent | 73.2749 | -1.4047 | Night | 202602 | 2026-02-17 | 1.4047
2026-02-17 01:43 | 72.6584 | FALSE | FALSE | -0.12185 | -0.16798 | -0.57401 | -0.78382 | 0 |  | 2026-02-17 00:28 | none | FALSE | 1 | 72.5366 | FALSE | FALSE | 0.4581 | 1.6979 | 72.8845 | 6 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.17396 | Persistent | 73.2324 | -1.2996 | Night | 202602 | 2026-02-17 | 1.2996
2026-02-17 01:58 | 72.3758 | FALSE | TRUE | 0.087142 | 0.12026 | -0.84544 | -1.1546 | -0.2826 |  | 2026-02-17 00:28 | lower | TRUE | 1 | 72.4629 | FALSE | TRUE | 0.5925 | 1.8067 | 72.8421 | 7 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.18957 | Confirmed/Materialized Shift | 73.2212 | -2.4597 | Night | 202602 | 2026-02-17 | 2.4597
2026-02-17 02:13 | 72.3758 | FALSE | TRUE | 0.0089558 | 0.012372 | -0.8671 | -1.1839 | 0 |  | 2026-02-17 00:28 | lower | TRUE | 1 | 72.3848 | FALSE | TRUE | 0.5647 | 1.8361 | 72.8138 | 8 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.21454 | Confirmed/Materialized Shift | 73.2429 | -2.0417 | Night | 202602 | 2026-02-17 | 2.0417
2026-02-17 02:27 | 72.3758 | FALSE | TRUE | -0.056847 | -0.078605 | -0.87639 | -1.1964 | 0 |  | 2026-02-17 00:28 | none | FALSE | 1 | 72.319 | FALSE | FALSE | 0.5457 | 1.8272 | 72.7856 | 9 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.23331 | Confirmed/Materialized Shift | 73.2522 | -1.7563 | Night | 202602 | 2026-02-17 | 1.7563
2026-02-17 02:43 | 72.3758 | FALSE | TRUE | -0.085523 | -0.11831 | -0.82028 | -1.1207 | 0 |  | 2026-02-17 00:28 | none | FALSE | 1 | 72.2903 | FALSE | FALSE | 0.5367 | 1.8067 | 72.7432 | 10 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.22645 | Confirmed/Materialized Shift | 73.1961 | -1.6223 | Night | 202602 | 2026-02-17 | 1.6223
2026-02-17 02:58 | 72.3758 | FALSE | TRUE | -0.13198 | -0.18269 | -0.81022 | -1.1071 | 0 |  | 2026-02-17 00:28 | none | FALSE | 0 | 72.2438 | FALSE | FALSE | 0.496 | 1.7734 | 72.7149 | 11 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.23555 | Confirmed/Materialized Shift | 73.186 | -1.4397 | Night | 202602 | 2026-02-17 | 1.4397
2026-02-17 03:13 | 72.3758 | FALSE | TRUE | -0.17083 | -0.23659 | -0.79255 | -1.0832 | 0 |  | 2026-02-17 00:28 | none | FALSE | 0 | 72.205 | FALSE | FALSE | 0.486 | 1.7331 | 72.6867 | 12 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.24084 | Confirmed/Materialized Shift | 73.1683 | -1.2907 | Night | 202602 | 2026-02-17 | 1.2907
2026-02-17 03:27 | 72.095 | TRUE | TRUE | 0.015912 | 0.022066 | -1.0828 | -1.4797 | -0.2808 |  | 2026-02-17 00:28 | lower | TRUE | 1 | 72.1109 | FALSE | TRUE | 0.5659 | 1.7583 | 72.6444 | 13 | -0.2808 | -0.0423 | 0.10331 | -2.3086 | 0.26672 | Confirmed/Materialized Shift | 73.1778 | -2.0597 | Night | 202602 | 2026-02-17 | 2.0597
2026-02-17 03:42 | 72.095 | FALSE | TRUE | -0.060429 | -0.083889 | -1.0745 | -1.4686 | 0 |  | 2026-02-17 00:28 | none | FALSE | 1 | 72.0346 | FALSE | FALSE | 0.5477 | 1.7603 | 72.6021 | 14 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.28374 | Confirmed/Materialized Shift | 73.1695 | -1.787 | Night | 202602 | 2026-02-17 | 1.787
2026-02-17 03:57 | 72.095 | FALSE | TRUE | -0.12214 | -0.1697 | -1.0517 | -1.4377 | 0 |  | 2026-02-17 00:28 | none | FALSE | 1 | 71.9729 | FALSE | FALSE | 0.5342 | 1.7485 | 72.5598 | 15 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.29345 | Confirmed/Materialized Shift | 73.1467 | -1.5838 | Night | 202602 | 2026-02-17 | 1.5838
2026-02-17 04:12 | 72.095 | FALSE | TRUE | -0.17066 | -0.23728 | -1.0156 | -1.3891 | 0 |  | 2026-02-17 00:28 | none | FALSE | 1 | 71.9243 | FALSE | FALSE | 0.5235 | 1.7283 | 72.5175 | 16 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.29656 | Confirmed/Materialized Shift | 73.1106 | -1.4245 | Night | 202602 | 2026-02-17 | 1.4245
2026-02-17 04:27 | 72.095 | FALSE | TRUE | -0.20641 | -0.28713 | -0.96673 | -1.3232 | 0 |  | 2026-02-17 00:28 | none | FALSE | 1 | 71.8886 | FALSE | FALSE | 0.515 | 1.7029 | 72.4752 | 17 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.29329 | Confirmed/Materialized Shift | 73.0617 | -1.2962 | Night | 202602 | 2026-02-17 | 1.2962
2026-02-17 04:42 | 72.095 | FALSE | TRUE | -0.22895 | -0.31858 | -0.90467 | -1.2393 | 0 |  | 2026-02-17 00:28 | none | FALSE | 1 | 71.866 | FALSE | FALSE | 0.508 | 1.6745 | 72.4329 | 18 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.28341 | Confirmed/Materialized Shift | 72.9997 | -1.1921 | Night | 202602 | 2026-02-17 | 1.1921
2026-02-17 04:57 | 72.095 | FALSE | TRUE | -0.23681 | -0.32955 | -0.82793 | -1.1353 | 0 |  | 2026-02-17 00:28 | none | FALSE | 1 | 71.8582 | FALSE | FALSE | 0.5026 | 1.6448 | 72.3906 | 19 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.26618 | Confirmed/Materialized Shift | 72.9229 | -1.1104 | Night | 202602 | 2026-02-17 | 1.1104
2026-02-17 05:12 | 72.095 | FALSE | TRUE | -0.22683 | -0.31562 | -0.73335 | -1.007 | 0 |  | 2026-02-17 00:28 | none | FALSE | 1 | 71.8682 | FALSE | FALSE | 0.4989 | 1.6153 | 72.3483 | 20 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.24004 | Confirmed/Materialized Shift | 72.8283 | -1.0551 | Night | 202602 | 2026-02-17 | 1.0551
2026-02-17 05:27 | 71.8124 | TRUE | TRUE | -0.019423 | -0.027054 | -1.0065 | -1.3823 | -0.2826 |  | 2026-02-17 00:28 | none | FALSE | 2 | 71.793 | TRUE | FALSE | 0.5854 | 1.63 | 72.306 | 21 | -0.2826 | -0.0423 | 0.10331 | -2.326 | 0.25649 | Confirmed/Materialized Shift | 72.8189 | -1.9243 | Night | 202602 | 2026-02-17 | 1.9243
2026-02-17 05:42 | 71.8124 | FALSE | TRUE | -0.0786 | -0.10957 | -0.98112 | -1.3478 | 0 |  | 2026-02-17 00:28 | none | FALSE | 2 | 71.7338 | FALSE | FALSE | 0.5707 | 1.6334 | 72.2637 | 22 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.26493 | Confirmed/Materialized Shift | 72.7935 | -1.7033 | Night | 202602 | 2026-02-17 | 1.7033
2026-02-17 05:57 | 71.8124 | FALSE | TRUE | -0.12328 | -0.17197 | -0.9412 | -1.2937 | 0 |  | 2026-02-17 00:28 | none | FALSE | 1 | 71.6891 | FALSE | FALSE | 0.531 | 1.6292 | 72.2214 | 23 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.26612 | Confirmed/Materialized Shift | 72.7536 | -1.5367 | Night | 202602 | 2026-02-17 | 1.5367
2026-02-17 06:12 | 71.8124 | FALSE | TRUE | -0.15368 | -0.21446 | -0.887 | -1.2201 | 0 |  | 2026-02-17 00:28 | none | FALSE | 1 | 71.6587 | FALSE | FALSE | 0.5225 | 1.62 | 72.1791 | 24 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.26017 | Confirmed/Materialized Shift | 72.6994 | -1.4093 | Night | 202602 | 2026-02-17 | 1.4093
2026-02-17 06:26 | 71.8124 | FALSE | TRUE | -0.16874 | -0.23553 | -0.81746 | -1.1255 | 0 |  | 2026-02-17 00:28 | none | FALSE | 1 | 71.6437 | FALSE | FALSE | 0.5163 | 1.6078 | 72.1368 | 25 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.24655 | Confirmed/Materialized Shift | 72.6299 | -1.3156 | Night | 202602 | 2026-02-17 | 1.3156
2026-02-17 06:41 | 71.8124 | FALSE | TRUE | -0.16569 | -0.23125 | -0.72981 | -1.006 | 0 |  | 2026-02-17 00:28 | none | FALSE | 1 | 71.6467 | FALSE | FALSE | 0.5126 | 1.5944 | 72.0945 | 26 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.22387 | Confirmed/Materialized Shift | 72.5422 | -1.2599 | Night | 202602 | 2026-02-17 | 1.2599
2026-02-17 06:56 | 71.5298 | TRUE | TRUE | 0.029001 | 0.040527 | -1.0157 | -1.4001 | -0.2826 |  | 2026-02-17 00:28 | lower | TRUE | 2 | 71.5588 | TRUE | TRUE | 0.5983 | 1.6138 | 72.0522 | 27 | -0.2826 | -0.0423 | 0.10331 | -2.326 | 0.24668 | Confirmed/Materialized Shift | 72.5455 | -2.1176 | Night | 202602 | 2026-02-17 | 2.1176
2026-02-17 07:11 | 71.5298 | FALSE | TRUE | -0.040769 | -0.057028 | -1.0009 | -1.38 | 0 |  | 2026-02-17 00:28 | none | FALSE | 2 | 71.489 | FALSE | FALSE | 0.58 | 1.622 | 72.0099 | 28 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.26041 | Confirmed/Materialized Shift | 72.5307 | -1.8434 | Day | 202602 | 2026-02-17 | 1.8434
2026-02-17 07:26 | 71.5298 | FALSE | TRUE | -0.095207 | -0.13328 | -0.97073 | -1.3389 | 0 |  | 2026-02-17 00:28 | none | FALSE | 2 | 71.4346 | FALSE | FALSE | 0.5667 | 1.6227 | 71.9676 | 29 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.26648 | Confirmed/Materialized Shift | 72.5005 | -1.6427 | Day | 202602 | 2026-02-17 | 1.6427
2026-02-17 07:30 | 71.5298 | FALSE | TRUE | -0.13537 | -0.18961 | -0.92629 | -1.2784 | 0 |  | 2026-02-17 00:28 | none | FALSE | 2 | 71.3944 | FALSE | FALSE | 0.5565 | 1.6183 | 71.9253 | 30 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.26541 | Confirmed/Materialized Shift | 72.4561 | -1.49 | Day | 202602 | 2026-02-17 | 1.49
2026-02-17 07:45 | 71.5298 | FALSE | TRUE | -0.16107 | -0.22569 | -0.86739 | -1.1981 | 0 |  | 2026-02-17 00:28 | none | FALSE | 1 | 71.3687 | FALSE | FALSE | 0.5201 | 1.6104 | 71.883 | 31 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.25712 | Confirmed/Materialized Shift | 72.3972 | -1.3735 | Day | 202602 | 2026-02-17 | 1.3735
2026-02-17 08:00 | 71.5298 | FALSE | TRUE | -0.17083 | -0.23939 | -0.79255 | -1.0959 | 0 |  | 2026-02-17 00:28 | none | FALSE | 1 | 71.359 | FALSE | FALSE | 0.5146 | 1.6004 | 71.8407 | 32 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.24084 | Confirmed/Materialized Shift | 72.3223 | -1.2907 | Day | 202602 | 2026-02-17 | 1.2907
2026-02-17 08:15 | 71.8124 | TRUE | FALSE | -0.45249 | -0.63409 | -0.48075 | -0.665 | 0.2826 |  |  | none | FALSE | 2 | 71.3599 | TRUE | FALSE | 0.0612 |  | 71.8265 | 0 | 0.2826 | -0.01413 | 0.11135 | 2.6647 | 0.23331 | Persistence ends | 72.2931 | -0.060564 | Day | 202602 | 2026-02-17 | 0.060564
2026-02-17 08:30 | 72.095 | TRUE | FALSE | -0.73509 | -1.0301 | -0.19815 | -0.27409 | 0.2826 |  |  | none | FALSE | 3 | 71.3599 | TRUE | FALSE | 0.1624 |  | 71.8265 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.23331 | Normal | 72.2931 | 1.1507 | Day | 202602 | 2026-02-17 | 1.1507
2026-02-17 08:30 | 72.095 | FALSE | FALSE | -0.73509 | -1.0301 | -0.19815 | -0.27409 | 0 |  |  | none | FALSE | 3 | 71.3599 | FALSE | FALSE | 0.1624 |  | 71.8265 | 0 | 0 | 0 | 0.12967 | 0 | 0.23331 | Normal | 72.2931 | 1.1507 | Day | 202602 | 2026-02-17 | 1.1507
2026-02-17 08:45 | 72.095 | FALSE | FALSE | -0.73509 | -1.0301 | -0.19815 | -0.27409 | 0 |  |  | none | FALSE | 3 | 71.3599 | FALSE | FALSE | 0.1624 |  | 71.8265 | 0 | 0 | 0 | 0.12967 | 0 | 0.23331 | Normal | 72.2931 | 1.1507 | Day | 202602 | 2026-02-17 | 1.1507
2026-02-17 09:00 | 72.095 | FALSE | FALSE | -0.73509 | -1.0301 | -0.19815 | -0.27409 | 0 |  |  | none | FALSE | 2 | 71.3599 | FALSE | FALSE | 0.1339 |  | 71.8265 | 0 | 0 | 0 | 0.12967 | 0 | 0.23331 | Normal | 72.2931 | 1.1507 | Day | 202602 | 2026-02-17 | 1.1507
2026-02-17 09:15 | 72.095 | FALSE | FALSE | -0.73509 | -1.0301 | -0.19815 | -0.27409 | 0 |  |  | none | FALSE | 2 | 71.3599 | FALSE | FALSE | 0.1339 |  | 71.8265 | 0 | 0 | 0 | 0.12967 | 0 | 0.23331 | Normal | 72.2931 | 1.1507 | Day | 202602 | 2026-02-17 | 1.1507
2026-02-17 09:30 | 72.3758 | FALSE | FALSE | -1.0502 | -1.4725 | 0.020213 | 0.027936 | 0.2808 | 2026-02-17 12:29 | 2026-02-17 09:30 | upper | TRUE | 2 | 71.3256 | FALSE | FALSE | 0.2529 | 2.0785 | 71.8406 | 1 | 0.2808 | 0.01404 | 0.14407 | 1.8516 | 0.25751 | Extreme triggered | 72.3556 | 2.0785 | Day | 202602 | 2026-02-17 | 2.0785
2026-02-17 09:45 | 72.6584 | FALSE | FALSE | -1.4134 | -1.9839 | 0.1659 | 0.22884 | 0.2826 |  | 2026-02-17 09:30 | upper | TRUE | 2 | 71.245 | FALSE | FALSE | 0.3402 | 2.3052 | 71.8687 | 2 | 0.2826 | 0.02817 | 0.15598 | 1.6311 | 0.31188 | Extreme/elevated | 72.4925 | 2.5319 | Day | 202602 | 2026-02-17 | 2.5319
2026-02-17 10:00 | 73.2236 | TRUE | FALSE | -2.1526 | -3.0288 | 0.41602 | 0.5714 | 0.5652 |  | 2026-02-17 09:30 | upper | TRUE | 3 | 71.071 | TRUE | TRUE | 0.4544 | 2.5229 | 71.9393 | 3 | 0.5652 | 0.07056 | 0.18038 | 2.7423 | 0.43414 | Persistent | 72.8076 | 2.9583 | Day | 202602 | 2026-02-17 | 2.9583
2026-02-17 10:15 | 73.2236 | FALSE | FALSE | -2.2514 | -3.1723 | 0.17605 | 0.24101 | 0 |  | 2026-02-17 09:30 | upper | TRUE | 3 | 70.9722 | FALSE | TRUE | 0.4702 | 2.477 | 72.0099 | 4 | 0 | 0.07056 | 0.18038 | -0.39118 | 0.51884 | Persistent | 73.0475 | 2.3393 | Day | 202602 | 2026-02-17 | 2.3393
2026-02-17 10:29 | 72.941 | FALSE | FALSE | -1.9872 | -2.8007 | -0.23782 | -0.32498 | -0.2826 |  | 2026-02-17 09:30 | none | FALSE | 2 | 70.9538 | FALSE | FALSE | 0.4477 | 2.2961 | 72.0663 | 5 | -0.2826 | 0.05643 | 0.19654 | -1.725 | 0.55626 | Persistent | 73.1788 | 1.5725 | Day | 202602 | 2026-02-17 | 1.5725
2026-02-17 10:44 | 73.2236 | FALSE | FALSE | -2.3054 | -3.2508 | -0.13192 | -0.17983 | 0.2826 |  | 2026-02-17 09:30 | none | FALSE | 1 | 70.9182 | FALSE | FALSE | 0.4903 | 2.2107 | 72.1368 | 6 | 0.2826 | 0.07056 | 0.20234 | 1.0479 | 0.60933 | Persistent | 73.3555 | 1.7835 | Day | 202602 | 2026-02-17 | 1.7835
2026-02-17 10:59 | 73.2236 | FALSE | TRUE | -2.3164 | -3.2669 | -0.28406 | -0.38644 | 0 |  | 2026-02-17 09:30 | none | FALSE | 1 | 70.9072 | FALSE | FALSE | 0.5328 | 2.1181 | 72.2074 | 7 | 0 | 0.07056 | 0.20234 | -0.34872 | 0.65013 | Confirmed/Materialized Shift | 73.5077 | 1.5631 | Day | 202602 | 2026-02-17 | 1.5631
2026-02-17 11:14 | 73.5062 | FALSE | TRUE | -2.6222 | -3.6993 | -0.194 | -0.26323 | 0.2826 |  | 2026-02-17 09:30 | none | FALSE | 1 | 70.884 | FALSE | FALSE | 0.5435 | 2.0689 | 72.2921 | 8 | 0.2826 | 0.08469 | 0.20697 | 0.95623 | 0.70405 | Confirmed/Materialized Shift | 73.7002 | 1.7245 | Day | 202602 | 2026-02-17 | 1.7245
2026-02-17 11:29 | 73.5062 | FALSE | TRUE | -2.5746 | -3.6297 | -0.34404 | -0.46586 | 0 |  | 2026-02-17 09:30 | none | FALSE | 1 | 70.9316 | FALSE | FALSE | 0.5305 | 2.0089 | 72.3909 | 9 | 0 | 0.09882 | 0.18948 | -0.52153 | 0.72966 | Confirmed/Materialized Shift | 73.8502 | 1.5285 | Day | 202602 | 2026-02-17 | 1.5285
2026-02-17 11:44 | 73.5062 | FALSE | TRUE | -2.4978 | -3.5176 | -0.46484 | -0.62841 | 0 |  | 2026-02-17 09:30 | none | FALSE | 1 | 71.0084 | FALSE | FALSE | 0.5201 | 1.9452 | 72.4897 | 10 | 0 | 0.09882 | 0.18948 | -0.52153 | 0.74065 | Confirmed/Materialized Shift | 73.971 | 1.3724 | Day | 202602 | 2026-02-17 | 1.3724
2026-02-17 11:59 | 73.7888 | FALSE | TRUE | -2.7033 | -3.8029 | -0.33106 | -0.44666 | 0.2826 |  | 2026-02-17 09:30 | none | FALSE | 1 | 71.0855 | FALSE | FALSE | 0.5328 | 1.9105 | 72.6027 | 11 | 0.2826 | 0.11295 | 0.19224 | 0.88248 | 0.75859 | Confirmed/Materialized Shift | 74.1199 | 1.5636 | Day | 202602 | 2026-02-17 | 1.5636
2026-02-17 12:14 | 73.7888 | FALSE | TRUE | -2.5904 | -3.6382 | -0.44405 | -0.59819 | 0 |  | 2026-02-17 09:30 | none | FALSE | 1 | 71.1984 | FALSE | FALSE | 0.5229 | 1.8692 | 72.7156 | 12 | 0 | 0.11295 | 0.19224 | -0.58754 | 0.75861 | Confirmed/Materialized Shift | 74.2329 | 1.4146 | Day | 202602 | 2026-02-17 | 1.4146
2026-02-17 12:29 | 73.5062 | FALSE | FALSE | -2.1396 | -2.9981 | -0.75614 | -1.0182 | -0.2826 |  |  | none | FALSE | 0 | 71.3666 | FALSE | FALSE | 0.0637 |  | 72.8145 | 0 | -0.2826 | 0.09882 | 0.2105 | -1.812 | 0.72394 | Persistence ends | 74.2623 | 0.95552 | Day | 202602 | 2026-02-17 | 0.95552
2026-02-17 12:44 | 73.7888 | FALSE | FALSE | -2.238 | -3.1278 | -0.51522 | -0.69339 | 0.2826 |  |  | none | FALSE | 0 | 71.5508 | FALSE | FALSE | 0.0834 |  | 72.9274 | 0 | 0.2826 | 0.11295 | 0.21299 | 0.79653 | 0.6883 | Normal | 74.304 | 1.2515 | Day | 202602 | 2026-02-17 | 1.2515
2026-02-17 12:59 | 73.7888 | FALSE | FALSE | -2.0848 | -2.9076 | -0.5597 | -0.75281 | 0 |  |  | none | FALSE | 0 | 71.704 | FALSE | FALSE | 0.0769 |  | 73.0262 | 0 | 0 | 0.09882 | 0.2105 | -0.46945 | 0.66114 | Normal | 74.3485 | 1.1534 | Day | 202602 | 2026-02-17 | 1.1534
2026-02-17 13:14 | 73.2236 | TRUE | FALSE | -1.3902 | -1.9353 | -1.1083 | -1.491 | -0.5652 |  |  | none | FALSE | 1 | 71.8334 | FALSE | FALSE | 0.0436 |  | 73.0827 | 0 | -0.5652 | 0.05643 | 0.25268 | -2.4601 | 0.62463 | Normal | 74.3319 | 0.22564 | Day | 202602 | 2026-02-17 | 0.22564
2026-02-17 13:28 | 72.3758 | TRUE | FALSE | -0.48725 | -0.67779 | -1.9291 | -2.5961 | -0.8478 |  |  | none | FALSE | 2 | 71.8885 | TRUE | FALSE | 0.1367 |  | 73.0967 | 0 | -0.8478 | 0.01404 | 0.32376 | -2.662 | 0.60408 | Normal | 74.3049 | -1.1934 | Day | 202602 | 2026-02-17 | 1.1934
2026-02-17 13:43 | 72.3758 | FALSE | FALSE | -0.42995 | -0.5976 | -1.8998 | -2.5578 | 0 |  |  | none | FALSE | 2 | 71.9459 | FALSE | FALSE | 0.1413 |  | 73.1107 | 0 | 0 | 0.01404 | 0.32376 | -0.043365 | 0.58244 | Normal | 74.2756 | -1.2618 | Day | 202602 | 2026-02-17 | 1.2618
2026-02-17 13:59 | 72.941 | FALSE | FALSE | -0.85487 | -1.1859 | -1.2789 | -1.7232 | 0.5652 |  |  | none | FALSE | 2 | 72.0861 | FALSE | FALSE | 0.0836 |  | 73.153 | 0 | 0.5652 | 0.0423 | 0.34635 | 1.5097 | 0.53345 | Normal | 74.2199 | -0.39749 | Day | 202602 | 2026-02-17 | 0.39749
2026-02-17 14:14 | 73.7888 | FALSE | FALSE | -1.5296 | -2.1168 | -0.42746 | -0.57596 | 0.8478 |  |  | none | FALSE | 2 | 72.2592 | FALSE | FALSE | 0.1322 |  | 73.2377 | 0 | 0.8478 | 0.08469 | 0.39003 | 1.9565 | 0.48926 | Normal | 74.2163 | 1.1263 | Day | 202602 | 2026-02-17 | 1.1263
2026-02-17 14:17 | 74.0714 | FALSE | FALSE | -1.7066 | -2.3583 | -0.2088 | -0.28109 | 0.2826 |  |  | none | FALSE | 2 | 72.3648 | FALSE | FALSE | 0.1614 |  | 73.3225 | 0 | 0.2826 | 0.08478 | 0.39008 | 0.50713 | 0.47884 | Normal | 74.2802 | 1.564 | Day | 202602 | 2026-02-17 | 1.564
2026-02-17 14:20 | 74.0714 | FALSE | FALSE | -1.6381 | -2.2616 | -0.28164 | -0.37878 | 0 |  |  | none | FALSE | 2 | 72.4333 | FALSE | FALSE | 0.1514 |  | 73.3932 | 0 | 0 | 0.07065 | 0.38764 | -0.18225 | 0.47994 | Normal | 74.353 | 1.4132 | Day | 202602 | 2026-02-17 | 1.4132
2026-02-17 14:28 | 73.7888 | FALSE | FALSE | -1.3394 | -1.8488 | -0.60468 | -0.81281 | -0.2826 |  |  | none | FALSE | 2 | 72.4494 | FALSE | FALSE | 0.1075 |  | 73.4214 | 0 | -0.2826 | 0.02826 | 0.37692 | -0.82473 | 0.48603 | Normal | 74.3935 | 0.75588 | Day | 202602 | 2026-02-17 | 0.75588
2026-02-17 14:43 | 73.5062 | FALSE | FALSE | -1.0388 | -1.4335 | -0.89751 | -1.2063 | -0.2826 |  |  | none | FALSE | 2 | 72.4674 | FALSE | FALSE | 0.0669 |  | 73.4356 | 0 | -0.2826 | 0.01413 | 0.38328 | -0.77418 | 0.48408 | Normal | 74.4037 | 0.14595 | Day | 202602 | 2026-02-17 | 0.14595
2026-02-17 14:58 | 72.941 | FALSE | FALSE | -0.47361 | -0.65355 | -1.4627 | -1.9659 | -0.5652 |  |  | none | FALSE | 2 | 72.4674 | FALSE | FALSE | 0.1253 |  | 73.4356 | 0 | -0.5652 | 0 | 0.39966 | -1.4142 | 0.48408 | Normal | 74.4037 | -1.0216 | Day | 202602 | 2026-02-17 | 1.0216
2026-02-17 15:13 | 72.6584 | FALSE | FALSE | -0.27662 | -0.38217 | -1.7744 | -2.3839 | -0.2826 |  |  | none | FALSE | 1 | 72.3818 | FALSE | FALSE | 0.1259 |  | 73.4073 | 0 | -0.2826 | -0.02826 | 0.3986 | -0.63808 | 0.51275 | Normal | 74.4328 | -1.4605 | Day | 202602 | 2026-02-17 | 1.4605
2026-02-17 15:28 | 72.3758 | FALSE | FALSE | -0.13384 | -0.18526 | -2.112 | -2.8354 | -0.2826 |  |  | none | FALSE | 0 | 72.242 | FALSE | FALSE | 0.1174 |  | 73.3649 | 0 | -0.2826 | -0.04239 | 0.40254 | -0.59674 | 0.56147 | Normal | 74.4878 | -1.7616 | Day | 202602 | 2026-02-17 | 1.7616
2026-02-17 15:43 | 72.095 | FALSE | FALSE | -0.055781 | -0.077432 | -2.4545 | -3.2924 | -0.2808 |  |  | none | FALSE | 0 | 72.0392 | FALSE | FALSE | 0.1274 |  | 73.2943 | 0 | -0.2808 | -0.07056 | 0.39829 | -0.52786 | 0.62756 | Normal | 74.5495 | -1.9111 | Day | 202602 | 2026-02-17 | 1.9111
2026-02-17 15:58 | 72.3758 | FALSE | FALSE | -0.45329 | -0.63025 | -2.1773 | -2.9205 | 0.2808 |  |  | none | FALSE | 0 | 71.9225 | FALSE | FALSE | 0.0874 |  | 73.2378 | 0 | 0.2808 | -0.05652 | 0.40579 | 0.83127 | 0.65766 | Normal | 74.5531 | -1.3107 | Day | 202602 | 2026-02-17 | 1.3107
2026-02-17 16:13 | 72.095 | FALSE | FALSE | -0.33091 | -0.46111 | -2.4754 | -3.3196 | -0.2808 |  |  | none | FALSE | 0 | 71.7641 | FALSE | FALSE | 0.1019 |  | 73.1673 | 0 | -0.2808 | -0.07056 | 0.40858 | -0.51457 | 0.70158 | Normal | 74.5704 | -1.5283 | Day | 202602 | 2026-02-17 | 1.5283
2026-02-17 16:28 | 72.6584 | FALSE | FALSE | -0.93641 | -1.3056 | -1.8411 | -2.4713 | 0.5634 |  |  | none | FALSE | 0 | 71.722 | FALSE | FALSE | 0.0434 |  | 73.1107 | 0 | 0.5634 | -0.05652 | 0.42581 | 1.4559 | 0.69437 | Normal | 74.4995 | -0.65144 | Day | 202602 | 2026-02-17 | 0.65144
2026-02-17 16:43 | 72.941 | FALSE | FALSE | -1.2255 | -1.7089 | -1.4802 | -1.989 | 0.2826 |  |  | none | FALSE | 0 | 71.7155 | FALSE | FALSE | 0.0126 |  | 73.0683 | 0 | 0.2826 | -0.04239 | 0.43242 | 0.75155 | 0.67645 | Normal | 74.4212 | -0.18826 | Day | 202602 | 2026-02-17 | 0.18826
2026-02-17 16:58 | 72.941 | FALSE | FALSE | -1.2388 | -1.7277 | -1.437 | -1.932 | 0 |  |  | none | FALSE | 0 | 71.7022 | FALSE | FALSE | 0.0099 |  | 73.0401 | 0 | 0 | -0.02826 | 0.42876 | 0.065911 | 0.66896 | Normal | 74.378 | -0.14813 | Day | 202602 | 2026-02-17 | 0.14813
2026-02-17 17:13 | 73.2236 | FALSE | FALSE | -1.5063 | -2.1003 | -1.0827 | -1.4571 | 0.2826 |  |  | none | FALSE | 0 | 71.7173 | FALSE | FALSE | 0.0218 |  | 73.0118 | 0 | 0.2826 | -0.02826 | 0.42876 | 0.72502 | 0.64725 | Normal | 74.3063 | 0.32718 | Day | 202602 | 2026-02-17 | 0.32718
2026-02-17 17:27 | 72.941 | FALSE | FALSE | -1.2134 | -1.6917 | -1.2703 | -1.7117 | -0.2826 |  |  | none | FALSE | 0 | 71.7276 | FALSE | FALSE | 0.0031 |  | 72.9694 | 0 | -0.2826 | -0.04239 | 0.43242 | -0.5555 | 0.62091 | Normal | 74.2113 | -0.045804 | Day | 202602 | 2026-02-17 | 0.045804
2026-02-17 17:42 | 72.941 | FALSE | FALSE | -1.2218 | -1.7035 | -1.2504 | -1.6853 | 0 |  |  | none | FALSE | 0 | 71.7192 | FALSE | FALSE | 0.0015 |  | 72.9553 | 0 | 0 | -0.01413 | 0.41456 | 0.034085 | 0.61803 | Normal | 74.1914 | -0.023154 | Day | 202602 | 2026-02-17 | 0.023154
2026-02-17 17:57 | 72.941 | FALSE | FALSE | -1.1632 | -1.6205 | -1.2483 | -1.6826 | 0 |  |  | none | FALSE | 0 | 71.7778 | FALSE | FALSE | 0.0047 |  | 72.9836 | 0 | 0 | 0.02826 | 0.36524 | -0.077374 | 0.60288 | Normal | 74.1893 | -0.070612 | Day | 202602 | 2026-02-17 | 0.070612
2026-02-17 18:12 | 72.6584 | FALSE | FALSE | -0.84285 | -1.1736 | -1.5215 | -2.051 | -0.2826 |  |  | none | FALSE | 0 | 71.8155 | FALSE | FALSE | 0.0383 |  | 72.9977 | 0 | -0.2826 | 0.01413 | 0.3718 | -0.7981 | 0.59108 | Normal | 74.1799 | -0.57404 | Day | 202602 | 2026-02-17 | 0.57404
2026-02-17 18:27 | 72.6584 | FALSE | FALSE | -0.86656 | -1.207 | -1.5169 | -2.045 | 0 |  |  | none | FALSE | 0 | 71.7918 | FALSE | FALSE | 0.0364 |  | 72.9836 | 0 | 0 | -0.01413 | 0.34845 | 0.040551 | 0.59586 | Normal | 74.1753 | -0.54571 | Night | 202602 | 2026-02-17 | 0.54571
2026-02-17 18:42 | 72.6584 | FALSE | FALSE | -0.86824 | -1.2094 | -1.4055 | -1.8977 | 0 |  |  | none | FALSE | 0 | 71.7902 | FALSE | FALSE | 0.0315 |  | 72.927 | 0 | 0 | -0.05652 | 0.28361 | 0.19929 | 0.56844 | Normal | 74.0639 | -0.47261 | Night | 202602 | 2026-02-17 | 0.47261
2026-02-17 18:42 | 72.6584 | FALSE | FALSE | -0.80748 | -1.1238 | -1.2035 | -1.6294 | 0 |  |  | none | FALSE | 0 | 71.8509 | FALSE | FALSE | 0.0263 |  | 72.8564 | 0 | 0 | -0.07065 | 0.27266 | 0.25912 | 0.50274 | Normal | 73.8619 | -0.39384 | Night | 202602 | 2026-02-17 | 0.39384
2026-02-17 18:43 | 72.6584 | FALSE | FALSE | -0.70178 | -0.97528 | -0.95648 | -1.2993 | 0 |  |  | none | FALSE | 0 | 71.9566 | FALSE | FALSE | 0.0205 |  | 72.7857 | 0 | 0 | -0.07065 | 0.27266 | 0.25912 | 0.41456 | Normal | 73.6149 | -0.30719 | Night | 202602 | 2026-02-17 | 0.30719
2026-02-17 18:58 | 73.2236 | FALSE | FALSE | -1.1821 | -1.6409 | -0.24988 | -0.34009 | 0.5652 |  |  | none | FALSE | 0 | 72.0415 | FALSE | FALSE | 0.0868 |  | 72.7575 | 0 | 0.5652 | -0.02826 | 0.30227 | 1.9634 | 0.35799 | Normal | 73.4735 | 1.302 | Night | 202602 | 2026-02-17 | 1.302
2026-02-17 19:13 | 73.2236 | FALSE | FALSE | -1.1432 | -1.586 | -0.18272 | -0.24892 | 0 |  |  | none | FALSE | 0 | 72.0804 | FALSE | FALSE | 0.0966 |  | 72.7434 | 0 | 0 | -0.01413 | 0.2963 | 0.047689 | 0.33148 | Normal | 73.4063 | 1.4488 | Night | 202602 | 2026-02-17 | 1.4488
2026-02-17 19:28 | 73.5062 | FALSE | FALSE | -1.4765 | -2.0499 | -0.0073408 | -0.0099857 | 0.2826 |  |  | none | FALSE | 0 | 72.0297 | FALSE | FALSE | 0.132 |  | 72.7716 | 0 | 0.2826 | 0.02826 | 0.27304 | 0.93151 | 0.37096 | Normal | 73.5135 | 1.9802 | Night | 202602 | 2026-02-17 | 1.9802
2026-02-17 19:42 | 73.5062 | FALSE | FALSE | -1.5008 | -2.0842 | -0.11638 | -0.15807 | 0 |  |  | none | FALSE | 0 | 72.0054 | FALSE | FALSE | 0.1141 |  | 72.814 | 0 | 0 | 0.04239 | 0.26324 | -0.16103 | 0.40428 | Normal | 73.6226 | 1.7121 | Night | 202602 | 2026-02-17 | 1.7121
2026-02-17 19:57 | 73.5062 | FALSE | FALSE | -1.4728 | -2.0446 | -0.20145 | -0.27331 | 0 |  |  | none | FALSE | 0 | 72.0334 | FALSE | FALSE | 0.1012 |  | 72.8705 | 0 | 0 | 0.05652 | 0.25224 | -0.22408 | 0.41856 | Normal | 73.7077 | 1.5187 | Night | 202602 | 2026-02-17 | 1.5187
2026-02-17 20:12 | 73.2236 | FALSE | FALSE | -1.0628 | -1.4728 | -0.46951 | -0.63712 | -0.2826 |  |  | none | FALSE | 0 | 72.1608 | FALSE | FALSE | 0.0516 |  | 72.927 | 0 | -0.2826 | 0.05643 | 0.25236 | -1.3434 | 0.38308 | Normal | 73.6931 | 0.77436 | Night | 202602 | 2026-02-17 | 0.77436
2026-02-17 20:27 | 73.2236 | FALSE | FALSE | -0.985 | -1.3635 | -0.4765 | -0.64654 | 0 |  |  | none | FALSE | 0 | 72.2386 | FALSE | FALSE | 0.0464 |  | 72.9694 | 0 | 0 | 0.04239 | 0.24698 | -0.17164 | 0.36538 | Normal | 73.7001 | 0.69586 | Night | 202602 | 2026-02-17 | 0.69586
2026-02-17 20:41 | 73.2236 | FALSE | FALSE | -0.80876 | -1.1168 | -0.41312 | -0.56103 | 0 |  |  | none | FALSE | 0 | 72.4148 | FALSE | FALSE | 0.0432 |  | 73.0258 | 0 | 0 | 0.05643 | 0.23535 | -0.23978 | 0.30547 | Normal | 73.6367 | 0.64759 | Night | 202602 | 2026-02-17 | 0.64759
2026-02-17 20:56 | 73.2236 | FALSE | FALSE | -0.76093 | -1.0501 | -0.42181 | -0.57275 | 0 |  |  | none | FALSE | 0 | 72.4627 | FALSE | FALSE | 0.0382 |  | 73.054 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.29568 | Normal | 73.6454 | 0.57345 | Night | 202602 | 2026-02-17 | 0.57345
2026-02-17 21:11 | 73.2236 | FALSE | FALSE | -0.74893 | -1.0334 | -0.43807 | -0.5947 | 0 |  |  | none | FALSE | 0 | 72.4747 | FALSE | FALSE | 0.0349 |  | 73.0682 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.29675 | Normal | 73.6617 | 0.52378 | Night | 202602 | 2026-02-17 | 0.52378
2026-02-17 21:26 | 73.2236 | FALSE | FALSE | -0.7355 | -1.0147 | -0.4529 | -0.61472 | 0 |  |  | none | FALSE | 0 | 72.4881 | FALSE | FALSE | 0.0317 |  | 73.0823 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.2971 | Normal | 73.6765 | 0.47559 | Night | 202602 | 2026-02-17 | 0.47559
2026-02-17 21:41 | 73.2236 | FALSE | FALSE | -0.7355 | -1.0147 | -0.4529 | -0.61472 | 0 |  |  | none | FALSE | 0 | 72.4881 | FALSE | FALSE | 0.0317 |  | 73.0823 | 0 | 0 | 0 | 0.18338 | 0 | 0.2971 | Normal | 73.6765 | 0.47559 | Night | 202602 | 2026-02-17 | 0.47559
2026-02-17 21:56 | 73.2236 | FALSE | FALSE | -0.72067 | -0.99398 | -0.46633 | -0.63282 | 0 |  |  | none | FALSE | 0 | 72.5029 | FALSE | FALSE | 0.0286 |  | 73.0964 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.29675 | Normal | 73.6899 | 0.42855 | Night | 202602 | 2026-02-17 | 0.42855
2026-02-17 22:11 | 73.2236 | FALSE | FALSE | -0.70441 | -0.97134 | -0.47833 | -0.649 | 0 |  |  | none | FALSE | 0 | 72.5192 | FALSE | FALSE | 0.0255 |  | 73.1106 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.29568 | Normal | 73.7019 | 0.3823 | Night | 202602 | 2026-02-17 | 0.3823
2026-02-17 22:26 | 73.2236 | FALSE | FALSE | -0.68671 | -0.94671 | -0.48889 | -0.66324 | 0 |  |  | none | FALSE | 0 | 72.5369 | FALSE | FALSE | 0.0224 |  | 73.1247 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.2939 | Normal | 73.7125 | 0.33654 | Night | 202602 | 2026-02-17 | 0.33654
2026-02-17 22:41 | 73.2236 | FALSE | FALSE | -0.61694 | -0.8497 | -0.47564 | -0.64538 | 0 |  |  | none | FALSE | 0 | 72.6067 | FALSE | FALSE | 0.0172 |  | 73.153 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.27315 | Normal | 73.6992 | 0.25865 | Night | 202602 | 2026-02-17 | 0.25865
2026-02-17 22:56 | 72.941 | FALSE | FALSE | -0.27945 | -0.38459 | -0.73161 | -0.99306 | -0.2826 |  |  | none | FALSE | 0 | 72.6615 | FALSE | FALSE | 0.0596 |  | 73.1671 | 0 | -0.2826 | 0.01413 | 0.17092 | -1.7361 | 0.25277 | Normal | 73.6726 | -0.89443 | Night | 202602 | 2026-02-17 | 0.89443
2026-02-17 23:11 | 72.941 | FALSE | FALSE | -0.21914 | -0.30135 | -0.69956 | -0.94997 | 0 |  |  | none | FALSE | 0 | 72.7219 | FALSE | FALSE | 0.0697 |  | 73.1812 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.22968 | Normal | 73.6406 | -1.0459 | Night | 202602 | 2026-02-17 | 1.0459
2026-02-17 23:26 | 72.941 | FALSE | FALSE | -0.15158 | -0.20824 | -0.66026 | -0.89707 | 0 |  |  | none | FALSE | 0 | 72.7894 | FALSE | FALSE | 0.0835 |  | 73.1953 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.20296 | Normal | 73.6013 | -1.2532 | Night | 202602 | 2026-02-17 | 1.2532
2026-02-17 23:40 | 72.941 | FALSE | FALSE | -0.073366 | -0.10068 | -0.61031 | -0.82977 | 0 |  |  | none | FALSE | 0 | 72.8676 | FALSE | FALSE | 0.1047 |  | 73.2095 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.17092 | Normal | 73.5513 | -1.5708 | Night | 202602 | 2026-02-17 | 1.5708
2026-02-17 23:55 | 72.941 | FALSE | FALSE | -0.1078 | -0.14801 | -0.61648 | -0.83809 | 0 |  |  | none | FALSE | 0 | 72.8332 | FALSE | FALSE | 0.0936 |  | 73.1953 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.18107 | Normal | 73.5575 | -1.4047 | Night | 202602 | 2026-02-17 | 1.4047
2026-02-18 00:10 | 72.941 | FALSE | FALSE | -0.13894 | -0.19084 | -0.61936 | -0.84197 | 0 |  |  | none | FALSE | 0 | 72.8021 | FALSE | FALSE | 0.0845 |  | 73.1812 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.18957 | Normal | 73.5604 | -1.2671 | Night | 202602 | 2026-02-18 | 1.2671
2026-02-18 00:26 | 72.941 | FALSE | FALSE | -0.14902 | -0.20473 | -0.57292 | -0.77934 | 0 |  |  | none | FALSE | 0 | 72.792 | FALSE | FALSE | 0.0783 |  | 73.153 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.18049 | Normal | 73.5139 | -1.1743 | Night | 202602 | 2026-02-18 | 1.1743
2026-02-18 00:40 | 72.6584 | TRUE | FALSE | 0.067509 | 0.092827 | -0.83681 | -1.1386 | -0.2826 | 2026-02-18 08:00 | 2026-02-18 00:40 | lower | TRUE | 1 | 72.7259 | FALSE | FALSE | 0.2424 | 2.351 | 73.1106 | 1 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.19233 | Extreme triggered | 73.4952 | -2.351 | Night | 202602 | 2026-02-18 | 2.351
2026-02-18 00:55 | 72.6584 | FALSE | FALSE | 0.021855 | 0.03007 | -0.79769 | -1.0859 | 0 |  | 2026-02-18 00:40 | lower | TRUE | 1 | 72.6803 | FALSE | FALSE | 0.2837 | 2.2318 | 73.0682 | 2 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.19396 | Extreme/elevated | 73.4561 | -2.1127 | Night | 202602 | 2026-02-18 | 2.1127
2026-02-18 01:10 | 72.6584 | FALSE | FALSE | -0.039654 | -0.054606 | -0.80267 | -1.0927 | 0 |  | 2026-02-18 00:40 | none | FALSE | 1 | 72.6187 | FALSE | FALSE | 0.3208 | 2.0918 | 73.0399 | 3 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21058 | Persistent | 73.4611 | -1.8117 | Night | 202602 | 2026-02-18 | 1.8117
2026-02-18 01:25 | 72.6584 | FALSE | FALSE | -0.091222 | -0.12571 | -0.79772 | -1.086 | 0 |  | 2026-02-18 00:40 | none | FALSE | 1 | 72.5672 | FALSE | FALSE | 0.3631 | 1.9662 | 73.0117 | 4 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22224 | Persistent | 73.4561 | -1.5895 | Night | 202602 | 2026-02-18 | 1.5895
2026-02-18 01:40 | 72.6584 | FALSE | FALSE | -0.13436 | -0.18527 | -0.78434 | -1.068 | 0 |  | 2026-02-18 00:40 | none | FALSE | 1 | 72.524 | FALSE | FALSE | 0.4086 | 1.856 | 72.9834 | 5 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.22968 | Persistent | 73.4427 | -1.415 | Night | 202602 | 2026-02-18 | 1.415
2026-02-18 01:55 | 72.6584 | FALSE | FALSE | -0.16989 | -0.23436 | -0.76335 | -1.0397 | 0 |  | 2026-02-18 00:40 | none | FALSE | 1 | 72.4885 | FALSE | FALSE | 0.4562 | 1.7586 | 72.9551 | 6 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.23331 | Persistent | 73.4217 | -1.2718 | Night | 202602 | 2026-02-18 | 1.2718
2026-02-18 02:10 | 72.3758 | TRUE | TRUE | 0.021529 | 0.029737 | -1.0524 | -1.4332 | -0.2826 |  | 2026-02-18 00:40 | lower | TRUE | 2 | 72.3973 | TRUE | TRUE | 0.596 | 1.805 | 72.9127 | 7 | -0.2826 | -0.04239 | 0.10353 | -2.3202 | 0.25771 | Confirmed/Materialized Shift | 73.4282 | -2.0835 | Night | 202602 | 2026-02-18 | 2.0835
2026-02-18 02:25 | 72.3758 | FALSE | TRUE | -0.051742 | -0.071541 | -1.0408 | -1.4177 | 0 |  | 2026-02-18 00:40 | none | FALSE | 2 | 72.3241 | FALSE | FALSE | 0.5778 | 1.8057 | 72.8704 | 8 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27315 | Confirmed/Materialized Shift | 73.4166 | -1.8106 | Night | 202602 | 2026-02-18 | 1.8106
2026-02-18 02:39 | 72.3758 | FALSE | TRUE | -0.11006 | -0.1523 | -1.0144 | -1.3822 | 0 |  | 2026-02-18 00:40 | none | FALSE | 2 | 72.2657 | FALSE | FALSE | 0.5644 | 1.7838 | 72.828 | 9 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.28111 | Confirmed/Materialized Shift | 73.3902 | -1.6085 | Night | 202602 | 2026-02-18 | 1.6085
2026-02-18 02:55 | 72.3758 | FALSE | TRUE | -0.15469 | -0.21418 | -0.97423 | -1.3282 | 0 |  | 2026-02-18 00:40 | none | FALSE | 2 | 72.2211 | FALSE | FALSE | 0.5539 | 1.7506 | 72.7856 | 10 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.28223 | Confirmed/Materialized Shift | 73.35 | -1.4519 | Night | 202602 | 2026-02-18 | 1.4519
2026-02-18 03:10 | 72.3758 | FALSE | TRUE | -0.18579 | -0.25737 | -0.92055 | -1.2559 | 0 |  | 2026-02-18 00:40 | none | FALSE | 1 | 72.19 | FALSE | FALSE | 0.5171 | 1.7122 | 72.7432 | 11 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27659 | Confirmed/Materialized Shift | 73.2964 | -1.3283 | Night | 202602 | 2026-02-18 | 1.3283
2026-02-18 03:25 | 72.095 | FALSE | TRUE | 0.015163 | 0.021028 | -1.1683 | -1.5947 | -0.2808 |  | 2026-02-18 00:40 | lower | TRUE | 1 | 72.1102 | FALSE | TRUE | 0.5654 | 1.7406 | 72.6868 | 12 | -0.2808 | -0.05643 | 0.11579 | -1.9377 | 0.28829 | Confirmed/Materialized Shift | 73.2633 | -2.0526 | Night | 202602 | 2026-02-18 | 2.0526
2026-02-18 03:39 | 72.3758 | TRUE | TRUE | -0.26489 | -0.36733 | -0.80201 | -1.096 | 0.2808 |  | 2026-02-18 00:40 | none | FALSE | 2 | 72.1109 | TRUE | FALSE | 0.5243 | 1.6842 | 72.6444 | 13 | 0.2808 | -0.04239 | 0.13791 | 2.3435 | 0.26672 | Confirmed/Materialized Shift | 73.1778 | -1.0069 | Night | 202602 | 2026-02-18 | 1.0069
2026-02-18 03:54 | 72.095 | FALSE | TRUE | -0.060429 | -0.083889 | -1.0745 | -1.4686 | -0.2808 |  | 2026-02-18 00:40 | none | FALSE | 2 | 72.0346 | FALSE | FALSE | 0.5763 | 1.6915 | 72.6021 | 14 | -0.2808 | -0.0423 | 0.13774 | -1.7315 | 0.28374 | Confirmed/Materialized Shift | 73.1695 | -1.787 | Night | 202602 | 2026-02-18 | 1.787
2026-02-18 04:09 | 72.095 | FALSE | TRUE | -0.12214 | -0.1697 | -1.0517 | -1.4377 | 0 |  | 2026-02-18 00:40 | none | FALSE | 2 | 71.9729 | FALSE | FALSE | 0.5627 | 1.6843 | 72.5598 | 15 | 0 | -0.0423 | 0.13774 | 0.3071 | 0.29345 | Confirmed/Materialized Shift | 73.1467 | -1.5838 | Night | 202602 | 2026-02-18 | 1.5838
2026-02-18 04:24 | 72.095 | FALSE | TRUE | -0.17066 | -0.23728 | -1.0156 | -1.3891 | 0 |  | 2026-02-18 00:40 | none | FALSE | 2 | 71.9243 | FALSE | FALSE | 0.5521 | 1.6681 | 72.5175 | 16 | 0 | -0.0423 | 0.13774 | 0.3071 | 0.29656 | Confirmed/Materialized Shift | 73.1106 | -1.4245 | Night | 202602 | 2026-02-18 | 1.4245
2026-02-18 04:39 | 72.095 | FALSE | TRUE | -0.20641 | -0.28713 | -0.96673 | -1.3232 | 0 |  | 2026-02-18 00:40 | none | FALSE | 1 | 71.8886 | FALSE | FALSE | 0.515 | 1.6462 | 72.4752 | 17 | 0 | -0.0423 | 0.13774 | 0.3071 | 0.29329 | Confirmed/Materialized Shift | 73.0617 | -1.2962 | Night | 202602 | 2026-02-18 | 1.2962
2026-02-18 04:54 | 72.095 | FALSE | TRUE | -0.22895 | -0.31858 | -0.90467 | -1.2393 | 0 |  | 2026-02-18 00:40 | none | FALSE | 1 | 71.866 | FALSE | FALSE | 0.508 | 1.621 | 72.4329 | 18 | 0 | -0.0423 | 0.13774 | 0.3071 | 0.28341 | Confirmed/Materialized Shift | 72.9997 | -1.1921 | Night | 202602 | 2026-02-18 | 1.1921
2026-02-18 05:09 | 72.095 | FALSE | TRUE | -0.23681 | -0.32955 | -0.82793 | -1.1353 | 0 |  | 2026-02-18 00:40 | none | FALSE | 1 | 71.8582 | FALSE | FALSE | 0.5026 | 1.5941 | 72.3906 | 19 | 0 | -0.0423 | 0.13774 | 0.3071 | 0.26618 | Confirmed/Materialized Shift | 72.9229 | -1.1104 | Night | 202602 | 2026-02-18 | 1.1104
2026-02-18 05:24 | 72.095 | FALSE | TRUE | -0.22683 | -0.31562 | -0.73335 | -1.007 | 0 |  | 2026-02-18 00:40 | none | FALSE | 1 | 71.8682 | FALSE | FALSE | 0.4989 | 1.5672 | 72.3483 | 20 | 0 | -0.0423 | 0.13774 | 0.3071 | 0.24004 | Confirmed/Materialized Shift | 72.8283 | -1.0551 | Night | 202602 | 2026-02-18 | 1.0551
2026-02-18 05:39 | 71.8124 | FALSE | TRUE | -0.019423 | -0.027054 | -1.0065 | -1.3823 | -0.2826 |  | 2026-02-18 00:40 | none | FALSE | 1 | 71.793 | FALSE | FALSE | 0.5569 | 1.5842 | 72.306 | 21 | -0.2826 | -0.0423 | 0.13774 | -1.7446 | 0.25649 | Confirmed/Materialized Shift | 72.8189 | -1.9243 | Night | 202602 | 2026-02-18 | 1.9243
2026-02-18 05:54 | 71.8124 | FALSE | TRUE | -0.0786 | -0.10957 | -0.98112 | -1.3478 | 0 |  | 2026-02-18 00:40 | none | FALSE | 1 | 71.7338 | FALSE | FALSE | 0.5421 | 1.5896 | 72.2637 | 22 | 0 | -0.0423 | 0.13774 | 0.3071 | 0.26493 | Confirmed/Materialized Shift | 72.7935 | -1.7033 | Night | 202602 | 2026-02-18 | 1.7033
2026-02-18 06:09 | 71.8124 | FALSE | TRUE | -0.12328 | -0.17197 | -0.9412 | -1.2937 | 0 |  | 2026-02-18 00:40 | none | FALSE | 0 | 71.6891 | FALSE | FALSE | 0.5024 | 1.5873 | 72.2214 | 23 | 0 | -0.0423 | 0.13774 | 0.3071 | 0.26612 | Confirmed/Materialized Shift | 72.7536 | -1.5367 | Night | 202602 | 2026-02-18 | 1.5367
2026-02-18 06:24 | 71.8124 | FALSE | TRUE | -0.15368 | -0.21446 | -0.887 | -1.2201 | 0 |  | 2026-02-18 00:40 | none | FALSE | 0 | 71.6587 | FALSE | FALSE | 0.494 | 1.5799 | 72.1791 | 24 | 0 | -0.0423 | 0.13774 | 0.3071 | 0.26017 | Confirmed/Materialized Shift | 72.6994 | -1.4093 | Night | 202602 | 2026-02-18 | 1.4093
2026-02-18 06:38 | 71.5298 | FALSE | TRUE | 0.047198 | 0.06594 | -1.1385 | -1.5667 | -0.2826 |  | 2026-02-18 00:40 | lower | TRUE | 0 | 71.577 | FALSE | TRUE | 0.5449 | 1.6036 | 72.1226 | 25 | -0.2826 | -0.05643 | 0.14734 | -1.5351 | 0.27282 | Confirmed/Materialized Shift | 72.6683 | -2.173 | Night | 202602 | 2026-02-18 | 2.173
2026-02-18 06:53 | 71.5298 | FALSE | TRUE | -0.0093696 | -0.013101 | -1.0822 | -1.4903 | 0 |  | 2026-02-18 00:40 | none | FALSE | 0 | 71.5204 | FALSE | FALSE | 0.531 | 1.6175 | 72.0662 | 26 | 0 | -0.05643 | 0.14734 | 0.383 | 0.27288 | Confirmed/Materialized Shift | 72.612 | -1.9657 | Night | 202602 | 2026-02-18 | 1.9657
2026-02-18 07:08 | 71.5298 | FALSE | TRUE | -0.080987 | -0.11335 | -1.0692 | -1.4727 | 0 |  | 2026-02-18 00:40 | none | FALSE | 0 | 71.4488 | FALSE | FALSE | 0.5146 | 1.6213 | 72.0239 | 27 | 0 | -0.0423 | 0.13774 | 0.3071 | 0.28754 | Confirmed/Materialized Shift | 72.599 | -1.7183 | Day | 202602 | 2026-02-18 | 1.7183
2026-02-18 07:23 | 71.5298 | FALSE | TRUE | -0.13855 | -0.19408 | -1.0422 | -1.436 | 0 |  | 2026-02-18 00:40 | none | FALSE | 0 | 71.3912 | FALSE | FALSE | 0.502 | 1.618 | 71.9816 | 28 | 0 | -0.0423 | 0.13774 | 0.3071 | 0.29518 | Confirmed/Materialized Shift | 72.572 | -1.5306 | Day | 202602 | 2026-02-18 | 1.5306
2026-02-18 07:30 | 71.5298 | FALSE | TRUE | -0.18316 | -0.25671 | -1.0022 | -1.3817 | 0 |  | 2026-02-18 00:40 | none | FALSE | 0 | 71.3466 | FALSE | FALSE | 0.4921 | 1.6099 | 71.9393 | 29 | 0 | -0.0423 | 0.13774 | 0.3071 | 0.29633 | Confirmed/Materialized Shift | 72.532 | -1.3819 | Day | 202602 | 2026-02-18 | 1.3819
2026-02-18 07:45 | 71.5298 | FALSE | TRUE | -0.21495 | -0.30141 | -0.94935 | -1.3098 | 0 |  | 2026-02-18 00:40 | none | FALSE | 0 | 71.3148 | FALSE | FALSE | 0.4841 | 1.5983 | 71.897 | 30 | 0 | -0.0423 | 0.13774 | 0.3071 | 0.29108 | Confirmed/Materialized Shift | 72.4792 | -1.2615 | Day | 202602 | 2026-02-18 | 1.2615
2026-02-18 08:00 | 71.8124 | FALSE | FALSE | -0.48097 | -0.67428 | -0.59383 | -0.82014 | 0.2826 |  |  | none | FALSE | 0 | 71.3314 | FALSE | FALSE | 0.014 |  | 71.8688 | 0 | 0.2826 | -0.02817 | 0.15564 | 1.9967 | 0.2687 | Persistence ends | 72.4062 | -0.21001 | Day | 202602 | 2026-02-18 | 0.21001
2026-02-18 08:16 | 72.095 | FALSE | FALSE | -0.76357 | -1.0705 | -0.31123 | -0.42984 | 0.2826 |  |  | none | FALSE | 0 | 71.3314 | FALSE | FALSE | 0.0561 |  | 71.8688 | 0 | 0.2826 | 0 | 0.15847 | 1.7833 | 0.2687 | Normal | 72.4062 | 0.84171 | Day | 202602 | 2026-02-18 | 0.84171
2026-02-18 08:30 | 72.095 | FALSE | FALSE | -0.73481 | -1.0297 | -0.25439 | -0.35162 | 0 |  |  | none | FALSE | 0 | 71.3602 | FALSE | FALSE | 0.0648 |  | 71.8548 | 0 | 0 | -0.01404 | 0.14407 | 0.097454 | 0.2473 | Normal | 72.3494 | 0.97132 | Day | 202602 | 2026-02-18 | 0.97132
2026-02-18 08:45 | 72.3758 | FALSE | FALSE | -1.0444 | -1.4641 | -0.030433 | -0.042031 | 0.2808 |  |  | none | FALSE | 0 | 71.3314 | FALSE | FALSE | 0.1258 |  | 71.8688 | 0 | 0.2808 | 0.01404 | 0.14407 | 1.8516 | 0.2687 | Normal | 72.4062 | 1.8867 | Day | 202602 | 2026-02-18 | 1.8867
2026-02-18 08:45 | 72.3758 | FALSE | FALSE | -1.0685 | -1.4985 | -0.082668 | -0.11409 | 0 |  |  | none | FALSE | 0 | 71.3073 | FALSE | FALSE | 0.1142 |  | 71.8829 | 0 | 0 | 0.01404 | 0.14407 | -0.097454 | 0.2878 | Normal | 72.4585 | 1.7128 | Day | 202602 | 2026-02-18 | 1.7128
2026-02-18 09:00 | 72.6584 | FALSE | FALSE | -1.4145 | -1.9855 | 0.080188 | 0.11049 | 0.2826 | 2026-02-18 13:14 | 2026-02-18 09:00 | upper | TRUE | 0 | 71.2439 | FALSE | FALSE | 0.2065 | 2.2404 | 71.911 | 1 | 0.2826 | 0.02817 | 0.15598 | 1.6311 | 0.33359 | Extreme triggered | 72.5782 | 2.2404 | Day | 202602 | 2026-02-18 | 2.2404
2026-02-18 09:15 | 72.941 | FALSE | FALSE | -1.7962 | -2.5248 | 0.17909 | 0.24613 | 0.2826 |  | 2026-02-18 09:00 | upper | TRUE | 0 | 71.1448 | FALSE | FALSE | 0.2772 | 2.3417 | 71.9533 | 2 | 0.2826 | 0.0423 | 0.16579 | 1.4494 | 0.40429 | Extreme/elevated | 72.7619 | 2.443 | Day | 202602 | 2026-02-18 | 2.443
2026-02-18 09:30 | 72.941 | FALSE | FALSE | -1.8659 | -2.6253 | 0.02482 | 0.034039 | 0 |  | 2026-02-18 09:00 | upper | TRUE | 0 | 71.0751 | FALSE | TRUE | 0.3084 | 2.2458 | 71.9956 | 3 | 0 | 0.0423 | 0.16579 | -0.25514 | 0.46027 | Persistent | 72.9162 | 2.0539 | Day | 202602 | 2026-02-18 | 2.0539
2026-02-18 09:44 | 72.941 | FALSE | FALSE | -1.9159 | -2.6976 | -0.10982 | -0.15034 | 0 |  | 2026-02-18 09:00 | none | FALSE | 0 | 71.0251 | FALSE | FALSE | 0.3474 | 2.1301 | 72.0379 | 4 | 0 | 0.0423 | 0.16579 | -0.25514 | 0.50644 | Persistent | 73.0508 | 1.7831 | Day | 202602 | 2026-02-18 | 1.7831
2026-02-18 09:59 | 72.941 | FALSE | FALSE | -1.9514 | -2.7488 | -0.22984 | -0.31411 | 0 |  | 2026-02-18 09:00 | none | FALSE | 0 | 70.9896 | FALSE | FALSE | 0.3909 | 2.0198 | 72.0802 | 5 | 0 | 0.0423 | 0.16579 | -0.25514 | 0.5453 | Persistent | 73.1708 | 1.5785 | Day | 202602 | 2026-02-18 | 1.5785
2026-02-18 10:15 | 73.2236 | FALSE | FALSE | -2.268 | -3.1964 | -0.12242 | -0.16691 | 0.2826 |  | 2026-02-18 09:00 | none | FALSE | 0 | 70.9556 | FALSE | FALSE | 0.4625 | 1.9823 | 72.1508 | 6 | 0.2826 | 0.07056 | 0.15534 | 1.365 | 0.59761 | Persistent | 73.346 | 1.7952 | Day | 202602 | 2026-02-18 | 1.7952
2026-02-18 10:30 | 73.2236 | FALSE | TRUE | -2.2773 | -3.2099 | -0.27282 | -0.3712 | 0 |  | 2026-02-18 09:00 | none | FALSE | 0 | 70.9463 | FALSE | FALSE | 0.5048 | 1.9237 | 72.2214 | 7 | 0 | 0.07056 | 0.15534 | -0.45424 | 0.63753 | Confirmed/Materialized Shift | 73.4964 | 1.5721 | Day | 202602 | 2026-02-18 | 1.5721
2026-02-18 10:44 | 73.2236 | FALSE | TRUE | -2.2662 | -3.1938 | -0.40289 | -0.5472 | 0 |  | 2026-02-18 09:00 | none | FALSE | 0 | 70.9574 | FALSE | FALSE | 0.4931 | 1.8578 | 72.2919 | 8 | 0 | 0.07056 | 0.15534 | -0.45424 | 0.66728 | Confirmed/Materialized Shift | 73.6265 | 1.3962 | Day | 202602 | 2026-02-18 | 1.3962
2026-02-18 10:59 | 73.2236 | FALSE | TRUE | -2.2375 | -3.152 | -0.51527 | -0.69877 | 0 |  | 2026-02-18 09:00 | none | FALSE | 0 | 70.9861 | FALSE | FALSE | 0.4834 | 1.7904 | 72.3625 | 9 | 0 | 0.07056 | 0.15534 | -0.45424 | 0.68819 | Confirmed/Materialized Shift | 73.7389 | 1.2513 | Day | 202602 | 2026-02-18 | 1.2513
2026-02-18 11:14 | 73.2236 | FALSE | TRUE | -2.1455 | -3.0185 | -0.59265 | -0.80287 | 0 |  | 2026-02-18 09:00 | none | FALSE | 0 | 71.0781 | FALSE | FALSE | 0.4756 | 1.7248 | 72.4472 | 10 | 0 | 0.08469 | 0.13273 | -0.63807 | 0.68454 | Confirmed/Materialized Shift | 73.8163 | 1.1342 | Day | 202602 | 2026-02-18 | 1.1342
2026-02-18 11:29 | 73.5062 | FALSE | TRUE | -2.3358 | -3.282 | -0.41537 | -0.5619 | 0.2826 |  | 2026-02-18 09:00 | none | FALSE | 0 | 71.1704 | FALSE | FALSE | 0.4931 | 1.6949 | 72.546 | 11 | 0.2826 | 0.09882 | 0.13817 | 1.3301 | 0.68779 | Confirmed/Materialized Shift | 73.9216 | 1.3961 | Day | 202602 | 2026-02-18 | 1.3961
2026-02-18 11:44 | 73.5062 | FALSE | TRUE | -2.2134 | -3.1046 | -0.49057 | -0.66296 | 0 |  | 2026-02-18 09:00 | none | FALSE | 0 | 71.2928 | FALSE | FALSE | 0.485 | 1.6599 | 72.6448 | 12 | 0 | 0.09882 | 0.13817 | -0.71522 | 0.67598 | Confirmed/Materialized Shift | 73.9968 | 1.2743 | Day | 202602 | 2026-02-18 | 1.2743
2026-02-18 11:59 | 73.5062 | FALSE | TRUE | -2.0592 | -2.8821 | -0.53402 | -0.72126 | 0 |  | 2026-02-18 09:00 | none | FALSE | 0 | 71.447 | FALSE | FALSE | 0.4784 | 1.6227 | 72.7436 | 13 | 0 | 0.09882 | 0.13817 | -0.71522 | 0.6483 | Confirmed/Materialized Shift | 74.0402 | 1.1763 | Day | 202602 | 2026-02-18 | 1.1763
2026-02-18 12:14 | 73.5062 | FALSE | TRUE | -1.8689 | -2.6088 | -0.54135 | -0.73109 | 0 |  | 2026-02-18 09:00 | none | FALSE | 0 | 71.6373 | FALSE | FALSE | 0.4734 | 1.5854 | 72.8424 | 14 | 0 | 0.09882 | 0.13817 | -0.71522 | 0.60255 | Confirmed/Materialized Shift | 74.0476 | 1.1016 | Day | 202602 | 2026-02-18 | 1.1016
2026-02-18 12:29 | 73.7888 | FALSE | TRUE | -1.9399 | -2.7 | -0.2731 | -0.36875 | 0.2826 |  | 2026-02-18 09:00 | none | FALSE | 0 | 71.8489 | FALSE | FALSE | 0.5004 | 1.5802 | 72.9554 | 15 | 0.2826 | 0.11295 | 0.14193 | 1.1953 | 0.55325 | Confirmed/Materialized Shift | 74.0619 | 1.5064 | Day | 202602 | 2026-02-18 | 1.5064
2026-02-18 12:44 | 73.7888 | FALSE | TRUE | -1.7614 | -2.4455 | -0.29227 | -0.39452 | 0 |  | 2026-02-18 09:00 | none | FALSE | 0 | 72.0274 | FALSE | FALSE | 0.4954 | 1.5708 | 73.0542 | 16 | 0 | 0.09882 | 0.13817 | -0.71522 | 0.51342 | Confirmed/Materialized Shift | 74.0811 | 1.4307 | Day | 202602 | 2026-02-18 | 1.4307
2026-02-18 12:59 | 73.7888 | FALSE | TRUE | -1.6215 | -2.2469 | -0.32176 | -0.43417 | 0 |  | 2026-02-18 09:00 | none | FALSE | 0 | 72.1673 | FALSE | FALSE | 0.4892 | 1.5571 | 73.1389 | 17 | 0 | 0.08469 | 0.13273 | -0.63807 | 0.48583 | Confirmed/Materialized Shift | 74.1106 | 1.3377 | Day | 202602 | 2026-02-18 | 1.3377
2026-02-18 13:14 | 73.5062 | TRUE | FALSE | -1.1465 | -1.5845 | -0.55305 | -0.74677 | -0.2826 |  |  | none | FALSE | 1 | 72.3597 | FALSE | FALSE | 0.0751 |  | 73.2095 | 0 | -0.2826 | 0.07056 | 0.15534 | -2.2735 | 0.42489 | Persistence ends | 74.0593 | 0.69837 | Day | 202602 | 2026-02-18 | 0.69837
2026-02-18 13:29 | 73.2236 | FALSE | FALSE | -0.72559 | -1.0008 | -0.78211 | -1.0568 | -0.2826 |  |  | none | FALSE | 1 | 72.498 | FALSE | FALSE | 0.0336 |  | 73.2519 | 0 | -0.2826 | 0.04239 | 0.16593 | -1.9586 | 0.37692 | Normal | 74.0057 | -0.074975 | Day | 202602 | 2026-02-18 | 0.074975
2026-02-18 13:43 | 73.2236 | FALSE | FALSE | -0.56126 | -0.77243 | -0.70256 | -0.95036 | 0 |  |  | none | FALSE | 1 | 72.6623 | FALSE | FALSE | 0.0435 |  | 73.2943 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.31596 | Normal | 73.9262 | -0.22361 | Day | 202602 | 2026-02-18 | 0.22361
2026-02-18 13:58 | 72.941 | FALSE | FALSE | -0.2154 | -0.29618 | -0.95016 | -1.2859 | -0.2826 |  |  | none | FALSE | 1 | 72.7256 | FALSE | FALSE | 0.1126 |  | 73.3084 | 0 | -0.2826 | 0.01413 | 0.17092 | -1.7361 | 0.29139 | Normal | 73.8912 | -1.2608 | Day | 202602 | 2026-02-18 | 1.2608
2026-02-18 14:13 | 72.6584 | FALSE | FALSE | 0.0039372 | 0.0054185 | -1.2678 | -1.7149 | -0.2826 | 2026-02-18 15:58 | 2026-02-18 14:13 | lower | TRUE | 1 | 72.6623 | FALSE | FALSE | 0.2199 | 2.0125 | 73.2943 | 1 | -0.2826 | -0.01413 | 0.17092 | -1.5708 | 0.31596 | Extreme triggered | 73.9262 | -2.0125 | Day | 202602 | 2026-02-18 | 2.0125
2026-02-18 14:28 | 72.6584 | FALSE | FALSE | -0.054534 | -0.075112 | -1.298 | -1.7551 | 0 |  | 2026-02-18 14:13 | none | FALSE | 1 | 72.6039 | FALSE | FALSE | 0.2654 | 1.9256 | 73.2801 | 2 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.33813 | Extreme/elevated | 73.9564 | -1.8387 | Day | 202602 | 2026-02-18 | 1.8387
2026-02-18 14:43 | 72.3758 | FALSE | FALSE | 0.10023 | 0.13829 | -1.6519 | -2.2314 | -0.2826 |  | 2026-02-18 14:13 | lower | TRUE | 1 | 72.476 | FALSE | TRUE | 0.3506 | 2.0365 | 73.2519 | 3 | -0.2826 | -0.02826 | 0.18107 | -1.4047 | 0.38792 | Persistent | 74.0277 | -2.2584 | Day | 202602 | 2026-02-18 | 2.2584
2026-02-18 14:58 | 72.3758 | FALSE | FALSE | -0.012305 | -0.017005 | -1.7079 | -2.3054 | 0 |  | 2026-02-18 14:13 | none | FALSE | 1 | 72.3635 | FALSE | FALSE | 0.3886 | 2.0202 | 73.2236 | 4 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.43005 | Persistent | 74.0837 | -1.9714 | Day | 202602 | 2026-02-18 | 1.9714
2026-02-18 15:13 | 72.3758 | FALSE | FALSE | -0.13456 | -0.18626 | -1.7454 | -2.3548 | 0 |  | 2026-02-18 14:13 | none | FALSE | 1 | 72.2412 | FALSE | FALSE | 0.4285 | 1.9589 | 73.1812 | 5 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.46998 | Persistent | 74.1212 | -1.7137 | Day | 202602 | 2026-02-18 | 1.7137
2026-02-18 15:28 | 72.6584 | FALSE | FALSE | -0.47361 | -0.65611 | -1.4627 | -1.9734 | 0.2826 |  | 2026-02-18 14:13 | none | FALSE | 1 | 72.1848 | FALSE | FALSE | 0.4395 | 1.8027 | 73.153 | 6 | 0.2826 | -0.02826 | 0.18107 | 1.7168 | 0.48408 | Persistent | 74.1211 | -1.0216 | Day | 202602 | 2026-02-18 | 1.0216
2026-02-18 15:43 | 72.3758 | FALSE | TRUE | -0.2928 | -0.40619 | -1.7623 | -2.3771 | -0.2826 |  | 2026-02-18 14:13 | none | FALSE | 0 | 72.083 | FALSE | FALSE | 0.4953 | 1.7495 | 73.1106 | 7 | -0.2826 | -0.04239 | 0.18957 | -1.2671 | 0.51378 | Confirmed/Materialized Shift | 74.1381 | -1.4301 | Day | 202602 | 2026-02-18 | 1.4301
2026-02-18 15:58 | 72.941 | TRUE | FALSE | -0.87335 | -1.2118 | -1.1842 | -1.5976 | 0.5652 |  |  | none | FALSE | 1 | 72.0676 | FALSE | FALSE | 0.0487 |  | 73.0964 | 0 | 0.5652 | -0.01413 | 0.23331 | 2.4831 | 0.51439 | Persistence ends | 74.1252 | -0.30216 | Day | 202602 | 2026-02-18 | 0.30216
2026-02-18 16:13 | 73.5062 | TRUE | FALSE | -1.4394 | -1.9974 | -0.64815 | -0.87405 | 0.5652 |  |  | none | FALSE | 2 | 72.0668 | TRUE | FALSE | 0.1077 |  | 73.1106 | 0 | 0.5652 | 0.01413 | 0.26692 | 2.0646 | 0.52189 | Normal | 74.1543 | 0.75808 | Day | 202602 | 2026-02-18 | 0.75808
2026-02-18 16:28 | 73.7888 | FALSE | FALSE | -1.7377 | -2.4117 | -0.40946 | -0.55184 | 0.2826 |  |  | none | FALSE | 2 | 72.0511 | FALSE | FALSE | 0.1396 |  | 73.1247 | 0 | 0.2826 | 0.01413 | 0.26692 | 1.0058 | 0.53678 | Normal | 74.1983 | 1.2372 | Day | 202602 | 2026-02-18 | 1.2372
2026-02-18 16:42 | 73.7888 | FALSE | FALSE | -1.7518 | -2.4317 | -0.4518 | -0.60856 | 0 |  |  | none | FALSE | 2 | 72.037 | FALSE | FALSE | 0.1358 |  | 73.1388 | 0 | 0 | 0.01413 | 0.26692 | -0.052937 | 0.55089 | Normal | 74.2406 | 1.1799 | Day | 202602 | 2026-02-18 | 1.1799
2026-02-18 16:44 | 74.0714 | FALSE | FALSE | -2.0728 | -2.8789 | -0.26411 | -0.3553 | 0.2826 |  |  | none | FALSE | 2 | 71.9986 | FALSE | FALSE | 0.1603 |  | 73.1671 | 0 | 0.2826 | 0.02826 | 0.27353 | 0.92984 | 0.58422 | Normal | 74.3355 | 1.5479 | Day | 202602 | 2026-02-18 | 1.5479
2026-02-18 16:47 | 74.0714 | FALSE | FALSE | -2.1048 | -2.9247 | -0.35269 | -0.47389 | 0 |  |  | none | FALSE | 2 | 71.9666 | FALSE | FALSE | 0.1522 |  | 73.1953 | 0 | 0 | 0.02826 | 0.27353 | -0.10332 | 0.61437 | Normal | 74.4241 | 1.4259 | Day | 202602 | 2026-02-18 | 1.4259
2026-02-18 17:03 | 73.2236 | TRUE | FALSE | -1.2534 | -1.7415 | -1.1403 | -1.5335 | -0.8478 |  |  | none | FALSE | 3 | 71.9702 | TRUE | FALSE | 0.092 |  | 73.1671 | 0 | -0.8478 | -0.02826 | 0.32931 | -2.4887 | 0.59843 | Normal | 74.3639 | 0.094447 | Day | 202602 | 2026-02-18 | 0.094447
2026-02-18 17:18 | 72.095 | TRUE | FALSE | -0.26276 | -0.3658 | -2.2375 | -3.0102 | -1.1286 |  |  | none | FALSE | 4 | 71.8322 | TRUE | FALSE | 0.2196 |  | 73.0824 | 0 | -1.1286 | -0.08469 | 0.41082 | -2.541 | 0.62508 | Normal | 74.3325 | -1.5796 | Day | 202602 | 2026-02-18 | 1.5796
2026-02-18 17:33 | 72.095 | FALSE | FALSE | -0.37514 | -0.52306 | -2.1805 | -2.9357 | 0 |  |  | none | FALSE | 4 | 71.7199 | FALSE | FALSE | 0.2085 |  | 72.9977 | 0 | 0 | -0.08469 | 0.41082 | 0.20615 | 0.63892 | Normal | 74.2755 | -1.4129 | Day | 202602 | 2026-02-18 | 1.4129
2026-02-18 17:42 | 72.095 | FALSE | FALSE | -0.48278 | -0.67417 | -2.1471 | -2.892 | 0 |  |  | none | FALSE | 4 | 71.6122 | FALSE | FALSE | 0.1987 |  | 72.9271 | 0 | 0 | -0.07056 | 0.40851 | 0.17273 | 0.65746 | Normal | 74.2421 | -1.2657 | Day | 202602 | 2026-02-18 | 1.2657
2026-02-18 17:57 | 72.095 | FALSE | FALSE | -0.58182 | -0.81359 | -2.1332 | -2.8739 | 0 |  |  | none | FALSE | 3 | 71.5132 | FALSE | FALSE | 0.1619 |  | 72.8707 | 0 | 0 | -0.05643 | 0.40567 | 0.1391 | 0.67877 | Normal | 74.2282 | -1.1428 | Day | 202602 | 2026-02-18 | 1.1428
2026-02-18 18:12 | 72.3758 | FALSE | FALSE | -0.91155 | -1.2755 | -1.8166 | -2.4485 | 0.2808 |  |  | none | FALSE | 2 | 71.4643 | FALSE | FALSE | 0.1014 |  | 72.8283 | 0 | 0.2808 | -0.04239 | 0.41252 | 0.78344 | 0.68203 | Normal | 74.1924 | -0.66349 | Day | 202602 | 2026-02-18 | 0.66349
2026-02-18 18:27 | 72.3758 | FALSE | FALSE | -0.95333 | -1.3348 | -1.8018 | -2.4291 | 0 |  |  | none | FALSE | 2 | 71.4225 | FALSE | FALSE | 0.0982 |  | 72.8001 | 0 | 0 | -0.02826 | 0.40869 | 0.069148 | 0.68879 | Normal | 74.1776 | -0.61595 | Night | 202602 | 2026-02-18 | 0.61595
2026-02-18 18:42 | 72.3758 | FALSE | FALSE | -0.97932 | -1.3717 | -1.7996 | -2.4261 | 0 |  |  | none | FALSE | 2 | 71.3965 | FALSE | FALSE | 0.0965 |  | 72.7859 | 0 | 0 | -0.01413 | 0.40429 | 0.03495 | 0.69473 | Normal | 74.1754 | -0.59035 | Night | 202602 | 2026-02-18 | 0.59035
2026-02-18 18:42 | 72.3758 | FALSE | FALSE | -1.0046 | -1.4076 | -1.7966 | -2.4222 | 0 |  |  | none | FALSE | 2 | 71.3712 | FALSE | FALSE | 0.0948 |  | 72.7718 | 0 | 0 | -0.01413 | 0.40429 | 0.03495 | 0.70031 | Normal | 74.1724 | -0.56546 | Night | 202602 | 2026-02-18 | 0.56546
2026-02-18 18:42 | 72.3758 | FALSE | FALSE | -1.0046 | -1.4076 | -1.7966 | -2.4222 | 0 |  |  | none | FALSE | 2 | 71.3712 | FALSE | FALSE | 0.0948 |  | 72.7718 | 0 | 0 | 0 | 0.39932 | 0 | 0.70031 | Normal | 74.1724 | -0.56546 | Night | 202602 | 2026-02-18 | 0.56546
2026-02-18 18:57 | 72.941 | FALSE | FALSE | -1.5307 | -2.1435 | -1.2488 | -1.6833 | 0.5652 |  |  | none | FALSE | 1 | 71.4103 | FALSE | FALSE | 0.0421 |  | 72.8001 | 0 | 0.5652 | 0.02826 | 0.41884 | 1.282 | 0.69487 | Normal | 74.1898 | 0.20283 | Night | 202602 | 2026-02-18 | 0.20283
2026-02-18 19:12 | 73.2236 | FALSE | FALSE | -1.7681 | -2.4744 | -1.0058 | -1.355 | 0.2826 |  |  | none | FALSE | 0 | 71.4555 | FALSE | FALSE | 0.0366 |  | 72.8424 | 0 | 0.2826 | 0.04239 | 0.42259 | 0.56842 | 0.69348 | Normal | 74.2294 | 0.54962 | Night | 202602 | 2026-02-18 | 0.54962
2026-02-18 19:27 | 73.5062 | FALSE | FALSE | -2.0362 | -2.849 | -0.79347 | -1.0679 | 0.2826 |  |  | none | FALSE | 0 | 71.47 | FALSE | FALSE | 0.0586 |  | 72.8848 | 0 | 0.2826 | 0.04239 | 0.42259 | 0.56842 | 0.70741 | Normal | 74.2997 | 0.87835 | Night | 202602 | 2026-02-18 | 0.87835
2026-02-18 19:41 | 73.7888 | FALSE | FALSE | -2.2818 | -3.1911 | -0.61521 | -0.82685 | 0.2826 |  |  | none | FALSE | 0 | 71.507 | FALSE | FALSE | 0.0767 |  | 72.9555 | 0 | 0.2826 | 0.07065 | 0.41859 | 0.50634 | 0.72426 | Normal | 74.404 | 1.1506 | Night | 202602 | 2026-02-18 | 1.1506
2026-02-18 19:56 | 73.7888 | FALSE | FALSE | -2.2865 | -3.1978 | -0.70467 | -0.94594 | 0 |  |  | none | FALSE | 0 | 71.5023 | FALSE | FALSE | 0.0705 |  | 72.9979 | 0 | 0 | 0.04239 | 0.40221 | -0.10539 | 0.74779 | Normal | 74.4935 | 1.0577 | Night | 202602 | 2026-02-18 | 1.0577
2026-02-18 20:11 | 73.7888 | FALSE | FALSE | -2.2977 | -3.214 | -0.74414 | -0.99841 | 0 |  |  | none | FALSE | 0 | 71.4911 | FALSE | FALSE | 0.0681 |  | 73.012 | 0 | 0 | 0.01413 | 0.38293 | -0.036899 | 0.76047 | Normal | 74.5329 | 1.0215 | Night | 202602 | 2026-02-18 | 1.0215
2026-02-18 20:27 | 73.7888 | FALSE | FALSE | -2.2977 | -3.214 | -0.74414 | -0.99841 | 0 |  |  | none | FALSE | 0 | 71.4911 | FALSE | FALSE | 0.0681 |  | 73.012 | 0 | 0 | 0 | 0.37768 | 0 | 0.76047 | Normal | 74.5329 | 1.0215 | Night | 202602 | 2026-02-18 | 1.0215
2026-02-18 20:41 | 73.7888 | FALSE | FALSE | -2.2977 | -3.214 | -0.74414 | -0.99841 | 0 |  |  | none | FALSE | 0 | 71.4911 | FALSE | FALSE | 0.0681 |  | 73.012 | 0 | 0 | 0 | 0.37768 | 0 | 0.76047 | Normal | 74.5329 | 1.0215 | Night | 202602 | 2026-02-18 | 1.0215
2026-02-18 20:56 | 73.7888 | FALSE | FALSE | -2.2752 | -3.1815 | -0.69338 | -0.93094 | 0 |  |  | none | FALSE | 0 | 71.5136 | FALSE | FALSE | 0.071 |  | 72.9979 | 0 | 0 | -0.01413 | 0.37179 | 0.038005 | 0.74215 | Normal | 74.4822 | 1.0657 | Night | 202602 | 2026-02-18 | 1.0657
2026-02-18 21:11 | 74.0714 | FALSE | FALSE | -2.5578 | -3.5767 | -0.41078 | -0.55152 | 0.2826 |  |  | none | FALSE | 0 | 71.5136 | FALSE | FALSE | 0.0964 |  | 72.9979 | 0 | 0.2826 | 0 | 0.37768 | 0.74825 | 0.74215 | Normal | 74.4822 | 1.4465 | Night | 202602 | 2026-02-18 | 1.4465
2026-02-18 21:26 | 73.7888 | FALSE | FALSE | -2.2861 | -3.1972 | -0.76074 | -1.0205 | -0.2826 |  |  | none | FALSE | 0 | 71.5027 | FALSE | FALSE | 0.0668 |  | 73.0261 | 0 | -0.2826 | 0.02826 | 0.3289 | -0.94514 | 0.7617 | Normal | 74.5495 | 1.0013 | Night | 202602 | 2026-02-18 | 1.0013
2026-02-18 21:41 | 74.0714 | FALSE | FALSE | -2.4719 | -3.4524 | -0.57905 | -0.77569 | 0.2826 |  |  | none | FALSE | 0 | 71.5995 | FALSE | FALSE | 0.0827 |  | 73.125 | 0 | 0.2826 | 0.09882 | 0.18948 | 0.96991 | 0.76275 | Normal | 74.6505 | 1.2408 | Night | 202602 | 2026-02-18 | 1.2408
2026-02-18 21:56 | 73.7888 | FALSE | FALSE | -2.051 | -2.859 | -0.89271 | -1.1954 | -0.2826 |  |  | none | FALSE | 0 | 71.7378 | FALSE | FALSE | 0.0525 |  | 73.2096 | 0 | -0.2826 | 0.08469 | 0.20697 | -1.7746 | 0.73593 | Normal | 74.6815 | 0.78696 | Night | 202602 | 2026-02-18 | 0.78696
2026-02-18 22:11 | 74.0714 | FALSE | FALSE | -2.1842 | -3.0384 | -0.65835 | -0.88097 | 0.2826 |  |  | none | FALSE | 0 | 71.8872 | FALSE | FALSE | 0.0716 |  | 73.3085 | 0 | 0.2826 | 0.09882 | 0.2105 | 0.87306 | 0.71064 | Normal | 74.7297 | 1.0736 | Night | 202602 | 2026-02-18 | 1.0736
2026-02-18 22:26 | 74.0714 | FALSE | FALSE | -2.0026 | -2.7787 | -0.67434 | -0.90218 | 0 |  |  | none | FALSE | 0 | 72.0688 | FALSE | FALSE | 0.0662 |  | 73.4073 | 0 | 0 | 0.09882 | 0.2105 | -0.46945 | 0.66922 | Normal | 74.7457 | 0.99236 | Night | 202602 | 2026-02-18 | 0.99236
2026-02-18 22:40 | 74.0714 | FALSE | FALSE | -1.8561 | -2.5702 | -0.6974 | -0.93274 | 0 |  |  | none | FALSE | 0 | 72.2153 | FALSE | FALSE | 0.0605 |  | 73.4921 | 0 | 0 | 0.08478 | 0.20706 | -0.40945 | 0.63837 | Normal | 74.7688 | 0.90752 | Night | 202602 | 2026-02-18 | 0.90752
2026-02-18 22:55 | 73.7888 | FALSE | FALSE | -1.3945 | -1.9263 | -0.94235 | -1.261 | -0.2826 |  |  | none | FALSE | 0 | 72.3943 | FALSE | FALSE | 0.0258 |  | 73.5627 | 0 | -0.2826 | 0.07065 | 0.22224 | -1.5895 | 0.58422 | Normal | 74.7312 | 0.38698 | Night | 202602 | 2026-02-18 | 0.38698
2026-02-18 23:11 | 74.0714 | FALSE | FALSE | -1.4693 | -2.0238 | -0.6215 | -0.83207 | 0.2826 |  |  | none | FALSE | 0 | 72.6021 | FALSE | FALSE | 0.0541 |  | 73.6475 | 0 | 0.2826 | 0.08478 | 0.22645 | 0.87356 | 0.5227 | Normal | 74.6929 | 0.81098 | Night | 202602 | 2026-02-18 | 0.81098
2026-02-18 23:26 | 73.7888 | FALSE | FALSE | -0.92831 | -1.2741 | -0.78701 | -1.0553 | -0.2826 |  |  | none | FALSE | 0 | 72.8605 | FALSE | FALSE | 0.011 |  | 73.7181 | 0 | -0.2826 | 0.07065 | 0.24041 | -1.4694 | 0.42883 | Normal | 74.5758 | 0.16475 | Night | 202602 | 2026-02-18 | 0.16475
2026-02-18 23:40 | 73.7888 | FALSE | FALSE | -0.57988 | -0.79209 | -0.57988 | -0.77974 | 0 |  |  | none | FALSE | 0 | 73.2089 | FALSE | FALSE | 0 |  | 73.7888 | 0 | 0 | 0.07065 | 0.24041 | -0.29388 | 0.28994 | Normal | 74.3687 | 0 | Night | 202602 | 2026-02-18 | 0
2026-02-18 23:55 | 73.7888 | FALSE | FALSE | -0.37877 | -0.51597 | -0.46355 | -0.6243 | 0 |  |  | none | FALSE | 0 | 73.41 | FALSE | FALSE | 0.0134 |  | 73.8312 | 0 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.21058 | Normal | 74.2524 | -0.2013 | Night | 202602 | 2026-02-18 | 0.2013
2026-02-19 00:10 | 73.7888 | FALSE | FALSE | -0.24028 | -0.32669 | -0.38158 | -0.51446 | 0 |  |  | none | FALSE | 0 | 73.5485 | FALSE | FALSE | 0.0303 |  | 73.8594 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.15546 | Normal | 74.1704 | -0.45445 | Night | 202602 | 2026-02-19 | 0.45445
2026-02-19 00:25 | 73.7888 | FALSE | FALSE | -0.18096 | -0.24584 | -0.35052 | -0.47278 | 0 |  |  | none | FALSE | 0 | 73.6078 | FALSE | FALSE | 0.0425 |  | 73.8736 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.13287 | Normal | 74.1393 | -0.63808 | Night | 202602 | 2026-02-19 | 0.63808
2026-02-19 00:40 | 73.7888 | FALSE | FALSE | -0.18096 | -0.24584 | -0.35052 | -0.47278 | 0 |  |  | none | FALSE | 0 | 73.6078 | FALSE | FALSE | 0.0425 |  | 73.8736 | 0 | 0 | 0 | 0.18338 | 0 | 0.13287 | Normal | 74.1393 | -0.63808 | Night | 202602 | 2026-02-19 | 0.63808
2026-02-19 00:55 | 73.7888 | FALSE | FALSE | -0.18096 | -0.24584 | -0.35052 | -0.47278 | 0 |  |  | none | FALSE | 0 | 73.6078 | FALSE | FALSE | 0.0425 |  | 73.8736 | 0 | 0 | 0 | 0.18338 | 0 | 0.13287 | Normal | 74.1393 | -0.63808 | Night | 202602 | 2026-02-19 | 0.63808
2026-02-19 01:10 | 73.7888 | FALSE | FALSE | -0.18096 | -0.24584 | -0.35052 | -0.47278 | 0 |  |  | none | FALSE | 0 | 73.6078 | FALSE | FALSE | 0.0425 |  | 73.8736 | 0 | 0 | 0 | 0.18338 | 0 | 0.13287 | Normal | 74.1393 | -0.63808 | Night | 202602 | 2026-02-19 | 0.63808
2026-02-19 01:25 | 73.7888 | FALSE | FALSE | -0.18096 | -0.24584 | -0.35052 | -0.47278 | 0 |  |  | none | FALSE | 0 | 73.6078 | FALSE | FALSE | 0.0425 |  | 73.8736 | 0 | 0 | 0 | 0.18338 | 0 | 0.13287 | Normal | 74.1393 | -0.63808 | Night | 202602 | 2026-02-19 | 0.63808
2026-02-19 01:40 | 73.7888 | FALSE | FALSE | -0.18096 | -0.24584 | -0.35052 | -0.47278 | 0 |  |  | none | FALSE | 0 | 73.6078 | FALSE | FALSE | 0.0425 |  | 73.8736 | 0 | 0 | 0 | 0.18338 | 0 | 0.13287 | Normal | 74.1393 | -0.63808 | Night | 202602 | 2026-02-19 | 0.63808
2026-02-19 01:55 | 73.5062 | FALSE | FALSE | 0.042322 | 0.057544 | -0.66418 | -0.89548 | -0.2826 | 2026-02-19 07:45 | 2026-02-19 01:55 | lower | TRUE | 0 | 73.5485 | FALSE | FALSE | 0.2086 | 2.2722 | 73.8594 | 1 | -0.2826 | -0.01413 | 0.19396 | -1.3842 | 0.15546 | Extreme triggered | 74.1704 | -2.2722 | Night | 202602 | 2026-02-19 | 2.2722
2026-02-19 02:10 | 73.5062 | FALSE | FALSE | -0.0068632 | -0.0093378 | -0.65684 | -0.88567 | 0 |  | 2026-02-19 01:55 | none | FALSE | 0 | 73.4993 | FALSE | FALSE | 0.2449 | 2.1154 | 73.8312 | 2 | 0 | -0.02826 | 0.18107 | 0.15607 | 0.16593 | Extreme/elevated | 74.163 | -1.9586 | Night | 202602 | 2026-02-19 | 1.9586
2026-02-19 02:25 | 73.5062 | FALSE | FALSE | -0.051277 | -0.069807 | -0.673 | -0.90726 | 0 |  | 2026-02-19 01:55 | none | FALSE | 0 | 73.4549 | FALSE | FALSE | 0.2859 | 1.9826 | 73.8171 | 3 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.18107 | Persistent | 74.1792 | -1.7168 | Night | 202602 | 2026-02-19 | 1.7168
2026-02-19 02:39 | 73.2236 | FALSE | FALSE | 0.122 | 0.16633 | -0.98014 | -1.3209 | -0.2826 |  | 2026-02-19 01:55 | lower | TRUE | 0 | 73.3456 | FALSE | TRUE | 0.3998 | 2.1291 | 73.7747 | 4 | -0.2826 | -0.04239 | 0.16593 | -1.4477 | 0.21454 | Persistent | 74.2037 | -2.5686 | Night | 202602 | 2026-02-19 | 2.5686
2026-02-19 02:54 | 73.2236 | FALSE | FALSE | 0.028207 | 0.038507 | -1.0174 | -1.3704 | 0 |  | 2026-02-19 01:55 | lower | TRUE | 0 | 73.2518 | FALSE | TRUE | 0.4267 | 2.1261 | 73.7464 | 5 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.2473 | Persistent | 74.241 | -2.1141 | Night | 202602 | 2026-02-19 | 2.1141
2026-02-19 03:09 | 73.2236 | FALSE | FALSE | -0.041475 | -0.056673 | -1.0023 | -1.3504 | 0 |  | 2026-02-19 01:55 | none | FALSE | 0 | 73.1821 | FALSE | FALSE | 0.4656 | 2.0786 | 73.704 | 6 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.26095 | Persistent | 74.2259 | -1.8411 | Night | 202602 | 2026-02-19 | 1.8411
2026-02-19 03:24 | 73.2236 | FALSE | TRUE | -0.095809 | -0.13102 | -0.97187 | -1.3099 | 0 |  | 2026-02-19 01:55 | none | FALSE | 0 | 73.1278 | FALSE | FALSE | 0.5094 | 2.0161 | 73.6616 | 7 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.26692 | Confirmed/Materialized Shift | 74.1955 | -1.6411 | Night | 202602 | 2026-02-19 | 1.6411
2026-02-19 03:39 | 73.2236 | FALSE | TRUE | -0.13583 | -0.18585 | -0.92711 | -1.2503 | 0 |  | 2026-02-19 01:55 | none | FALSE | 0 | 73.0878 | FALSE | FALSE | 0.4993 | 1.9502 | 73.6192 | 8 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.26574 | Confirmed/Materialized Shift | 74.1507 | -1.4888 | Night | 202602 | 2026-02-19 | 1.4888
2026-02-19 03:54 | 73.2236 | FALSE | TRUE | -0.18579 | -0.25438 | -0.92055 | -1.2416 | 0 |  | 2026-02-19 01:55 | none | FALSE | 0 | 73.0378 | FALSE | FALSE | 0.4886 | 1.8811 | 73.591 | 9 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.27659 | Confirmed/Materialized Shift | 74.1442 | -1.3283 | Night | 202602 | 2026-02-19 | 1.3283
2026-02-19 04:09 | 72.941 | FALSE | TRUE | 0.016484 | 0.022594 | -1.1704 | -1.5793 | -0.2826 |  | 2026-02-19 01:55 | lower | TRUE | 0 | 72.9575 | FALSE | TRUE | 0.5371 | 1.8987 | 73.5345 | 10 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.28849 | Confirmed/Materialized Shift | 74.1114 | -2.0571 | Night | 202602 | 2026-02-19 | 2.0571
2026-02-19 04:24 | 72.941 | FALSE | TRUE | -0.070109 | -0.09621 | -1.1722 | -1.5817 | 0 |  | 2026-02-19 01:55 | none | FALSE | 0 | 72.8709 | FALSE | FALSE | 0.5183 | 1.8874 | 73.4921 | 11 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.31059 | Confirmed/Materialized Shift | 74.1132 | -1.7743 | Night | 202602 | 2026-02-19 | 1.7743
2026-02-19 04:39 | 72.941 | FALSE | TRUE | -0.14224 | -0.19538 | -1.1596 | -1.5649 | 0 |  | 2026-02-19 01:55 | none | FALSE | 0 | 72.7988 | FALSE | FALSE | 0.5042 | 1.8603 | 73.4497 | 12 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.32546 | Confirmed/Materialized Shift | 74.1006 | -1.563 | Night | 202602 | 2026-02-19 | 1.563
2026-02-19 04:54 | 72.941 | FALSE | TRUE | -0.20183 | -0.27748 | -1.1344 | -1.5314 | 0 |  | 2026-02-19 01:55 | none | FALSE | 0 | 72.7392 | FALSE | FALSE | 0.4931 | 1.8246 | 73.4073 | 13 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.33406 | Confirmed/Materialized Shift | 74.0754 | -1.3958 | Night | 202602 | 2026-02-19 | 1.3958
2026-02-19 05:09 | 72.6584 | FALSE | TRUE | -0.028996 | -0.039923 | -1.4137 | -1.9086 | -0.2826 |  | 2026-02-19 01:55 | none | FALSE | 0 | 72.6294 | FALSE | FALSE | 0.528 | 1.8314 | 73.3508 | 14 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.36068 | Confirmed/Materialized Shift | 74.0721 | -1.9196 | Night | 202602 | 2026-02-19 | 1.9196
2026-02-19 05:24 | 72.6584 | FALSE | TRUE | -0.11744 | -0.16189 | -1.3891 | -1.876 | 0 |  | 2026-02-19 01:55 | none | FALSE | 0 | 72.541 | FALSE | FALSE | 0.5125 | 1.8218 | 73.2943 | 15 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.37665 | Confirmed/Materialized Shift | 74.0475 | -1.6882 | Night | 202602 | 2026-02-19 | 1.6882
2026-02-19 05:38 | 72.6584 | FALSE | TRUE | -0.18723 | -0.25836 | -1.3459 | -1.8187 | 0 |  | 2026-02-19 01:55 | none | FALSE | 0 | 72.4712 | FALSE | FALSE | 0.5008 | 1.8024 | 73.2377 | 16 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.38328 | Confirmed/Materialized Shift | 74.0043 | -1.5115 | Night | 202602 | 2026-02-19 | 1.5115
2026-02-19 05:53 | 72.6584 | FALSE | TRUE | -0.23936 | -0.33051 | -1.285 | -1.7378 | 0 |  | 2026-02-19 01:55 | none | FALSE | 0 | 72.419 | FALSE | FALSE | 0.4915 | 1.7771 | 73.1812 | 17 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.38108 | Confirmed/Materialized Shift | 73.9434 | -1.3719 | Night | 202602 | 2026-02-19 | 1.3719
2026-02-19 06:08 | 72.3758 | FALSE | TRUE | -0.051832 | -0.071666 | -1.5214 | -2.0587 | -0.2826 |  | 2026-02-19 01:55 | none | FALSE | 0 | 72.324 | FALSE | FALSE | 0.5245 | 1.7822 | 73.1106 | 18 | -0.2826 | -0.07065 | 0.12555 | -1.6882 | 0.3933 | Confirmed/Materialized Shift | 73.8972 | -1.8682 | Night | 202602 | 2026-02-19 | 1.8682
2026-02-19 06:23 | 72.3758 | FALSE | TRUE | -0.11981 | -0.16581 | -1.448 | -1.9615 | 0 |  | 2026-02-19 01:55 | none | FALSE | 0 | 72.256 | FALSE | FALSE | 0.513 | 1.7776 | 73.0399 | 19 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.39196 | Confirmed/Materialized Shift | 73.8238 | -1.6943 | Night | 202602 | 2026-02-19 | 1.6943
2026-02-19 06:38 | 72.3758 | FALSE | TRUE | -0.16039 | -0.2221 | -1.3473 | -1.8275 | 0 |  | 2026-02-19 01:55 | none | FALSE | 0 | 72.2154 | FALSE | FALSE | 0.505 | 1.7674 | 72.9693 | 20 | 0 | -0.07065 | 0.12555 | 0.56273 | 0.37692 | Confirmed/Materialized Shift | 73.7231 | -1.5745 | Night | 202602 | 2026-02-19 | 1.5745
2026-02-19 06:53 | 72.3758 | FALSE | TRUE | -0.21691 | -0.3006 | -1.2908 | -1.7522 | 0 |  | 2026-02-19 01:55 | none | FALSE | 0 | 72.1589 | FALSE | FALSE | 0.495 | 1.7511 | 72.9127 | 21 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.37692 | Confirmed/Materialized Shift | 73.6666 | -1.4245 | Night | 202602 | 2026-02-19 | 1.4245
2026-02-19 07:08 | 72.095 | FALSE | TRUE | -0.036373 | -0.050478 | -1.5307 | -2.0791 | -0.2808 |  | 2026-02-19 01:55 | none | FALSE | 0 | 72.0586 | FALSE | FALSE | 0.5271 | 1.7582 | 72.8422 | 22 | -0.2808 | -0.07056 | 0.12539 | -1.6767 | 0.39178 | Confirmed/Materialized Shift | 73.6257 | -1.9072 | Day | 202602 | 2026-02-19 | 1.9072
2026-02-19 07:23 | 72.3758 | TRUE | TRUE | -0.3341 | -0.46375 | -1.1538 | -1.5692 | 0.2808 |  | 2026-02-19 01:55 | none | FALSE | 1 | 72.0417 | FALSE | FALSE | 0.502 | 1.7296 | 72.7857 | 23 | 0.2808 | -0.05652 | 0.14748 | 2.2872 | 0.37198 | Confirmed/Materialized Shift | 73.5296 | -1.1018 | Day | 202602 | 2026-02-19 | 1.1018
2026-02-19 07:30 | 72.095 | FALSE | TRUE | -0.14044 | -0.19518 | -1.4089 | -1.9168 | -0.2808 |  | 2026-02-19 01:55 | none | FALSE | 1 | 71.9546 | FALSE | FALSE | 0.5377 | 1.7258 | 72.7292 | 24 | -0.2808 | -0.05643 | 0.14734 | -1.5229 | 0.38733 | Confirmed/Materialized Shift | 73.5039 | -1.6374 | Day | 202602 | 2026-02-19 | 1.6374
2026-02-19 07:45 | 72.3758 | FALSE | FALSE | -0.44221 | -0.61475 | -1.0643 | -1.4492 | 0.2808 |  |  | none | FALSE | 1 | 71.9336 | FALSE | FALSE | 0.0836 |  | 72.6868 | 0 | 0.2808 | -0.04239 | 0.16528 | 1.9554 | 0.37663 | Persistence ends | 73.4401 | -0.82586 | Day | 202602 | 2026-02-19 | 0.82586
2026-02-19 08:00 | 72.3758 | FALSE | FALSE | -0.45214 | -0.62864 | -0.98944 | -1.3486 | 0 |  |  | none | FALSE | 1 | 71.9237 | FALSE | FALSE | 0.0783 |  | 72.6445 | 0 | 0 | -0.04239 | 0.16528 | 0.25647 | 0.36039 | Normal | 73.3652 | -0.74543 | Day | 202602 | 2026-02-19 | 0.74543
2026-02-19 08:15 | 72.3758 | FALSE | FALSE | -0.44942 | -0.62484 | -0.90194 | -1.2309 | 0 |  |  | none | FALSE | 1 | 71.9264 | FALSE | FALSE | 0.0732 |  | 72.6021 | 0 | 0 | -0.04239 | 0.16528 | 0.25647 | 0.33784 | Normal | 73.2777 | -0.66972 | Day | 202602 | 2026-02-19 | 0.66972
2026-02-19 08:30 | 72.3758 | FALSE | FALSE | -0.4313 | -0.59949 | -0.79904 | -1.092 | 0 |  |  | none | FALSE | 1 | 71.9445 | FALSE | FALSE | 0.0684 |  | 72.5597 | 0 | 0 | -0.04239 | 0.16528 | 0.25647 | 0.30758 | Normal | 73.1748 | -0.59779 | Day | 202602 | 2026-02-19 | 0.59779
2026-02-19 08:45 | 72.941 | TRUE | FALSE | -0.95707 | -1.3296 | -0.16615 | -0.22727 | 0.5652 |  |  | none | FALSE | 2 | 71.9839 | TRUE | FALSE | 0.151 |  | 72.5455 | 0 | 0.5652 | -0.01413 | 0.21404 | 2.7067 | 0.2808 | Normal | 73.1071 | 1.4083 | Day | 202602 | 2026-02-19 | 1.4083
2026-02-19 08:45 | 72.941 | FALSE | FALSE | -0.95707 | -1.3296 | -0.16615 | -0.22727 | 0 |  |  | none | FALSE | 2 | 71.9839 | FALSE | FALSE | 0.151 |  | 72.5455 | 0 | 0 | 0 | 0.2045 | 0 | 0.2808 | Normal | 73.1071 | 1.4083 | Day | 202602 | 2026-02-19 | 1.4083
2026-02-19 09:00 | 72.941 | FALSE | FALSE | -0.95707 | -1.3296 | -0.16615 | -0.22727 | 0 |  |  | none | FALSE | 2 | 71.9839 | FALSE | FALSE | 0.151 |  | 72.5455 | 0 | 0 | 0 | 0.2045 | 0 | 0.2808 | Normal | 73.1071 | 1.4083 | Day | 202602 | 2026-02-19 | 1.4083
2026-02-19 09:15 | 73.2236 | FALSE | FALSE | -1.2791 | -1.7779 | 0.048761 | 0.066637 | 0.2826 | 2026-02-19 11:44 | 2026-02-19 09:15 | upper | TRUE | 2 | 71.9445 | FALSE | FALSE | 0.2582 | 2.1585 | 72.5597 | 1 | 0.2826 | 0.01413 | 0.21404 | 1.2543 | 0.30758 | Extreme triggered | 73.1748 | 2.1585 | Day | 202602 | 2026-02-19 | 2.1585
2026-02-19 09:30 | 73.2236 | FALSE | FALSE | -1.313 | -1.8258 | -0.013358 | -0.01824 | 0 |  | 2026-02-19 09:15 | none | FALSE | 1 | 71.9106 | FALSE | FALSE | 0.2735 | 2.0591 | 72.5738 | 2 | 0 | 0.01413 | 0.21404 | -0.066016 | 0.33158 | Extreme/elevated | 73.237 | 1.9597 | Day | 202602 | 2026-02-19 | 1.9597
2026-02-19 09:44 | 73.2236 | FALSE | FALSE | -1.3453 | -1.8716 | -0.1022 | -0.13938 | 0 |  | 2026-02-19 09:15 | none | FALSE | 1 | 71.8783 | FALSE | FALSE | 0.3145 | 1.9453 | 72.6021 | 3 | 0 | 0.02826 | 0.20243 | -0.1396 | 0.36187 | Persistent | 73.3258 | 1.7176 | Day | 202602 | 2026-02-19 | 1.7176
2026-02-19 09:59 | 73.2236 | FALSE | FALSE | -1.3686 | -1.9047 | -0.18203 | -0.24797 | 0 |  | 2026-02-19 09:15 | none | FALSE | 1 | 71.855 | FALSE | FALSE | 0.3592 | 1.8416 | 72.6303 | 4 | 0 | 0.02826 | 0.20243 | -0.1396 | 0.38765 | Persistent | 73.4056 | 1.5304 | Day | 202602 | 2026-02-19 | 1.5304
2026-02-19 10:14 | 73.2236 | FALSE | FALSE | -1.3846 | -1.9273 | -0.25454 | -0.34641 | 0 |  | 2026-02-19 09:15 | none | FALSE | 1 | 71.839 | FALSE | FALSE | 0.4062 | 1.749 | 72.6586 | 5 | 0 | 0.02826 | 0.20243 | -0.1396 | 0.40978 | Persistent | 73.4781 | 1.3788 | Day | 202602 | 2026-02-19 | 1.3788
2026-02-19 10:30 | 73.5062 | FALSE | FALSE | -1.7082 | -2.3792 | -0.097744 | -0.1328 | 0.2826 |  | 2026-02-19 09:15 | none | FALSE | 1 | 71.798 | FALSE | FALSE | 0.4903 | 1.7548 | 72.701 | 6 | 0.2826 | 0.04239 | 0.21007 | 1.1435 | 0.45149 | Persistent | 73.6039 | 1.7835 | Day | 202602 | 2026-02-19 | 1.7835
2026-02-19 10:44 | 73.5062 | FALSE | TRUE | -1.7059 | -2.3759 | -0.20845 | -0.28278 | 0 |  | 2026-02-19 09:15 | none | FALSE | 1 | 71.8003 | FALSE | FALSE | 0.5329 | 1.7276 | 72.7575 | 7 | 0 | 0.05652 | 0.1961 | -0.28821 | 0.47858 | Confirmed/Materialized Shift | 73.7147 | 1.5644 | Day | 202602 | 2026-02-19 | 1.5644
2026-02-19 10:59 | 73.7888 | FALSE | TRUE | -2.0039 | -2.7916 | -0.082596 | -0.11181 | 0.2826 |  | 2026-02-19 09:15 | none | FALSE | 0 | 71.7849 | FALSE | FALSE | 0.5228 | 1.7418 | 72.8281 | 8 | 0.2826 | 0.07065 | 0.20191 | 1.0497 | 0.52163 | Confirmed/Materialized Shift | 73.8714 | 1.8417 | Day | 202602 | 2026-02-19 | 1.8417
2026-02-19 11:02 | 74.0714 | FALSE | TRUE | -2.3163 | -3.228 | 0.00070051 | 0.00094573 | 0.2826 |  | 2026-02-19 09:15 | upper | TRUE | 0 | 71.7551 | FALSE | TRUE | 0.5334 | 1.7707 | 72.9129 | 9 | 0.2826 | 0.08478 | 0.20654 | 0.95776 | 0.57889 | Confirmed/Materialized Shift | 74.0707 | 2.0012 | Day | 202602 | 2026-02-19 | 2.0012
2026-02-19 11:05 | 74.0714 | FALSE | TRUE | -2.3114 | -3.2211 | -0.16404 | -0.22097 | 0 |  | 2026-02-19 09:15 | none | FALSE | 0 | 71.76 | FALSE | FALSE | 0.5157 | 1.7671 | 72.9977 | 10 | 0 | 0.08478 | 0.20654 | -0.41047 | 0.61887 | Confirmed/Materialized Shift | 74.2354 | 1.7349 | Day | 202602 | 2026-02-19 | 1.7349
2026-02-19 11:20 | 74.0714 | FALSE | TRUE | -2.2247 | -3.0964 | -0.27493 | -0.3698 | 0 |  | 2026-02-19 09:15 | none | FALSE | 0 | 71.8467 | FALSE | FALSE | 0.504 | 1.7483 | 73.0965 | 11 | 0 | 0.09882 | 0.1892 | -0.5223 | 0.62491 | Confirmed/Materialized Shift | 74.3463 | 1.56 | Day | 202602 | 2026-02-19 | 1.56
2026-02-19 11:35 | 73.7888 | FALSE | TRUE | -1.8596 | -2.5853 | -0.61633 | -0.82835 | -0.2826 |  | 2026-02-19 09:15 | none | FALSE | 0 | 71.9292 | FALSE | FALSE | 0.467 | 1.6863 | 73.1672 | 12 | -0.2826 | 0.07065 | 0.20218 | -1.7472 | 0.61898 | Confirmed/Materialized Shift | 74.4051 | 1.0043 | Day | 202602 | 2026-02-19 | 1.0043
2026-02-19 11:44 | 73.7888 | FALSE | FALSE | -1.6953 | -2.3515 | -0.62138 | -0.83507 | 0 |  |  | none | FALSE | 0 | 72.0935 | FALSE | FALSE | 0.0618 |  | 73.2519 | 0 | 0 | 0.08469 | 0.18555 | -0.45642 | 0.57916 | Persistence ends | 74.4102 | 0.92711 | Day | 202602 | 2026-02-19 | 0.92711
2026-02-19 11:59 | 73.7888 | FALSE | FALSE | -1.5707 | -2.175 | -0.63815 | -0.85742 | 0 |  |  | none | FALSE | 0 | 72.2181 | FALSE | FALSE | 0.0563 |  | 73.3225 | 0 | 0 | 0.07065 | 0.18049 | -0.39144 | 0.55222 | Normal | 74.427 | 0.84439 | Day | 202602 | 2026-02-19 | 0.84439
2026-02-19 12:14 | 73.7888 | FALSE | FALSE | -1.4232 | -1.9667 | -0.63192 | -0.84911 | 0 |  |  | none | FALSE | 0 | 72.3656 | FALSE | FALSE | 0.0513 |  | 73.3932 | 0 | 0 | 0.07065 | 0.18049 | -0.39144 | 0.51378 | Normal | 74.4207 | 0.77006 | Day | 202602 | 2026-02-19 | 0.77006
2026-02-19 12:29 | 73.7888 | FALSE | FALSE | -1.2469 | -1.7189 | -0.59691 | -0.80246 | 0 |  |  | none | FALSE | 0 | 72.5419 | FALSE | FALSE | 0.047 |  | 73.4638 | 0 | 0 | 0.07065 | 0.18049 | -0.39144 | 0.46095 | Normal | 74.3857 | 0.70504 | Day | 202602 | 2026-02-19 | 0.70504
2026-02-19 12:43 | 73.7888 | FALSE | FALSE | -1.0302 | -1.4159 | -0.52149 | -0.70177 | 0 |  |  | none | FALSE | 0 | 72.7586 | FALSE | FALSE | 0.0437 |  | 73.5345 | 0 | 0 | 0.07065 | 0.18049 | -0.39144 | 0.38792 | Normal | 74.3103 | 0.65566 | Day | 202602 | 2026-02-19 | 0.65566
2026-02-19 12:58 | 73.5062 | FALSE | FALSE | -0.66775 | -0.91676 | -0.78079 | -1.0511 | -0.2826 |  |  | none | FALSE | 0 | 72.8384 | FALSE | FALSE | 0.0104 |  | 73.5627 | 0 | -0.2826 | 0.02826 | 0.15614 | -1.9909 | 0.36214 | Normal | 74.287 | -0.15607 | Day | 202602 | 2026-02-19 | 0.15607
2026-02-19 13:14 | 73.5062 | FALSE | FALSE | -0.57893 | -0.79384 | -0.74849 | -1.008 | 0 |  |  | none | FALSE | 0 | 72.9273 | FALSE | FALSE | 0.017 |  | 73.591 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.33185 | Normal | 74.2547 | -0.25547 | Day | 202602 | 2026-02-19 | 0.25547
2026-02-19 13:29 | 73.5062 | FALSE | FALSE | -0.47833 | -0.65499 | -0.70441 | -0.9492 | 0 |  |  | none | FALSE | 0 | 73.0279 | FALSE | FALSE | 0.0255 |  | 73.6192 | 0 | 0 | 0.02826 | 0.15614 | -0.18099 | 0.29568 | Normal | 74.2106 | -0.3823 | Day | 202602 | 2026-02-19 | 0.3823
2026-02-19 13:43 | 73.5062 | FALSE | FALSE | -0.43729 | -0.59846 | -0.69163 | -0.93214 | 0 |  |  | none | FALSE | 0 | 73.0689 | FALSE | FALSE | 0.03 |  | 73.6334 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.28223 | Normal | 74.1978 | -0.45059 | Day | 202602 | 2026-02-19 | 0.45059
2026-02-19 13:58 | 73.5062 | FALSE | FALSE | -0.39333 | -0.53797 | -0.67593 | -0.91117 | 0 |  |  | none | FALSE | 0 | 73.1129 | FALSE | FALSE | 0.0352 |  | 73.6475 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.26731 | Normal | 74.1821 | -0.52859 | Day | 202602 | 2026-02-19 | 0.52859
2026-02-19 14:13 | 73.5062 | FALSE | FALSE | -0.34593 | -0.47283 | -0.65679 | -0.8856 | 0 |  |  | none | FALSE | 0 | 73.1603 | FALSE | FALSE | 0.0413 |  | 73.6616 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.25068 | Normal | 74.163 | -0.62004 | Day | 202602 | 2026-02-19 | 0.62004
2026-02-19 14:28 | 73.5062 | FALSE | FALSE | -0.29435 | -0.40205 | -0.63347 | -0.85442 | 0 |  |  | none | FALSE | 0 | 73.2119 | FALSE | FALSE | 0.0487 |  | 73.6758 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.23195 | Normal | 74.1397 | -0.73101 | Day | 202602 | 2026-02-19 | 0.73101
2026-02-19 14:43 | 73.5062 | FALSE | FALSE | -0.23747 | -0.32411 | -0.60485 | -0.81615 | 0 |  |  | none | FALSE | 0 | 73.2687 | FALSE | FALSE | 0.0582 |  | 73.6899 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.21058 | Normal | 74.1111 | -0.8723 | Day | 202602 | 2026-02-19 | 0.8723
2026-02-19 14:58 | 73.5062 | FALSE | FALSE | -0.23747 | -0.32411 | -0.60485 | -0.81615 | 0 |  |  | none | FALSE | 0 | 73.2687 | FALSE | FALSE | 0.0582 |  | 73.6899 | 0 | 0 | 0 | 0.12967 | 0 | 0.21058 | Normal | 74.1111 | -0.8723 | Day | 202602 | 2026-02-19 | 0.8723
2026-02-19 15:13 | 73.5062 | FALSE | FALSE | -0.23747 | -0.32411 | -0.60485 | -0.81615 | 0 |  |  | none | FALSE | 0 | 73.2687 | FALSE | FALSE | 0.0582 |  | 73.6899 | 0 | 0 | 0 | 0.12967 | 0 | 0.21058 | Normal | 74.1111 | -0.8723 | Day | 202602 | 2026-02-19 | 0.8723
2026-02-19 15:28 | 73.5062 | FALSE | FALSE | -0.25657 | -0.35026 | -0.59569 | -0.80387 | 0 |  |  | none | FALSE | 0 | 73.2496 | FALSE | FALSE | 0.0531 |  | 73.6758 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.21306 | Normal | 74.1019 | -0.79582 | Day | 202602 | 2026-02-19 | 0.79582
2026-02-19 15:43 | 73.5062 | FALSE | FALSE | -0.2477 | -0.33811 | -0.5303 | -0.71626 | 0 |  |  | none | FALSE | 0 | 73.2585 | FALSE | FALSE | 0.0484 |  | 73.6475 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.1945 | Normal | 74.0365 | -0.72648 | Day | 202602 | 2026-02-19 | 0.72648
2026-02-19 15:58 | 73.5062 | FALSE | FALSE | -0.22509 | -0.30716 | -0.45117 | -0.61004 | 0 |  |  | none | FALSE | 0 | 73.2811 | FALSE | FALSE | 0.0446 |  | 73.6192 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.16906 | Normal | 73.9574 | -0.66862 | Day | 202602 | 2026-02-19 | 0.66862
2026-02-19 16:13 | 73.7888 | TRUE | FALSE | -0.46028 | -0.62769 | -0.092897 | -0.12574 | 0.2826 |  |  | none | FALSE | 1 | 73.3285 | FALSE | FALSE | 0.1171 |  | 73.6051 | 0 | 0.2826 | -0.01413 | 0.11135 | 2.6647 | 0.13829 | Normal | 73.8817 | 1.3283 | Day | 202602 | 2026-02-19 | 1.3283
2026-02-19 16:28 | 73.5062 | TRUE | FALSE | -0.18096 | -0.24679 | -0.35052 | -0.47459 | -0.2826 |  |  | none | FALSE | 2 | 73.3252 | TRUE | FALSE | 0.0997 |  | 73.591 | 0 | -0.2826 | -0.01413 | 0.11135 | -2.411 | 0.13287 | Normal | 73.8567 | -0.63808 | Day | 202602 | 2026-02-19 | 0.63808
2026-02-19 16:42 | 73.5062 | FALSE | FALSE | -0.18045 | -0.24609 | -0.32175 | -0.43581 | 0 |  |  | none | FALSE | 2 | 73.3258 | FALSE | FALSE | 0.0947 |  | 73.5768 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.12555 | Normal | 73.8279 | -0.56273 | Day | 202602 | 2026-02-19 | 0.56273
2026-02-19 16:57 | 73.2236 | TRUE | FALSE | 0.048403 | 0.06606 | -0.60158 | -0.81487 | -0.2826 | 2026-02-19 18:57 | 2026-02-19 16:57 | lower | TRUE | 3 | 73.272 | TRUE | FALSE | 0.2995 | 2.35 | 73.5486 | 1 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.13829 | Extreme triggered | 73.8252 | -2.35 | Day | 202602 | 2026-02-19 | 2.35
2026-02-19 17:12 | 73.2236 | FALSE | FALSE | 0.0082419 | 0.011254 | -0.58522 | -0.79288 | 0 |  | 2026-02-19 16:57 | lower | TRUE | 3 | 73.2318 | FALSE | FALSE | 0.3371 | 2.2036 | 73.5203 | 2 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.14424 | Extreme/elevated | 73.8088 | -2.0571 | Day | 202602 | 2026-02-19 | 2.0571
2026-02-19 17:28 | 73.2236 | FALSE | FALSE | -0.020018 | -0.027346 | -0.55696 | -0.75488 | 0 |  | 2026-02-19 16:57 | none | FALSE | 3 | 73.2036 | FALSE | FALSE | 0.3812 | 2.0895 | 73.4921 | 3 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.14424 | Persistent | 73.7806 | -1.8612 | Day | 202602 | 2026-02-19 | 1.8612
2026-02-19 17:42 | 73.2236 | FALSE | FALSE | -0.036377 | -0.049703 | -0.5168 | -0.70083 | 0 |  | 2026-02-19 16:57 | none | FALSE | 3 | 73.1872 | FALSE | FALSE | 0.4301 | 2.0013 | 73.4638 | 4 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.13829 | Persistent | 73.7404 | -1.737 | Day | 202602 | 2026-02-19 | 1.737
2026-02-19 17:57 | 72.941 | TRUE | FALSE | 0.13358 | 0.18279 | -0.85552 | -1.1593 | -0.2826 |  | 2026-02-19 16:57 | lower | TRUE | 4 | 73.0746 | TRUE | TRUE | 0.5827 | 2.1491 | 73.4356 | 5 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.18049 | Persistent | 73.7965 | -2.7401 | Day | 202602 | 2026-02-19 | 2.7401
2026-02-19 18:12 | 72.6584 | FALSE | FALSE | 0.23593 | 0.32365 | -1.2336 | -1.6695 | -0.2826 |  | 2026-02-19 16:57 | lower | TRUE | 4 | 72.8943 | FALSE | TRUE | 0.6535 | 2.2819 | 73.3932 | 6 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.24942 | Persistent | 73.892 | -2.9459 | Day | 202602 | 2026-02-19 | 2.9459
2026-02-19 18:27 | 72.6584 | FALSE | TRUE | 0.098875 | 0.1359 | -1.2859 | -1.739 | 0 |  | 2026-02-19 16:57 | lower | TRUE | 4 | 72.7573 | FALSE | TRUE | 0.6698 | 2.2892 | 73.3508 | 7 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.29675 | Confirmed/Materialized Shift | 73.9443 | -2.3332 | Night | 202602 | 2026-02-19 | 2.3332
2026-02-19 18:42 | 72.3758 | FALSE | TRUE | 0.18782 | 0.25884 | -1.6491 | -2.2277 | -0.2826 |  | 2026-02-19 16:57 | lower | TRUE | 3 | 72.5636 | FALSE | TRUE | 0.6533 | 2.3173 | 73.2943 | 8 | -0.2826 | -0.05652 | 0.14784 | -1.5292 | 0.36531 | Confirmed/Materialized Shift | 74.0249 | -2.5141 | Night | 202602 | 2026-02-19 | 2.5141
2026-02-19 18:42 | 72.3758 | FALSE | TRUE | 0.03217 | 0.044429 | -1.6917 | -2.284 | 0 |  | 2026-02-19 16:57 | lower | TRUE | 2 | 72.408 | FALSE | TRUE | 0.5956 | 2.2907 | 73.2377 | 9 | 0 | -0.05652 | 0.14784 | 0.3823 | 0.41488 | Confirmed/Materialized Shift | 74.0675 | -2.0775 | Night | 202602 | 2026-02-19 | 2.0775
2026-02-19 18:42 | 72.3758 | FALSE | TRUE | -0.098073 | -0.13569 | -1.7089 | -2.3067 | 0 |  | 2026-02-19 16:57 | none | FALSE | 2 | 72.2777 | FALSE | FALSE | 0.576 | 2.2399 | 73.1812 | 10 | 0 | -0.05652 | 0.14784 | 0.3823 | 0.45174 | Confirmed/Materialized Shift | 74.0847 | -1.7829 | Night | 202602 | 2026-02-19 | 1.7829
2026-02-19 18:57 | 73.2236 | TRUE | FALSE | -0.94735 | -1.3107 | -0.83431 | -1.1266 | 0.8478 |  |  | none | FALSE | 2 | 72.2762 | TRUE | FALSE | 0.0656 |  | 73.1671 | 0 | 0.8478 | -0.01413 | 0.25068 | 3.4384 | 0.44542 | Persistence ends | 74.0579 | 0.12689 | Night | 202602 | 2026-02-19 | 0.12689
2026-02-19 19:13 | 73.5062 | FALSE | FALSE | -1.23 | -1.7017 | -0.55171 | -0.74498 | 0.2826 |  |  | none | FALSE | 2 | 72.2762 | FALSE | FALSE | 0.1079 |  | 73.1671 | 0 | 0.2826 | 0 | 0.25933 | 1.0897 | 0.44542 | Normal | 74.0579 | 0.76135 | Night | 202602 | 2026-02-19 | 0.76135
2026-02-19 19:28 | 73.7888 | FALSE | FALSE | -1.5295 | -2.1167 | -0.31431 | -0.42416 | 0.2826 |  |  | none | FALSE | 2 | 72.2593 | FALSE | FALSE | 0.145 |  | 73.1812 | 0 | 0.2826 | 0.01413 | 0.26692 | 1.0058 | 0.46095 | Normal | 74.1031 | 1.3181 | Night | 202602 | 2026-02-19 | 1.3181
2026-02-19 19:41 | 74.0714 | FALSE | FALSE | -1.8575 | -2.5722 | -0.13363 | -0.18008 | 0.2826 |  |  | none | FALSE | 2 | 72.2139 | FALSE | FALSE | 0.1726 |  | 73.2095 | 0 | 0.2826 | 0.02826 | 0.27353 | 0.92984 | 0.49778 | Normal | 74.205 | 1.7315 | Night | 202602 | 2026-02-19 | 1.7315
2026-02-19 19:57 | 74.0714 | FALSE | FALSE | -1.8946 | -2.625 | -0.22729 | -0.30592 | 0 |  |  | none | FALSE | 1 | 72.1768 | FALSE | FALSE | 0.1333 |  | 73.2377 | 0 | 0 | 0.02826 | 0.27353 | -0.10332 | 0.53048 | Normal | 74.2987 | 1.5715 | Night | 202602 | 2026-02-19 | 1.5715
2026-02-19 20:12 | 74.0714 | FALSE | FALSE | -1.925 | -2.6681 | -0.31415 | -0.42233 | 0 |  |  | none | FALSE | 1 | 72.1464 | FALSE | FALSE | 0.1245 |  | 73.266 | 0 | 0 | 0.02826 | 0.27353 | -0.10332 | 0.55978 | Normal | 74.3856 | 1.4388 | Night | 202602 | 2026-02-19 | 1.4388
2026-02-19 20:27 | 74.0714 | FALSE | FALSE | -1.9495 | -2.7031 | -0.39523 | -0.53075 | 0 |  |  | none | FALSE | 1 | 72.1219 | FALSE | FALSE | 0.117 |  | 73.2943 | 0 | 0 | 0.02826 | 0.27353 | -0.10332 | 0.58619 | Normal | 74.4666 | 1.3258 | Night | 202602 | 2026-02-19 | 1.3258
2026-02-19 20:41 | 74.0714 | FALSE | FALSE | -1.9669 | -2.7278 | -0.44085 | -0.59165 | 0 |  |  | none | FALSE | 1 | 72.1045 | FALSE | FALSE | 0.1131 |  | 73.3084 | 0 | 0 | 0.01413 | 0.26692 | -0.052937 | 0.60193 | Normal | 74.5122 | 1.2676 | Night | 202602 | 2026-02-19 | 1.2676
2026-02-19 20:56 | 74.0714 | FALSE | FALSE | -1.9839 | -2.752 | -0.51435 | -0.6896 | 0 |  |  | none | FALSE | 1 | 72.0875 | FALSE | FALSE | 0.107 |  | 73.3366 | 0 | 0 | 0.02826 | 0.25771 | -0.10966 | 0.62455 | Normal | 74.5857 | 1.1765 | Night | 202602 | 2026-02-19 | 1.1765
2026-02-19 21:11 | 74.0714 | FALSE | FALSE | -1.9967 | -2.7703 | -0.58366 | -0.78181 | 0 |  |  | none | FALSE | 1 | 72.0747 | FALSE | FALSE | 0.1016 |  | 73.3649 | 0 | 0 | 0.02826 | 0.25771 | -0.10966 | 0.64508 | Normal | 74.6551 | 1.0952 | Night | 202602 | 2026-02-19 | 1.0952
2026-02-19 21:26 | 74.0714 | FALSE | FALSE | -1.9899 | -2.7607 | -0.66172 | -0.88544 | 0 |  |  | none | FALSE | 0 | 72.0815 | FALSE | FALSE | 0.0668 |  | 73.4073 | 0 | 0 | 0.04239 | 0.2473 | -0.17141 | 0.66291 | Normal | 74.7331 | 1.0018 | Night | 202602 | 2026-02-19 | 1.0018
2026-02-19 21:41 | 74.0714 | FALSE | FALSE | -1.9767 | -2.7418 | -0.73327 | -0.98025 | 0 |  |  | none | FALSE | 0 | 72.0947 | FALSE | FALSE | 0.0612 |  | 73.4497 | 0 | 0 | 0.04239 | 0.2473 | -0.17141 | 0.6775 | Normal | 74.8047 | 0.91767 | Night | 202602 | 2026-02-19 | 0.91767
2026-02-19 21:56 | 74.3522 | FALSE | FALSE | -2.2544 | -3.1269 | -0.56221 | -0.75047 | 0.2808 |  |  | none | FALSE | 0 | 72.0978 | FALSE | FALSE | 0.0801 |  | 73.5061 | 0 | 0.2808 | 0.05643 | 0.25268 | 0.88796 | 0.70415 | Normal | 74.9144 | 1.2016 | Night | 202602 | 2026-02-19 | 1.2016
2026-02-19 22:11 | 74.3522 | FALSE | FALSE | -2.2401 | -3.1064 | -0.66079 | -0.88091 | 0 |  |  | none | FALSE | 0 | 72.1121 | FALSE | FALSE | 0.0726 |  | 73.5625 | 0 | 0 | 0.05643 | 0.25268 | -0.22333 | 0.72523 | Normal | 75.013 | 1.0888 | Night | 202602 | 2026-02-19 | 1.0888
2026-02-19 22:26 | 74.3522 | FALSE | FALSE | -2.1795 | -3.0199 | -0.74131 | -0.98718 | 0 |  |  | none | FALSE | 0 | 72.1727 | FALSE | FALSE | 0.0657 |  | 73.6331 | 0 | 0 | 0.07056 | 0.24032 | -0.2936 | 0.73021 | Normal | 75.0935 | 0.98479 | Night | 202602 | 2026-02-19 | 0.98479
2026-02-19 22:41 | 74.3522 | FALSE | FALSE | -2.0527 | -2.8391 | -0.78385 | -1.0432 | 0 |  |  | none | FALSE | 0 | 72.2995 | FALSE | FALSE | 0.0596 |  | 73.7178 | 0 | 0 | 0.08469 | 0.22637 | -0.37412 | 0.70913 | Normal | 75.136 | 0.89463 | Night | 202602 | 2026-02-19 | 0.89463
2026-02-19 22:56 | 74.3522 | FALSE | FALSE | -1.9024 | -2.6258 | -0.80295 | -1.0684 | 0 |  |  | none | FALSE | 0 | 72.4498 | FALSE | FALSE | 0.0542 |  | 73.8025 | 0 | 0 | 0.08469 | 0.22637 | -0.37412 | 0.67633 | Normal | 75.1551 | 0.81279 | Night | 202602 | 2026-02-19 | 0.81279
2026-02-19 23:11 | 74.3522 | FALSE | FALSE | -1.6441 | -2.2612 | -0.74229 | -0.98848 | 0 |  |  | none | FALSE | 0 | 72.7081 | FALSE | FALSE | 0.0504 |  | 73.9013 | 0 | 0 | 0.09882 | 0.2105 | -0.46945 | 0.5966 | Normal | 75.0945 | 0.75579 | Night | 202602 | 2026-02-19 | 0.75579
2026-02-19 23:26 | 74.0714 | FALSE | FALSE | -1.0391 | -1.4227 | -0.86841 | -1.1588 | -0.2808 |  |  | none | FALSE | 0 | 73.0323 | FALSE | FALSE | 0.0119 |  | 73.9861 | 0 | -0.2808 | 0.08478 | 0.22622 | -1.6161 | 0.47687 | Normal | 74.9398 | 0.17892 | Night | 202602 | 2026-02-19 | 0.17892
2026-02-19 23:40 | 74.0714 | FALSE | FALSE | -0.57932 | -0.78827 | -0.57824 | -0.7746 | 0 |  |  | none | FALSE | 0 | 73.4921 | FALSE | FALSE | 0.0001 |  | 74.0709 | 0 | 0 | 0.08478 | 0.22622 | -0.37478 | 0.28939 | Normal | 74.6496 | 0.001866 | Night | 202602 | 2026-02-19 | 0.001866
2026-02-19 23:55 | 74.0714 | FALSE | FALSE | -0.37802 | -0.51296 | -0.46172 | -0.61948 | 0 |  |  | none | FALSE | 0 | 73.6934 | FALSE | FALSE | 0.0133 |  | 74.1132 | 0 | 0 | 0.04239 | 0.13791 | -0.30738 | 0.20993 | Normal | 74.5331 | -0.19935 | Night | 202602 | 2026-02-19 | 0.19935
2026-02-20 00:10 | 74.0714 | FALSE | FALSE | -0.23927 | -0.32407 | -0.37949 | -0.50972 | 0 |  |  | none | FALSE | 0 | 73.8321 | FALSE | FALSE | 0.0302 |  | 74.1415 | 0 | 0 | 0.02826 | 0.12596 | -0.22436 | 0.15469 | Normal | 74.4509 | -0.45323 | Night | 202602 | 2026-02-20 | 0.45323
2026-02-20 00:25 | 74.0714 | FALSE | FALSE | -0.1798 | -0.24333 | -0.34828 | -0.468 | 0 |  |  | none | FALSE | 0 | 73.8916 | FALSE | FALSE | 0.0425 |  | 74.1556 | 0 | 0 | 0.01413 | 0.11087 | -0.12744 | 0.13202 | Normal | 74.4197 | -0.63808 | Night | 202602 | 2026-02-20 | 0.63808
2026-02-20 00:40 | 74.0714 | FALSE | FALSE | -0.1798 | -0.24333 | -0.34828 | -0.468 | 0 |  |  | none | FALSE | 0 | 73.8916 | FALSE | FALSE | 0.0425 |  | 74.1556 | 0 | 0 | 0 | 0.091104 | 0 | 0.13202 | Normal | 74.4197 | -0.63808 | Night | 202602 | 2026-02-20 | 0.63808
2026-02-20 00:55 | 74.0714 | FALSE | FALSE | -0.1798 | -0.24333 | -0.34828 | -0.468 | 0 |  |  | none | FALSE | 0 | 73.8916 | FALSE | FALSE | 0.0425 |  | 74.1556 | 0 | 0 | 0 | 0.091104 | 0 | 0.13202 | Normal | 74.4197 | -0.63808 | Night | 202602 | 2026-02-20 | 0.63808
2026-02-20 01:10 | 74.0714 | FALSE | FALSE | -0.1798 | -0.24333 | -0.34828 | -0.468 | 0 |  |  | none | FALSE | 0 | 73.8916 | FALSE | FALSE | 0.0425 |  | 74.1556 | 0 | 0 | 0 | 0.091104 | 0 | 0.13202 | Normal | 74.4197 | -0.63808 | Night | 202602 | 2026-02-20 | 0.63808
2026-02-20 01:25 | 74.0714 | FALSE | FALSE | -0.1798 | -0.24333 | -0.34828 | -0.468 | 0 |  |  | none | FALSE | 0 | 73.8916 | FALSE | FALSE | 0.0425 |  | 74.1556 | 0 | 0 | 0 | 0.091104 | 0 | 0.13202 | Normal | 74.4197 | -0.63808 | Night | 202602 | 2026-02-20 | 0.63808
2026-02-20 01:40 | 74.0714 | FALSE | FALSE | -0.1798 | -0.24333 | -0.34828 | -0.468 | 0 |  |  | none | FALSE | 0 | 73.8916 | FALSE | FALSE | 0.0425 |  | 74.1556 | 0 | 0 | 0 | 0.091104 | 0 | 0.13202 | Normal | 74.4197 | -0.63808 | Night | 202602 | 2026-02-20 | 0.63808
2026-02-20 01:55 | 73.7888 | TRUE | FALSE | 0.043332 | 0.058689 | -0.66209 | -0.8893 | -0.2826 | 2026-02-20 05:24 | 2026-02-20 01:55 | lower | TRUE | 1 | 73.8321 | FALSE | FALSE | 0.2377 | 2.2801 | 74.1415 | 1 | -0.2826 | -0.01413 | 0.11087 | -2.4214 | 0.15469 | Extreme triggered | 74.4509 | -2.2801 | Night | 202602 | 2026-02-20 | 2.2801
2026-02-20 02:10 | 73.7888 | FALSE | FALSE | -0.0078734 | -0.010671 | -0.68503 | -0.91983 | 0 |  | 2026-02-20 01:55 | none | FALSE | 1 | 73.7809 | FALSE | FALSE | 0.2732 | 2.1173 | 74.1274 | 2 | 0 | -0.01413 | 0.11087 | 0.12744 | 0.17323 | Extreme/elevated | 74.4738 | -1.9545 | Night | 202602 | 2026-02-20 | 1.9545
2026-02-20 02:25 | 73.7888 | FALSE | FALSE | -0.053258 | -0.072229 | -0.70216 | -0.94261 | 0 |  | 2026-02-20 01:55 | none | FALSE | 1 | 73.7355 | FALSE | FALSE | 0.3145 | 1.9842 | 74.1132 | 3 | 0 | -0.01413 | 0.11087 | 0.12744 | 0.18885 | Persistent | 74.491 | -1.718 | Night | 202602 | 2026-02-20 | 1.718
2026-02-20 02:39 | 73.5062 | TRUE | FALSE | 0.11348 | 0.15414 | -1.0441 | -1.4005 | -0.2826 |  | 2026-02-20 01:55 | lower | TRUE | 2 | 73.6197 | TRUE | TRUE | 0.4516 | 2.1101 | 74.085 | 4 | -0.2826 | -0.02826 | 0.12596 | -2.0192 | 0.23265 | Persistent | 74.5503 | -2.4878 | Night | 202602 | 2026-02-20 | 2.4878
2026-02-20 02:54 | 73.5062 | FALSE | FALSE | 0.02222 | 0.03022 | -1.0508 | -1.4093 | 0 |  | 2026-02-20 01:55 | lower | TRUE | 2 | 73.5284 | FALSE | TRUE | 0.482 | 2.1054 | 74.0427 | 5 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.25713 | Persistent | 74.557 | -2.0864 | Night | 202602 | 2026-02-20 | 2.0864
2026-02-20 03:09 | 73.5062 | FALSE | FALSE | -0.051123 | -0.069597 | -1.0395 | -1.3945 | 0 |  | 2026-02-20 01:55 | none | FALSE | 2 | 73.4551 | FALSE | FALSE | 0.5208 | 2.0566 | 74.0004 | 6 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.27266 | Persistent | 74.5457 | -1.8125 | Night | 202602 | 2026-02-20 | 1.8125
2026-02-20 03:24 | 73.5062 | FALSE | TRUE | -0.10953 | -0.14923 | -1.0133 | -1.3598 | 0 |  | 2026-02-20 01:55 | none | FALSE | 2 | 73.3967 | FALSE | FALSE | 0.5645 | 1.9927 | 73.9581 | 7 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.28071 | Confirmed/Materialized Shift | 74.5195 | -1.6098 | Night | 202602 | 2026-02-20 | 1.6098
2026-02-20 03:39 | 73.2236 | FALSE | TRUE | 0.059467 | 0.081147 | -1.2967 | -1.74 | -0.2826 |  | 2026-02-20 01:55 | lower | TRUE | 2 | 73.2831 | FALSE | TRUE | 0.6033 | 2.0177 | 73.9017 | 8 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.3093 | Confirmed/Materialized Shift | 74.5203 | -2.1923 | Night | 202602 | 2026-02-20 | 2.1923
2026-02-20 03:54 | 73.2236 | FALSE | TRUE | -0.028991 | -0.039609 | -1.2723 | -1.7078 | 0 |  | 2026-02-20 01:55 | none | FALSE | 2 | 73.1946 | FALSE | FALSE | 0.5845 | 2.0058 | 73.8452 | 9 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.32531 | Confirmed/Materialized Shift | 74.4959 | -1.9109 | Night | 202602 | 2026-02-20 | 1.9109
2026-02-20 04:09 | 73.2236 | FALSE | TRUE | -0.095968 | -0.13123 | -1.2264 | -1.6472 | 0 |  | 2026-02-20 01:55 | none | FALSE | 2 | 73.1276 | FALSE | FALSE | 0.5711 | 1.9762 | 73.7888 | 10 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.33058 | Confirmed/Materialized Shift | 74.45 | -1.7097 | Night | 202602 | 2026-02-20 | 1.7097
2026-02-20 04:24 | 73.2236 | FALSE | TRUE | -0.17002 | -0.23274 | -1.2156 | -1.6331 | 0 |  | 2026-02-20 01:55 | none | FALSE | 1 | 73.0536 | FALSE | FALSE | 0.5292 | 1.9337 | 73.7464 | 11 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.34642 | Confirmed/Materialized Shift | 74.4392 | -1.5092 | Night | 202602 | 2026-02-20 | 1.5092
2026-02-20 04:39 | 73.2236 | FALSE | TRUE | -0.23215 | -0.31805 | -1.193 | -1.6031 | 0 |  | 2026-02-20 01:55 | none | FALSE | 1 | 72.9914 | FALSE | FALSE | 0.5185 | 1.885 | 73.704 | 12 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.35629 | Confirmed/Materialized Shift | 74.4166 | -1.3484 | Night | 202602 | 2026-02-20 | 1.3484
2026-02-20 04:54 | 73.2236 | FALSE | TRUE | -0.28334 | -0.38845 | -1.1594 | -1.5587 | 0 |  | 2026-02-20 01:55 | none | FALSE | 1 | 72.9403 | FALSE | FALSE | 0.5095 | 1.8334 | 73.6616 | 13 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.36068 | Confirmed/Materialized Shift | 74.383 | -1.2144 | Night | 202602 | 2026-02-20 | 1.2144
2026-02-20 05:09 | 73.2236 | FALSE | TRUE | -0.32398 | -0.44441 | -1.1153 | -1.5002 | 0 |  | 2026-02-20 01:55 | none | FALSE | 0 | 72.8996 | FALSE | FALSE | 0.4733 | 1.781 | 73.6192 | 14 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.35981 | Confirmed/Materialized Shift | 74.3389 | -1.0996 | Night | 202602 | 2026-02-20 | 1.0996
2026-02-20 05:24 | 73.2236 | FALSE | FALSE | -0.35399 | -0.48579 | -1.0605 | -1.4276 | 0 |  |  | none | FALSE | 0 | 72.8696 | FALSE | FALSE | 0.0666 |  | 73.5768 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.35362 | Persistence ends | 74.2841 | -0.99895 | Night | 202602 | 2026-02-20 | 0.99895
2026-02-20 05:38 | 72.941 | FALSE | FALSE | -0.14204 | -0.19511 | -1.3007 | -1.752 | -0.2826 |  |  | none | FALSE | 0 | 72.799 | FALSE | FALSE | 0.1071 |  | 73.5203 | 0 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.36068 | Normal | 74.2417 | -1.6062 | Night | 202602 | 2026-02-20 | 1.6062
2026-02-20 05:53 | 72.941 | FALSE | FALSE | -0.19388 | -0.26651 | -1.2395 | -1.6709 | 0 |  |  | none | FALSE | 0 | 72.7471 | FALSE | FALSE | 0.0973 |  | 73.4638 | 0 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.35834 | Normal | 74.1805 | -1.459 | Night | 202602 | 2026-02-20 | 1.459
2026-02-20 06:08 | 72.941 | FALSE | FALSE | -0.22654 | -0.31155 | -1.1591 | -1.5643 | 0 |  |  | none | FALSE | 0 | 72.7145 | FALSE | FALSE | 0.0897 |  | 73.4073 | 0 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.34642 | Normal | 74.1001 | -1.346 | Night | 202602 | 2026-02-20 | 1.346
2026-02-20 06:23 | 72.941 | FALSE | FALSE | -0.23791 | -0.32724 | -1.0575 | -1.429 | 0 |  |  | none | FALSE | 0 | 72.7031 | FALSE | FALSE | 0.0844 |  | 73.3508 | 0 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.32384 | Normal | 73.9985 | -1.2653 | Night | 202602 | 2026-02-20 | 1.2653
2026-02-20 06:38 | 72.941 | FALSE | FALSE | -0.223 | -0.30666 | -0.9295 | -1.2583 | 0 |  |  | none | FALSE | 0 | 72.718 | FALSE | FALSE | 0.0817 |  | 73.2943 | 0 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.28812 | Normal | 73.8705 | -1.226 | Night | 202602 | 2026-02-20 | 1.226
2026-02-20 06:53 | 72.941 | FALSE | FALSE | -0.2362 | -0.32488 | -0.85792 | -1.1625 | 0 |  |  | none | FALSE | 0 | 72.7048 | FALSE | FALSE | 0.0758 |  | 73.2519 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27353 | Normal | 73.7989 | -1.1365 | Night | 202602 | 2026-02-20 | 1.1365
2026-02-20 07:08 | 72.941 | FALSE | FALSE | -0.23289 | -0.3203 | -0.76983 | -1.0444 | 0 |  |  | none | FALSE | 0 | 72.7081 | FALSE | FALSE | 0.0714 |  | 73.2095 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.25068 | Normal | 73.7108 | -1.071 | Day | 202602 | 2026-02-20 | 1.071
2026-02-20 07:23 | 72.941 | FALSE | FALSE | -0.20786 | -0.28579 | -0.66002 | -0.89676 | 0 |  |  | none | FALSE | 0 | 72.7331 | FALSE | FALSE | 0.0695 |  | 73.1671 | 0 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.21697 | Normal | 73.601 | -1.042 | Day | 202602 | 2026-02-20 | 1.042
2026-02-20 07:30 | 72.941 | FALSE | FALSE | -0.2163 | -0.29742 | -0.61194 | -0.83197 | 0 |  |  | none | FALSE | 0 | 72.7247 | FALSE | FALSE | 0.0637 |  | 73.1388 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.20706 | Normal | 73.5529 | -0.95538 | Day | 202602 | 2026-02-20 | 0.95538
2026-02-20 07:45 | 72.941 | FALSE | FALSE | -0.21509 | -0.29576 | -0.55421 | -0.75408 | 0 |  |  | none | FALSE | 0 | 72.7259 | FALSE | FALSE | 0.0588 |  | 73.1106 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.19233 | Normal | 73.4952 | -0.88163 | Day | 202602 | 2026-02-20 | 0.88163
2026-02-20 08:00 | 72.941 | FALSE | FALSE | -0.20176 | -0.27738 | -0.48436 | -0.65967 | 0 |  |  | none | FALSE | 0 | 72.7392 | FALSE | FALSE | 0.0549 |  | 73.0823 | 0 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.17153 | Normal | 73.4254 | -0.82375 | Day | 202602 | 2026-02-20 | 0.82375
2026-02-20 08:15 | 73.2236 | TRUE | FALSE | -0.44392 | -0.60995 | -0.13306 | -0.18139 | 0.2826 |  |  | none | FALSE | 1 | 72.7797 | FALSE | FALSE | 0.1004 |  | 73.0682 | 0 | 0.2826 | -0.01413 | 0.11135 | 2.6647 | 0.14424 | Normal | 73.3567 | 1.0775 | Day | 202602 | 2026-02-20 | 1.0775
2026-02-20 08:30 | 73.5062 | TRUE | FALSE | -0.76696 | -1.0544 | 0.080837 | 0.11009 | 0.2826 | 2026-02-20 09:34 | 2026-02-20 08:30 | upper | TRUE | 2 | 72.7392 | TRUE | FALSE | 0.279 | 2.4713 | 73.0823 | 1 | 0.2826 | 0.01413 | 0.11135 | 2.411 | 0.17153 | Extreme triggered | 73.4254 | 2.4713 | Day | 202602 | 2026-02-20 | 2.4713
2026-02-20 08:45 | 73.5062 | FALSE | FALSE | -0.79769 | -1.0971 | 0.021855 | 0.029741 | 0 |  | 2026-02-20 08:30 | upper | TRUE | 2 | 72.7085 | FALSE | FALSE | 0.3123 | 2.292 | 73.0964 | 2 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.19396 | Extreme/elevated | 73.4843 | 2.1127 | Day | 202602 | 2026-02-20 | 2.1127
2026-02-20 08:45 | 73.5062 | FALSE | FALSE | -0.82177 | -1.1306 | -0.030485 | -0.041456 | 0 |  | 2026-02-20 08:30 | none | FALSE | 2 | 72.6844 | FALSE | FALSE | 0.3524 | 2.147 | 73.1106 | 3 | 0 | 0.01413 | 0.11135 | -0.12689 | 0.21306 | Persistent | 73.5367 | 1.8569 | Day | 202602 | 2026-02-20 | 1.8569
2026-02-20 09:00 | 73.7888 | TRUE | FALSE | -1.1719 | -1.6138 | 0.12809 | 0.17389 | 0.2826 |  | 2026-02-20 08:30 | upper | TRUE | 3 | 72.6169 | TRUE | TRUE | 0.4803 | 2.2329 | 73.1388 | 4 | 0.2826 | 0.02826 | 0.12638 | 2.0125 | 0.26095 | Persistent | 73.6607 | 2.4908 | Day | 202602 | 2026-02-20 | 2.4908
2026-02-20 09:01 | 74.0714 | FALSE | FALSE | -1.5583 | -2.149 | 0.22207 | 0.3007 | 0.2826 |  | 2026-02-20 08:30 | upper | TRUE | 3 | 72.5131 | FALSE | TRUE | 0.5491 | 2.3193 | 73.1812 | 5 | 0.2826 | 0.04239 | 0.13829 | 1.737 | 0.33406 | Persistent | 73.8493 | 2.6647 | Day | 202602 | 2026-02-20 | 2.6647
2026-02-20 09:04 | 74.0714 | FALSE | FALSE | -1.6258 | -2.2442 | 0.069805 | 0.09433 | 0 |  | 2026-02-20 08:30 | upper | TRUE | 3 | 72.4456 | FALSE | TRUE | 0.5739 | 2.296 | 73.2236 | 6 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.389 | Persistent | 74.0016 | 2.1794 | Day | 202602 | 2026-02-20 | 2.1794
2026-02-20 09:19 | 74.0714 | FALSE | TRUE | -1.6709 | -2.3078 | -0.060054 | -0.081011 | 0 |  | 2026-02-20 08:30 | none | FALSE | 3 | 72.4005 | FALSE | FALSE | 0.6098 | 2.2339 | 73.266 | 7 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.43273 | Confirmed/Materialized Shift | 74.1315 | 1.8612 | Day | 202602 | 2026-02-20 | 1.8612
2026-02-20 09:34 | 73.2236 | TRUE | FALSE | -0.82307 | -1.1368 | -0.90785 | -1.2247 | -0.8478 |  |  | none | FALSE | 4 | 72.4005 | TRUE | FALSE | 0.1208 |  | 73.266 | 0 | -0.8478 | 0 | 0.24258 | -3.4949 | 0.43273 | Persistence ends | 74.1315 | -0.097959 | Day | 202602 | 2026-02-20 | 0.097959
2026-02-20 09:44 | 73.2236 | FALSE | FALSE | -0.79573 | -1.0987 | -0.90877 | -1.2259 | 0 |  |  | none | FALSE | 4 | 72.4279 | FALSE | FALSE | 0.1231 |  | 73.2801 | 0 | 0 | 0.01413 | 0.23331 | -0.060564 | 0.42613 | Normal | 74.1324 | -0.13264 | Day | 202602 | 2026-02-20 | 0.13264
2026-02-20 09:59 | 72.941 | FALSE | FALSE | -0.51313 | -0.70847 | -1.1914 | -1.6071 | -0.2826 |  |  | none | FALSE | 3 | 72.4279 | FALSE | FALSE | 0.1388 |  | 73.2801 | 0 | -0.2826 | 0 | 0.24258 | -1.165 | 0.42613 | Normal | 74.1324 | -0.79582 | Day | 202602 | 2026-02-20 | 0.79582
2026-02-20 10:14 | 73.2236 | FALSE | FALSE | -0.76718 | -1.0588 | -0.90848 | -1.2255 | 0.2826 |  |  | none | FALSE | 2 | 72.4564 | FALSE | FALSE | 0.0684 |  | 73.2943 | 0 | 0.2826 | 0.01413 | 0.25068 | 1.071 | 0.41891 | Normal | 74.1321 | -0.16865 | Day | 202602 | 2026-02-20 | 0.16865
2026-02-20 10:30 | 72.941 | FALSE | FALSE | -0.48458 | -0.66878 | -1.1911 | -1.6067 | -0.2826 |  |  | none | FALSE | 2 | 72.4564 | FALSE | FALSE | 0.1134 |  | 73.2943 | 0 | -0.2826 | 0 | 0.25933 | -1.0897 | 0.41891 | Normal | 74.1321 | -0.84325 | Day | 202602 | 2026-02-20 | 0.84325
2026-02-20 10:44 | 72.941 | FALSE | FALSE | -0.48458 | -0.66878 | -1.1911 | -1.6067 | 0 |  |  | none | FALSE | 2 | 72.4564 | FALSE | FALSE | 0.1134 |  | 73.2943 | 0 | 0 | 0 | 0.25933 | 0 | 0.41891 | Normal | 74.1321 | -0.84325 | Day | 202602 | 2026-02-20 | 0.84325
2026-02-20 10:59 | 72.941 | FALSE | FALSE | -0.48458 | -0.66878 | -1.1911 | -1.6067 | 0 |  |  | none | FALSE | 1 | 72.4564 | FALSE | FALSE | 0.0848 |  | 73.2943 | 0 | 0 | 0 | 0.25933 | 0 | 0.41891 | Normal | 74.1321 | -0.84325 | Day | 202602 | 2026-02-20 | 0.84325
2026-02-20 11:14 | 72.941 | FALSE | FALSE | -0.48458 | -0.66878 | -1.1911 | -1.6067 | 0 |  |  | none | FALSE | 1 | 72.4564 | FALSE | FALSE | 0.0848 |  | 73.2943 | 0 | 0 | 0 | 0.25933 | 0 | 0.41891 | Normal | 74.1321 | -0.84325 | Day | 202602 | 2026-02-20 | 0.84325
2026-02-20 11:29 | 72.941 | FALSE | FALSE | -0.48458 | -0.66878 | -1.1911 | -1.6067 | 0 |  |  | none | FALSE | 1 | 72.4564 | FALSE | FALSE | 0.0848 |  | 73.2943 | 0 | 0 | 0 | 0.25933 | 0 | 0.41891 | Normal | 74.1321 | -0.84325 | Day | 202602 | 2026-02-20 | 0.84325
2026-02-20 11:44 | 73.2236 | FALSE | FALSE | -0.73735 | -1.0172 | -0.90691 | -1.2234 | 0.2826 |  |  | none | FALSE | 1 | 72.4863 | FALSE | FALSE | 0.0423 |  | 73.3084 | 0 | 0.2826 | 0.01413 | 0.26692 | 1.0058 | 0.41106 | Normal | 74.1305 | -0.20625 | Day | 202602 | 2026-02-20 | 0.20625
2026-02-20 11:59 | 73.2236 | FALSE | FALSE | -0.70617 | -0.97379 | -0.90399 | -1.2195 | 0 |  |  | none | FALSE | 0 | 72.5174 | FALSE | FALSE | 0.0164 |  | 73.3225 | 0 | 0 | 0.01413 | 0.26692 | -0.052937 | 0.40254 | Normal | 74.1276 | -0.24572 | Day | 202602 | 2026-02-20 | 0.24572
2026-02-20 12:14 | 73.2236 | FALSE | FALSE | -0.67355 | -0.9284 | -0.89963 | -1.2137 | 0 |  |  | none | FALSE | 0 | 72.55 | FALSE | FALSE | 0.0192 |  | 73.3366 | 0 | 0 | 0.01413 | 0.26692 | -0.052937 | 0.3933 | Normal | 74.1232 | -0.28742 | Day | 202602 | 2026-02-20 | 0.28742
2026-02-20 12:29 | 73.5062 | FALSE | FALSE | -0.94362 | -1.3004 | -0.63276 | -0.85348 | 0.2826 |  |  | none | FALSE | 0 | 72.5626 | FALSE | FALSE | 0.0263 |  | 73.3508 | 0 | 0.2826 | 0.01413 | 0.26692 | 1.0058 | 0.3941 | Normal | 74.139 | 0.3944 | Day | 202602 | 2026-02-20 | 0.3944
2026-02-20 12:43 | 73.7888 | FALSE | FALSE | -1.2337 | -1.7003 | -0.38586 | -0.52021 | 0.2826 |  |  | none | FALSE | 0 | 72.5551 | FALSE | FALSE | 0.0698 |  | 73.3649 | 0 | 0.2826 | 0.01413 | 0.26692 | 1.0058 | 0.40488 | Normal | 74.1747 | 1.047 | Day | 202602 | 2026-02-20 | 1.047
2026-02-20 12:58 | 73.5062 | FALSE | FALSE | -0.95106 | -1.3108 | -0.66846 | -0.9012 | -0.2826 |  |  | none | FALSE | 0 | 72.5551 | FALSE | FALSE | 0.0233 |  | 73.3649 | 0 | -0.2826 | 0 | 0.27506 | -1.0274 | 0.40488 | Normal | 74.1747 | 0.34899 | Day | 202602 | 2026-02-20 | 0.34899
2026-02-20 13:14 | 73.7888 | FALSE | FALSE | -1.2395 | -1.7085 | -0.41999 | -0.56596 | 0.2826 |  |  | none | FALSE | 0 | 72.5493 | FALSE | FALSE | 0.0658 |  | 73.379 | 0 | 0.2826 | 0.01413 | 0.28223 | 0.95125 | 0.41488 | Normal | 74.2088 | 0.98768 | Day | 202602 | 2026-02-20 | 0.98768
2026-02-20 13:29 | 73.7888 | FALSE | FALSE | -1.2395 | -1.7085 | -0.41999 | -0.56596 | 0 |  |  | none | FALSE | 0 | 72.5493 | FALSE | FALSE | 0.0658 |  | 73.379 | 0 | 0 | 0 | 0.27506 | 0 | 0.41488 | Normal | 74.2088 | 0.98768 | Day | 202602 | 2026-02-20 | 0.98768
2026-02-20 13:43 | 74.0714 | FALSE | FALSE | -1.5221 | -2.0981 | -0.13739 | -0.18514 | 0.2826 |  |  | none | FALSE | 0 | 72.5493 | FALSE | FALSE | 0.1113 |  | 73.379 | 0 | 0.2826 | 0 | 0.27506 | 1.0274 | 0.41488 | Normal | 74.2088 | 1.6688 | Day | 202602 | 2026-02-20 | 1.6688
2026-02-20 13:58 | 73.7888 | FALSE | FALSE | -1.2126 | -1.6708 | -0.36483 | -0.49199 | -0.2826 |  |  | none | FALSE | 0 | 72.5762 | FALSE | FALSE | 0.0717 |  | 73.3649 | 0 | -0.2826 | -0.01413 | 0.28223 | -0.95125 | 0.39436 | Normal | 74.1536 | 1.0749 | Day | 202602 | 2026-02-20 | 1.0749
2026-02-20 14:13 | 73.7888 | FALSE | FALSE | -1.1823 | -1.6284 | -0.30628 | -0.41336 | 0 |  |  | none | FALSE | 0 | 72.6065 | FALSE | FALSE | 0.0785 |  | 73.3508 | 0 | 0 | -0.01413 | 0.28223 | 0.050066 | 0.37215 | Normal | 74.0951 | 1.177 | Day | 202602 | 2026-02-20 | 1.177
2026-02-20 14:28 | 73.7888 | FALSE | FALSE | -1.1763 | -1.62 | -0.35679 | -0.48121 | 0 |  |  | none | FALSE | 0 | 72.6125 | FALSE | FALSE | 0.0713 |  | 73.379 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.38328 | Normal | 74.1456 | 1.0691 | Day | 202602 | 2026-02-20 | 1.0691
2026-02-20 14:43 | 74.0714 | FALSE | FALSE | -1.4721 | -2.0277 | -0.17215 | -0.23187 | 0.2826 |  |  | none | FALSE | 0 | 72.5993 | FALSE | FALSE | 0.1054 |  | 73.4214 | 0 | 0.2826 | 0.04239 | 0.21058 | 1.1407 | 0.41106 | Normal | 74.2435 | 1.5812 | Day | 202602 | 2026-02-20 | 1.5812
2026-02-20 14:58 | 74.0714 | FALSE | FALSE | -1.4318 | -1.9711 | -0.24487 | -0.32949 | 0 |  |  | none | FALSE | 0 | 72.6396 | FALSE | FALSE | 0.0944 |  | 73.4779 | 0 | 0 | 0.05652 | 0.19665 | -0.28742 | 0.41916 | Normal | 74.3163 | 1.4158 | Day | 202602 | 2026-02-20 | 1.4158
2026-02-20 15:13 | 74.0714 | FALSE | FALSE | -1.4204 | -1.9551 | -0.31827 | -0.42784 | 0 |  |  | none | FALSE | 0 | 72.651 | FALSE | FALSE | 0.0845 |  | 73.5203 | 0 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.43467 | Normal | 74.3897 | 1.2678 | Day | 202602 | 2026-02-20 | 1.2678
2026-02-20 15:28 | 74.0714 | FALSE | FALSE | -1.3522 | -1.8595 | -0.36311 | -0.48782 | 0 |  |  | none | FALSE | 0 | 72.7192 | FALSE | FALSE | 0.0769 |  | 73.5768 | 0 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.42883 | Normal | 74.4345 | 1.1533 | Day | 202602 | 2026-02-20 | 1.1533
2026-02-20 15:43 | 74.0714 | FALSE | FALSE | -1.2678 | -1.7414 | -0.39173 | -0.52607 | 0 |  |  | none | FALSE | 0 | 72.8036 | FALSE | FALSE | 0.0704 |  | 73.6334 | 0 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.41488 | Normal | 74.4631 | 1.0558 | Day | 202602 | 2026-02-20 | 1.0558
2026-02-20 15:58 | 73.7888 | FALSE | FALSE | -0.87796 | -1.2042 | -0.65188 | -0.8757 | -0.2826 |  |  | none | FALSE | 0 | 72.9108 | FALSE | FALSE | 0.0197 |  | 73.6758 | 0 | -0.2826 | 0.04239 | 0.18957 | -1.7143 | 0.38246 | Normal | 74.4407 | 0.29556 | Day | 202602 | 2026-02-20 | 0.29556
2026-02-20 16:13 | 73.7888 | FALSE | FALSE | -0.75371 | -1.032 | -0.61241 | -0.82311 | 0 |  |  | none | FALSE | 0 | 73.0351 | FALSE | FALSE | 0.0138 |  | 73.7181 | 0 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.34153 | Normal | 74.4012 | 0.20686 | Day | 202602 | 2026-02-20 | 0.20686
2026-02-20 16:28 | 73.7888 | FALSE | FALSE | -0.60524 | -0.82701 | -0.54872 | -0.73814 | 0 |  |  | none | FALSE | 0 | 73.1836 | FALSE | FALSE | 0.0065 |  | 73.7605 | 0 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.28849 | Normal | 74.3375 | 0.097959 | Day | 202602 | 2026-02-20 | 0.097959
2026-02-20 16:42 | 73.7888 | FALSE | FALSE | -0.51866 | -0.70788 | -0.51866 | -0.698 | 0 |  |  | none | FALSE | 0 | 73.2701 | FALSE | FALSE | 0 |  | 73.7888 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.25933 | Normal | 74.3075 | 0 | Day | 202602 | 2026-02-20 | 0
2026-02-20 16:57 | 73.7888 | FALSE | FALSE | -0.41716 | -0.56855 | -0.47368 | -0.63784 | 0 |  |  | none | FALSE | 0 | 73.3716 | FALSE | FALSE | 0.0085 |  | 73.8171 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.22271 | Normal | 74.2625 | -0.12689 | Day | 202602 | 2026-02-20 | 0.12689
2026-02-20 17:12 | 73.7888 | FALSE | FALSE | -0.29141 | -0.39649 | -0.40445 | -0.54513 | 0 |  |  | none | FALSE | 0 | 73.4974 | FALSE | FALSE | 0.0217 |  | 73.8453 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.17396 | Normal | 74.1932 | -0.32489 | Day | 202602 | 2026-02-20 | 0.32489
2026-02-20 17:27 | 73.5062 | FALSE | FALSE | -0.0088098 | -0.011987 | -0.68705 | -0.92603 | -0.2826 |  |  | none | FALSE | 0 | 73.4974 | FALSE | FALSE | 0.13 |  | 73.8453 | 0 | -0.2826 | 0 | 0.18338 | -1.5411 | 0.17396 | Normal | 74.1932 | -1.9494 | Day | 202602 | 2026-02-20 | 1.9494
2026-02-20 17:42 | 73.5062 | FALSE | FALSE | -0.054158 | -0.073732 | -0.70414 | -0.94884 | 0 |  |  | none | FALSE | 0 | 73.452 | FALSE | FALSE | 0.1143 |  | 73.8312 | 0 | 0 | -0.01413 | 0.17092 | 0.082671 | 0.18957 | Normal | 74.2103 | -1.7143 | Day | 202602 | 2026-02-20 | 1.7143
2026-02-20 17:57 | 73.2236 | FALSE | FALSE | 0.14804 | 0.20177 | -1.0389 | -1.3989 | -0.2826 | 2026-02-20 18:57 | 2026-02-20 17:57 | lower | TRUE | 0 | 73.3716 | FALSE | FALSE | 0.2348 | 2.6647 | 73.8171 | 1 | -0.2826 | -0.01413 | 0.17092 | -1.5708 | 0.22271 | Extreme triggered | 74.2625 | -2.6647 | Day | 202602 | 2026-02-20 | 2.6647
2026-02-20 18:12 | 73.2236 | FALSE | FALSE | 0.046537 | 0.063514 | -1.0839 | -1.4586 | 0 |  | 2026-02-20 17:57 | lower | TRUE | 0 | 73.2701 | FALSE | FALSE | 0.2596 | 2.4221 | 73.7888 | 2 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.25933 | Extreme/elevated | 74.3075 | -2.1794 | Day | 202602 | 2026-02-20 | 2.1794
2026-02-20 18:27 | 72.941 | FALSE | FALSE | 0.16294 | 0.22289 | -1.4479 | -1.9464 | -0.2826 |  | 2026-02-20 17:57 | lower | TRUE | 0 | 73.1039 | FALSE | TRUE | 0.3386 | 2.4505 | 73.7464 | 3 | -0.2826 | -0.04239 | 0.16593 | -1.4477 | 0.32123 | Persistent | 74.3889 | -2.5072 | Night | 202602 | 2026-02-20 | 2.5072
2026-02-20 18:42 | 72.941 | FALSE | FALSE | 0.032201 | 0.044127 | -1.4656 | -1.9697 | 0 |  | 2026-02-20 17:57 | lower | TRUE | 0 | 72.9732 | FALSE | TRUE | 0.3679 | 2.3603 | 73.6899 | 4 | 0 | -0.05652 | 0.14784 | 0.3823 | 0.35834 | Persistent | 74.4066 | -2.0899 | Night | 202602 | 2026-02-20 | 2.0899
2026-02-20 18:42 | 72.941 | FALSE | FALSE | -0.082226 | -0.11286 | -1.4952 | -2.0087 | 0 |  | 2026-02-20 17:57 | none | FALSE | 0 | 72.8588 | FALSE | FALSE | 0.4051 | 2.2466 | 73.6475 | 5 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.39436 | Persistent | 74.4362 | -1.7915 | Night | 202602 | 2026-02-20 | 1.7915
2026-02-20 18:42 | 72.941 | FALSE | FALSE | -0.1817 | -0.24973 | -1.5099 | -2.0281 | 0 |  | 2026-02-20 17:57 | none | FALSE | 0 | 72.7593 | FALSE | FALSE | 0.4475 | 2.1339 | 73.6051 | 6 | 0 | -0.04239 | 0.13829 | 0.30652 | 0.42291 | Persistent | 74.4509 | -1.5703 | Night | 202602 | 2026-02-20 | 1.5703
2026-02-20 18:57 | 73.5062 | TRUE | FALSE | -0.75755 | -1.0413 | -0.92711 | -1.2456 | 0.5652 |  |  | none | FALSE | 1 | 72.7487 | FALSE | FALSE | 0.042 |  | 73.591 | 0 | 0.5652 | -0.01413 | 0.19396 | 2.9869 | 0.42116 | Persistence ends | 74.4333 | -0.2013 | Night | 202602 | 2026-02-20 | 0.2013
2026-02-20 19:12 | 74.0714 | TRUE | FALSE | -1.3227 | -1.8182 | -0.36191 | -0.48622 | 0.5652 |  |  | none | FALSE | 2 | 72.7487 | TRUE | FALSE | 0.1332 |  | 73.591 | 0 | 0.5652 | 0 | 0.22459 | 2.5166 | 0.42116 | Normal | 74.4333 | 1.1407 | Night | 202602 | 2026-02-20 | 1.1407
2026-02-20 19:27 | 74.0714 | FALSE | FALSE | -1.3227 | -1.8182 | -0.36191 | -0.48622 | 0 |  |  | none | FALSE | 2 | 72.7487 | FALSE | FALSE | 0.1332 |  | 73.591 | 0 | 0 | 0 | 0.22459 | 0 | 0.42116 | Normal | 74.4333 | 1.1407 | Night | 202602 | 2026-02-20 | 1.1407
2026-02-20 19:41 | 74.0714 | FALSE | FALSE | -1.3227 | -1.8182 | -0.36191 | -0.48622 | 0 |  |  | none | FALSE | 2 | 72.7487 | FALSE | FALSE | 0.1332 |  | 73.591 | 0 | 0 | 0 | 0.22459 | 0 | 0.42116 | Normal | 74.4333 | 1.1407 | Night | 202602 | 2026-02-20 | 1.1407
2026-02-20 19:56 | 74.0714 | FALSE | FALSE | -1.3227 | -1.8182 | -0.36191 | -0.48622 | 0 |  |  | none | FALSE | 2 | 72.7487 | FALSE | FALSE | 0.1332 |  | 73.591 | 0 | 0 | 0 | 0.22459 | 0 | 0.42116 | Normal | 74.4333 | 1.1407 | Night | 202602 | 2026-02-20 | 1.1407
2026-02-20 20:11 | 74.0714 | FALSE | FALSE | -1.3227 | -1.8182 | -0.36191 | -0.48622 | 0 |  |  | none | FALSE | 2 | 72.7487 | FALSE | FALSE | 0.1332 |  | 73.591 | 0 | 0 | 0 | 0.22459 | 0 | 0.42116 | Normal | 74.4333 | 1.1407 | Night | 202602 | 2026-02-20 | 1.1407
2026-02-20 20:26 | 74.3522 | FALSE | FALSE | -1.6385 | -2.2534 | -0.17245 | -0.2314 | 0.2808 |  |  | none | FALSE | 2 | 72.7137 | FALSE | FALSE | 0.1651 |  | 73.6192 | 0 | 0.2808 | 0.02817 | 0.2226 | 1.1349 | 0.45275 | Normal | 74.5246 | 1.6191 | Night | 202602 | 2026-02-20 | 1.6191
2026-02-20 20:41 | 74.3522 | FALSE | FALSE | -1.666 | -2.292 | -0.25619 | -0.34338 | 0 |  |  | none | FALSE | 2 | 72.6862 | FALSE | FALSE | 0.1549 |  | 73.6473 | 0 | 0 | 0.02817 | 0.2226 | -0.12655 | 0.48054 | Normal | 74.6084 | 1.4669 | Night | 202602 | 2026-02-20 | 1.4669
2026-02-20 20:56 | 74.3522 | FALSE | FALSE | -1.687 | -2.3216 | -0.33359 | -0.44666 | 0 |  |  | none | FALSE | 2 | 72.6652 | FALSE | FALSE | 0.1465 |  | 73.6755 | 0 | 0 | 0.02817 | 0.2226 | -0.12655 | 0.50515 | Normal | 74.6858 | 1.3396 | Night | 202602 | 2026-02-20 | 1.3396
2026-02-20 21:11 | 74.3522 | FALSE | FALSE | -1.7026 | -2.3436 | -0.40553 | -0.54246 | 0 |  |  | none | FALSE | 2 | 72.6496 | FALSE | FALSE | 0.1392 |  | 73.7037 | 0 | 0 | 0.02817 | 0.2226 | -0.12655 | 0.52704 | Normal | 74.7577 | 1.2305 | Night | 202602 | 2026-02-20 | 1.2305
2026-02-20 21:26 | 74.3522 | FALSE | FALSE | -1.7134 | -2.3588 | -0.47267 | -0.63171 | 0 |  |  | none | FALSE | 1 | 72.6388 | FALSE | FALSE | 0.1042 |  | 73.7318 | 0 | 0 | 0.02817 | 0.2226 | -0.12655 | 0.54652 | Normal | 74.8249 | 1.1351 | Night | 202602 | 2026-02-20 | 1.1351
2026-02-20 21:41 | 74.3522 | FALSE | FALSE | -1.7199 | -2.368 | -0.53552 | -0.71509 | 0 |  |  | none | FALSE | 0 | 72.6323 | FALSE | FALSE | 0.07 |  | 73.76 | 0 | 0 | 0.02817 | 0.2226 | -0.12655 | 0.56386 | Normal | 74.8877 | 1.0503 | Night | 202602 | 2026-02-20 | 1.0503
2026-02-20 21:56 | 74.6348 | FALSE | FALSE | -2.0041 | -2.7593 | -0.36733 | -0.48976 | 0.2826 |  |  | none | FALSE | 0 | 72.6307 | FALSE | FALSE | 0.092 |  | 73.8164 | 0 | 0.2826 | 0.05643 | 0.21687 | 1.0429 | 0.59285 | Normal | 75.0021 | 1.3804 | Night | 202602 | 2026-02-20 | 1.3804
2026-02-20 22:11 | 74.6348 | FALSE | FALSE | -1.9921 | -2.7423 | -0.46819 | -0.62339 | 0 |  |  | none | FALSE | 0 | 72.6427 | FALSE | FALSE | 0.0826 |  | 73.8729 | 0 | 0 | 0.05643 | 0.21687 | -0.2602 | 0.61506 | Normal | 75.103 | 1.2388 | Night | 202602 | 2026-02-20 | 1.2388
2026-02-20 22:26 | 74.3522 | FALSE | FALSE | -1.631 | -2.2428 | -0.78516 | -1.045 | -0.2826 |  |  | none | FALSE | 0 | 72.7212 | FALSE | FALSE | 0.0467 |  | 73.9293 | 0 | -0.2826 | 0.05643 | 0.21687 | -1.5633 | 0.60403 | Normal | 75.1374 | 0.70014 | Night | 202602 | 2026-02-20 | 0.70014
2026-02-20 22:40 | 74.6348 | FALSE | FALSE | -1.8343 | -2.5196 | -0.56439 | -0.75053 | 0.2826 |  |  | none | FALSE | 0 | 72.8005 | FALSE | FALSE | 0.0706 |  | 73.9998 | 0 | 0.2826 | 0.07056 | 0.22215 | 0.95451 | 0.59967 | Normal | 75.1992 | 1.0588 | Night | 202602 | 2026-02-20 | 1.0588
2026-02-20 22:55 | 74.6348 | FALSE | FALSE | -1.6714 | -2.2908 | -0.57093 | -0.75915 | 0 |  |  | none | FALSE | 0 | 72.9634 | FALSE | FALSE | 0.0654 |  | 74.0845 | 0 | 0 | 0.08469 | 0.20697 | -0.40919 | 0.56059 | Normal | 75.2057 | 0.98157 | Night | 202602 | 2026-02-20 | 0.98157
2026-02-20 23:11 | 74.3522 | FALSE | FALSE | -1.185 | -1.6195 | -0.79076 | -1.0523 | -0.2826 |  |  | none | FALSE | 0 | 73.1672 | FALSE | FALSE | 0.0266 |  | 74.1551 | 0 | -0.2826 | 0.07056 | 0.22215 | -1.5898 | 0.49393 | Normal | 75.143 | 0.39904 | Night | 202602 | 2026-02-20 | 0.39904
2026-02-20 23:26 | 74.6348 | FALSE | FALSE | -1.2219 | -1.6645 | -0.43191 | -0.57537 | 0.2826 |  |  | none | FALSE | 0 | 73.4129 | FALSE | FALSE | 0.0637 |  | 74.2398 | 0 | 0.2826 | 0.08469 | 0.22637 | 0.87428 | 0.41346 | Normal | 75.0667 | 0.95538 | Night | 202602 | 2026-02-20 | 0.95538
2026-02-20 23:40 | 74.3522 | FALSE | FALSE | -0.59896 | -0.81211 | -0.51526 | -0.68822 | -0.2826 |  |  | none | FALSE | 0 | 73.7532 | FALSE | FALSE | 0.01 |  | 74.3103 | 0 | -0.2826 | 0.07056 | 0.24032 | -1.4695 | 0.27855 | Normal | 74.8675 | 0.15024 | Night | 202602 | 2026-02-20 | 0.15024
2026-02-20 23:55 | 74.3522 | FALSE | FALSE | -0.40828 | -0.55215 | -0.40918 | -0.54732 | 0 |  |  | none | FALSE | 0 | 73.9439 | FALSE | FALSE | 0.0001 |  | 74.3526 | 0 | 0 | 0.0423 | 0.21047 | -0.20097 | 0.20437 | Normal | 74.7614 | -0.0022019 | Night | 202602 | 2026-02-20 | 0.0022019
2026-02-21 00:10 | 74.3522 | FALSE | FALSE | -0.37227 | -0.5032 | -0.40125 | -0.53676 | 0 |  |  | none | FALSE | 0 | 73.9799 | FALSE | FALSE | 0.005 |  | 74.3667 | 0 | 0 | 0.01404 | 0.17077 | -0.082216 | 0.19338 | Normal | 74.7534 | -0.074931 | Night | 202602 | 2026-02-21 | 0.074931
2026-02-21 00:25 | 74.3522 | FALSE | FALSE | -0.33263 | -0.44938 | -0.38969 | -0.52138 | 0 |  |  | none | FALSE | 0 | 74.0196 | FALSE | FALSE | 0.0105 |  | 74.3807 | 0 | 0 | 0.01404 | 0.17077 | -0.082216 | 0.18058 | Normal | 74.7419 | -0.15799 | Night | 202602 | 2026-02-21 | 0.15799
2026-02-21 00:40 | 74.3522 | FALSE | FALSE | -0.28854 | -0.38959 | -0.37368 | -0.50007 | 0 |  |  | none | FALSE | 0 | 74.0637 | FALSE | FALSE | 0.0171 |  | 74.3948 | 0 | 0 | 0.01404 | 0.17077 | -0.082216 | 0.16556 | Normal | 74.7259 | -0.25713 | Night | 202602 | 2026-02-21 | 0.25713
2026-02-21 00:55 | 74.0714 | FALSE | FALSE | -0.007742 | -0.010453 | -0.65448 | -0.87584 | -0.2808 |  |  | none | FALSE | 0 | 74.0637 | FALSE | FALSE | 0.1302 |  | 74.3948 | 0 | -0.2808 | 0 | 0.18308 | -1.5337 | 0.16556 | Normal | 74.7259 | -1.9532 | Night | 202602 | 2026-02-21 | 1.9532
2026-02-21 01:10 | 74.0714 | FALSE | FALSE | -0.007742 | -0.010453 | -0.65448 | -0.87584 | 0 |  |  | none | FALSE | 0 | 74.0637 | FALSE | FALSE | 0.1302 |  | 74.3948 | 0 | 0 | 0 | 0.18308 | 0 | 0.16556 | Normal | 74.7259 | -1.9532 | Night | 202602 | 2026-02-21 | 1.9532
2026-02-21 01:25 | 74.0714 | FALSE | FALSE | -0.051832 | -0.070025 | -0.67049 | -0.89708 | 0 |  |  | none | FALSE | 0 | 74.0196 | FALSE | FALSE | 0.1142 |  | 74.3807 | 0 | 0 | -0.01404 | 0.17077 | 0.082216 | 0.18058 | Normal | 74.7419 | -1.713 | Night | 202602 | 2026-02-21 | 1.713
2026-02-21 01:40 | 74.0714 | FALSE | FALSE | -0.091467 | -0.12364 | -0.68205 | -0.9124 | 0 |  |  | none | FALSE | 0 | 73.9799 | FALSE | FALSE | 0.1018 |  | 74.3667 | 0 | 0 | -0.01404 | 0.17077 | 0.082216 | 0.19338 | Normal | 74.7534 | -1.527 | Night | 202602 | 2026-02-21 | 1.527
2026-02-21 01:55 | 73.7888 | FALSE | FALSE | 0.084422 | 0.11428 | -1.015 | -1.3569 | -0.2826 | 2026-02-21 08:00 | 2026-02-21 01:55 | lower | TRUE | 0 | 73.8732 | FALSE | FALSE | 0.2147 | 2.3629 | 74.3385 | 1 | -0.2826 | -0.02817 | 0.18094 | -1.4062 | 0.23265 | Extreme triggered | 74.8038 | -2.3629 | Night | 202602 | 2026-02-21 | 2.3629
2026-02-21 02:10 | 73.7888 | FALSE | FALSE | -0.0045116 | -0.0061146 | -1.0476 | -1.3999 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 73.7843 | FALSE | FALSE | 0.2465 | 2.1729 | 74.3103 | 2 | 0 | -0.02817 | 0.18094 | 0.15569 | 0.26303 | Extreme/elevated | 74.8364 | -1.9828 | Night | 202602 | 2026-02-21 | 1.9828
2026-02-21 02:25 | 73.7888 | FALSE | FALSE | -0.081335 | -0.11035 | -1.0681 | -1.4268 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 73.7075 | FALSE | FALSE | 0.2859 | 2.0209 | 74.2822 | 3 | 0 | -0.02817 | 0.18094 | 0.15569 | 0.28736 | Persistent | 74.8569 | -1.717 | Night | 202602 | 2026-02-21 | 1.717
2026-02-21 02:39 | 73.7888 | FALSE | FALSE | -0.14893 | -0.20224 | -1.0794 | -1.4417 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 73.6399 | FALSE | FALSE | 0.3296 | 1.8944 | 74.254 | 4 | 0 | -0.02817 | 0.18094 | 0.15569 | 0.30707 | Persistent | 74.8682 | -1.515 | Night | 202602 | 2026-02-21 | 1.515
2026-02-21 02:54 | 73.7888 | FALSE | FALSE | -0.19731 | -0.26811 | -1.0431 | -1.394 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 73.5915 | FALSE | FALSE | 0.3766 | 1.7883 | 74.2117 | 5 | 0 | -0.0423 | 0.16579 | 0.25514 | 0.31011 | Persistent | 74.8319 | -1.3637 | Night | 202602 | 2026-02-21 | 1.3637
2026-02-21 03:09 | 73.5062 | FALSE | FALSE | -0.013013 | -0.017707 | -1.3112 | -1.7525 | -0.2826 |  | 2026-02-21 01:55 | none | FALSE | 0 | 73.4932 | FALSE | FALSE | 0.4736 | 1.817 | 74.1553 | 6 | -0.2826 | -0.05643 | 0.17384 | -1.301 | 0.33105 | Persistent | 74.8174 | -1.9607 | Night | 202602 | 2026-02-21 | 1.9607
2026-02-21 03:24 | 73.5062 | FALSE | TRUE | -0.10832 | -0.14758 | -1.3219 | -1.7666 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 73.3979 | FALSE | FALSE | 0.5131 | 1.7999 | 74.113 | 7 | 0 | -0.0423 | 0.16579 | 0.25514 | 0.35755 | Confirmed/Materialized Shift | 74.8281 | -1.6971 | Night | 202602 | 2026-02-21 | 1.6971
2026-02-21 03:39 | 73.5062 | FALSE | TRUE | -0.16947 | -0.23109 | -1.2702 | -1.6986 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 73.3367 | FALSE | FALSE | 0.5019 | 1.766 | 74.0566 | 8 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.35991 | Confirmed/Materialized Shift | 74.7764 | -1.5291 | Night | 202602 | 2026-02-21 | 1.5291
2026-02-21 03:54 | 73.5062 | FALSE | TRUE | -0.21185 | -0.28904 | -1.1997 | -1.6059 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 73.2944 | FALSE | FALSE | 0.4933 | 1.7253 | 74.0001 | 9 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.35288 | Confirmed/Materialized Shift | 74.7059 | -1.3997 | Night | 202602 | 2026-02-21 | 1.3997
2026-02-21 04:09 | 73.5062 | FALSE | TRUE | -0.2666 | -0.36401 | -1.1698 | -1.5666 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 73.2396 | FALSE | FALSE | 0.4838 | 1.6786 | 73.9578 | 10 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.35911 | Confirmed/Materialized Shift | 74.676 | -1.2576 | Night | 202602 | 2026-02-21 | 1.2576
2026-02-21 04:24 | 73.2236 | FALSE | TRUE | -0.051797 | -0.070789 | -1.3791 | -1.8486 | -0.2826 |  | 2026-02-21 01:55 | none | FALSE | 0 | 73.1718 | FALSE | FALSE | 0.5237 | 1.6946 | 73.8873 | 11 | -0.2826 | -0.07056 | 0.12539 | -1.6911 | 0.35773 | Confirmed/Materialized Shift | 74.6027 | -1.8552 | Night | 202602 | 2026-02-21 | 1.8552
2026-02-21 04:39 | 73.2236 | FALSE | TRUE | -0.13148 | -0.17988 | -1.3459 | -1.8049 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 73.0921 | FALSE | FALSE | 0.5096 | 1.6904 | 73.8308 | 12 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.36935 | Confirmed/Materialized Shift | 74.5695 | -1.644 | Night | 202602 | 2026-02-21 | 1.644
2026-02-21 04:54 | 73.2236 | FALSE | TRUE | -0.19262 | -0.26376 | -1.2942 | -1.7368 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 73.031 | FALSE | FALSE | 0.4988 | 1.6744 | 73.7744 | 13 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.37171 | Confirmed/Materialized Shift | 74.5178 | -1.4818 | Night | 202602 | 2026-02-21 | 1.4818
2026-02-21 05:09 | 73.2236 | FALSE | TRUE | -0.2356 | -0.32279 | -1.2243 | -1.6446 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 72.988 | FALSE | FALSE | 0.4903 | 1.6515 | 73.718 | 14 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.36499 | Confirmed/Materialized Shift | 74.4479 | -1.3545 | Night | 202602 | 2026-02-21 | 1.3545
2026-02-21 05:24 | 73.2236 | FALSE | TRUE | -0.25935 | -0.35545 | -1.1352 | -1.5267 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 72.9642 | FALSE | FALSE | 0.4837 | 1.6251 | 73.6615 | 15 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.34865 | Confirmed/Materialized Shift | 74.3588 | -1.2561 | Night | 202602 | 2026-02-21 | 1.2561
2026-02-21 05:38 | 73.2236 | FALSE | TRUE | -0.26096 | -0.35766 | -1.024 | -1.3791 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 72.9626 | FALSE | FALSE | 0.4792 | 1.5978 | 73.6051 | 16 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.32123 | Confirmed/Materialized Shift | 74.2476 | -1.1876 | Night | 202602 | 2026-02-21 | 1.1876
2026-02-21 05:53 | 73.2236 | FALSE | TRUE | -0.28543 | -0.39134 | -0.96367 | -1.299 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 72.9382 | FALSE | FALSE | 0.4724 | 1.5677 | 73.5627 | 17 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.31228 | Confirmed/Materialized Shift | 74.1873 | -1.086 | Night | 202602 | 2026-02-21 | 1.086
2026-02-21 06:08 | 72.941 | FALSE | TRUE | -0.07003 | -0.096101 | -1.2004 | -1.6191 | -0.2826 |  | 2026-02-21 01:55 | none | FALSE | 0 | 72.871 | FALSE | FALSE | 0.5186 | 1.5795 | 73.5062 | 18 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.31761 | Confirmed/Materialized Shift | 74.1414 | -1.7795 | Night | 202602 | 2026-02-21 | 1.7795
2026-02-21 06:23 | 72.941 | FALSE | TRUE | -0.11587 | -0.15911 | -1.1332 | -1.5299 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 72.8251 | FALSE | FALSE | 0.5086 | 1.5821 | 73.4497 | 19 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.31228 | Confirmed/Materialized Shift | 74.0742 | -1.6289 | Night | 202602 | 2026-02-21 | 1.6289
2026-02-21 06:38 | 72.941 | FALSE | TRUE | -0.13921 | -0.19121 | -1.0435 | -1.4105 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 72.8018 | FALSE | FALSE | 0.5019 | 1.5794 | 73.3932 | 20 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.29568 | Confirmed/Materialized Shift | 73.9845 | -1.5292 | Night | 202602 | 2026-02-21 | 1.5292
2026-02-21 06:53 | 72.941 | FALSE | TRUE | -0.18373 | -0.25252 | -1.0033 | -1.3568 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 72.7573 | FALSE | FALSE | 0.4921 | 1.57 | 73.3508 | 21 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.29675 | Confirmed/Materialized Shift | 73.9443 | -1.3809 | Night | 202602 | 2026-02-21 | 1.3809
2026-02-21 07:08 | 72.941 | FALSE | TRUE | -0.2154 | -0.29618 | -0.95016 | -1.2859 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 72.7256 | FALSE | FALSE | 0.4841 | 1.5559 | 73.3084 | 22 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.29139 | Confirmed/Materialized Shift | 73.8912 | -1.2608 | Day | 202602 | 2026-02-21 | 1.2608
2026-02-21 07:23 | 72.941 | FALSE | TRUE | -0.23348 | -0.32112 | -0.88346 | -1.1967 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 72.7075 | FALSE | FALSE | 0.4776 | 1.5389 | 73.266 | 23 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.27923 | Confirmed/Materialized Shift | 73.8245 | -1.1639 | Day | 202602 | 2026-02-21 | 1.1639
2026-02-21 07:30 | 72.941 | FALSE | TRUE | -0.23606 | -0.32469 | -0.80126 | -1.0866 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 72.7049 | FALSE | FALSE | 0.4726 | 1.5202 | 73.2236 | 24 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.25933 | Confirmed/Materialized Shift | 73.7423 | -1.0897 | Day | 202602 | 2026-02-21 | 1.0897
2026-02-21 07:45 | 72.941 | FALSE | TRUE | -0.21914 | -0.30135 | -0.69956 | -0.94997 | 0 |  | 2026-02-21 01:55 | none | FALSE | 0 | 72.7219 | FALSE | FALSE | 0.4697 | 1.5012 | 73.1812 | 25 | 0 | -0.04239 | 0.10353 | 0.40945 | 0.22968 | Confirmed/Materialized Shift | 73.6406 | -1.0459 | Day | 202602 | 2026-02-21 | 1.0459
2026-02-21 08:00 | 73.2236 | TRUE | FALSE | -0.49046 | -0.67433 | -0.37742 | -0.5128 | 0.2826 |  |  | none | FALSE | 1 | 72.7331 | FALSE | FALSE | 0.0459 |  | 73.1671 | 0 | 0.2826 | -0.01413 | 0.11135 | 2.6647 | 0.21697 | Persistence ends | 73.601 | 0.26049 | Day | 202602 | 2026-02-21 | 0.26049
2026-02-21 08:15 | 73.2236 | FALSE | FALSE | -0.47553 | -0.65367 | -0.33423 | -0.45438 | 0 |  |  | none | FALSE | 1 | 72.7481 | FALSE | FALSE | 0.0518 |  | 73.153 | 0 | 0 | -0.01413 | 0.11135 | 0.12689 | 0.20244 | Normal | 73.5578 | 0.34899 | Day | 202602 | 2026-02-21 | 0.34899
2026-02-21 08:30 | 73.5062 | TRUE | FALSE | -0.75813 | -1.0421 | -0.051631 | -0.070191 | 0.2826 |  |  | none | FALSE | 2 | 72.7481 | TRUE | FALSE | 0.1735 |  | 73.153 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.20244 | Normal | 73.5578 | 1.745 | Day | 202602 | 2026-02-21 | 1.745
2026-02-21 08:45 | 73.7888 | FALSE | FALSE | -1.0928 | -1.5033 | 0.15062 | 0.20454 | 0.2826 | 2026-02-21 09:27 | 2026-02-21 08:45 | upper | TRUE | 2 | 72.696 | FALSE | FALSE | 0.2902 | 2.6394 | 73.1671 | 1 | 0.2826 | 0.01413 | 0.14424 | 1.8612 | 0.23555 | Extreme triggered | 73.6382 | 2.6394 | Day | 202602 | 2026-02-21 | 2.6394
2026-02-21 08:45 | 73.7888 | FALSE | FALSE | -1.1351 | -1.5623 | 0.080088 | 0.10865 | 0 |  | 2026-02-21 08:45 | upper | TRUE | 2 | 72.6537 | FALSE | FALSE | 0.325 | 2.4715 | 73.1812 | 2 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.26375 | Extreme/elevated | 73.7087 | 2.3036 | Day | 202602 | 2026-02-21 | 2.3036
2026-02-21 08:54 | 74.0714 | FALSE | FALSE | -1.509 | -2.0795 | 0.18663 | 0.2526 | 0.2826 |  | 2026-02-21 08:45 | upper | TRUE | 2 | 72.5624 | FALSE | TRUE | 0.3995 | 2.5025 | 73.2236 | 3 | 0.2826 | 0.04239 | 0.13829 | 1.737 | 0.33058 | Persistent | 73.8848 | 2.5646 | Day | 202602 | 2026-02-21 | 2.5646
2026-02-21 08:57 | 74.0714 | FALSE | FALSE | -1.5676 | -2.1621 | 0.043244 | 0.058416 | 0 |  | 2026-02-21 08:45 | upper | TRUE | 2 | 72.5038 | FALSE | TRUE | 0.4266 | 2.4053 | 73.266 | 4 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.38108 | Persistent | 74.0282 | 2.1135 | Day | 202602 | 2026-02-21 | 2.1135
2026-02-21 09:12 | 74.0714 | FALSE | FALSE | -1.6053 | -2.2153 | -0.079309 | -0.10696 | 0 |  | 2026-02-21 08:45 | none | FALSE | 2 | 72.4661 | FALSE | FALSE | 0.4636 | 2.2866 | 73.3084 | 5 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.42116 | Persistent | 74.1507 | 1.8117 | Day | 202602 | 2026-02-21 | 1.8117
2026-02-21 09:27 | 73.2236 | TRUE | FALSE | -0.75755 | -1.0454 | -0.92711 | -1.2503 | -0.8478 |  |  | none | FALSE | 3 | 72.4661 | TRUE | FALSE | 0.0991 |  | 73.3084 | 0 | -0.8478 | 0 | 0.24258 | -3.4949 | 0.42116 | Persistence ends | 74.1507 | -0.2013 | Day | 202602 | 2026-02-21 | 0.2013
2026-02-21 09:42 | 72.6584 | FALSE | FALSE | -0.26911 | -0.37176 | -1.5126 | -2.0393 | -0.5652 |  |  | none | FALSE | 3 | 72.3893 | FALSE | FALSE | 0.1788 |  | 73.2801 | 0 | -0.5652 | -0.02826 | 0.27353 | -1.963 | 0.44542 | Normal | 74.171 | -1.3958 | Day | 202602 | 2026-02-21 | 1.3958
2026-02-21 09:44 | 72.941 | FALSE | FALSE | -0.57849 | -0.79944 | -1.2285 | -1.6563 | 0.2826 |  |  | none | FALSE | 2 | 72.3625 | FALSE | FALSE | 0.1051 |  | 73.266 | 0 | 0.2826 | -0.01413 | 0.28223 | 1.0514 | 0.45174 | Normal | 74.1695 | -0.71942 | Day | 202602 | 2026-02-21 | 0.71942
2026-02-21 09:59 | 72.6584 | FALSE | FALSE | -0.36421 | -0.50378 | -1.5229 | -2.0529 | -0.2826 |  |  | none | FALSE | 2 | 72.2942 | FALSE | FALSE | 0.139 |  | 73.2377 | 0 | -0.2826 | -0.02826 | 0.28849 | -0.88163 | 0.47177 | Normal | 74.1813 | -1.228 | Day | 202602 | 2026-02-21 | 1.228
2026-02-21 10:14 | 72.941 | FALSE | FALSE | -0.64681 | -0.89469 | -1.2403 | -1.6719 | 0.2826 |  |  | none | FALSE | 1 | 72.2942 | FALSE | FALSE | 0.0705 |  | 73.2377 | 0 | 0.2826 | 0 | 0.28994 | 0.97468 | 0.47177 | Normal | 74.1813 | -0.62897 | Day | 202602 | 2026-02-21 | 0.62897
2026-02-21 10:30 | 72.941 | FALSE | FALSE | -0.64681 | -0.89469 | -1.2403 | -1.6719 | 0 |  |  | none | FALSE | 1 | 72.2942 | FALSE | FALSE | 0.0705 |  | 73.2377 | 0 | 0 | 0 | 0.28994 | 0 | 0.47177 | Normal | 74.1813 | -0.62897 | Day | 202602 | 2026-02-21 | 0.62897
2026-02-21 10:44 | 72.941 | FALSE | FALSE | -0.64681 | -0.89469 | -1.2403 | -1.6719 | 0 |  |  | none | FALSE | 1 | 72.2942 | FALSE | FALSE | 0.0705 |  | 73.2377 | 0 | 0 | 0 | 0.28994 | 0 | 0.47177 | Normal | 74.1813 | -0.62897 | Day | 202602 | 2026-02-21 | 0.62897
2026-02-21 10:59 | 72.6584 | FALSE | FALSE | -0.40513 | -0.56071 | -1.5355 | -2.0696 | -0.2826 |  |  | none | FALSE | 1 | 72.2533 | FALSE | FALSE | 0.1062 |  | 73.2236 | 0 | -0.2826 | -0.01413 | 0.29675 | -0.90471 | 0.48516 | Normal | 74.1939 | -1.165 | Day | 202602 | 2026-02-21 | 1.165
2026-02-21 11:14 | 72.941 | FALSE | FALSE | -0.68773 | -0.95183 | -1.2529 | -1.6887 | 0.2826 |  |  | none | FALSE | 1 | 72.2533 | FALSE | FALSE | 0.0674 |  | 73.2236 | 0 | 0.2826 | 0 | 0.30409 | 0.92932 | 0.48516 | Normal | 74.1939 | -0.58248 | Day | 202602 | 2026-02-21 | 0.58248
2026-02-21 11:29 | 72.941 | FALSE | FALSE | -0.68773 | -0.95183 | -1.2529 | -1.6887 | 0 |  |  | none | FALSE | 1 | 72.2533 | FALSE | FALSE | 0.0674 |  | 73.2236 | 0 | 0 | 0 | 0.30409 | 0 | 0.48516 | Normal | 74.1939 | -0.58248 | Day | 202602 | 2026-02-21 | 0.58248
2026-02-21 11:44 | 73.2236 | FALSE | FALSE | -0.94706 | -1.3103 | -0.97532 | -1.3145 | 0.2826 |  |  | none | FALSE | 0 | 72.2765 | FALSE | FALSE | 0.002 |  | 73.2377 | 0 | 0.2826 | 0.01413 | 0.31059 | 0.86439 | 0.48059 | Normal | 74.1989 | -0.029401 | Day | 202602 | 2026-02-21 | 0.029401
2026-02-21 11:59 | 73.2236 | FALSE | FALSE | -0.92282 | -1.2764 | -0.97934 | -1.3198 | 0 |  |  | none | FALSE | 0 | 72.3008 | FALSE | FALSE | 0.004 |  | 73.2519 | 0 | 0 | 0.01413 | 0.31059 | -0.045494 | 0.47554 | Normal | 74.2029 | -0.059427 | Day | 202602 | 2026-02-21 | 0.059427
2026-02-21 12:14 | 73.5062 | FALSE | FALSE | -1.1979 | -1.6566 | -0.71748 | -0.96664 | 0.2826 |  |  | none | FALSE | 0 | 72.3083 | FALSE | FALSE | 0.0334 |  | 73.266 | 0 | 0.2826 | 0.01413 | 0.31059 | 0.86439 | 0.47884 | Normal | 74.2237 | 0.50165 | Day | 202602 | 2026-02-21 | 0.50165
2026-02-21 12:29 | 73.5062 | FALSE | FALSE | -1.1895 | -1.6448 | -0.73729 | -0.99308 | 0 |  |  | none | FALSE | 0 | 72.3167 | FALSE | FALSE | 0.0313 |  | 73.2801 | 0 | 0 | 0.01413 | 0.31059 | -0.045494 | 0.48169 | Normal | 74.2435 | 0.46935 | Day | 202602 | 2026-02-21 | 0.46935
2026-02-21 12:43 | 73.5062 | FALSE | FALSE | -1.1895 | -1.6448 | -0.73729 | -0.99308 | 0 |  |  | none | FALSE | 0 | 72.3167 | FALSE | FALSE | 0.0313 |  | 73.2801 | 0 | 0 | 0 | 0.30409 | 0 | 0.48169 | Normal | 74.2435 | 0.46935 | Day | 202602 | 2026-02-21 | 0.46935
2026-02-21 12:58 | 73.7888 | FALSE | FALSE | -1.4721 | -2.0356 | -0.45469 | -0.61244 | 0.2826 |  |  | none | FALSE | 0 | 72.3167 | FALSE | FALSE | 0.0704 |  | 73.2801 | 0 | 0.2826 | 0 | 0.30409 | 0.92932 | 0.48169 | Normal | 74.2435 | 1.056 | Day | 202602 | 2026-02-21 | 1.056
2026-02-21 13:14 | 73.7888 | FALSE | FALSE | -1.4721 | -2.0356 | -0.45469 | -0.61244 | 0 |  |  | none | FALSE | 0 | 72.3167 | FALSE | FALSE | 0.0704 |  | 73.2801 | 0 | 0 | 0 | 0.30409 | 0 | 0.48169 | Normal | 74.2435 | 1.056 | Day | 202602 | 2026-02-21 | 1.056
2026-02-21 13:29 | 73.7888 | FALSE | FALSE | -1.4447 | -1.997 | -0.39909 | -0.53795 | 0 |  |  | none | FALSE | 0 | 72.3441 | FALSE | FALSE | 0.0756 |  | 73.266 | 0 | 0 | -0.01413 | 0.29675 | 0.047616 | 0.46095 | Normal | 74.1879 | 1.1342 | Day | 202602 | 2026-02-21 | 1.1342
2026-02-21 13:43 | 73.7888 | FALSE | FALSE | -1.4145 | -1.9544 | -0.34058 | -0.45944 | 0 |  |  | none | FALSE | 0 | 72.3743 | FALSE | FALSE | 0.0816 |  | 73.2519 | 0 | 0 | -0.01413 | 0.29675 | 0.047616 | 0.43876 | Normal | 74.1294 | 1.2238 | Day | 202602 | 2026-02-21 | 1.2238
2026-02-21 13:58 | 73.7888 | FALSE | FALSE | -1.3808 | -1.907 | -0.27869 | -0.37626 | 0 |  |  | none | FALSE | 0 | 72.408 | FALSE | FALSE | 0.0886 |  | 73.2377 | 0 | 0 | -0.01413 | 0.29675 | 0.047616 | 0.41488 | Normal | 74.0675 | 1.3283 | Day | 202602 | 2026-02-21 | 1.3283
2026-02-21 14:13 | 73.7888 | FALSE | FALSE | -1.3883 | -1.9175 | -0.34265 | -0.46223 | 0 |  |  | none | FALSE | 0 | 72.4005 | FALSE | FALSE | 0.0805 |  | 73.266 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.43273 | Normal | 74.1315 | 1.2082 | Day | 202602 | 2026-02-21 | 1.2082
2026-02-21 14:28 | 73.7888 | FALSE | FALSE | -1.3121 | -1.8104 | -0.37952 | -0.51171 | 0 |  |  | none | FALSE | 0 | 72.4767 | FALSE | FALSE | 0.0735 |  | 73.3225 | 0 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.42291 | Normal | 74.1683 | 1.1026 | Day | 202602 | 2026-02-21 | 1.1026
2026-02-21 14:43 | 73.7888 | FALSE | FALSE | -1.2742 | -1.7571 | -0.42638 | -0.57451 | 0 |  |  | none | FALSE | 0 | 72.5146 | FALSE | FALSE | 0.0665 |  | 73.3649 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.42514 | Normal | 74.2152 | 0.99709 | Day | 202602 | 2026-02-21 | 0.99709
2026-02-21 14:58 | 73.7888 | FALSE | FALSE | -1.1688 | -1.6095 | -0.43403 | -0.58477 | 0 |  |  | none | FALSE | 0 | 72.62 | FALSE | FALSE | 0.0611 |  | 73.4214 | 0 | 0 | 0.05652 | 0.14784 | -0.3823 | 0.40071 | Normal | 74.2228 | 0.91683 | Day | 202602 | 2026-02-21 | 0.91683
2026-02-21 15:13 | 73.7888 | FALSE | FALSE | -1.1089 | -1.5257 | -0.45893 | -0.6181 | 0 |  |  | none | FALSE | 0 | 72.6799 | FALSE | FALSE | 0.0553 |  | 73.4638 | 0 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.39196 | Normal | 74.2477 | 0.82915 | Day | 202602 | 2026-02-21 | 0.82915
2026-02-21 15:28 | 73.7888 | FALSE | FALSE | -1.0387 | -1.4277 | -0.47347 | -0.63757 | 0 |  |  | none | FALSE | 0 | 72.7501 | FALSE | FALSE | 0.0498 |  | 73.5062 | 0 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.37804 | Normal | 74.2623 | 0.74755 | Day | 202602 | 2026-02-21 | 0.74755
2026-02-21 15:43 | 73.7888 | FALSE | FALSE | -0.9569 | -1.3138 | -0.47648 | -0.64159 | 0 |  |  | none | FALSE | 0 | 72.8319 | FALSE | FALSE | 0.0447 |  | 73.5486 | 0 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.35834 | Normal | 74.2653 | 0.67033 | Day | 202602 | 2026-02-21 | 0.67033
2026-02-21 15:58 | 74.0714 | FALSE | FALSE | -1.0713 | -1.4675 | -0.16699 | -0.22493 | 0.2826 |  |  | none | FALSE | 0 | 73.0001 | FALSE | FALSE | 0.0974 |  | 73.6192 | 0 | 0.2826 | 0.07065 | 0.12555 | 1.6882 | 0.30957 | Normal | 74.2384 | 1.4606 | Day | 202602 | 2026-02-21 | 1.4606
2026-02-21 16:13 | 74.0714 | FALSE | FALSE | -0.95786 | -1.3101 | -0.16658 | -0.22438 | 0 |  |  | none | FALSE | 0 | 73.1135 | FALSE | FALSE | 0.0938 |  | 73.6758 | 0 | 0 | 0.05652 | 0.11598 | -0.48734 | 0.28111 | Normal | 74.238 | 1.4074 | Day | 202602 | 2026-02-21 | 1.4074
2026-02-21 16:28 | 73.7888 | TRUE | FALSE | -0.51512 | -0.70301 | -0.37382 | -0.50406 | -0.2826 |  |  | none | FALSE | 1 | 73.2737 | FALSE | FALSE | 0.0498 |  | 73.7181 | 0 | -0.2826 | 0.04239 | 0.13829 | -2.35 | 0.22224 | Normal | 74.1626 | 0.31791 | Day | 202602 | 2026-02-21 | 0.31791
2026-02-21 16:42 | 74.0714 | FALSE | FALSE | -0.71678 | -0.97714 | -0.095058 | -0.12817 | 0.2826 |  |  | none | FALSE | 1 | 73.3546 | FALSE | FALSE | 0.1307 |  | 73.7605 | 0 | 0.2826 | 0.04239 | 0.13829 | 1.737 | 0.20296 | Normal | 74.1665 | 1.5316 | Day | 202602 | 2026-02-21 | 1.5316
2026-02-21 16:57 | 73.5062 | TRUE | FALSE | -0.073366 | -0.099909 | -0.61031 | -0.82344 | -0.5652 |  |  | none | FALSE | 2 | 73.4328 | TRUE | FALSE | 0.1619 |  | 73.7747 | 0 | -0.5652 | 0.01413 | 0.19396 | -2.9869 | 0.17092 | Normal | 74.1165 | -1.5708 | Day | 202602 | 2026-02-21 | 1.5708
2026-02-21 17:12 | 73.2236 | FALSE | FALSE | 0.13102 | 0.17861 | -0.94286 | -1.2713 | -0.2826 | 2026-02-21 18:01 | 2026-02-21 17:12 | lower | TRUE | 2 | 73.3546 | FALSE | FALSE | 0.2907 | 2.6456 | 73.7605 | 1 | -0.2826 | -0.01413 | 0.19396 | -1.3842 | 0.20296 | Extreme triggered | 74.1665 | -2.6456 | Day | 202602 | 2026-02-21 | 2.6456
2026-02-21 17:27 | 72.941 | FALSE | FALSE | 0.25352 | 0.34636 | -1.329 | -1.7895 | -0.2826 |  | 2026-02-21 17:12 | lower | TRUE | 2 | 73.1945 | FALSE | FALSE | 0.3676 | 2.7942 | 73.7323 | 2 | -0.2826 | -0.02826 | 0.20296 | -1.2532 | 0.26888 | Extreme/elevated | 74.27 | -2.9429 | Day | 202602 | 2026-02-21 | 2.9429
2026-02-21 17:30 | 72.941 | FALSE | FALSE | 0.12515 | 0.17128 | -1.4009 | -1.8844 | 0 |  | 2026-02-21 17:12 | lower | TRUE | 2 | 73.0661 | FALSE | TRUE | 0.3881 | 2.6603 | 73.704 | 3 | 0 | -0.02826 | 0.20296 | 0.13924 | 0.31894 | Persistent | 74.3419 | -2.3924 | Day | 202602 | 2026-02-21 | 2.3924
2026-02-21 17:31 | 72.941 | FALSE | FALSE | -0.00073602 | -0.0010091 | -1.442 | -1.9386 | 0 |  | 2026-02-21 17:12 | none | FALSE | 2 | 72.9403 | FALSE | FALSE | 0.4189 | 2.4947 | 73.6616 | 4 | 0 | -0.04239 | 0.18957 | 0.22361 | 0.36068 | Persistent | 74.383 | -1.998 | Day | 202602 | 2026-02-21 | 1.998
2026-02-21 17:46 | 73.2236 | FALSE | FALSE | -0.33454 | -0.45897 | -1.1541 | -1.5516 | 0.2826 |  | 2026-02-21 17:12 | none | FALSE | 2 | 72.8891 | FALSE | FALSE | 0.4163 | 2.216 | 73.6334 | 5 | 0.2826 | -0.02826 | 0.20296 | 1.5316 | 0.37215 | Persistent | 74.3777 | -1.1011 | Day | 202602 | 2026-02-21 | 1.1011
2026-02-21 18:01 | 73.7888 | TRUE | FALSE | -0.89974 | -1.2344 | -0.58888 | -0.79174 | 0.5652 |  |  | none | FALSE | 3 | 72.8891 | TRUE | FALSE | 0.1136 |  | 73.6334 | 0 | 0.5652 | 0 | 0.24258 | 2.3299 | 0.37215 | Persistence ends | 74.3777 | 0.41765 | Day | 202602 | 2026-02-21 | 0.41765
2026-02-21 18:16 | 74.0714 | FALSE | FALSE | -1.191 | -1.6342 | -0.34321 | -0.46122 | 0.2826 |  |  | none | FALSE | 3 | 72.8804 | FALSE | FALSE | 0.1594 |  | 73.6475 | 0 | 0.2826 | 0.01413 | 0.25068 | 1.071 | 0.38356 | Normal | 74.4146 | 1.1052 | Day | 202602 | 2026-02-21 | 1.1052
2026-02-21 18:30 | 74.3522 | FALSE | FALSE | -1.5045 | -2.0652 | -0.1514 | -0.20321 | 0.2808 |  |  | none | FALSE | 2 | 72.8477 | FALSE | FALSE | 0.1661 |  | 73.6757 | 0 | 0.2808 | 0.02817 | 0.25761 | 0.98066 | 0.41396 | Normal | 74.5036 | 1.6343 | Night | 202602 | 2026-02-21 | 1.6343
2026-02-21 18:45 | 74.3522 | FALSE | FALSE | -1.5291 | -2.0998 | -0.23243 | -0.31163 | 0 |  |  | none | FALSE | 2 | 72.8231 | FALSE | FALSE | 0.1553 |  | 73.7038 | 0 | 0 | 0.02817 | 0.25761 | -0.10935 | 0.44039 | Normal | 74.5846 | 1.4722 | Night | 202602 | 2026-02-21 | 1.4722
2026-02-21 19:00 | 74.6348 | FALSE | FALSE | -1.8629 | -2.56 | -0.085606 | -0.11457 | 0.2826 |  |  | none | FALSE | 1 | 72.7719 | FALSE | FALSE | 0.1502 |  | 73.7461 | 0 | 0.2826 | 0.0423 | 0.26367 | 0.91138 | 0.48713 | Normal | 74.7204 | 1.8243 | Night | 202602 | 2026-02-21 | 1.8243
2026-02-21 19:15 | 74.6348 | FALSE | FALSE | -1.8988 | -2.6105 | -0.20603 | -0.2753 | 0 |  |  | none | FALSE | 1 | 72.736 | FALSE | FALSE | 0.1358 |  | 73.7884 | 0 | 0 | 0.0423 | 0.26367 | -0.16043 | 0.5262 | Normal | 74.8408 | 1.6084 | Night | 202602 | 2026-02-21 | 1.6084
2026-02-21 19:29 | 74.6348 | FALSE | FALSE | -1.9225 | -2.6439 | -0.31433 | -0.4194 | 0 |  |  | none | FALSE | 1 | 72.7123 | FALSE | FALSE | 0.1244 |  | 73.8307 | 0 | 0 | 0.0423 | 0.26367 | -0.16043 | 0.5592 | Normal | 74.9491 | 1.4379 | Night | 202602 | 2026-02-21 | 1.4379
2026-02-21 19:44 | 74.6348 | FALSE | FALSE | -1.9361 | -2.6631 | -0.41255 | -0.54972 | 0 |  |  | none | FALSE | 1 | 72.6987 | FALSE | FALSE | 0.1151 |  | 73.873 | 0 | 0 | 0.0423 | 0.26367 | -0.16043 | 0.58716 | Normal | 75.0474 | 1.2974 | Night | 202602 | 2026-02-21 | 1.2974
2026-02-21 19:59 | 74.9174 | FALSE | FALSE | -2.2504 | -3.0968 | -0.2745 | -0.36506 | 0.2826 |  |  | none | FALSE | 1 | 72.667 | FALSE | FALSE | 0.1329 |  | 73.9295 | 0 | 0.2826 | 0.05643 | 0.2688 | 0.8414 | 0.63121 | Normal | 75.1919 | 1.5651 | Night | 202602 | 2026-02-21 | 1.5651
2026-02-21 20:14 | 74.9174 | FALSE | FALSE | -2.2663 | -3.1194 | -0.40328 | -0.53541 | 0 |  |  | none | FALSE | 1 | 72.6511 | FALSE | FALSE | 0.1216 |  | 73.9859 | 0 | 0 | 0.05643 | 0.2688 | -0.20993 | 0.66739 | Normal | 75.3207 | 1.3957 | Night | 202602 | 2026-02-21 | 1.3957
2026-02-21 20:29 | 74.9174 | FALSE | FALSE | -2.2875 | -3.1495 | -0.50909 | -0.67495 | 0 |  |  | none | FALSE | 0 | 72.6299 | FALSE | FALSE | 0.0848 |  | 74.0282 | 0 | 0 | 0.0423 | 0.26367 | -0.16043 | 0.69915 | Normal | 75.4265 | 1.2718 | Night | 202602 | 2026-02-21 | 1.2718
2026-02-21 20:44 | 74.9174 | FALSE | FALSE | -2.3008 | -3.1684 | -0.60698 | -0.80368 | 0 |  |  | none | FALSE | 0 | 72.6166 | FALSE | FALSE | 0.0777 |  | 74.0705 | 0 | 0 | 0.0423 | 0.26367 | -0.16043 | 0.72694 | Normal | 75.5244 | 1.165 | Night | 202602 | 2026-02-21 | 1.165
2026-02-21 20:59 | 74.9174 | FALSE | FALSE | -2.2853 | -3.1465 | -0.7044 | -0.93148 | 0 |  |  | none | FALSE | 0 | 72.6321 | FALSE | FALSE | 0.0705 |  | 74.1269 | 0 | 0 | 0.05643 | 0.25268 | -0.22333 | 0.74744 | Normal | 75.6218 | 1.0576 | Night | 202602 | 2026-02-21 | 1.0576
2026-02-21 21:14 | 74.9174 | FALSE | FALSE | -2.2837 | -3.1442 | -0.78741 | -1.0401 | 0 |  |  | none | FALSE | 0 | 72.6337 | FALSE | FALSE | 0.065 |  | 74.1692 | 0 | 0 | 0.0423 | 0.24721 | -0.17111 | 0.76779 | Normal | 75.7048 | 0.97445 | Night | 202602 | 2026-02-21 | 0.97445
2026-02-21 21:29 | 74.9174 | FALSE | FALSE | -2.2146 | -3.0461 | -0.85938 | -1.1341 | 0 |  |  | none | FALSE | 0 | 72.7028 | FALSE | FALSE | 0.0588 |  | 74.2398 | 0 | 0 | 0.07056 | 0.20234 | -0.34872 | 0.76849 | Normal | 75.7768 | 0.88174 | Night | 202602 | 2026-02-21 | 0.88174
2026-02-21 21:44 | 74.9174 | FALSE | FALSE | -2.08 | -2.8557 | -0.89416 | -1.1794 | 0 |  |  | none | FALSE | 0 | 72.8374 | FALSE | FALSE | 0.0532 |  | 74.3245 | 0 | 0 | 0.08469 | 0.18555 | -0.45642 | 0.74354 | Normal | 75.8116 | 0.79743 | Night | 202602 | 2026-02-21 | 0.79743
2026-02-21 21:59 | 74.9174 | FALSE | FALSE | -1.8511 | -2.5334 | -0.86286 | -1.1386 | 0 |  |  | none | FALSE | 0 | 73.0663 | FALSE | FALSE | 0.0485 |  | 74.4233 | 0 | 0 | 0.09882 | 0.16582 | -0.59594 | 0.67848 | Normal | 75.7803 | 0.72824 | Night | 202602 | 2026-02-21 | 0.72824
2026-02-21 22:14 | 74.9174 | FALSE | FALSE | -1.5739 | -2.1459 | -0.7833 | -1.0347 | 0 |  |  | none | FALSE | 0 | 73.3435 | FALSE | FALSE | 0.0447 |  | 74.5221 | 0 | 0 | 0.09882 | 0.16582 | -0.59594 | 0.58929 | Normal | 75.7007 | 0.67077 | Night | 202602 | 2026-02-21 | 0.67077
2026-02-21 22:28 | 74.9174 | FALSE | FALSE | -1.2209 | -1.6566 | -0.62795 | -0.83122 | 0 |  |  | none | FALSE | 0 | 73.6965 | FALSE | FALSE | 0.0428 |  | 74.6209 | 0 | 0 | 0.09882 | 0.16582 | -0.59594 | 0.4622 | Normal | 75.5453 | 0.64141 | Night | 202602 | 2026-02-21 | 0.64141
2026-02-21 22:43 | 74.9174 | FALSE | FALSE | -0.86886 | -1.1734 | -0.44532 | -0.5909 | 0 |  |  | none | FALSE | 0 | 74.0485 | FALSE | FALSE | 0.043 |  | 74.7056 | 0 | 0 | 0.08469 | 0.16132 | -0.52499 | 0.32854 | Normal | 75.3627 | 0.64457 | Night | 202602 | 2026-02-21 | 0.64457
2026-02-21 22:59 | 74.9174 | FALSE | FALSE | -0.65617 | -0.8836 | -0.34549 | -0.45905 | 0 |  |  | none | FALSE | 0 | 74.2612 | FALSE | FALSE | 0.0414 |  | 74.7621 | 0 | 0 | 0.05643 | 0.11579 | -0.48734 | 0.25042 | Normal | 75.2629 | 0.62033 | Night | 202602 | 2026-02-21 | 0.62033
2026-02-21 23:14 | 74.9174 | FALSE | FALSE | -0.49769 | -0.66876 | -0.27161 | -0.36124 | 0 |  |  | none | FALSE | 0 | 74.4197 | FALSE | FALSE | 0.0392 |  | 74.8044 | 0 | 0 | 0.0423 | 0.10331 | -0.40945 | 0.19233 | Normal | 75.189 | 0.58775 | Night | 202602 | 2026-02-21 | 0.58775
2026-02-21 23:28 | 74.9174 | FALSE | FALSE | -0.40765 | -0.5471 | -0.23809 | -0.31679 | 0 |  |  | none | FALSE | 0 | 74.5098 | FALSE | FALSE | 0.035 |  | 74.8326 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.16143 | Normal | 75.1555 | 0.52517 | Night | 202602 | 2026-02-21 | 0.52517
2026-02-21 23:43 | 74.9174 | FALSE | FALSE | -0.28847 | -0.38654 | -0.17543 | -0.23362 | 0 |  |  | none | FALSE | 0 | 74.6289 | FALSE | FALSE | 0.0325 |  | 74.8609 | 0 | 0 | 0.02826 | 0.086982 | -0.32489 | 0.11598 | Normal | 75.0928 | 0.48734 | Night | 202602 | 2026-02-21 | 0.48734
2026-02-21 23:58 | 74.9174 | FALSE | FALSE | -0.24945 | -0.33408 | -0.16467 | -0.21932 | 0 |  |  | none | FALSE | 0 | 74.668 | FALSE | FALSE | 0.0273 |  | 74.875 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.10353 | Normal | 75.0821 | 0.40945 | Night | 202602 | 2026-02-21 | 0.40945
2026-02-22 00:13 | 74.9174 | FALSE | FALSE | -0.20222 | -0.27066 | -0.1457 | -0.19411 | 0 |  |  | none | FALSE | 0 | 74.7152 | FALSE | FALSE | 0.0217 |  | 74.8891 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.086982 | Normal | 75.0631 | 0.32489 | Night | 202602 | 2026-02-22 | 0.32489
2026-02-22 00:28 | 74.9174 | FALSE | FALSE | -0.14051 | -0.18791 | -0.11225 | -0.14961 | 0 |  |  | none | FALSE | 0 | 74.7769 | FALSE | FALSE | 0.0149 |  | 74.9033 | 0 | 0 | 0.01413 | 0.063191 | -0.22361 | 0.063191 | Normal | 75.0297 | 0.22361 | Night | 202602 | 2026-02-22 | 0.22361
2026-02-22 00:43 | 74.6348 | TRUE | FALSE | 0.14209 | 0.19002 | -0.39485 | -0.52626 | -0.2826 | 2026-02-22 07:41 | 2026-02-22 00:43 | lower | TRUE | 1 | 74.7769 | FALSE | FALSE | 0.3689 | 4.2485 | 74.9033 | 1 | -0.2826 | 0 | 0.091688 | -3.0822 | 0.063191 | Extreme triggered | 75.0297 | -4.2485 | Night | 202602 | 2026-02-22 | 4.2485
2026-02-22 00:58 | 74.6348 | FALSE | FALSE | 0.080375 | 0.10758 | -0.4283 | -0.57059 | 0 |  | 2026-02-22 00:43 | lower | TRUE | 1 | 74.7152 | FALSE | FALSE | 0.3378 | 3.5863 | 74.8891 | 2 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.086982 | Extreme/elevated | 75.0631 | -2.924 | Night | 202602 | 2026-02-22 | 2.924
2026-02-22 01:13 | 74.6348 | FALSE | FALSE | 0.03315 | 0.044397 | -0.44727 | -0.59571 | 0 |  | 2026-02-22 00:43 | lower | TRUE | 1 | 74.668 | FALSE | TRUE | 0.3547 | 3.1643 | 74.875 | 3 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.10353 | Persistent | 75.0821 | -2.3202 | Night | 202602 | 2026-02-22 | 2.3202
2026-02-22 01:27 | 74.6348 | FALSE | FALSE | -0.0058732 | -0.0078699 | -0.45803 | -0.60996 | 0 |  | 2026-02-22 00:43 | none | FALSE | 1 | 74.6289 | FALSE | FALSE | 0.3871 | 2.8605 | 74.8609 | 4 | 0 | -0.01413 | 0.063191 | 0.22361 | 0.11598 | Persistent | 75.0928 | -1.9494 | Night | 202602 | 2026-02-22 | 1.9494
2026-02-22 01:43 | 74.3522 | TRUE | FALSE | 0.15755 | 0.21146 | -0.80329 | -1.0688 | -0.2826 |  | 2026-02-22 00:43 | lower | TRUE | 2 | 74.5098 | TRUE | TRUE | 0.5413 | 2.8836 | 74.8326 | 5 | -0.2826 | -0.02826 | 0.086982 | -2.924 | 0.16143 | Persistent | 75.1555 | -2.976 | Night | 202602 | 2026-02-22 | 2.976
2026-02-22 01:58 | 74.3522 | FALSE | FALSE | 0.067509 | 0.090714 | -0.83681 | -1.1129 | 0 |  | 2026-02-22 00:43 | lower | TRUE | 2 | 74.4197 | FALSE | TRUE | 0.5567 | 2.7949 | 74.8044 | 6 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.19233 | Persistent | 75.189 | -2.351 | Night | 202602 | 2026-02-22 | 2.351
2026-02-22 02:13 | 74.3522 | FALSE | TRUE | -0.0061527 | -0.0082758 | -0.85395 | -1.1355 | 0 |  | 2026-02-22 00:43 | none | FALSE | 2 | 74.346 | FALSE | FALSE | 0.5886 | 2.6772 | 74.7761 | 7 | 0 | -0.02826 | 0.086982 | 0.32489 | 0.21503 | Confirmed/Materialized Shift | 75.2062 | -1.9714 | Night | 202602 | 2026-02-22 | 1.9714
2026-02-22 02:27 | 74.0714 | TRUE | TRUE | 0.13537 | 0.18243 | -1.1894 | -1.5804 | -0.2808 |  | 2026-02-22 00:43 | lower | TRUE | 3 | 74.2068 | TRUE | TRUE | 0.6533 | 2.6568 | 74.7338 | 8 | -0.2808 | -0.0423 | 0.10331 | -2.3086 | 0.26351 | Confirmed/Materialized Shift | 75.2608 | -2.5137 | Night | 202602 | 2026-02-22 | 2.5137
2026-02-22 02:42 | 74.0714 | FALSE | TRUE | 0.023863 | 0.032205 | -1.2163 | -1.6156 | 0 |  | 2026-02-22 00:43 | lower | TRUE | 3 | 74.0953 | FALSE | TRUE | 0.6244 | 2.5927 | 74.6915 | 9 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.29812 | Confirmed/Materialized Shift | 75.2877 | -2.08 | Night | 202602 | 2026-02-22 | 2.08
2026-02-22 02:57 | 74.0714 | FALSE | TRUE | -0.068864 | -0.093056 | -1.2245 | -1.6262 | 0 |  | 2026-02-22 00:43 | none | FALSE | 3 | 74.0025 | FALSE | FALSE | 0.6048 | 2.5121 | 74.6492 | 10 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.32333 | Confirmed/Materialized Shift | 75.2959 | -1.787 | Night | 202602 | 2026-02-22 | 1.787
2026-02-22 03:12 | 74.0714 | FALSE | TRUE | -0.14698 | -0.19883 | -1.218 | -1.6177 | 0 |  | 2026-02-22 00:43 | none | FALSE | 2 | 73.9244 | FALSE | FALSE | 0.5618 | 2.4264 | 74.6069 | 11 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.34124 | Confirmed/Materialized Shift | 75.2894 | -1.5693 | Night | 202602 | 2026-02-22 | 1.5693
2026-02-22 03:27 | 74.0714 | FALSE | TRUE | -0.21272 | -0.28801 | -1.1991 | -1.5931 | 0 |  | 2026-02-22 00:43 | none | FALSE | 2 | 73.8587 | FALSE | FALSE | 0.5503 | 2.3407 | 74.5646 | 12 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.35296 | Confirmed/Materialized Shift | 75.2705 | -1.3973 | Night | 202602 | 2026-02-22 | 1.3973
2026-02-22 03:42 | 74.0714 | FALSE | TRUE | -0.26729 | -0.36216 | -1.1691 | -1.5538 | 0 |  | 2026-02-22 00:43 | none | FALSE | 2 | 73.8041 | FALSE | FALSE | 0.5409 | 2.2572 | 74.5223 | 13 | 0 | -0.0423 | 0.10331 | 0.40945 | 0.35909 | Confirmed/Materialized Shift | 75.2405 | -1.2557 | Night | 202602 | 2026-02-22 | 1.2557
2026-02-22 03:57 | 73.7888 | FALSE | TRUE | -0.086337 | -0.11714 | -1.4405 | -1.9148 | -0.2826 |  | 2026-02-22 00:43 | none | FALSE | 2 | 73.7025 | FALSE | FALSE | 0.5754 | 2.2227 | 74.4659 | 14 | -0.2826 | -0.05643 | 0.11579 | -1.9532 | 0.3817 | Confirmed/Materialized Shift | 75.2293 | -1.7738 | Night | 202602 | 2026-02-22 | 1.7738
2026-02-22 04:12 | 73.7888 | FALSE | TRUE | -0.16864 | -0.22907 | -1.4099 | -1.8749 | 0 |  | 2026-02-22 00:43 | none | FALSE | 1 | 73.6202 | FALSE | FALSE | 0.5334 | 2.1793 | 74.4094 | 15 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.39464 | Confirmed/Materialized Shift | 75.1987 | -1.5727 | Night | 202602 | 2026-02-22 | 1.5727
2026-02-22 04:27 | 73.7888 | FALSE | TRUE | -0.2335 | -0.31744 | -1.3619 | -1.8122 | 0 |  | 2026-02-22 00:43 | none | FALSE | 1 | 73.5553 | FALSE | FALSE | 0.5229 | 2.1315 | 74.353 | 16 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.39885 | Confirmed/Materialized Shift | 75.1507 | -1.4146 | Night | 202602 | 2026-02-22 | 1.4146
2026-02-22 04:42 | 73.7888 | FALSE | TRUE | -0.28145 | -0.38289 | -1.297 | -1.7274 | 0 |  | 2026-02-22 00:43 | none | FALSE | 1 | 73.5073 | FALSE | FALSE | 0.5144 | 2.0818 | 74.2966 | 17 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.39462 | Confirmed/Materialized Shift | 75.0858 | -1.2868 | Night | 202602 | 2026-02-22 | 1.2868
2026-02-22 04:57 | 73.7888 | FALSE | TRUE | -0.31194 | -0.42455 | -1.2146 | -1.6195 | 0 |  | 2026-02-22 00:43 | none | FALSE | 0 | 73.4769 | FALSE | FALSE | 0.4788 | 2.0319 | 74.2401 | 18 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.38165 | Confirmed/Materialized Shift | 75.0034 | -1.1826 | Night | 202602 | 2026-02-22 | 1.1826
2026-02-22 05:12 | 73.5062 | FALSE | TRUE | -0.097202 | -0.13241 | -1.424 | -1.9004 | -0.2826 |  | 2026-02-22 00:43 | none | FALSE | 0 | 73.409 | FALSE | FALSE | 0.5163 | 2.0168 | 74.1696 | 19 | -0.2826 | -0.07056 | 0.12539 | -1.6911 | 0.3803 | Confirmed/Materialized Shift | 74.9302 | -1.7444 | Night | 202602 | 2026-02-22 | 1.7444
2026-02-22 05:26 | 73.5062 | FALSE | TRUE | -0.13687 | -0.18654 | -1.3225 | -1.7674 | 0 |  | 2026-02-22 00:43 | none | FALSE | 0 | 73.3693 | FALSE | FALSE | 0.5083 | 1.9972 | 74.099 | 20 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.36485 | Confirmed/Materialized Shift | 74.8287 | -1.6249 | Night | 202602 | 2026-02-22 | 1.6249
2026-02-22 05:41 | 73.5062 | FALSE | TRUE | -0.1934 | -0.2638 | -1.2662 | -1.6934 | 0 |  | 2026-02-22 00:43 | none | FALSE | 0 | 73.3128 | FALSE | FALSE | 0.498 | 1.9721 | 74.0426 | 21 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.3649 | Confirmed/Materialized Shift | 74.7724 | -1.47 | Night | 202602 | 2026-02-22 | 1.47
2026-02-22 05:56 | 73.2236 | FALSE | TRUE | -0.012497 | -0.01707 | -1.5094 | -2.0197 | -0.2826 |  | 2026-02-22 00:43 | none | FALSE | 0 | 73.2111 | FALSE | FALSE | 0.5311 | 1.9718 | 73.972 | 22 | -0.2826 | -0.07056 | 0.12539 | -1.6911 | 0.38047 | Confirmed/Materialized Shift | 74.733 | -1.9672 | Night | 202602 | 2026-02-22 | 1.9672
2026-02-22 06:11 | 73.2236 | FALSE | TRUE | -0.086003 | -0.11759 | -1.4418 | -1.931 | 0 |  | 2026-02-22 00:43 | none | FALSE | 0 | 73.1376 | FALSE | FALSE | 0.5183 | 1.9633 | 73.9015 | 23 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.38194 | Confirmed/Materialized Shift | 74.6654 | -1.7748 | Night | 202602 | 2026-02-22 | 1.7748
2026-02-22 06:26 | 73.2236 | FALSE | TRUE | -0.13165 | -0.18012 | -1.3463 | -1.8054 | 0 |  | 2026-02-22 00:43 | none | FALSE | 0 | 73.0919 | FALSE | FALSE | 0.5096 | 1.95 | 73.8309 | 24 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.36949 | Confirmed/Materialized Shift | 74.5699 | -1.6437 | Night | 202602 | 2026-02-22 | 1.6437
2026-02-22 06:41 | 73.2236 | FALSE | TRUE | -0.19283 | -0.26404 | -1.2946 | -1.7373 | 0 |  | 2026-02-22 00:43 | none | FALSE | 0 | 73.0308 | FALSE | FALSE | 0.4988 | 1.9312 | 73.7745 | 25 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.37186 | Confirmed/Materialized Shift | 74.5182 | -1.4814 | Night | 202602 | 2026-02-22 | 1.4814
2026-02-22 06:56 | 73.2236 | FALSE | TRUE | -0.23584 | -0.32312 | -1.2248 | -1.6451 | 0 |  | 2026-02-22 00:43 | none | FALSE | 0 | 72.9878 | FALSE | FALSE | 0.4903 | 1.909 | 73.7181 | 26 | 0 | -0.05643 | 0.11579 | 0.48734 | 0.36515 | Confirmed/Materialized Shift | 74.4484 | -1.3541 | Day | 202602 | 2026-02-22 | 1.3541
2026-02-22 07:11 | 72.941 | FALSE | TRUE | -0.038373 | -0.052636 | -1.4514 | -1.951 | -0.2826 |  | 2026-02-22 00:43 | none | FALSE | 0 | 72.9026 | FALSE | FALSE | 0.5265 | 1.9086 | 73.6475 | 27 | -0.2826 | -0.07056 | 0.12539 | -1.6911 | 0.37244 | Confirmed/Materialized Shift | 74.3924 | -1.897 | Day | 202602 | 2026-02-22 | 1.897
2026-02-22 07:26 | 72.941 | FALSE | TRUE | -0.13017 | -0.17878 | -1.4301 | -1.923 | 0 |  | 2026-02-22 00:43 | none | FALSE | 0 | 72.8108 | FALSE | FALSE | 0.5111 | 1.8999 | 73.591 | 28 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.39008 | Confirmed/Materialized Shift | 74.3711 | -1.6663 | Day | 202602 | 2026-02-22 | 1.6663
2026-02-22 07:41 | 73.2236 | TRUE | FALSE | -0.43718 | -0.60063 | -1.0872 | -1.463 | 0.2826 |  |  | none | FALSE | 1 | 72.7864 | FALSE | FALSE | 0.0854 |  | 73.5486 | 0 | 0.2826 | -0.04239 | 0.13829 | 2.35 | 0.38108 | Persistence ends | 74.3108 | -0.85281 | Day | 202602 | 2026-02-22 | 0.85281
2026-02-22 07:56 | 72.941 | FALSE | FALSE | -0.21549 | -0.29631 | -1.3176 | -1.7744 | -0.2826 |  |  | none | FALSE | 1 | 72.7255 | FALSE | FALSE | 0.1244 |  | 73.4921 | 0 | -0.2826 | -0.05652 | 0.14784 | -1.5292 | 0.38328 | Normal | 74.2586 | -1.4378 | Day | 202602 | 2026-02-22 | 1.4378
2026-02-22 08:11 | 73.2236 | FALSE | FALSE | -0.49819 | -0.68503 | -0.95035 | -1.2812 | 0.2826 |  |  | none | FALSE | 1 | 72.7254 | FALSE | FALSE | 0.0702 |  | 73.4497 | 0 | 0.2826 | -0.04239 | 0.16593 | 1.9586 | 0.36214 | Normal | 74.174 | -0.62429 | Day | 202602 | 2026-02-22 | 0.62429
2026-02-22 08:25 | 73.2236 | FALSE | FALSE | -0.48443 | -0.66599 | -0.85181 | -1.1499 | 0 |  |  | none | FALSE | 1 | 72.7392 | FALSE | FALSE | 0.0652 |  | 73.4073 | 0 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.33406 | Normal | 74.0754 | -0.54987 | Day | 202602 | 2026-02-22 | 0.54987
2026-02-22 08:30 | 73.2236 | FALSE | FALSE | -0.4529 | -0.62237 | -0.7355 | -0.99447 | 0 |  |  | none | FALSE | 1 | 72.7707 | FALSE | FALSE | 0.0603 |  | 73.3649 | 0 | 0 | -0.04239 | 0.16593 | 0.25547 | 0.2971 | Normal | 73.9591 | -0.47559 | Day | 202602 | 2026-02-22 | 0.47559
2026-02-22 08:45 | 73.2236 | FALSE | FALSE | -0.44918 | -0.61722 | -0.67526 | -0.91376 | 0 |  |  | none | FALSE | 1 | 72.7744 | FALSE | FALSE | 0.0554 |  | 73.3366 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.28111 | Normal | 73.8989 | -0.40212 | Day | 202602 | 2026-02-22 | 0.40212
2026-02-22 09:00 | 73.2236 | FALSE | FALSE | -0.43711 | -0.60054 | -0.60667 | -0.82172 | 0 |  |  | none | FALSE | 1 | 72.7865 | FALSE | FALSE | 0.0502 |  | 73.3084 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.26095 | Normal | 73.8303 | -0.32489 | Day | 202602 | 2026-02-22 | 0.32489
2026-02-22 09:16 | 73.2236 | FALSE | FALSE | -0.41458 | -0.56941 | -0.52762 | -0.7154 | 0 |  |  | none | FALSE | 1 | 72.809 | FALSE | FALSE | 0.0446 |  | 73.2801 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.23555 | Normal | 73.7512 | -0.23995 | Day | 202602 | 2026-02-22 | 0.23995
2026-02-22 09:30 | 73.2236 | FALSE | FALSE | -0.37766 | -0.51843 | -0.43418 | -0.58945 | 0 |  |  | none | FALSE | 1 | 72.8459 | FALSE | FALSE | 0.0379 |  | 73.2519 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.20296 | Normal | 73.6578 | -0.13924 | Day | 202602 | 2026-02-22 | 0.13924
2026-02-22 09:30 | 73.2236 | FALSE | FALSE | -0.31761 | -0.43565 | -0.31761 | -0.43189 | 0 |  |  | none | FALSE | 1 | 72.906 | FALSE | FALSE | 0.0286 |  | 73.2236 | 0 | 0 | -0.02826 | 0.15614 | 0.18099 | 0.15881 | Normal | 73.5412 | 0 | Day | 202602 | 2026-02-22 | 0
2026-02-22 09:45 | 73.5062 | FALSE | FALSE | -0.60021 | -0.82327 | -0.035015 | -0.047613 | 0.2826 |  |  | none | FALSE | 0 | 72.906 | FALSE | FALSE | 0.1186 |  | 73.2236 | 0 | 0.2826 | 0 | 0.15881 | 1.7795 | 0.15881 | Normal | 73.5412 | 1.7795 | Day | 202602 | 2026-02-22 | 1.7795
2026-02-22 10:00 | 73.5062 | FALSE | FALSE | -0.60021 | -0.82327 | -0.035015 | -0.047613 | 0 |  |  | none | FALSE | 0 | 72.906 | FALSE | FALSE | 0.1186 |  | 73.2236 | 0 | 0 | 0 | 0.15881 | 0 | 0.15881 | Normal | 73.5412 | 1.7795 | Day | 202602 | 2026-02-22 | 1.7795
2026-02-22 10:15 | 73.2236 | FALSE | FALSE | -0.30262 | -0.41499 | -0.27436 | -0.37329 | -0.2826 |  |  | none | FALSE | 0 | 72.921 | FALSE | FALSE | 0.0065 |  | 73.2095 | 0 | -0.2826 | -0.01413 | 0.17092 | -1.5708 | 0.14424 | Normal | 73.498 | 0.097959 | Day | 202602 | 2026-02-22 | 0.097959
2026-02-22 10:30 | 73.5062 | FALSE | FALSE | -0.60021 | -0.82327 | -0.035015 | -0.047613 | 0.2826 |  |  | none | FALSE | 0 | 72.906 | FALSE | FALSE | 0.1186 |  | 73.2236 | 0 | 0.2826 | 0.01413 | 0.17092 | 1.5708 | 0.15881 | Normal | 73.5412 | 1.7795 | Day | 202602 | 2026-02-22 | 1.7795
2026-02-22 10:45 | 73.5062 | FALSE | FALSE | -0.61031 | -0.83723 | -0.073366 | -0.09971 | 0 |  |  | none | FALSE | 0 | 72.8959 | FALSE | FALSE | 0.1047 |  | 73.2377 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.17092 | Normal | 73.5796 | 1.5708 | Day | 202602 | 2026-02-22 | 1.5708
2026-02-22 11:00 | 73.7888 | FALSE | FALSE | -0.94397 | -1.2959 | 0.10165 | 0.13794 | 0.2826 | 2026-02-22 11:44 | 2026-02-22 11:00 | upper | TRUE | 0 | 72.8448 | FALSE | FALSE | 0.2227 | 2.4827 | 73.266 | 1 | 0.2826 | 0.02826 | 0.18107 | 1.4047 | 0.21058 | Extreme triggered | 73.6872 | 2.4827 | Day | 202602 | 2026-02-22 | 2.4827
2026-02-22 11:08 | 74.0714 | FALSE | FALSE | -1.3162 | -1.8091 | 0.20985 | 0.28411 | 0.2826 |  | 2026-02-22 11:00 | upper | TRUE | 0 | 72.7552 | FALSE | FALSE | 0.2982 | 2.6207 | 73.3084 | 2 | 0.2826 | 0.04239 | 0.18957 | 1.2671 | 0.27659 | Extreme/elevated | 73.8616 | 2.7587 | Day | 202602 | 2026-02-22 | 2.7587
2026-02-22 11:11 | 74.0714 | FALSE | FALSE | -1.3683 | -1.8821 | 0.07295 | 0.098583 | 0 |  | 2026-02-22 11:00 | upper | TRUE | 0 | 72.7031 | FALSE | TRUE | 0.3198 | 2.4889 | 73.3508 | 3 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.32384 | Persistent | 73.9985 | 2.2253 | Day | 202602 | 2026-02-22 | 2.2253
2026-02-22 11:26 | 73.7888 | FALSE | FALSE | -1.0414 | -1.4315 | -0.25009 | -0.33778 | -0.2826 |  | 2026-02-22 11:00 | none | FALSE | 0 | 72.7474 | FALSE | FALSE | 0.3103 | 2.173 | 73.3932 | 4 | -0.2826 | 0.04239 | 0.18957 | -1.7143 | 0.32287 | Persistent | 74.0389 | 1.2254 | Day | 202602 | 2026-02-22 | 1.2254
2026-02-22 11:29 | 73.7888 | FALSE | FALSE | -0.98516 | -1.3532 | -0.27866 | -0.37623 | 0 |  | 2026-02-22 11:00 | none | FALSE | 0 | 72.8036 | FALSE | FALSE | 0.3602 | 1.962 | 73.4356 | 5 | 0 | 0.04239 | 0.18957 | -0.22361 | 0.31596 | Persistent | 74.0675 | 1.118 | Day | 202602 | 2026-02-22 | 1.118
2026-02-22 11:44 | 73.5062 | FALSE | FALSE | -0.68107 | -0.93522 | -0.56803 | -0.76684 | -0.2826 |  |  | none | FALSE | 0 | 72.8251 | FALSE | FALSE | 0.0121 |  | 73.4497 | 0 | -0.2826 | 0.01413 | 0.19396 | -1.5299 | 0.31228 | Persistence ends | 74.0742 | 0.18099 | Day | 202602 | 2026-02-22 | 0.18099
2026-02-22 11:59 | 73.5062 | FALSE | FALSE | -0.60524 | -0.83022 | -0.54872 | -0.74096 | 0 |  |  | none | FALSE | 0 | 72.901 | FALSE | FALSE | 0.0065 |  | 73.4779 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.28849 | Normal | 74.0549 | 0.097959 | Day | 202602 | 2026-02-22 | 0.097959
2026-02-22 12:14 | 73.2236 | FALSE | FALSE | -0.32264 | -0.44257 | -0.83132 | -1.1226 | -0.2826 |  |  | none | FALSE | 0 | 72.901 | FALSE | FALSE | 0.0588 |  | 73.4779 | 0 | -0.2826 | 0 | 0.18338 | -1.5411 | 0.28849 | Normal | 74.0549 | -0.88163 | Day | 202602 | 2026-02-22 | 0.88163
2026-02-22 12:29 | 73.2236 | FALSE | FALSE | -0.32264 | -0.44257 | -0.83132 | -1.1226 | 0 |  |  | none | FALSE | 0 | 72.901 | FALSE | FALSE | 0.0588 |  | 73.4779 | 0 | 0 | 0 | 0.18338 | 0 | 0.28849 | Normal | 74.0549 | -0.88163 | Day | 202602 | 2026-02-22 | 0.88163
2026-02-22 12:44 | 73.5062 | FALSE | FALSE | -0.57859 | -0.79337 | -0.55033 | -0.74312 | 0.2826 |  |  | none | FALSE | 0 | 72.9276 | FALSE | FALSE | 0.0033 |  | 73.4921 | 0 | 0.2826 | 0.01413 | 0.19396 | 1.3842 | 0.28223 | Normal | 74.0565 | 0.050066 | Day | 202602 | 2026-02-22 | 0.050066
2026-02-22 12:59 | 73.5062 | FALSE | FALSE | -0.55013 | -0.75405 | -0.55013 | -0.74285 | 0 |  |  | none | FALSE | 0 | 72.9561 | FALSE | FALSE | 0 |  | 73.5062 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.27506 | Normal | 74.0563 | 0 | Day | 202602 | 2026-02-22 | 0
2026-02-22 13:14 | 73.5062 | FALSE | FALSE | -0.51971 | -0.71206 | -0.54797 | -0.73996 | 0 |  |  | none | FALSE | 0 | 72.9865 | FALSE | FALSE | 0.0035 |  | 73.5203 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.26692 | Normal | 74.0542 | -0.052937 | Day | 202602 | 2026-02-22 | 0.052937
2026-02-22 13:29 | 73.5062 | FALSE | FALSE | -0.48715 | -0.66716 | -0.54367 | -0.7342 | 0 |  |  | none | FALSE | 0 | 73.019 | FALSE | FALSE | 0.0073 |  | 73.5345 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.25771 | Normal | 74.0499 | -0.10966 | Day | 202602 | 2026-02-22 | 0.10966
2026-02-22 13:44 | 73.5062 | FALSE | FALSE | -0.45221 | -0.61901 | -0.53699 | -0.72524 | 0 |  |  | none | FALSE | 0 | 73.054 | FALSE | FALSE | 0.0114 |  | 73.5486 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.2473 | Normal | 74.0432 | -0.17141 | Day | 202602 | 2026-02-22 | 0.17141
2026-02-22 13:59 | 73.5062 | FALSE | FALSE | -0.41458 | -0.5672 | -0.52762 | -0.71267 | 0 |  |  | none | FALSE | 0 | 73.0916 | FALSE | FALSE | 0.016 |  | 73.5627 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.23555 | Normal | 74.0338 | -0.23995 | Day | 202602 | 2026-02-22 | 0.23995
2026-02-22 14:14 | 73.5062 | FALSE | FALSE | -0.41458 | -0.5672 | -0.52762 | -0.71267 | 0 |  |  | none | FALSE | 0 | 73.0916 | FALSE | FALSE | 0.016 |  | 73.5627 | 0 | 0 | 0 | 0.18338 | 0 | 0.23555 | Normal | 74.0338 | -0.23995 | Day | 202602 | 2026-02-22 | 0.23995
2026-02-22 14:29 | 73.5062 | FALSE | FALSE | -0.41458 | -0.5672 | -0.52762 | -0.71267 | 0 |  |  | none | FALSE | 0 | 73.0916 | FALSE | FALSE | 0.016 |  | 73.5627 | 0 | 0 | 0 | 0.18338 | 0 | 0.23555 | Normal | 74.0338 | -0.23995 | Day | 202602 | 2026-02-22 | 0.23995
2026-02-22 14:44 | 73.5062 | FALSE | FALSE | -0.37382 | -0.51116 | -0.51512 | -0.69591 | 0 |  |  | none | FALSE | 0 | 73.1324 | FALSE | FALSE | 0.0212 |  | 73.5768 | 0 | 0 | 0.01413 | 0.17092 | -0.082671 | 0.22224 | Normal | 74.0213 | -0.31791 | Day | 202602 | 2026-02-22 | 0.31791
2026-02-22 14:59 | 73.2236 | FALSE | FALSE | -0.13198 | -0.18057 | -0.81022 | -1.0944 | -0.2826 |  |  | none | FALSE | 0 | 73.0916 | FALSE | FALSE | 0.096 |  | 73.5627 | 0 | -0.2826 | -0.01413 | 0.17092 | -1.5708 | 0.23555 | Normal | 74.0338 | -1.4397 | Day | 202602 | 2026-02-22 | 1.4397
2026-02-22 15:14 | 72.941 | FALSE | FALSE | 0.0464 | 0.063572 | -1.1405 | -1.5395 | -0.2826 | 2026-02-22 16:28 | 2026-02-22 15:14 | lower | TRUE | 0 | 72.9874 | FALSE | FALSE | 0.2018 | 2.1696 | 73.5345 | 1 | -0.2826 | -0.02826 | 0.18107 | -1.4047 | 0.27353 | Extreme triggered | 74.0815 | -2.1696 | Day | 202602 | 2026-02-22 | 2.1696
2026-02-22 15:28 | 72.6584 | FALSE | FALSE | 0.16092 | 0.22098 | -1.4782 | -1.9938 | -0.2826 |  | 2026-02-22 15:14 | lower | TRUE | 0 | 72.8193 | FALSE | FALSE | 0.2802 | 2.3291 | 73.4779 | 2 | -0.2826 | -0.05652 | 0.17396 | -1.2996 | 0.32931 | Extreme/elevated | 74.1366 | -2.4887 | Day | 202602 | 2026-02-22 | 2.4887
2026-02-22 15:43 | 72.3758 | FALSE | FALSE | 0.25244 | 0.34758 | -1.7823 | -2.4033 | -0.2826 |  | 2026-02-22 15:14 | lower | TRUE | 0 | 72.6282 | FALSE | TRUE | 0.3488 | 2.4394 | 73.3932 | 3 | -0.2826 | -0.08478 | 0.16143 | -1.2254 | 0.38246 | Persistent | 74.1581 | -2.66 | Day | 202602 | 2026-02-22 | 2.66
2026-02-22 15:58 | 72.3758 | FALSE | FALSE | 0.11045 | 0.15238 | -1.7547 | -2.367 | 0 |  | 2026-02-22 15:14 | lower | TRUE | 0 | 72.4863 | FALSE | TRUE | 0.3798 | 2.3968 | 73.3084 | 4 | 0 | -0.08478 | 0.16143 | 0.52517 | 0.41106 | Persistent | 74.1305 | -2.2687 | Day | 202602 | 2026-02-22 | 2.2687
2026-02-22 16:13 | 72.095 | FALSE | FALSE | 0.17629 | 0.24393 | -2.0811 | -2.8056 | -0.2808 |  | 2026-02-22 15:14 | lower | TRUE | 0 | 72.2713 | FALSE | TRUE | 0.4437 | 2.3915 | 73.2237 | 5 | -0.2808 | -0.08469 | 0.16132 | -1.2157 | 0.4762 | Persistent | 74.1761 | -2.3702 | Day | 202602 | 2026-02-22 | 2.3702
2026-02-22 16:13 | 72.095 | FALSE | FALSE | 0.0058167 | 0.0080675 | -2.0822 | -2.807 | 0 |  | 2026-02-22 15:14 | lower | TRUE | 0 | 72.1008 | FALSE | TRUE | 0.4769 | 2.3281 | 73.139 | 6 | 0 | -0.08469 | 0.16132 | 0.52499 | 0.51909 | Persistent | 74.1772 | -2.0112 | Day | 202602 | 2026-02-22 | 2.0112
2026-02-22 16:28 | 72.6584 | TRUE | FALSE | -0.60606 | -0.84114 | -1.4825 | -1.9995 | 0.5634 |  |  | none | FALSE | 1 | 72.0523 | FALSE | FALSE | 0.0845 |  | 73.0966 | 0 | 0.5634 | -0.04239 | 0.2102 | 2.882 | 0.52213 | Persistence ends | 74.1409 | -0.83927 | Day | 202602 | 2026-02-22 | 0.83927
2026-02-22 16:44 | 72.941 | FALSE | FALSE | -0.90071 | -1.2503 | -1.1554 | -1.5593 | 0.2826 |  |  | none | FALSE | 1 | 72.0403 | FALSE | FALSE | 0.0451 |  | 73.0683 | 0 | 0.2826 | -0.02826 | 0.22235 | 1.3981 | 0.51403 | Normal | 74.0964 | -0.24775 | Day | 202602 | 2026-02-22 | 0.24775
2026-02-22 16:59 | 72.941 | FALSE | FALSE | -0.91363 | -1.2684 | -1.1401 | -1.5389 | 0 |  |  | none | FALSE | 1 | 72.0274 | FALSE | FALSE | 0.0433 |  | 73.0542 | 0 | 0 | -0.01413 | 0.21416 | 0.065978 | 0.51342 | Normal | 74.0811 | -0.22052 | Day | 202602 | 2026-02-22 | 0.22052
2026-02-22 17:13 | 72.941 | FALSE | FALSE | -0.92572 | -1.2854 | -1.1239 | -1.5175 | 0 |  |  | none | FALSE | 1 | 72.0153 | FALSE | FALSE | 0.0415 |  | 73.0401 | 0 | 0 | -0.01413 | 0.21416 | 0.065978 | 0.5124 | Normal | 74.0649 | -0.19338 | Day | 202602 | 2026-02-22 | 0.19338
2026-02-22 17:28 | 72.941 | FALSE | FALSE | -0.93077 | -1.2925 | -1.0724 | -1.449 | 0 |  |  | none | FALSE | 1 | 72.0102 | FALSE | FALSE | 0.038 |  | 73.0118 | 0 | 0 | -0.02826 | 0.20256 | 0.13951 | 0.5008 | Normal | 74.0134 | -0.14143 | Day | 202602 | 2026-02-22 | 0.14143
2026-02-22 17:30 | 72.941 | FALSE | FALSE | -0.93182 | -1.294 | -1.017 | -1.3751 | 0 |  |  | none | FALSE | 1 | 72.0092 | FALSE | FALSE | 0.0344 |  | 72.9836 | 0 | 0 | -0.02826 | 0.20256 | 0.13951 | 0.4872 | Normal | 73.958 | -0.087378 | Day | 202602 | 2026-02-22 | 0.087378
2026-02-22 17:31 | 72.941 | FALSE | FALSE | -0.92853 | -1.2894 | -0.95715 | -1.2952 | 0 |  |  | none | FALSE | 1 | 72.0125 | FALSE | FALSE | 0.0306 |  | 72.9553 | 0 | 0 | -0.02826 | 0.20256 | 0.13951 | 0.47142 | Normal | 73.8982 | -0.030355 | Day | 202602 | 2026-02-22 | 0.030355
2026-02-22 17:46 | 72.941 | FALSE | FALSE | -0.92045 | -1.278 | -0.89255 | -1.2089 | 0 |  |  | none | FALSE | 1 | 72.0205 | FALSE | FALSE | 0.0306 |  | 72.927 | 0 | 0 | -0.02826 | 0.20256 | 0.13951 | 0.45325 | Normal | 73.8336 | 0.030778 | Day | 202602 | 2026-02-22 | 0.030778
2026-02-22 18:01 | 73.5062 | TRUE | FALSE | -1.4857 | -2.0628 | -0.32735 | -0.44336 | 0.5652 |  |  | none | FALSE | 2 | 72.0205 | TRUE | FALSE | 0.1423 |  | 72.927 | 0 | 0.5652 | 0 | 0.24225 | 2.3331 | 0.45325 | Normal | 73.8336 | 1.2778 | Day | 202602 | 2026-02-22 | 1.2778
2026-02-22 18:16 | 73.7888 | FALSE | FALSE | -1.7998 | -2.5001 | -0.10455 | -0.14149 | 0.2826 |  |  | none | FALSE | 2 | 71.989 | FALSE | FALSE | 0.1758 |  | 72.9412 | 0 | 0.2826 | 0.01413 | 0.25036 | 1.0723 | 0.47609 | Normal | 73.8934 | 1.7804 | Day | 202602 | 2026-02-22 | 1.7804
2026-02-22 18:30 | 74.0714 | FALSE | FALSE | -2.1531 | -2.9939 | 0.050778 | 0.0686 | 0.2826 | 2026-02-22 20:29 | 2026-02-22 18:30 | upper | TRUE | 1 | 71.9183 | FALSE | FALSE | 0.2255 | 2.0966 | 72.9694 | 1 | 0.2826 | 0.02826 | 0.25739 | 0.98813 | 0.52559 | Extreme triggered | 74.0206 | 2.0966 | Night | 202602 | 2026-02-22 | 2.0966
2026-02-22 18:45 | 74.0714 | FALSE | FALSE | -2.2124 | -3.0788 | -0.064988 | -0.08766 | 0 |  | 2026-02-22 18:30 | none | FALSE | 1 | 71.859 | FALSE | FALSE | 0.2686 | 1.9912 | 72.9977 | 2 | 0 | 0.02826 | 0.25739 | -0.10979 | 0.56934 | Extreme/elevated | 74.1364 | 1.8859 | Night | 202602 | 2026-02-22 | 1.8859
2026-02-22 19:00 | 74.0714 | FALSE | FALSE | -2.2626 | -3.1509 | -0.17173 | -0.23131 | 0 |  | 2026-02-22 18:30 | none | FALSE | 1 | 71.8088 | FALSE | FALSE | 0.3145 | 1.9001 | 73.026 | 3 | 0 | 0.02826 | 0.25739 | -0.10979 | 0.60859 | Persistent | 74.2431 | 1.7178 | Night | 202602 | 2026-02-22 | 1.7178
2026-02-22 19:15 | 74.0714 | FALSE | FALSE | -2.3053 | -3.2122 | -0.29919 | -0.40229 | 0 |  | 2026-02-22 18:30 | none | FALSE | 1 | 71.7661 | FALSE | FALSE | 0.3598 | 1.8102 | 73.0683 | 4 | 0 | 0.04239 | 0.24698 | -0.17164 | 0.65112 | Persistent | 74.3706 | 1.5405 | Night | 202602 | 2026-02-22 | 1.5405
2026-02-22 19:29 | 74.0714 | FALSE | FALSE | -2.3216 | -3.2357 | -0.42852 | -0.5752 | 0 |  | 2026-02-22 18:30 | none | FALSE | 1 | 71.7498 | FALSE | FALSE | 0.4061 | 1.7235 | 73.1249 | 5 | 0 | 0.05652 | 0.23521 | -0.2403 | 0.68753 | Persistent | 74.4999 | 1.3767 | Night | 202602 | 2026-02-22 | 1.3767
2026-02-22 19:44 | 74.0714 | FALSE | FALSE | -2.2945 | -3.1967 | -0.54276 | -0.72743 | 0 |  | 2026-02-22 18:30 | none | FALSE | 1 | 71.7769 | FALSE | FALSE | 0.4537 | 1.6421 | 73.1955 | 6 | 0 | 0.07065 | 0.22188 | -0.31842 | 0.70932 | Persistent | 74.6142 | 1.2348 | Night | 202602 | 2026-02-22 | 1.2348
2026-02-22 19:59 | 74.0714 | FALSE | TRUE | -2.2061 | -3.0698 | -0.62394 | -0.83531 | 0 |  | 2026-02-22 18:30 | none | FALSE | 1 | 71.8653 | FALSE | FALSE | 0.5031 | 1.5672 | 73.2803 | 7 | 0 | 0.08478 | 0.20667 | -0.41021 | 0.70752 | Confirmed/Materialized Shift | 74.6953 | 1.1181 | Night | 202602 | 2026-02-22 | 1.1181
2026-02-22 20:14 | 74.0714 | FALSE | TRUE | -2.0961 | -2.9123 | -0.6835 | -0.91432 | 0 |  | 2026-02-22 18:30 | none | FALSE | 1 | 71.9753 | FALSE | FALSE | 0.4963 | 1.4984 | 73.3651 | 8 | 0 | 0.08478 | 0.20667 | -0.41021 | 0.69491 | Confirmed/Materialized Shift | 74.7549 | 1.0164 | Night | 202602 | 2026-02-22 | 1.0164
2026-02-22 20:29 | 74.0714 | FALSE | FALSE | -1.8943 | -2.6245 | -0.67932 | -0.90878 | 0 |  |  | none | FALSE | 0 | 72.1771 | FALSE | FALSE | 0.0629 |  | 73.4639 | 0 | 0 | 0.09882 | 0.18934 | -0.52192 | 0.64341 | Persistence ends | 74.7507 | 0.94419 | Night | 202602 | 2026-02-22 | 0.94419
2026-02-22 20:44 | 73.7888 | FALSE | FALSE | -1.3598 | -1.8774 | -0.87935 | -1.1777 | -0.2826 |  |  | none | FALSE | 0 | 72.429 | FALSE | FALSE | 0.0286 |  | 73.5486 | 0 | -0.2826 | 0.08469 | 0.20684 | -1.7757 | 0.55978 | Normal | 74.6682 | 0.42911 | Night | 202602 | 2026-02-22 | 0.42911
2026-02-22 20:59 | 73.7888 | FALSE | FALSE | -1.2255 | -1.6888 | -0.85808 | -1.1495 | 0 |  |  | none | FALSE | 0 | 72.5633 | FALSE | FALSE | 0.0235 |  | 73.6051 | 0 | 0 | 0.05652 | 0.17396 | -0.32489 | 0.52089 | Normal | 74.6469 | 0.35265 | Night | 202602 | 2026-02-22 | 0.35265
2026-02-22 21:14 | 73.7888 | FALSE | FALSE | -1.1373 | -1.5654 | -0.85468 | -1.145 | 0 |  |  | none | FALSE | 0 | 72.6515 | FALSE | FALSE | 0.0189 |  | 73.6475 | 0 | 0 | 0.04239 | 0.16593 | -0.25547 | 0.49799 | Normal | 74.6435 | 0.28374 | Night | 202602 | 2026-02-22 | 0.28374
2026-02-22 21:29 | 73.5062 | FALSE | FALSE | -0.77264 | -1.0623 | -1.1118 | -1.4899 | -0.2826 |  |  | none | FALSE | 0 | 72.7336 | FALSE | FALSE | 0.024 |  | 73.6758 | 0 | -0.2826 | 0.02826 | 0.18107 | -1.7168 | 0.4711 | Normal | 74.618 | -0.35992 | Night | 202602 | 2026-02-22 | 0.35992
2026-02-22 21:44 | 73.5062 | FALSE | FALSE | -0.68353 | -0.93862 | -1.0792 | -1.4469 | 0 |  |  | none | FALSE | 0 | 72.8227 | FALSE | FALSE | 0.0299 |  | 73.704 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.44067 | Normal | 74.5854 | -0.4489 | Night | 202602 | 2026-02-22 | 0.4489
2026-02-22 21:59 | 73.5062 | FALSE | FALSE | -0.58576 | -0.80328 | -1.0379 | -1.3924 | 0 |  |  | none | FALSE | 0 | 72.9204 | FALSE | FALSE | 0.0371 |  | 73.7323 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.40592 | Normal | 74.5441 | -0.55696 | Night | 202602 | 2026-02-22 | 0.55696
2026-02-22 22:14 | 73.5062 | FALSE | FALSE | -0.47686 | -0.65298 | -0.98554 | -1.323 | 0 |  |  | none | FALSE | 0 | 73.0293 | FALSE | FALSE | 0.0464 |  | 73.7605 | 0 | 0 | 0.02826 | 0.18107 | -0.15607 | 0.3656 | Normal | 74.4917 | -0.69567 | Night | 202602 | 2026-02-22 | 0.69567
2026-02-22 22:28 | 73.2236 | FALSE | FALSE | -0.12207 | -0.16699 | -1.2242 | -1.6444 | -0.2826 |  |  | none | FALSE | 0 | 73.1015 | FALSE | FALSE | 0.1092 |  | 73.7747 | 0 | -0.2826 | 0.01413 | 0.19396 | -1.5299 | 0.33657 | Normal | 74.4478 | -1.6373 | Night | 202602 | 2026-02-22 | 1.6373
2026-02-22 22:43 | 73.2236 | FALSE | FALSE | -0.042986 | -0.05874 | -1.1734 | -1.5772 | 0 |  |  | none | FALSE | 0 | 73.1806 | FALSE | FALSE | 0.1239 |  | 73.7888 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.30409 | Normal | 74.397 | -1.8586 | Night | 202602 | 2026-02-22 | 1.8586
2026-02-22 22:59 | 73.2236 | FALSE | FALSE | -0.09661 | -0.13211 | -1.1988 | -1.6107 | 0 |  |  | none | FALSE | 0 | 73.127 | FALSE | FALSE | 0.1134 |  | 73.7747 | 0 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.32384 | Normal | 74.4224 | -1.7017 | Night | 202602 | 2026-02-22 | 1.7017
2026-02-22 23:14 | 73.2236 | FALSE | FALSE | -0.17002 | -0.23274 | -1.2156 | -1.6331 | 0 |  |  | none | FALSE | 0 | 73.0536 | FALSE | FALSE | 0.1006 |  | 73.7464 | 0 | 0 | -0.02826 | 0.12638 | 0.22361 | 0.34642 | Normal | 74.4392 | -1.5092 | Night | 202602 | 2026-02-22 | 1.5092
2026-02-22 23:28 | 72.941 | FALSE | FALSE | -0.013276 | -0.018204 | -1.5111 | -2.0296 | -0.2826 |  |  | none | FALSE | 0 | 72.9277 | FALSE | FALSE | 0.131 |  | 73.6899 | 0 | -0.2826 | -0.05652 | 0.11598 | -1.9494 | 0.38108 | Normal | 74.4521 | -1.9652 | Night | 202602 | 2026-02-22 | 1.9652
2026-02-22 23:43 | 72.941 | FALSE | FALSE | -0.11687 | -0.16049 | -1.5016 | -2.0171 | 0 |  |  | none | FALSE | 0 | 72.8241 | FALSE | FALSE | 0.1141 |  | 73.6334 | 0 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.40462 | Normal | 74.4426 | -1.7112 | Night | 202602 | 2026-02-22 | 1.7112
2026-02-22 23:58 | 72.941 | FALSE | FALSE | -0.20198 | -0.27767 | -1.4737 | -1.9804 | 0 |  |  | none | FALSE | 0 | 72.739 | FALSE | FALSE | 0.1012 |  | 73.5768 | 0 | 0 | -0.05652 | 0.11598 | 0.48734 | 0.41891 | Normal | 74.4147 | -1.5179 | Night | 202602 | 2026-02-22 | 1.5179
2026-02-23 00:13 | 72.6584 | FALSE | FALSE | -0.050551 | -0.069622 | -1.7462 | -2.3468 | -0.2826 |  |  | none | FALSE | 0 | 72.6078 | FALSE | FALSE | 0.1258 |  | 73.5062 | 0 | -0.2826 | -0.07065 | 0.12555 | -1.6882 | 0.44918 | Normal | 74.4046 | -1.8875 | Night | 202602 | 2026-02-23 | 1.8875
2026-02-23 00:28 | 72.3758 | FALSE | FALSE | 0.056414 | 0.077885 | -2.0348 | -2.7346 | -0.2826 | 2026-02-23 08:00 | 2026-02-23 00:28 | lower | TRUE | 0 | 72.4322 | FALSE | FALSE | 0.1981 | 2.1141 | 73.4214 | 1 | -0.2826 | -0.08478 | 0.13287 | -1.4888 | 0.4946 | Extreme triggered | 74.4106 | -2.1141 | Night | 202602 | 2026-02-23 | 2.1141
2026-02-23 00:43 | 72.3758 | FALSE | FALSE | -0.082949 | -0.11474 | -2.0046 | -2.6951 | 0 |  | 2026-02-23 00:28 | none | FALSE | 0 | 72.2929 | FALSE | FALSE | 0.237 | 1.9776 | 73.3366 | 2 | 0 | -0.08478 | 0.13287 | 0.63808 | 0.52189 | Extreme/elevated | 74.3804 | -1.8411 | Night | 202602 | 2026-02-23 | 1.8411
2026-02-23 00:58 | 72.3758 | FALSE | FALSE | -0.19162 | -0.26546 | -1.9437 | -2.6154 | 0 |  | 2026-02-23 00:28 | none | FALSE | 0 | 72.1842 | FALSE | FALSE | 0.2808 | 1.8654 | 73.2519 | 3 | 0 | -0.08478 | 0.13287 | 0.63808 | 0.53384 | Persistent | 74.3195 | -1.6411 | Night | 202602 | 2026-02-23 | 1.6411
2026-02-23 01:13 | 72.095 | FALSE | FALSE | -0.055141 | -0.076542 | -2.1712 | -2.9236 | -0.2808 |  | 2026-02-23 00:28 | none | FALSE | 0 | 72.0399 | FALSE | FALSE | 0.3553 | 1.8743 | 73.153 | 4 | -0.2808 | -0.09882 | 0.13817 | -1.3171 | 0.55659 | Persistent | 74.2662 | -1.9009 | Night | 202602 | 2026-02-23 | 1.9009
2026-02-23 01:28 | 72.095 | FALSE | FALSE | -0.16157 | -0.22461 | -2.08 | -2.8042 | 0 |  | 2026-02-23 00:28 | none | FALSE | 0 | 71.9334 | FALSE | FALSE | 0.3998 | 1.8418 | 73.0542 | 5 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.5604 | Persistent | 74.175 | -1.7117 | Night | 202602 | 2026-02-23 | 1.7117
2026-02-23 01:43 | 72.095 | FALSE | FALSE | -0.26831 | -0.37355 | -2.0174 | -2.722 | 0 |  | 2026-02-23 00:28 | none | FALSE | 0 | 71.8267 | FALSE | FALSE | 0.4449 | 1.7899 | 72.9695 | 6 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.57142 | Persistent | 74.1124 | -1.5305 | Night | 202602 | 2026-02-23 | 1.5305
2026-02-23 01:58 | 71.8124 | FALSE | TRUE | -0.12724 | -0.1775 | -2.2439 | -3.0299 | -0.2826 |  | 2026-02-23 00:28 | none | FALSE | 0 | 71.6852 | FALSE | FALSE | 0.519 | 1.7892 | 72.8707 | 7 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.59278 | Confirmed/Materialized Shift | 74.0563 | -1.7853 | Night | 202602 | 2026-02-23 | 1.7853
2026-02-23 02:13 | 71.5298 | FALSE | TRUE | -0.018197 | -0.025446 | -2.4741 | -3.3432 | -0.2826 |  | 2026-02-23 00:28 | none | FALSE | 0 | 71.5116 | FALSE | FALSE | 0.5314 | 1.8119 | 72.7578 | 8 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.62308 | Confirmed/Materialized Shift | 74.0039 | -1.9708 | Night | 202602 | 2026-02-23 | 1.9708
2026-02-23 02:27 | 71.5298 | FALSE | TRUE | -0.17903 | -0.25092 | -2.4373 | -3.2951 | 0 |  | 2026-02-23 00:28 | none | FALSE | 0 | 71.3508 | FALSE | FALSE | 0.5151 | 1.8024 | 72.6589 | 9 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.65409 | Confirmed/Materialized Shift | 73.9671 | -1.7263 | Night | 202602 | 2026-02-23 | 1.7263
2026-02-23 02:42 | 71.5298 | FALSE | TRUE | -0.30665 | -0.43054 | -2.3673 | -3.2035 | 0 |  | 2026-02-23 00:28 | none | FALSE | 0 | 71.2232 | FALSE | FALSE | 0.5028 | 1.7763 | 72.5601 | 10 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.66848 | Confirmed/Materialized Shift | 73.8971 | -1.5413 | Night | 202602 | 2026-02-23 | 1.5413
2026-02-23 02:57 | 71.2472 | FALSE | TRUE | -0.18141 | -0.25528 | -2.5814 | -3.4964 | -0.2826 |  | 2026-02-23 00:28 | none | FALSE | 0 | 71.0658 | FALSE | FALSE | 0.5158 | 1.7728 | 72.4472 | 11 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.69069 | Confirmed/Materialized Shift | 73.8286 | -1.7373 | Night | 202602 | 2026-02-23 | 1.7373
2026-02-23 03:12 | 71.2472 | FALSE | TRUE | -0.29917 | -0.42168 | -2.4732 | -3.3549 | 0 |  | 2026-02-23 00:28 | none | FALSE | 0 | 70.948 | FALSE | FALSE | 0.5046 | 1.7557 | 72.3342 | 12 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.6931 | Confirmed/Materialized Shift | 73.7204 | -1.5684 | Night | 202602 | 2026-02-23 | 1.5684
2026-02-23 03:27 | 70.9646 | FALSE | TRUE | -0.19116 | -0.2701 | -2.7045 | -3.6711 | -0.2826 |  | 2026-02-23 00:28 | none | FALSE | 0 | 70.7734 | FALSE | FALSE | 0.5157 | 1.7542 | 72.2213 | 13 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.72391 | Confirmed/Materialized Shift | 73.6691 | -1.7359 | Night | 202602 | 2026-02-23 | 1.7359
2026-02-23 03:42 | 70.682 | FALSE | TRUE | -0.10949 | -0.15515 | -2.9339 | -3.9854 | -0.2826 |  | 2026-02-23 00:28 | none | FALSE | 0 | 70.5725 | FALSE | FALSE | 0.5237 | 1.7615 | 72.0942 | 14 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.76084 | Confirmed/Materialized Shift | 73.6159 | -1.8561 | Night | 202602 | 2026-02-23 | 1.8561
2026-02-23 03:57 | 70.682 | FALSE | TRUE | -0.2637 | -0.37448 | -2.8339 | -3.8548 | 0 |  | 2026-02-23 00:28 | none | FALSE | 0 | 70.4183 | FALSE | FALSE | 0.5106 | 1.7547 | 71.9671 | 15 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.77441 | Confirmed/Materialized Shift | 73.5159 | -1.6595 | Night | 202602 | 2026-02-23 | 1.6595
2026-02-23 04:12 | 70.3994 | FALSE | TRUE | -0.15461 | -0.2201 | -3.0076 | -4.0972 | -0.2826 |  | 2026-02-23 00:28 | none | FALSE | 0 | 70.2448 | FALSE | FALSE | 0.5203 | 1.7578 | 71.8259 | 16 | -0.2826 | -0.14121 | 0.14488 | -0.97592 | 0.79055 | Confirmed/Materialized Shift | 73.407 | -1.8044 | Night | 202602 | 2026-02-23 | 1.8044
2026-02-23 04:27 | 70.3994 | FALSE | TRUE | -0.31258 | -0.44598 | -2.9114 | -3.9713 | 0 |  | 2026-02-23 00:28 | none | FALSE | 0 | 70.0868 | FALSE | FALSE | 0.5075 | 1.7492 | 71.6988 | 17 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.806 | Confirmed/Materialized Shift | 73.3108 | -1.6122 | Night | 202602 | 2026-02-23 | 1.6122
2026-02-23 04:42 | 70.1168 | FALSE | TRUE | -0.20741 | -0.29669 | -3.089 | -4.2197 | -0.2826 |  | 2026-02-23 00:28 | none | FALSE | 0 | 69.9094 | FALSE | FALSE | 0.5166 | 1.7492 | 71.5576 | 18 | -0.2826 | -0.14121 | 0.14488 | -0.97592 | 0.82411 | Confirmed/Materialized Shift | 73.2058 | -1.7483 | Night | 202602 | 2026-02-23 | 1.7483
2026-02-23 04:57 | 70.1168 | FALSE | TRUE | -0.33344 | -0.47782 | -2.9326 | -4.0146 | 0 |  | 2026-02-23 00:28 | none | FALSE | 0 | 69.7834 | FALSE | FALSE | 0.5061 | 1.7409 | 71.4164 | 19 | 0 | -0.14121 | 0.14488 | 0.97468 | 0.81652 | Confirmed/Materialized Shift | 73.0494 | -1.5916 | Night | 202602 | 2026-02-23 | 1.5916
2026-02-23 05:12 | 70.1168 | FALSE | TRUE | -0.4491 | -0.64462 | -2.7941 | -3.8323 | 0 |  | 2026-02-23 00:28 | none | FALSE | 0 | 69.6677 | FALSE | FALSE | 0.4964 | 1.7261 | 71.2893 | 20 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.81081 | Confirmed/Materialized Shift | 72.9109 | -1.4461 | Night | 202602 | 2026-02-23 | 1.4461
2026-02-23 05:26 | 69.836 | FALSE | TRUE | -0.33436 | -0.48108 | -2.987 | -4.1017 | -0.2808 |  | 2026-02-23 00:28 | none | FALSE | 0 | 69.5016 | FALSE | FALSE | 0.5065 | 1.72 | 71.1623 | 21 | -0.2808 | -0.12699 | 0.14404 | -1.0678 | 0.83034 | Confirmed/Materialized Shift | 72.823 | -1.5973 | Night | 202602 | 2026-02-23 | 1.5973
2026-02-23 05:41 | 69.836 | FALSE | TRUE | -0.45907 | -0.66171 | -2.8578 | -3.9312 | 0 |  | 2026-02-23 00:28 | none | FALSE | 0 | 69.3769 | FALSE | FALSE | 0.4964 | 1.7076 | 71.0353 | 22 | 0 | -0.12699 | 0.14404 | 0.88163 | 0.82921 | Confirmed/Materialized Shift | 72.6938 | -1.4464 | Night | 202602 | 2026-02-23 | 1.4464
2026-02-23 05:56 | 69.5534 | FALSE | TRUE | -0.31766 | -0.4588 | -2.9993 | -4.134 | -0.2826 |  | 2026-02-23 00:28 | none | FALSE | 0 | 69.2357 | FALSE | FALSE | 0.5078 | 1.7036 | 70.8942 | 23 | -0.2826 | -0.14112 | 0.14479 | -0.97716 | 0.82924 | Confirmed/Materialized Shift | 72.5527 | -1.6169 | Night | 202602 | 2026-02-23 | 1.6169
2026-02-23 06:11 | 69.5534 | FALSE | TRUE | -0.44683 | -0.64657 | -2.8743 | -3.9685 | 0 |  | 2026-02-23 00:28 | none | FALSE | 0 | 69.1066 | FALSE | FALSE | 0.4975 | 1.6936 | 70.7671 | 24 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.83028 | Confirmed/Materialized Shift | 72.4277 | -1.4618 | Night | 202602 | 2026-02-23 | 1.4618
2026-02-23 06:26 | 69.2708 | FALSE | TRUE | -0.31031 | -0.44998 | -3.0206 | -4.1783 | -0.2826 |  | 2026-02-23 00:28 | none | FALSE | 0 | 68.9605 | FALSE | FALSE | 0.5085 | 1.6909 | 70.6259 | 25 | -0.2826 | -0.14121 | 0.14488 | -0.97592 | 0.83272 | Confirmed/Materialized Shift | 72.2914 | -1.6274 | Night | 202602 | 2026-02-23 | 1.6274
2026-02-23 06:41 | 69.2708 | FALSE | TRUE | -0.40533 | -0.58859 | -2.8332 | -3.9293 | 0 |  | 2026-02-23 00:28 | none | FALSE | 0 | 68.8655 | FALSE | FALSE | 0.5 | 1.6835 | 70.4847 | 26 | 0 | -0.14121 | 0.14488 | 0.97468 | 0.80963 | Confirmed/Materialized Shift | 72.104 | -1.4994 | Night | 202602 | 2026-02-23 | 1.4994
2026-02-23 06:56 | 68.9882 | FALSE | TRUE | -0.26901 | -0.39146 | -2.9796 | -4.1402 | -0.2826 |  | 2026-02-23 00:28 | none | FALSE | 0 | 68.7192 | FALSE | FALSE | 0.5113 | 1.683 | 70.3435 | 27 | -0.2826 | -0.14121 | 0.14488 | -0.97592 | 0.81216 | Confirmed/Materialized Shift | 71.9678 | -1.6688 | Day | 202602 | 2026-02-23 | 1.6688
2026-02-23 07:11 | 68.9882 | FALSE | TRUE | -0.40298 | -0.58756 | -2.8594 | -3.9799 | 0 |  | 2026-02-23 00:28 | none | FALSE | 0 | 68.5852 | FALSE | FALSE | 0.5004 | 1.6767 | 70.2164 | 28 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.81561 | Confirmed/Materialized Shift | 71.8476 | -1.5059 | Day | 202602 | 2026-02-23 | 1.5059
2026-02-23 07:26 | 68.9882 | FALSE | TRUE | -0.49488 | -0.72252 | -2.6972 | -3.7625 | 0 |  | 2026-02-23 00:28 | none | FALSE | 0 | 68.4933 | FALSE | FALSE | 0.492 | 1.6664 | 70.0893 | 29 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.79801 | Confirmed/Materialized Shift | 71.6854 | -1.3799 | Day | 202602 | 2026-02-23 | 1.3799
2026-02-23 07:30 | 68.7056 | FALSE | TRUE | -0.31619 | -0.46233 | -2.8013 | -3.9175 | -0.2826 |  | 2026-02-23 00:28 | none | FALSE | 0 | 68.3894 | FALSE | FALSE | 0.5063 | 1.664 | 69.9481 | 30 | -0.2826 | -0.14121 | 0.14488 | -0.97592 | 0.77936 | Confirmed/Materialized Shift | 71.5069 | -1.5943 | Day | 202602 | 2026-02-23 | 1.5943
2026-02-23 07:45 | 68.9882 | TRUE | TRUE | -0.64118 | -0.93812 | -2.3352 | -3.274 | 0.2826 |  | 2026-02-23 00:28 | none | FALSE | 1 | 68.347 | FALSE | FALSE | 0.5045 | 1.6471 | 69.8352 | 31 | 0.2826 | -0.11295 | 0.16897 | 2.341 | 0.74408 | Confirmed/Materialized Shift | 71.3234 | -1.1383 | Day | 202602 | 2026-02-23 | 1.1383
2026-02-23 08:00 | 69.2708 | TRUE | FALSE | -0.88381 | -1.2924 | -1.815 | -2.5532 | 0.2826 |  |  | none | FALSE | 2 | 68.387 | TRUE | FALSE | 0.1031 |  | 69.7364 | 0 | 0.2826 | -0.09882 | 0.18948 | 2.013 | 0.67469 | Persistence ends | 71.0858 | -0.69005 | Day | 202602 | 2026-02-23 | 0.69005
2026-02-23 08:16 | 69.2708 | FALSE | FALSE | -0.85147 | -1.2445 | -1.6132 | -2.2759 | 0 |  |  | none | FALSE | 2 | 68.4193 | FALSE | FALSE | 0.0984 |  | 69.6517 | 0 | 0 | -0.08469 | 0.18555 | 0.45642 | 0.61617 | Normal | 70.884 | -0.61814 | Day | 202602 | 2026-02-23 | 0.61814
2026-02-23 08:30 | 69.2708 | FALSE | FALSE | -0.83195 | -1.2156 | -1.4526 | -2.0539 | 0 |  |  | none | FALSE | 2 | 68.4389 | FALSE | FALSE | 0.0934 |  | 69.5811 | 0 | 0 | -0.07056 | 0.18038 | 0.39118 | 0.57113 | Normal | 70.7234 | -0.54334 | Day | 202602 | 2026-02-23 | 0.54334
2026-02-23 08:45 | 69.5534 | FALSE | FALSE | -1.0467 | -1.5279 | -0.98932 | -1.4024 | 0.2826 |  |  | none | FALSE | 2 | 68.5067 | FALSE | FALSE | 0.0609 |  | 69.5247 | 0 | 0.2826 | -0.05643 | 0.19654 | 1.725 | 0.50901 | Normal | 70.5427 | 0.056403 | Day | 202602 | 2026-02-23 | 0.056403
2026-02-23 08:45 | 69.5534 | FALSE | FALSE | -1.0026 | -1.4626 | -0.86063 | -1.2222 | 0 |  |  | none | FALSE | 2 | 68.5508 | FALSE | FALSE | 0.0673 |  | 69.4824 | 0 | 0 | -0.0423 | 0.18945 | 0.22327 | 0.46582 | Normal | 70.414 | 0.15244 | Day | 202602 | 2026-02-23 | 0.15244
2026-02-23 09:00 | 69.836 | FALSE | FALSE | -1.2267 | -1.788 | -0.46314 | -0.65882 | 0.2826 |  |  | none | FALSE | 2 | 68.6093 | FALSE | FALSE | 0.1174 |  | 69.4542 | 0 | 0.2826 | -0.02817 | 0.20284 | 1.5321 | 0.42246 | Normal | 70.2991 | 0.9037 | Day | 202602 | 2026-02-23 | 0.9037
2026-02-23 09:15 | 70.1168 | FALSE | FALSE | -1.5075 | -2.1972 | -0.18234 | -0.25938 | 0.2808 |  |  | none | FALSE | 2 | 68.6093 | FALSE | FALSE | 0.1617 |  | 69.4542 | 0 | 0.2808 | 0 | 0.20476 | 1.3714 | 0.42246 | Normal | 70.2991 | 1.5684 | Day | 202602 | 2026-02-23 | 1.5684
2026-02-23 09:30 | 70.1168 | FALSE | FALSE | -1.5075 | -2.1972 | -0.18234 | -0.25938 | 0 |  |  | none | FALSE | 2 | 68.6093 | FALSE | FALSE | 0.1617 |  | 69.4542 | 0 | 0 | 0 | 0.20476 | 0 | 0.42246 | Normal | 70.2991 | 1.5684 | Day | 202602 | 2026-02-23 | 1.5684
2026-02-23 09:44 | 70.3994 | FALSE | FALSE | -1.8303 | -2.6693 | 0.031769 | 0.045147 | 0.2826 | 2026-02-23 17:57 | 2026-02-23 09:44 | upper | TRUE | 2 | 68.5691 | FALSE | FALSE | 0.2523 | 2.0707 | 69.4684 | 1 | 0.2826 | 0.01413 | 0.21429 | 1.2528 | 0.44964 | Extreme triggered | 70.3676 | 2.0707 | Day | 202602 | 2026-02-23 | 2.0707
2026-02-23 09:59 | 70.3994 | FALSE | FALSE | -1.8824 | -2.7473 | -0.076612 | -0.10871 | 0 |  | 2026-02-23 09:44 | none | FALSE | 1 | 68.517 | FALSE | FALSE | 0.2658 | 1.9571 | 69.4965 | 2 | 0 | 0.02817 | 0.20284 | -0.13888 | 0.48975 | Extreme/elevated | 70.476 | 1.8436 | Day | 202602 | 2026-02-23 | 1.8436
2026-02-23 10:14 | 70.682 | FALSE | FALSE | -2.2493 | -3.2869 | 0.037072 | 0.052477 | 0.2826 |  | 2026-02-23 09:44 | upper | TRUE | 0 | 68.4327 | FALSE | TRUE | 0.3092 | 1.9938 | 69.5388 | 3 | 0.2826 | 0.0423 | 0.21047 | 1.1417 | 0.55305 | Persistent | 70.6449 | 2.067 | Day | 202602 | 2026-02-23 | 2.067
2026-02-23 10:30 | 70.9646 | FALSE | FALSE | -2.6321 | -3.8519 | 0.078335 | 0.11051 | 0.2826 |  | 2026-02-23 09:44 | upper | TRUE | 0 | 68.3325 | FALSE | TRUE | 0.3701 | 2.026 | 69.6094 | 4 | 0.2826 | 0.07056 | 0.20234 | 1.0479 | 0.63844 | Persistent | 70.8863 | 2.1227 | Day | 202602 | 2026-02-23 | 2.1227
2026-02-23 10:44 | 71.2472 | FALSE | FALSE | -3.0243 | -4.4329 | 0.081973 | 0.11519 | 0.2826 |  | 2026-02-23 09:44 | upper | TRUE | 0 | 68.2229 | FALSE | TRUE | 0.4265 | 2.0431 | 69.6941 | 5 | 0.2826 | 0.08469 | 0.20697 | 0.95623 | 0.73558 | Persistent | 71.1652 | 2.1114 | Day | 202602 | 2026-02-23 | 2.1114
2026-02-23 10:59 | 71.5298 | FALSE | FALSE | -3.3908 | -4.9763 | 0.054751 | 0.076601 | 0.2826 |  | 2026-02-23 09:44 | upper | TRUE | 0 | 68.139 | FALSE | TRUE | 0.4806 | 2.0468 | 69.807 | 6 | 0.2826 | 0.11295 | 0.19224 | 0.88248 | 0.83401 | Persistent | 71.475 | 2.0656 | Day | 202602 | 2026-02-23 | 2.0656
2026-02-23 11:14 | 71.8124 | FALSE | TRUE | -3.7492 | -5.5085 | 0.0073553 | 0.010243 | 0.2826 |  | 2026-02-23 09:44 | upper | TRUE | 0 | 68.0632 | FALSE | TRUE | 0.5339 | 2.0413 | 69.9341 | 7 | 0.2826 | 0.12708 | 0.19388 | 0.80214 | 0.93547 | Confirmed/Materialized Shift | 71.805 | 2.0079 | Day | 202602 | 2026-02-23 | 2.0079
2026-02-23 11:29 | 71.8124 | FALSE | TRUE | -3.7298 | -5.4783 | -0.25561 | -0.35468 | 0 |  | 2026-02-23 09:44 | none | FALSE | 0 | 68.0826 | FALSE | FALSE | 0.5162 | 2.004 | 70.0753 | 8 | 0 | 0.14121 | 0.17145 | -0.8236 | 0.99635 | Confirmed/Materialized Shift | 72.068 | 1.7435 | Day | 202602 | 2026-02-23 | 1.7435
2026-02-23 11:44 | 72.095 | FALSE | TRUE | -3.9808 | -5.8442 | -0.25207 | -0.34841 | 0.2826 |  | 2026-02-23 09:44 | none | FALSE | 0 | 68.1142 | FALSE | FALSE | 0.5175 | 1.9771 | 70.2306 | 9 | 0.2826 | 0.15534 | 0.17085 | 0.74487 | 1.0582 | Confirmed/Materialized Shift | 72.3471 | 1.7618 | Day | 202602 | 2026-02-23 | 1.7618
2026-02-23 11:59 | 72.095 | FALSE | TRUE | -3.8963 | -5.7132 | -0.47831 | -0.65907 | 0 |  | 2026-02-23 09:44 | none | FALSE | 0 | 68.1987 | FALSE | FALSE | 0.5042 | 1.9357 | 70.386 | 10 | 0 | 0.15534 | 0.17085 | -0.90923 | 1.0937 | Confirmed/Materialized Shift | 72.5733 | 1.5627 | Day | 202602 | 2026-02-23 | 1.5627
2026-02-23 12:14 | 72.095 | FALSE | TRUE | -3.7038 | -5.4156 | -0.62468 | -0.85903 | 0 |  | 2026-02-23 09:44 | none | FALSE | 0 | 68.3912 | FALSE | FALSE | 0.4948 | 1.889 | 70.5555 | 11 | 0 | 0.16947 | 0.14197 | -1.1937 | 1.0821 | Confirmed/Materialized Shift | 72.7197 | 1.4227 | Day | 202602 | 2026-02-23 | 1.4227
2026-02-23 12:29 | 72.3758 | FALSE | TRUE | -3.8289 | -5.5859 | -0.52701 | -0.7229 | 0.2808 |  | 2026-02-23 09:44 | none | FALSE | 0 | 68.5469 | FALSE | FALSE | 0.5011 | 1.858 | 70.7248 | 12 | 0.2808 | 0.16938 | 0.14189 | 0.78525 | 1.089 | Confirmed/Materialized Shift | 72.9028 | 1.5161 | Day | 202602 | 2026-02-23 | 1.5161
2026-02-23 12:43 | 72.3758 | FALSE | TRUE | -3.6799 | -5.3568 | -0.68851 | -0.94233 | 0 |  | 2026-02-23 09:44 | none | FALSE | 0 | 68.6959 | FALSE | FALSE | 0.4913 | 1.8204 | 70.8801 | 13 | 0 | 0.15525 | 0.14408 | -1.0775 | 1.0921 | Confirmed/Materialized Shift | 73.0643 | 1.3696 | Day | 202602 | 2026-02-23 | 1.3696
2026-02-23 12:59 | 72.3758 | FALSE | TRUE | -3.4841 | -5.0573 | -0.80315 | -1.0975 | 0 |  | 2026-02-23 09:44 | none | FALSE | 0 | 68.8917 | FALSE | FALSE | 0.4834 | 1.7797 | 71.0353 | 14 | 0 | 0.15525 | 0.14408 | -1.0775 | 1.0718 | Confirmed/Materialized Shift | 73.179 | 1.2507 | Day | 202602 | 2026-02-23 | 1.2507
2026-02-23 13:14 | 72.6584 | FALSE | TRUE | -3.5449 | -5.1292 | -0.63758 | -0.86987 | 0.2826 |  | 2026-02-23 09:44 | none | FALSE | 0 | 69.1135 | FALSE | FALSE | 0.4927 | 1.7537 | 71.2047 | 15 | 0.2826 | 0.16938 | 0.14189 | 0.79793 | 1.0456 | Confirmed/Materialized Shift | 73.296 | 1.3902 | Day | 202602 | 2026-02-23 | 1.3902
2026-02-23 13:29 | 72.6584 | FALSE | TRUE | -3.3338 | -4.809 | -0.73693 | -1.0041 | 0 |  | 2026-02-23 09:44 | none | FALSE | 0 | 69.3246 | FALSE | FALSE | 0.4851 | 1.7239 | 71.36 | 16 | 0 | 0.15525 | 0.14408 | -1.0775 | 1.0177 | Confirmed/Materialized Shift | 73.3953 | 1.2759 | Day | 202602 | 2026-02-23 | 1.2759
2026-02-23 13:43 | 72.6584 | FALSE | TRUE | -3.0691 | -4.4103 | -0.78271 | -1.0658 | 0 |  | 2026-02-23 09:44 | none | FALSE | 0 | 69.5893 | FALSE | FALSE | 0.4791 | 1.6923 | 71.5152 | 17 | 0 | 0.15525 | 0.14408 | -1.0775 | 0.96294 | Confirmed/Materialized Shift | 73.4411 | 1.1872 | Day | 202602 | 2026-02-23 | 1.1872
2026-02-23 13:58 | 72.941 | FALSE | TRUE | -3.1258 | -4.4772 | -0.5847 | -0.79524 | 0.2826 |  | 2026-02-23 09:44 | none | FALSE | 0 | 69.8152 | FALSE | FALSE | 0.4913 | 1.6744 | 71.6705 | 18 | 0.2826 | 0.15525 | 0.14408 | 0.8839 | 0.92762 | Confirmed/Materialized Shift | 73.5257 | 1.3697 | Day | 202602 | 2026-02-23 | 1.3697
2026-02-23 14:13 | 72.941 | FALSE | TRUE | -2.9153 | -4.1631 | -0.65662 | -0.89218 | 0 |  | 2026-02-23 09:44 | none | FALSE | 0 | 70.0257 | FALSE | FALSE | 0.4843 | 1.6528 | 71.8117 | 19 | 0 | 0.14121 | 0.14488 | -0.97468 | 0.89297 | Confirmed/Materialized Shift | 73.5976 | 1.2647 | Day | 202602 | 2026-02-23 | 1.2647
2026-02-23 14:28 | 72.941 | FALSE | TRUE | -2.6523 | -3.7734 | -0.67603 | -0.91831 | 0 |  | 2026-02-23 09:44 | none | FALSE | 0 | 70.2887 | FALSE | FALSE | 0.4792 | 1.6295 | 71.9529 | 20 | 0 | 0.14121 | 0.14488 | -0.97468 | 0.83207 | Confirmed/Materialized Shift | 73.617 | 1.1875 | Day | 202602 | 2026-02-23 | 1.1875
2026-02-23 14:43 | 72.941 | FALSE | TRUE | -2.4099 | -3.4167 | -0.68779 | -0.93413 | 0 |  | 2026-02-23 09:44 | none | FALSE | 0 | 70.5311 | FALSE | FALSE | 0.4741 | 1.6049 | 72.08 | 21 | 0 | 0.12708 | 0.14414 | -0.88163 | 0.77441 | Confirmed/Materialized Shift | 73.6288 | 1.1119 | Day | 202602 | 2026-02-23 | 1.1119
2026-02-23 14:58 | 73.2236 | FALSE | TRUE | -2.4151 | -3.4107 | -0.41025 | -0.55715 | 0.2826 |  | 2026-02-23 09:44 | none | FALSE | 0 | 70.8085 | FALSE | FALSE | 0.4946 | 1.5965 | 72.2212 | 22 | 0.2826 | 0.14121 | 0.14488 | 0.97592 | 0.70634 | Confirmed/Materialized Shift | 73.6339 | 1.4192 | Day | 202602 | 2026-02-23 | 1.4192
2026-02-23 15:13 | 73.2236 | FALSE | TRUE | -2.1561 | -3.0339 | -0.40546 | -0.55067 | 0 |  | 2026-02-23 09:44 | none | FALSE | 0 | 71.0675 | FALSE | FALSE | 0.4911 | 1.5865 | 72.3483 | 23 | 0 | 0.12708 | 0.14414 | -0.88163 | 0.6404 | Confirmed/Materialized Shift | 73.6291 | 1.3669 | Day | 202602 | 2026-02-23 | 1.3669
2026-02-23 15:28 | 73.2236 | FALSE | TRUE | -1.9221 | -2.6958 | -0.39734 | -0.53971 | 0 |  | 2026-02-23 09:44 | none | FALSE | 0 | 71.3015 | FALSE | FALSE | 0.4877 | 1.5752 | 72.4612 | 24 | 0 | 0.11295 | 0.14193 | -0.79582 | 0.57987 | Confirmed/Materialized Shift | 73.6209 | 1.3148 | Day | 202602 | 2026-02-23 | 1.3148
2026-02-23 15:43 | 73.2236 | FALSE | TRUE | -1.72 | -2.4054 | -0.39281 | -0.53359 | 0 |  | 2026-02-23 09:44 | none | FALSE | 0 | 71.5036 | FALSE | FALSE | 0.4838 | 1.5624 | 72.56 | 25 | 0 | 0.09882 | 0.13817 | -0.71522 | 0.52819 | Confirmed/Materialized Shift | 73.6164 | 1.2563 | Day | 202602 | 2026-02-23 | 1.2563
2026-02-23 15:58 | 73.2236 | FALSE | TRUE | -1.5561 | -2.1713 | -0.39836 | -0.54109 | 0 |  | 2026-02-23 09:44 | none | FALSE | 0 | 71.6675 | FALSE | FALSE | 0.479 | 1.5479 | 72.6447 | 26 | 0 | 0.08469 | 0.13273 | -0.63807 | 0.48862 | Confirmed/Materialized Shift | 73.622 | 1.1847 | Day | 202602 | 2026-02-23 | 1.1847
2026-02-23 16:13 | 73.2236 | FALSE | TRUE | -1.435 | -1.9989 | -0.41836 | -0.5681 | 0 |  | 2026-02-23 09:44 | none | FALSE | 0 | 71.7886 | FALSE | FALSE | 0.4731 | 1.5312 | 72.7153 | 27 | 0 | 0.07056 | 0.12539 | -0.56273 | 0.46334 | Confirmed/Materialized Shift | 73.642 | 1.0971 | Day | 202602 | 2026-02-23 | 1.0971
2026-02-23 16:28 | 73.5062 | FALSE | TRUE | -1.5943 | -2.217 | -0.18181 | -0.24673 | 0.2826 |  | 2026-02-23 09:44 | none | FALSE | 0 | 71.9119 | FALSE | FALSE | 0.506 | 1.5333 | 72.8 | 28 | 0.2826 | 0.08469 | 0.13273 | 1.4911 | 0.44402 | Confirmed/Materialized Shift | 73.688 | 1.5905 | Day | 202602 | 2026-02-23 | 1.5905
2026-02-23 16:42 | 73.5062 | FALSE | TRUE | -1.512 | -2.1002 | -0.2407 | -0.32639 | 0 |  | 2026-02-23 09:44 | none | FALSE | 0 | 71.9942 | FALSE | FALSE | 0.4967 | 1.5304 | 72.8705 | 29 | 0 | 0.07056 | 0.12539 | -0.56273 | 0.43819 | Confirmed/Materialized Shift | 73.7469 | 1.4507 | Day | 202602 | 2026-02-23 | 1.4507
2026-02-23 16:57 | 73.5062 | FALSE | TRUE | -1.4051 | -1.9487 | -0.27484 | -0.37251 | 0 |  | 2026-02-23 09:44 | none | FALSE | 0 | 72.1011 | FALSE | FALSE | 0.4897 | 1.5243 | 72.9411 | 30 | 0 | 0.07056 | 0.12539 | -0.56273 | 0.41997 | Confirmed/Materialized Shift | 73.781 | 1.3456 | Day | 202602 | 2026-02-23 | 1.3456
2026-02-23 17:12 | 73.5062 | FALSE | TRUE | -1.2698 | -1.7579 | -0.28074 | -0.38047 | 0 |  | 2026-02-23 09:44 | none | FALSE | 0 | 72.2364 | FALSE | FALSE | 0.4851 | 1.5163 | 73.0117 | 31 | 0 | 0.07056 | 0.12539 | -0.56273 | 0.38764 | Confirmed/Materialized Shift | 73.7869 | 1.2758 | Day | 202602 | 2026-02-23 | 1.2758
2026-02-23 17:27 | 73.5062 | FALSE | TRUE | -1.1823 | -1.6348 | -0.30628 | -0.41494 | 0 |  | 2026-02-23 09:44 | none | FALSE | 0 | 72.3239 | FALSE | FALSE | 0.4785 | 1.5057 | 73.0682 | 32 | 0 | 0.05652 | 0.11598 | -0.48734 | 0.37215 | Confirmed/Materialized Shift | 73.8125 | 1.177 | Day | 202602 | 2026-02-23 | 1.177
2026-02-23 17:42 | 73.5062 | FALSE | TRUE | -1.0743 | -1.4832 | -0.31132 | -0.42175 | 0 |  | 2026-02-23 09:44 | none | FALSE | 0 | 72.4319 | FALSE | FALSE | 0.4734 | 1.4934 | 73.1247 | 33 | 0 | 0.05652 | 0.11598 | -0.48734 | 0.34642 | Confirmed/Materialized Shift | 73.8175 | 1.1013 | Day | 202602 | 2026-02-23 | 1.1013
2026-02-23 17:57 | 73.2236 | TRUE | FALSE | -0.65355 | -0.90057 | -0.54051 | -0.73275 | -0.2826 |  |  | none | FALSE | 1 | 72.5701 | FALSE | FALSE | 0.0412 |  | 73.1671 | 0 | -0.2826 | 0.04239 | 0.13829 | -2.35 | 0.29851 | Persistence ends | 73.7641 | 0.18934 | Day | 202602 | 2026-02-23 | 0.18934
2026-02-23 18:12 | 73.5062 | FALSE | FALSE | -0.86119 | -1.1855 | -0.26773 | -0.3629 | 0.2826 |  |  | none | FALSE | 1 | 72.645 | FALSE | FALSE | 0.0987 |  | 73.2095 | 0 | 0.2826 | 0.04239 | 0.13829 | 1.737 | 0.28223 | Normal | 73.7739 | 1.0514 | Day | 202602 | 2026-02-23 | 1.0514
2026-02-23 18:27 | 73.5062 | FALSE | FALSE | -0.76975 | -1.0583 | -0.26107 | -0.35391 | 0 |  |  | none | FALSE | 1 | 72.7364 | FALSE | FALSE | 0.0944 |  | 73.2519 | 0 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.25771 | Normal | 73.7673 | 0.98694 | Night | 202602 | 2026-02-23 | 0.98694
2026-02-23 18:42 | 73.2236 | FALSE | FALSE | -0.37742 | -0.51811 | -0.49046 | -0.66536 | -0.2826 |  |  | none | FALSE | 1 | 72.8462 | FALSE | FALSE | 0.0459 |  | 73.2801 | 0 | -0.2826 | 0.02826 | 0.15614 | -1.9909 | 0.21697 | Normal | 73.7141 | -0.26049 | Night | 202602 | 2026-02-23 | 0.26049
2026-02-23 18:42 | 73.2236 | FALSE | FALSE | -0.33423 | -0.45855 | -0.47553 | -0.64523 | 0 |  |  | none | FALSE | 1 | 72.8894 | FALSE | FALSE | 0.0518 |  | 73.2943 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.20244 | Normal | 73.6991 | -0.34899 | Night | 202602 | 2026-02-23 | 0.34899
2026-02-23 18:57 | 73.2236 | FALSE | FALSE | -0.28653 | -0.39284 | -0.45609 | -0.61901 | 0 |  |  | none | FALSE | 1 | 72.9371 | FALSE | FALSE | 0.059 |  | 73.3084 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.18565 | Normal | 73.6797 | -0.45666 | Night | 202602 | 2026-02-23 | 0.45666
2026-02-23 19:12 | 73.2236 | FALSE | FALSE | -0.23294 | -0.31914 | -0.43076 | -0.58484 | 0 |  |  | none | FALSE | 1 | 72.9907 | FALSE | FALSE | 0.0683 |  | 73.3225 | 0 | 0 | 0.01413 | 0.14424 | -0.097959 | 0.16593 | Normal | 73.6544 | -0.59611 | Night | 202602 | 2026-02-23 | 0.59611
2026-02-23 19:27 | 72.941 | FALSE | FALSE | 0.049657 | 0.068032 | -0.71336 | -0.96853 | -0.2826 | 2026-02-24 05:53 | 2026-02-23 19:27 | lower | TRUE | 1 | 72.9907 | FALSE | FALSE | 0.239 | 2.2993 | 73.3225 | 1 | -0.2826 | 0 | 0.15881 | -1.7795 | 0.16593 | Extreme triggered | 73.6544 | -2.2993 | Night | 202602 | 2026-02-23 | 2.2993
2026-02-23 19:41 | 72.941 | FALSE | FALSE | -0.0039263 | -0.0053831 | -0.73869 | -1.0026 | 0 |  | 2026-02-23 19:27 | none | FALSE | 1 | 72.9371 | FALSE | FALSE | 0.2748 | 2.1391 | 73.3084 | 2 | 0 | -0.01413 | 0.14424 | 0.097959 | 0.18565 | Extreme/elevated | 73.6797 | -1.9789 | Night | 202602 | 2026-02-23 | 1.9789
2026-02-23 19:56 | 72.3758 | TRUE | FALSE | 0.33172 | 0.45624 | -1.4487 | -1.9623 | -0.5652 |  | 2026-02-23 19:27 | lower | TRUE | 2 | 72.7075 | TRUE | TRUE | 0.4411 | 2.4887 | 73.266 | 3 | -0.5652 | -0.04239 | 0.18957 | -2.7578 | 0.27923 | Persistent | 73.8245 | -3.188 | Night | 202602 | 2026-02-23 | 3.188
2026-02-23 20:11 | 72.3758 | FALSE | FALSE | 0.16167 | 0.22288 | -1.5339 | -2.0754 | 0 |  | 2026-02-23 19:27 | lower | TRUE | 1 | 72.5375 | FALSE | TRUE | 0.4219 | 2.4843 | 73.2236 | 4 | 0 | -0.04239 | 0.18957 | 0.22361 | 0.34306 | Persistent | 73.9097 | -2.4713 | Night | 202602 | 2026-02-23 | 2.4713
2026-02-23 20:27 | 72.095 | FALSE | FALSE | 0.2204 | 0.30477 | -1.9239 | -2.5993 | -0.2808 |  | 2026-02-23 19:27 | lower | TRUE | 1 | 72.3154 | FALSE | TRUE | 0.4821 | 2.491 | 73.1672 | 5 | -0.2808 | -0.05643 | 0.19654 | -1.1416 | 0.42589 | Persistent | 74.0189 | -2.5175 | Night | 202602 | 2026-02-23 | 2.5175
2026-02-23 20:41 | 72.095 | FALSE | FALSE | 0.039293 | 0.054471 | -1.9922 | -2.689 | 0 |  | 2026-02-23 19:27 | lower | TRUE | 1 | 72.1343 | FALSE | TRUE | 0.5101 | 2.4226 | 73.1107 | 6 | 0 | -0.05643 | 0.19654 | 0.28712 | 0.48822 | Persistent | 74.0872 | -2.0805 | Night | 202602 | 2026-02-23 | 2.0805
2026-02-23 20:56 | 71.8124 | FALSE | TRUE | 0.09434 | 0.1312 | -2.3612 | -3.1834 | -0.2826 |  | 2026-02-23 19:27 | lower | TRUE | 1 | 71.9067 | FALSE | TRUE | 0.573 | 2.386 | 73.0402 | 7 | -0.2826 | -0.07056 | 0.20234 | -1.0479 | 0.56672 | Confirmed/Materialized Shift | 74.1736 | -2.1665 | Night | 202602 | 2026-02-23 | 2.1665
2026-02-23 21:11 | 71.5298 | FALSE | TRUE | 0.11614 | 0.1621 | -2.707 | -3.6464 | -0.2826 |  | 2026-02-23 19:27 | lower | TRUE | 1 | 71.6459 | FALSE | TRUE | 0.5739 | 2.3601 | 72.9414 | 8 | -0.2826 | -0.09882 | 0.18948 | -0.96991 | 0.64771 | Confirmed/Materialized Shift | 74.2368 | -2.1793 | Night | 202602 | 2026-02-23 | 2.1793
2026-02-23 21:26 | 71.5298 | FALSE | TRUE | -0.097686 | -0.13675 | -2.7232 | -3.6674 | 0 |  | 2026-02-23 19:27 | none | FALSE | 1 | 71.4321 | FALSE | FALSE | 0.5527 | 2.3047 | 72.8425 | 9 | 0 | -0.09882 | 0.18948 | 0.52153 | 0.70521 | Confirmed/Materialized Shift | 74.253 | -1.8615 | Night | 202602 | 2026-02-23 | 1.8615
2026-02-23 21:41 | 71.2472 | FALSE | TRUE | -0.059904 | -0.08415 | -3.0247 | -4.0724 | -0.2826 |  | 2026-02-23 19:27 | none | FALSE | 1 | 71.1873 | FALSE | FALSE | 0.5567 | 2.2665 | 72.7296 | 10 | -0.2826 | -0.11295 | 0.19224 | -0.88248 | 0.77115 | Confirmed/Materialized Shift | 74.2719 | -1.9223 | Night | 202602 | 2026-02-23 | 1.9223
2026-02-23 21:56 | 70.9646 | FALSE | TRUE | -0.04718 | -0.066529 | -3.323 | -4.4732 | -0.2826 |  | 2026-02-23 19:27 | none | FALSE | 1 | 70.9174 | FALSE | FALSE | 0.5582 | 2.2372 | 72.6025 | 11 | -0.2826 | -0.12708 | 0.19388 | -0.80214 | 0.84255 | Confirmed/Materialized Shift | 74.2876 | -1.944 | Night | 202602 | 2026-02-23 | 1.944
2026-02-23 22:11 | 70.682 | FALSE | TRUE | -0.053768 | -0.076129 | -3.6124 | -4.8622 | -0.2826 |  | 2026-02-23 19:27 | none | FALSE | 1 | 70.6282 | FALSE | FALSE | 0.558 | 2.2125 | 72.4613 | 12 | -0.2826 | -0.14121 | 0.19443 | -0.7272 | 0.91653 | Confirmed/Materialized Shift | 74.2944 | -1.9413 | Night | 202602 | 2026-02-23 | 1.9413
2026-02-23 22:26 | 70.3994 | FALSE | TRUE | -0.074278 | -0.10562 | -3.8874 | -5.233 | -0.2826 |  | 2026-02-23 19:27 | none | FALSE | 0 | 70.3251 | FALSE | FALSE | 0.5283 | 2.1904 | 72.306 | 13 | -0.2826 | -0.15534 | 0.1939 | -0.65633 | 0.99042 | Confirmed/Materialized Shift | 74.2868 | -1.925 | Night | 202602 | 2026-02-23 | 1.925
2026-02-23 22:40 | 70.3994 | FALSE | TRUE | -0.33887 | -0.48368 | -3.8696 | -5.2102 | 0 |  | 2026-02-23 19:27 | none | FALSE | 0 | 70.0605 | FALSE | FALSE | 0.5119 | 2.1538 | 72.1647 | 14 | 0 | -0.14121 | 0.19443 | 0.72628 | 1.0521 | Confirmed/Materialized Shift | 74.269 | -1.6779 | Night | 202602 | 2026-02-23 | 1.6779
2026-02-23 22:56 | 70.3994 | FALSE | TRUE | -0.53554 | -0.76655 | -3.7556 | -5.0645 | 0 |  | 2026-02-23 19:27 | none | FALSE | 0 | 69.8639 | FALSE | FALSE | 0.5001 | 2.1103 | 72.0094 | 15 | 0 | -0.15534 | 0.17085 | 0.90923 | 1.0728 | Confirmed/Materialized Shift | 74.155 | -1.5008 | Night | 202602 | 2026-02-23 | 1.5008
2026-02-23 23:11 | 70.1168 | FALSE | TRUE | -0.45973 | -0.65999 | -3.906 | -5.2768 | -0.2826 |  | 2026-02-23 19:27 | none | FALSE | 0 | 69.6571 | FALSE | FALSE | 0.5053 | 2.077 | 71.8399 | 16 | -0.2826 | -0.16947 | 0.169 | -0.66941 | 1.0914 | Confirmed/Materialized Shift | 74.0228 | -1.5788 | Night | 202602 | 2026-02-23 | 1.5788
2026-02-23 23:26 | 69.836 | FALSE | TRUE | -0.42076 | -0.60615 | -4.0899 | -5.5324 | -0.2808 |  | 2026-02-23 19:27 | none | FALSE | 0 | 69.4152 | FALSE | FALSE | 0.5085 | 2.0506 | 71.6706 | 17 | -0.2808 | -0.16938 | 0.16894 | -0.65953 | 1.1277 | Confirmed/Materialized Shift | 73.9259 | -1.6269 | Night | 202602 | 2026-02-23 | 1.6269
2026-02-23 23:40 | 69.836 | FALSE | TRUE | -0.6078 | -0.87797 | -3.9382 | -5.3381 | 0 |  | 2026-02-23 19:27 | none | FALSE | 0 | 69.2282 | FALSE | FALSE | 0.4977 | 2.018 | 71.5012 | 18 | 0 | -0.16938 | 0.16894 | 1.0026 | 1.1365 | Confirmed/Materialized Shift | 73.7742 | -1.4652 | Night | 202602 | 2026-02-23 | 1.4652
2026-02-23 23:55 | 69.5534 | FALSE | TRUE | -0.51582 | -0.74715 | -4.0444 | -5.4952 | -0.2826 |  | 2026-02-23 19:27 | none | FALSE | 0 | 69.0376 | FALSE | FALSE | 0.5032 | 1.9933 | 71.3177 | 19 | -0.2826 | -0.18351 | 0.16581 | -0.5976 | 1.14 | Confirmed/Materialized Shift | 73.5978 | -1.5475 | Night | 202602 | 2026-02-23 | 1.5475
2026-02-24 00:10 | 69.2708 | FALSE | TRUE | -0.42049 | -0.61073 | -4.1189 | -5.6124 | -0.2826 |  | 2026-02-23 19:27 | none | FALSE | 0 | 68.8503 | FALSE | FALSE | 0.5086 | 1.9751 | 71.12 | 20 | -0.2826 | -0.19764 | 0.16133 | -0.52661 | 1.1349 | Confirmed/Materialized Shift | 73.3897 | -1.6295 | Night | 202602 | 2026-02-24 | 1.6295
2026-02-24 00:25 | 69.2708 | FALSE | TRUE | -0.57741 | -0.84057 | -3.9089 | -5.3415 | 0 |  | 2026-02-23 19:27 | none | FALSE | 0 | 68.6934 | FALSE | FALSE | 0.499 | 1.9518 | 70.9365 | 21 | 0 | -0.18351 | 0.16581 | 1.1067 | 1.1216 | Confirmed/Materialized Shift | 73.1797 | -1.4852 | Night | 202602 | 2026-02-24 | 1.4852
2026-02-24 00:40 | 69.2708 | FALSE | TRUE | -0.66909 | -0.97533 | -3.6335 | -4.9839 | 0 |  | 2026-02-23 19:27 | none | FALSE | 0 | 68.6017 | FALSE | FALSE | 0.4919 | 1.9257 | 70.753 | 22 | 0 | -0.18351 | 0.16581 | 1.1067 | 1.0757 | Confirmed/Materialized Shift | 72.9043 | -1.378 | Night | 202602 | 2026-02-24 | 1.378
2026-02-24 00:55 | 68.9882 | FALSE | TRUE | -0.55133 | -0.80561 | -3.7422 | -5.1453 | -0.2826 |  | 2026-02-23 19:27 | none | FALSE | 0 | 68.4369 | FALSE | FALSE | 0.4991 | 1.9066 | 70.5836 | 23 | -0.2826 | -0.16938 | 0.14189 | -0.79793 | 1.0734 | Confirmed/Materialized Shift | 72.7304 | -1.4864 | Night | 202602 | 2026-02-24 | 1.4864
2026-02-24 01:10 | 68.9882 | FALSE | TRUE | -0.65901 | -0.96447 | -3.5111 | -4.843 | 0 |  | 2026-02-23 19:27 | none | FALSE | 0 | 68.3292 | FALSE | FALSE | 0.4912 | 1.8841 | 70.4142 | 24 | 0 | -0.16938 | 0.14189 | 1.1937 | 1.0425 | Confirmed/Materialized Shift | 72.4993 | -1.3679 | Night | 202602 | 2026-02-24 | 1.3679
2026-02-24 01:25 | 68.7056 | FALSE | TRUE | -0.52152 | -0.76487 | -3.5999 | -4.9787 | -0.2826 |  | 2026-02-23 19:27 | none | FALSE | 0 | 68.1841 | FALSE | FALSE | 0.4996 | 1.8685 | 70.2448 | 25 | -0.2826 | -0.16947 | 0.14197 | -0.79688 | 1.0303 | Confirmed/Materialized Shift | 72.3055 | -1.4938 | Night | 202602 | 2026-02-24 | 1.4938
2026-02-24 01:40 | 68.7056 | FALSE | TRUE | -0.60604 | -0.88994 | -3.3455 | -4.6432 | 0 |  | 2026-02-23 19:27 | none | FALSE | 0 | 68.0996 | FALSE | FALSE | 0.4924 | 1.85 | 70.0753 | 26 | 0 | -0.16947 | 0.14197 | 1.1937 | 0.98788 | Confirmed/Materialized Shift | 72.0511 | -1.3865 | Night | 202602 | 2026-02-24 | 1.3865
2026-02-24 01:55 | 68.7056 | FALSE | TRUE | -0.67288 | -0.98905 | -3.1016 | -4.3194 | 0 |  | 2026-02-23 19:27 | none | FALSE | 0 | 68.0327 | FALSE | FALSE | 0.4858 | 1.8291 | 69.92 | 27 | 0 | -0.15534 | 0.14416 | 1.0775 | 0.94362 | Confirmed/Materialized Shift | 71.8072 | -1.2869 | Night | 202602 | 2026-02-24 | 1.2869
2026-02-24 02:10 | 68.423 | FALSE | TRUE | -0.49856 | -0.73399 | -3.1818 | -4.4436 | -0.2826 |  | 2026-02-23 19:27 | none | FALSE | 0 | 67.9244 | FALSE | FALSE | 0.4972 | 1.8159 | 69.7646 | 28 | -0.2826 | -0.15534 | 0.14416 | -0.88276 | 0.92009 | Confirmed/Materialized Shift | 71.6048 | -1.4581 | Night | 202602 | 2026-02-24 | 1.4581
2026-02-24 02:25 | 68.423 | FALSE | TRUE | -0.54797 | -0.80732 | -2.9206 | -4.0936 | 0 |  | 2026-02-23 19:27 | none | FALSE | 0 | 67.875 | FALSE | FALSE | 0.4912 | 1.8004 | 69.6093 | 29 | 0 | -0.15534 | 0.14416 | 1.0775 | 0.86713 | Confirmed/Materialized Shift | 71.3436 | -1.3681 | Night | 202602 | 2026-02-24 | 1.3681
2026-02-24 02:39 | 68.1404 | FALSE | TRUE | -0.35843 | -0.5288 | -2.9855 | -4.1975 | -0.2826 |  | 2026-02-23 19:27 | none | FALSE | 0 | 67.782 | FALSE | FALSE | 0.5048 | 1.7928 | 69.454 | 30 | -0.2826 | -0.15534 | 0.14416 | -0.88276 | 0.83599 | Confirmed/Materialized Shift | 71.1259 | -1.5713 | Night | 202602 | 2026-02-24 | 1.5713
2026-02-24 02:54 | 68.1404 | FALSE | TRUE | -0.43836 | -0.64749 | -2.783 | -3.924 | 0 |  | 2026-02-23 19:27 | none | FALSE | 0 | 67.702 | FALSE | FALSE | 0.497 | 1.7819 | 69.3127 | 31 | 0 | -0.14121 | 0.14488 | 0.97468 | 0.80535 | Confirmed/Materialized Shift | 70.9234 | -1.4557 | Night | 202602 | 2026-02-24 | 1.4557
2026-02-24 03:09 | 68.1404 | FALSE | TRUE | -0.5107 | -0.75513 | -2.6012 | -3.6771 | 0 |  | 2026-02-23 19:27 | none | FALSE | 0 | 67.6297 | FALSE | FALSE | 0.4896 | 1.7682 | 69.1857 | 32 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.77798 | Confirmed/Materialized Shift | 70.7416 | -1.3436 | Night | 202602 | 2026-02-24 | 1.3436
2026-02-24 03:24 | 68.1404 | FALSE | TRUE | -0.58002 | -0.85853 | -2.4446 | -3.4634 | 0 |  | 2026-02-23 19:27 | none | FALSE | 0 | 67.5604 | FALSE | FALSE | 0.4822 | 1.752 | 69.0727 | 33 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.75617 | Confirmed/Materialized Shift | 70.585 | -1.2329 | Night | 202602 | 2026-02-24 | 1.2329
2026-02-24 03:39 | 67.8596 | FALSE | TRUE | -0.38307 | -0.56771 | -2.5553 | -3.6289 | -0.2808 |  | 2026-02-23 19:27 | none | FALSE | 0 | 67.4765 | FALSE | FALSE | 0.4986 | 1.744 | 68.9457 | 34 | -0.2808 | -0.12699 | 0.14404 | -1.0678 | 0.7346 | Confirmed/Materialized Shift | 70.4149 | -1.4785 | Night | 202602 | 2026-02-24 | 1.4785
2026-02-24 03:54 | 67.8596 | FALSE | TRUE | -0.41713 | -0.6185 | -2.3354 | -3.327 | 0 |  | 2026-02-23 19:27 | none | FALSE | 0 | 67.4425 | FALSE | FALSE | 0.4929 | 1.734 | 68.8187 | 35 | 0 | -0.12699 | 0.14404 | 0.88163 | 0.68813 | Confirmed/Materialized Shift | 70.195 | -1.3938 | Night | 202602 | 2026-02-24 | 1.3938
2026-02-24 04:09 | 67.577 | FALSE | TRUE | -0.22543 | -0.33471 | -2.4549 | -3.5054 | -0.2826 |  | 2026-02-23 19:27 | none | FALSE | 0 | 67.3516 | FALSE | FALSE | 0.5109 | 1.732 | 68.6917 | 36 | -0.2826 | -0.12699 | 0.14404 | -1.0803 | 0.67009 | Confirmed/Materialized Shift | 70.0319 | -1.6636 | Night | 202602 | 2026-02-24 | 1.6636
2026-02-24 04:24 | 67.577 | FALSE | TRUE | -0.31286 | -0.46512 | -2.3164 | -3.3142 | 0 |  | 2026-02-23 19:27 | none | FALSE | 0 | 67.2641 | FALSE | FALSE | 0.5016 | 1.7264 | 68.5788 | 37 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.65733 | Confirmed/Materialized Shift | 69.8934 | -1.524 | Night | 202602 | 2026-02-24 | 1.524
2026-02-24 04:39 | 67.577 | FALSE | TRUE | -0.3574 | -0.53169 | -2.1351 | -3.0627 | 0 |  | 2026-02-23 19:27 | none | FALSE | 0 | 67.2196 | FALSE | FALSE | 0.4951 | 1.7185 | 68.4658 | 38 | 0 | -0.11295 | 0.14193 | 0.79582 | 0.62312 | Confirmed/Materialized Shift | 69.7121 | -1.4264 | Night | 202602 | 2026-02-24 | 1.4264
2026-02-24 04:54 | 67.577 | FALSE | TRUE | -0.40552 | -0.60371 | -1.9856 | -2.8544 | 0 |  | 2026-02-23 19:27 | none | FALSE | 0 | 67.1715 | FALSE | FALSE | 0.4881 | 1.7083 | 68.367 | 39 | 0 | -0.09882 | 0.13817 | 0.71522 | 0.59777 | Confirmed/Materialized Shift | 69.5626 | -1.3216 | Night | 202602 | 2026-02-24 | 1.3216
2026-02-24 05:09 | 67.577 | FALSE | TRUE | -0.46024 | -0.68573 | -1.8709 | -2.694 | 0 |  | 2026-02-23 19:27 | none | FALSE | 0 | 67.1168 | FALSE | FALSE | 0.4807 | 1.6959 | 68.2823 | 40 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.58279 | Confirmed/Materialized Shift | 69.4479 | -1.2103 | Night | 202602 | 2026-02-24 | 1.2103
2026-02-24 05:24 | 67.577 | FALSE | TRUE | -0.48724 | -0.72624 | -1.7285 | -2.4941 | 0 |  | 2026-02-23 19:27 | none | FALSE | 0 | 67.0898 | FALSE | FALSE | 0.4747 | 1.6818 | 68.1976 | 41 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.55394 | Confirmed/Materialized Shift | 69.3055 | -1.1204 | Night | 202602 | 2026-02-24 | 1.1204
2026-02-24 05:38 | 67.577 | FALSE | TRUE | -0.48181 | -0.71809 | -1.5537 | -2.2475 | 0 |  | 2026-02-23 19:27 | none | FALSE | 0 | 67.0952 | FALSE | FALSE | 0.4702 | 1.6669 | 68.1129 | 42 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.50888 | Confirmed/Materialized Shift | 69.1307 | -1.0532 | Night | 202602 | 2026-02-24 | 1.0532
2026-02-24 05:53 | 67.577 | FALSE | FALSE | -0.49067 | -0.73141 | -1.4215 | -2.0601 | 0 |  |  | none | FALSE | 0 | 67.0863 | FALSE | FALSE | 0.0649 |  | 68.0424 | 0 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.47803 | Persistence ends | 68.9985 | -0.97355 | Night | 202602 | 2026-02-24 | 0.97355
2026-02-24 06:08 | 67.2944 | FALSE | FALSE | -0.23854 | -0.35574 | -1.5651 | -2.2729 | -0.2826 |  |  | none | FALSE | 0 | 67.0559 | FALSE | FALSE | 0.0981 |  | 67.9577 | 0 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.45092 | Normal | 68.8595 | -1.471 | Night | 202602 | 2026-02-24 | 1.471
2026-02-24 06:23 | 67.2944 | FALSE | FALSE | -0.28317 | -0.42257 | -1.4687 | -2.1358 | 0 |  |  | none | FALSE | 0 | 67.0112 | FALSE | FALSE | 0.0902 |  | 67.8871 | 0 | 0 | -0.07056 | 0.12539 | 0.56273 | 0.43796 | Normal | 68.7631 | -1.3534 | Night | 202602 | 2026-02-24 | 1.3534
2026-02-24 06:38 | 67.577 | TRUE | FALSE | -0.54193 | -0.80842 | -1.0493 | -1.5291 | 0.2826 |  |  | none | FALSE | 1 | 67.0351 | FALSE | FALSE | 0.0711 |  | 67.8307 | 0 | 0.2826 | -0.05643 | 0.1477 | 2.2954 | 0.39782 | Normal | 68.6263 | -0.63775 | Night | 202602 | 2026-02-24 | 0.63775
2026-02-24 06:53 | 67.2944 | FALSE | FALSE | -0.24943 | -0.37203 | -1.1809 | -1.7246 | -0.2826 |  |  | none | FALSE | 1 | 67.045 | FALSE | FALSE | 0.1154 |  | 67.7601 | 0 | -0.2826 | -0.07056 | 0.15534 | -1.365 | 0.35759 | Normal | 68.4753 | -1.3025 | Day | 202602 | 2026-02-24 | 1.3025
2026-02-24 07:08 | 67.2944 | FALSE | FALSE | -0.26243 | -0.3915 | -1.0811 | -1.5811 | 0 |  |  | none | FALSE | 1 | 67.032 | FALSE | FALSE | 0.1098 |  | 67.7037 | 0 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.33587 | Normal | 68.3755 | -1.2187 | Day | 202602 | 2026-02-24 | 1.2187
2026-02-24 07:23 | 67.577 | FALSE | FALSE | -0.49711 | -0.74107 | -0.66595 | -0.97585 | 0.2826 |  |  | none | FALSE | 1 | 67.0799 | FALSE | FALSE | 0.0479 |  | 67.6614 | 0 | 0.2826 | -0.0423 | 0.16579 | 1.9597 | 0.29076 | Normal | 68.2429 | -0.29034 | Day | 202602 | 2026-02-24 | 0.29034
2026-02-24 07:30 | 67.577 | FALSE | FALSE | -0.48044 | -0.71604 | -0.59294 | -0.86979 | 0 |  |  | none | FALSE | 1 | 67.0966 | FALSE | FALSE | 0.0425 |  | 67.6333 | 0 | 0 | -0.02817 | 0.15598 | 0.18059 | 0.26834 | Normal | 68.1699 | -0.20962 | Day | 202602 | 2026-02-24 | 0.20962
2026-02-24 07:45 | 67.577 | FALSE | FALSE | -0.45276 | -0.67451 | -0.50892 | -0.74747 | 0 |  |  | none | FALSE | 1 | 67.1242 | FALSE | FALSE | 0.0364 |  | 67.6051 | 0 | 0 | -0.02817 | 0.15598 | 0.18059 | 0.24042 | Normal | 68.0859 | -0.11679 | Day | 202602 | 2026-02-24 | 0.11679
2026-02-24 08:00 | 67.577 | FALSE | FALSE | -0.40961 | -0.60983 | -0.40943 | -0.60222 | 0 |  |  | none | FALSE | 1 | 67.1674 | FALSE | FALSE | 0.0286 |  | 67.5769 | 0 | 0 | -0.02817 | 0.15598 | 0.18059 | 0.20476 | Normal | 67.9864 | 0.00043954 | Day | 202602 | 2026-02-24 | 0.00043954
2026-02-24 08:16 | 67.8596 | FALSE | FALSE | -0.63857 | -0.94995 | -0.045106 | -0.066425 | 0.2826 |  |  | none | FALSE | 1 | 67.221 | FALSE | FALSE | 0.1443 |  | 67.5629 | 0 | 0.2826 | -0.01404 | 0.17077 | 1.7371 | 0.17092 | Normal | 67.9047 | 1.7361 | Day | 202602 | 2026-02-24 | 1.7361
2026-02-24 08:30 | 68.1404 | FALSE | FALSE | -0.97301 | -1.4486 | 0.15397 | 0.22648 | 0.2808 | 2026-02-24 13:59 | 2026-02-24 08:30 | upper | TRUE | 1 | 67.1674 | FALSE | FALSE | 0.2692 | 2.752 | 67.5769 | 1 | 0.2808 | 0.01404 | 0.17077 | 1.5621 | 0.20476 | Extreme triggered | 67.9864 | 2.752 | Day | 202602 | 2026-02-24 | 2.752
2026-02-24 08:30 | 68.1404 | FALSE | FALSE | -1.0152 | -1.5124 | 0.083728 | 0.12303 | 0 |  | 2026-02-24 08:30 | upper | TRUE | 1 | 67.1252 | FALSE | FALSE | 0.3002 | 2.5558 | 67.591 | 2 | 0 | 0.01404 | 0.17077 | -0.082216 | 0.23286 | Extreme/elevated | 68.0567 | 2.3596 | Day | 202602 | 2026-02-24 | 2.3596
2026-02-24 08:45 | 68.423 | FALSE | FALSE | -1.3856 | -2.0669 | 0.19387 | 0.28415 | 0.2826 |  | 2026-02-24 08:30 | upper | TRUE | 0 | 67.0374 | FALSE | TRUE | 0.3481 | 2.5874 | 67.6333 | 3 | 0.2826 | 0.0423 | 0.16579 | 1.4494 | 0.29794 | Persistent | 68.2291 | 2.6507 | Day | 202602 | 2026-02-24 | 2.6507
2026-02-24 09:00 | 68.7056 | FALSE | FALSE | -1.7795 | -2.6589 | 0.25232 | 0.3686 | 0.2826 |  | 2026-02-24 08:30 | upper | TRUE | 0 | 66.9261 | FALSE | TRUE | 0.406 | 2.6058 | 67.6897 | 4 | 0.2826 | 0.05643 | 0.17384 | 1.301 | 0.3818 | Persistent | 68.4533 | 2.6609 | Day | 202602 | 2026-02-24 | 2.6609
2026-02-24 09:15 | 68.9882 | FALSE | FALSE | -2.1842 | -3.2696 | 0.2717 | 0.39539 | 0.2826 |  | 2026-02-24 08:30 | upper | TRUE | 0 | 66.804 | FALSE | TRUE | 0.4569 | 2.5983 | 67.7602 | 5 | 0.2826 | 0.07056 | 0.18038 | 1.1755 | 0.47813 | Persistent | 68.7165 | 2.5683 | Day | 202602 | 2026-02-24 | 2.5683
2026-02-24 09:30 | 69.2708 | FALSE | FALSE | -2.591 | -3.8857 | 0.26073 | 0.37782 | 0.2826 |  | 2026-02-24 08:30 | upper | TRUE | 0 | 66.6798 | FALSE | TRUE | 0.506 | 2.5732 | 67.8449 | 6 | 0.2826 | 0.08469 | 0.18555 | 1.0666 | 0.58257 | Persistent | 69.0101 | 2.4476 | Day | 202602 | 2026-02-24 | 2.4476
2026-02-24 09:45 | 69.5534 | FALSE | TRUE | -2.9938 | -4.4979 | 0.22552 | 0.3253 | 0.2826 |  | 2026-02-24 08:30 | upper | TRUE | 0 | 66.5596 | FALSE | TRUE | 0.5551 | 2.5378 | 67.9437 | 7 | 0.2826 | 0.09882 | 0.18948 | 0.96991 | 0.69206 | Confirmed/Materialized Shift | 69.3279 | 2.3259 | Day | 202602 | 2026-02-24 | 2.3259
2026-02-24 10:00 | 69.836 | FALSE | TRUE | -3.3879 | -5.0986 | 0.1707 | 0.24503 | 0.2826 |  | 2026-02-24 08:30 | upper | TRUE | 0 | 66.4481 | FALSE | TRUE | 0.5475 | 2.4971 | 68.0567 | 8 | 0.2826 | 0.11295 | 0.19224 | 0.88248 | 0.8043 | Confirmed/Materialized Shift | 69.6653 | 2.2122 | Day | 202602 | 2026-02-24 | 2.2122
2026-02-24 10:15 | 70.1168 | FALSE | TRUE | -3.7674 | -5.6782 | 0.098793 | 0.1411 | 0.2808 |  | 2026-02-24 08:30 | upper | TRUE | 0 | 66.3494 | FALSE | TRUE | 0.5405 | 2.4539 | 68.1837 | 9 | 0.2808 | 0.12699 | 0.19381 | 0.79363 | 0.91716 | Confirmed/Materialized Shift | 70.018 | 2.1077 | Day | 202602 | 2026-02-24 | 2.1077
2026-02-24 10:29 | 70.682 | FALSE | TRUE | -4.4643 | -6.7419 | 0.2218 | 0.31478 | 0.5652 |  | 2026-02-24 08:30 | upper | TRUE | 0 | 66.2177 | FALSE | TRUE | 0.5473 | 2.4294 | 68.3389 | 10 | 0.5652 | 0.15525 | 0.21443 | 1.9119 | 1.0606 | Confirmed/Materialized Shift | 70.4602 | 2.2091 | Day | 202602 | 2026-02-24 | 2.2091
2026-02-24 10:44 | 70.9646 | FALSE | TRUE | -4.8043 | -7.2616 | 0.080021 | 0.11289 | 0.2826 |  | 2026-02-24 08:30 | upper | TRUE | 0 | 66.1603 | FALSE | TRUE | 0.5379 | 2.3965 | 68.5225 | 11 | 0.2826 | 0.18351 | 0.18948 | 0.52297 | 1.1811 | Confirmed/Materialized Shift | 70.8846 | 2.0678 | Day | 202602 | 2026-02-24 | 2.0678
2026-02-24 10:59 | 71.2472 | FALSE | TRUE | -5.1079 | -7.723 | -0.053721 | -0.075345 | 0.2826 |  | 2026-02-24 08:30 | none | FALSE | 0 | 66.1393 | FALSE | FALSE | 0.5306 | 2.36 | 68.7201 | 12 | 0.2826 | 0.19764 | 0.18557 | 0.45784 | 1.2904 | Confirmed/Materialized Shift | 71.3009 | 1.9584 | Day | 202602 | 2026-02-24 | 1.9584
2026-02-24 11:14 | 71.5298 | FALSE | TRUE | -5.4198 | -8.1981 | -0.19562 | -0.27274 | 0.2826 |  | 2026-02-24 08:30 | none | FALSE | 0 | 66.11 | FALSE | FALSE | 0.524 | 2.3216 | 68.9177 | 13 | 0.2826 | 0.19764 | 0.18557 | 0.45784 | 1.4038 | Confirmed/Materialized Shift | 71.7254 | 1.8607 | Day | 202602 | 2026-02-24 | 1.8607
2026-02-24 11:29 | 71.8124 | FALSE | TRUE | -5.6483 | -8.5368 | -0.31074 | -0.43085 | 0.2826 |  | 2026-02-24 08:30 | none | FALSE | 0 | 66.1641 | FALSE | FALSE | 0.5194 | 2.2837 | 69.1436 | 14 | 0.2826 | 0.2259 | 0.14777 | 0.3837 | 1.4898 | Confirmed/Materialized Shift | 72.1231 | 1.7914 | Day | 202602 | 2026-02-24 | 1.7914
2026-02-24 11:44 | 71.8124 | FALSE | TRUE | -5.5157 | -8.3197 | -0.62994 | -0.86957 | 0 |  | 2026-02-24 08:30 | none | FALSE | 0 | 66.2967 | FALSE | FALSE | 0.506 | 2.2375 | 69.3695 | 15 | 0 | 0.2259 | 0.14777 | -1.5287 | 1.5364 | Confirmed/Materialized Shift | 72.4423 | 1.59 | Day | 202602 | 2026-02-24 | 1.59
2026-02-24 11:59 | 72.095 | FALSE | TRUE | -5.6799 | -8.5522 | -0.68079 | -0.93546 | 0.2826 |  | 2026-02-24 08:30 | none | FALSE | 0 | 66.4151 | FALSE | FALSE | 0.5048 | 2.1959 | 69.5954 | 16 | 0.2826 | 0.2259 | 0.14777 | 0.3837 | 1.5902 | Confirmed/Materialized Shift | 72.7758 | 1.5719 | Day | 202602 | 2026-02-24 | 1.5719
2026-02-24 12:14 | 72.3758 | FALSE | TRUE | -5.8026 | -8.7162 | -0.72178 | -0.98742 | 0.2808 |  | 2026-02-24 08:30 | none | FALSE | 0 | 66.5732 | FALSE | FALSE | 0.5038 | 2.1583 | 69.8354 | 17 | 0.2808 | 0.23994 | 0.13821 | 0.29564 | 1.6311 | Confirmed/Materialized Shift | 73.0976 | 1.5575 | Day | 202602 | 2026-02-24 | 1.5575
2026-02-24 12:29 | 72.6584 | FALSE | TRUE | -5.8817 | -8.808 | -0.74379 | -1.0133 | 0.2826 |  | 2026-02-24 08:30 | none | FALSE | 0 | 66.7767 | FALSE | FALSE | 0.5034 | 2.1246 | 70.0894 | 18 | 0.2826 | 0.25407 | 0.12632 | 0.22585 | 1.6564 | Confirmed/Materialized Shift | 73.4022 | 1.551 | Day | 202602 | 2026-02-24 | 1.551
2026-02-24 12:44 | 72.6584 | TRUE | TRUE | -5.5956 | -8.3438 | -0.9658 | -1.3118 | 0 |  | 2026-02-24 08:30 | none | FALSE | 1 | 67.0628 | FALSE | FALSE | 0.5227 | 2.087 | 70.3435 | 19 | 0 | 0.25407 | 0.12632 | -2.0113 | 1.6403 | Confirmed/Materialized Shift | 73.6242 | 1.4112 | Day | 202602 | 2026-02-24 | 1.4112
2026-02-24 12:59 | 72.3758 | TRUE | TRUE | -4.9875 | -7.4011 | -1.3745 | -1.8638 | -0.2826 |  | 2026-02-24 08:30 | none | FALSE | 2 | 67.3883 | TRUE | FALSE | 0.5329 | 2.0395 | 70.5693 | 20 | -0.2826 | 0.22581 | 0.17387 | -2.924 | 1.5905 | Confirmed/Materialized Shift | 73.7503 | 1.1358 | Day | 202602 | 2026-02-24 | 1.1358
2026-02-24 13:14 | 72.3758 | FALSE | TRUE | -4.6566 | -6.8763 | -1.4672 | -1.9869 | 0 |  | 2026-02-24 08:30 | none | FALSE | 2 | 67.7192 | FALSE | FALSE | 0.5266 | 1.992 | 70.7811 | 21 | 0 | 0.21177 | 0.18041 | -1.1738 | 1.5309 | Confirmed/Materialized Shift | 73.843 | 1.0417 | Day | 202602 | 2026-02-24 | 1.0417
2026-02-24 13:28 | 72.6584 | FALSE | TRUE | -4.5556 | -6.6892 | -1.2527 | -1.6949 | 0.2826 |  | 2026-02-24 08:30 | none | FALSE | 2 | 68.1028 | FALSE | FALSE | 0.533 | 1.9531 | 71.007 | 22 | 0.2826 | 0.2259 | 0.1739 | 0.32604 | 1.4521 | Confirmed/Materialized Shift | 73.9111 | 1.1373 | Day | 202602 | 2026-02-24 | 1.1373
2026-02-24 13:43 | 72.941 | FALSE | TRUE | -4.4651 | -6.5207 | -1.0489 | -1.4176 | 0.2826 |  | 2026-02-24 08:30 | none | FALSE | 2 | 68.4759 | FALSE | FALSE | 0.5398 | 1.9221 | 71.2329 | 23 | 0.2826 | 0.2259 | 0.1739 | 0.32604 | 1.3785 | Confirmed/Materialized Shift | 73.9899 | 1.2391 | Day | 202602 | 2026-02-24 | 1.2391
2026-02-24 13:59 | 72.3758 | TRUE | FALSE | -3.4871 | -5.062 | -1.5683 | -2.121 | -0.5652 |  |  | none | FALSE | 3 | 68.8887 | TRUE | FALSE | 0.1363 |  | 71.4164 | 0 | -0.5652 | 0.18351 | 0.24723 | -3.0284 | 1.2639 | Persistence ends | 73.9441 | 0.7591 | Day | 202602 | 2026-02-24 | 0.7591
2026-02-24 14:14 | 72.6584 | FALSE | FALSE | -3.3674 | -4.8598 | -1.2504 | -1.6919 | 0.2826 |  |  | none | FALSE | 3 | 69.291 | FALSE | FALSE | 0.1468 |  | 71.5999 | 0 | 0.2826 | 0.18351 | 0.24723 | 0.40081 | 1.1545 | Normal | 73.9088 | 0.91687 | Day | 202602 | 2026-02-24 | 0.91687
2026-02-24 14:28 | 72.6584 | FALSE | FALSE | -2.9638 | -4.2525 | -1.1855 | -1.6055 | 0 |  |  | none | FALSE | 3 | 69.6946 | FALSE | FALSE | 0.1429 |  | 71.7693 | 0 | 0 | 0.16938 | 0.24933 | -0.67934 | 1.0373 | Normal | 73.8439 | 0.85712 | Day | 202602 | 2026-02-24 | 0.85712
2026-02-24 14:43 | 72.941 | FALSE | FALSE | -2.8567 | -4.0761 | -0.85204 | -1.1546 | 0.2826 |  |  | none | FALSE | 3 | 70.0843 | FALSE | FALSE | 0.1578 |  | 71.9387 | 0 | 0.2826 | 0.16938 | 0.24933 | 0.45409 | 0.92719 | Normal | 73.793 | 1.081 | Day | 202602 | 2026-02-24 | 1.081
2026-02-24 14:58 | 72.941 | FALSE | FALSE | -2.4651 | -3.4978 | -0.77092 | -1.0459 | 0 |  |  | none | FALSE | 3 | 70.4759 | FALSE | FALSE | 0.1555 |  | 72.0939 | 0 | 0 | 0.15525 | 0.25058 | -0.61956 | 0.809 | Normal | 73.7119 | 1.0471 | Day | 202602 | 2026-02-24 | 1.0471
2026-02-24 15:13 | 73.2236 | FALSE | FALSE | -2.3751 | -3.3523 | -0.42639 | -0.57895 | 0.2826 |  |  | none | FALSE | 2 | 70.8485 | FALSE | FALSE | 0.1499 |  | 72.2493 | 0 | 0.2826 | 0.15534 | 0.25063 | 0.50776 | 0.70037 | Normal | 73.65 | 1.3912 | Day | 202602 | 2026-02-24 | 1.3912
2026-02-24 15:28 | 73.2236 | FALSE | FALSE | -2.103 | -2.9569 | -0.40845 | -0.55472 | 0 |  |  | none | FALSE | 1 | 71.1206 | FALSE | FALSE | 0.1185 |  | 72.3763 | 0 | 0 | 0.12708 | 0.23325 | -0.54483 | 0.62785 | Normal | 73.632 | 1.3495 | Day | 202602 | 2026-02-24 | 1.3495
2026-02-24 15:43 | 73.2236 | FALSE | FALSE | -1.8544 | -2.5983 | -0.38579 | -0.52411 | 0 |  |  | none | FALSE | 1 | 71.3692 | FALSE | FALSE | 0.116 |  | 72.4893 | 0 | 0 | 0.11295 | 0.23188 | -0.4871 | 0.56005 | Normal | 73.6094 | 1.3111 | Day | 202602 | 2026-02-24 | 1.3111
2026-02-24 15:58 | 73.2236 | FALSE | FALSE | -1.6366 | -2.2862 | -0.36563 | -0.49685 | 0 |  |  | none | FALSE | 1 | 71.587 | FALSE | FALSE | 0.1132 |  | 72.5881 | 0 | 0 | 0.09882 | 0.2296 | -0.4304 | 0.50056 | Normal | 73.5892 | 1.2696 | Day | 202602 | 2026-02-24 | 1.2696
2026-02-24 16:13 | 73.2236 | FALSE | FALSE | -1.457 | -2.0302 | -0.35544 | -0.48307 | 0 |  |  | none | FALSE | 1 | 71.7666 | FALSE | FALSE | 0.1096 |  | 72.6728 | 0 | 0 | 0.08469 | 0.22637 | -0.37412 | 0.45312 | Normal | 73.579 | 1.2156 | Day | 202602 | 2026-02-24 | 1.2156
2026-02-24 16:27 | 73.2236 | FALSE | FALSE | -1.3219 | -1.8384 | -0.36138 | -0.4911 | 0 |  |  | none | FALSE | 0 | 71.9017 | FALSE | FALSE | 0.0761 |  | 72.7434 | 0 | 0 | 0.07056 | 0.22215 | -0.31763 | 0.42081 | Normal | 73.585 | 1.1412 | Day | 202602 | 2026-02-24 | 1.1412
2026-02-24 16:43 | 73.5062 | FALSE | FALSE | -1.4644 | -2.0327 | -0.10809 | -0.14683 | 0.2826 |  |  | none | FALSE | 0 | 72.0418 | FALSE | FALSE | 0.115 |  | 72.8281 | 0 | 0.2826 | 0.08469 | 0.22637 | 0.87428 | 0.39312 | Normal | 73.6143 | 1.7251 | Day | 202602 | 2026-02-24 | 1.7251
2026-02-24 16:58 | 73.2236 | FALSE | FALSE | -1.0634 | -1.4737 | -0.38515 | -0.52324 | -0.2826 |  |  | none | FALSE | 0 | 72.1602 | FALSE | FALSE | 0.0624 |  | 72.8845 | 0 | -0.2826 | 0.05643 | 0.23546 | -1.4399 | 0.36214 | Normal | 73.6088 | 0.93644 | Day | 202602 | 2026-02-24 | 0.93644
2026-02-24 17:13 | 73.2236 | FALSE | FALSE | -0.9944 | -1.3767 | -0.40094 | -0.54457 | 0 |  |  | none | FALSE | 0 | 72.2292 | FALSE | FALSE | 0.0567 |  | 72.9269 | 0 | 0 | 0.04239 | 0.22968 | -0.18456 | 0.34883 | Normal | 73.6245 | 0.85063 | Day | 202602 | 2026-02-24 | 0.85063
2026-02-24 17:27 | 73.2236 | FALSE | FALSE | -0.96614 | -1.3371 | -0.4292 | -0.58273 | 0 |  |  | none | FALSE | 0 | 72.2575 | FALSE | FALSE | 0.0513 |  | 72.9551 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.34883 | Normal | 73.6528 | 0.76962 | Day | 202602 | 2026-02-24 | 0.76962
2026-02-24 17:42 | 73.2236 | FALSE | FALSE | -0.93304 | -1.2907 | -0.45262 | -0.61434 | 0 |  |  | none | FALSE | 0 | 72.2906 | FALSE | FALSE | 0.0462 |  | 72.9834 | 0 | 0 | 0.02826 | 0.22271 | -0.12689 | 0.34642 | Normal | 73.6762 | 0.69341 | Day | 202602 | 2026-02-24 | 0.69341
2026-02-24 17:57 | 73.2236 | FALSE | FALSE | -0.83569 | -1.1545 | -0.44005 | -0.59738 | 0 |  |  | none | FALSE | 0 | 72.3879 | FALSE | FALSE | 0.0414 |  | 73.0258 | 0 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.31894 | Normal | 73.6637 | 0.62025 | Day | 202602 | 2026-02-24 | 0.62025
2026-02-24 18:12 | 73.2236 | FALSE | FALSE | -0.71989 | -0.9929 | -0.40903 | -0.5555 | 0 |  |  | none | FALSE | 0 | 72.5037 | FALSE | FALSE | 0.0367 |  | 73.0682 | 0 | 0 | 0.04239 | 0.21058 | -0.2013 | 0.28223 | Normal | 73.6326 | 0.55073 | Day | 202602 | 2026-02-24 | 0.55073
2026-02-24 18:27 | 73.2236 | FALSE | FALSE | -0.66101 | -0.91095 | -0.40667 | -0.55231 | 0 |  |  | none | FALSE | 0 | 72.5626 | FALSE | FALSE | 0.0318 |  | 73.0964 | 0 | 0 | 0.02826 | 0.20296 | -0.13924 | 0.26692 | Normal | 73.6303 | 0.47644 | Night | 202602 | 2026-02-24 | 0.47644
2026-02-24 18:42 | 73.2236 | FALSE | FALSE | -0.64451 | -0.88801 | -0.41843 | -0.5682 | 0 |  |  | none | FALSE | 0 | 72.5791 | FALSE | FALSE | 0.0284 |  | 73.1106 | 0 | 0 | 0.01413 | 0.19396 | -0.072851 | 0.26574 | Normal | 73.642 | 0.42538 | Night | 202602 | 2026-02-24 | 0.42538
2026-02-24 18:42 | 73.2236 | FALSE | FALSE | -0.47553 | -0.65367 | -0.33423 | -0.45438 | 0 |  |  | none | FALSE | 0 | 72.7481 | FALSE | FALSE | 0.0233 |  | 73.153 | 0 | 0 | 0.04239 | 0.13829 | -0.30652 | 0.20244 | Normal | 73.5578 | 0.34899 | Night | 202602 | 2026-02-24 | 0.34899
2026-02-24 18:57 | 73.2236 | FALSE | FALSE | -0.37424 | -0.51372 | -0.28946 | -0.39376 | 0 |  |  | none | FALSE | 0 | 72.8494 | FALSE | FALSE | 0.017 |  | 73.1812 | 0 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.16593 | Normal | 73.5131 | 0.25547 | Night | 202602 | 2026-02-24 | 0.25547
2026-02-24 19:12 | 73.2236 | FALSE | FALSE | -0.23684 | -0.32449 | -0.20858 | -0.28404 | 0 |  |  | none | FALSE | 0 | 72.9868 | FALSE | FALSE | 0.0085 |  | 73.2095 | 0 | 0 | 0.02826 | 0.12638 | -0.22361 | 0.11135 | Normal | 73.4322 | 0.12689 | Night | 202602 | 2026-02-24 | 0.12689
2026-02-24 19:27 | 72.941 | TRUE | FALSE | 0.045762 | 0.062699 | -0.49118 | -0.66889 | -0.2826 | 2026-02-25 05:39 | 2026-02-24 19:27 | lower | TRUE | 1 | 72.9868 | FALSE | FALSE | 0.2464 | 2.411 | 73.2095 | 1 | -0.2826 | 0 | 0.12967 | -2.1794 | 0.11135 | Extreme triggered | 73.4322 | -2.411 | Night | 202602 | 2026-02-24 | 2.411
2026-02-24 19:42 | 72.941 | FALSE | FALSE | 0.045762 | 0.062699 | -0.49118 | -0.66889 | 0 |  | 2026-02-24 19:27 | lower | TRUE | 1 | 72.9868 | FALSE | FALSE | 0.3036 | 2.411 | 73.2095 | 2 | 0 | 0 | 0.12967 | 0 | 0.11135 | Extreme/elevated | 73.4322 | -2.411 | Night | 202602 | 2026-02-24 | 2.411
2026-02-24 19:57 | 72.6584 | TRUE | FALSE | 0.19096 | 0.26213 | -0.85466 | -1.1626 | -0.2826 |  | 2026-02-24 19:27 | lower | TRUE | 2 | 72.8494 | TRUE | TRUE | 0.4386 | 2.6576 | 73.1812 | 3 | -0.2826 | -0.02826 | 0.12638 | -2.0125 | 0.16593 | Persistent | 73.5131 | -3.1509 | Night | 202602 | 2026-02-24 | 3.1509
2026-02-24 20:12 | 72.3758 | FALSE | FALSE | 0.2744 | 0.3777 | -1.2516 | -1.7 | -0.2826 |  | 2026-02-24 19:27 | lower | TRUE | 2 | 72.6502 | FALSE | TRUE | 0.4939 | 2.774 | 73.1388 | 4 | -0.2826 | -0.04239 | 0.13829 | -1.737 | 0.24431 | Persistent | 73.6274 | -3.1232 | Night | 202602 | 2026-02-24 | 3.1232
2026-02-24 20:27 | 72.095 | FALSE | FALSE | 0.31418 | 0.4339 | -1.6606 | -2.2515 | -0.2808 |  | 2026-02-24 19:27 | lower | TRUE | 2 | 72.4092 | FALSE | TRUE | 0.5384 | 2.8059 | 73.0824 | 5 | -0.2808 | -0.05643 | 0.1477 | -1.5191 | 0.3366 | Persistent | 73.7556 | -2.9334 | Night | 202602 | 2026-02-24 | 2.9334
2026-02-24 20:41 | 71.8124 | FALSE | FALSE | 0.3233 | 0.44819 | -2.0756 | -2.8091 | -0.2826 |  | 2026-02-24 19:27 | lower | TRUE | 2 | 72.1357 | FALSE | TRUE | 0.5825 | 2.7946 | 73.0118 | 6 | -0.2826 | -0.07056 | 0.15534 | -1.365 | 0.43806 | Persistent | 73.888 | -2.738 | Night | 202602 | 2026-02-24 | 2.738
2026-02-24 20:56 | 71.5298 | FALSE | TRUE | 0.3063 | 0.42639 | -2.4884 | -3.3618 | -0.2826 |  | 2026-02-24 19:27 | lower | TRUE | 2 | 71.8361 | FALSE | TRUE | 0.6279 | 2.7613 | 72.9271 | 7 | -0.2826 | -0.08469 | 0.16132 | -1.2268 | 0.54552 | Confirmed/Materialized Shift | 74.0182 | -2.5615 | Night | 202602 | 2026-02-24 | 2.5615
2026-02-24 21:11 | 71.5298 | FALSE | TRUE | 0.066567 | 0.092975 | -2.5587 | -3.4536 | 0 |  | 2026-02-24 19:27 | lower | TRUE | 2 | 71.5964 | FALSE | TRUE | 0.5976 | 2.6795 | 72.8424 | 8 | 0 | -0.08469 | 0.16132 | 0.52499 | 0.62304 | Confirmed/Materialized Shift | 74.0885 | -2.1068 | Night | 202602 | 2026-02-24 | 2.1068
2026-02-24 21:26 | 71.2472 | FALSE | TRUE | 0.08874 | 0.1244 | -2.8759 | -3.8798 | -0.2826 |  | 2026-02-24 19:27 | lower | TRUE | 2 | 71.3359 | FALSE | TRUE | 0.599 | 2.6181 | 72.7295 | 9 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.69678 | Confirmed/Materialized Shift | 74.1231 | -2.1274 | Night | 202602 | 2026-02-24 | 2.1274
2026-02-24 21:41 | 70.9646 | FALSE | TRUE | 0.073135 | 0.10295 | -3.2308 | -4.3544 | -0.2826 |  | 2026-02-24 19:27 | lower | TRUE | 2 | 71.0377 | FALSE | TRUE | 0.5967 | 2.5656 | 72.6166 | 10 | -0.2826 | -0.11295 | 0.14193 | -1.1953 | 0.78941 | Confirmed/Materialized Shift | 74.1954 | -2.0926 | Night | 202602 | 2026-02-24 | 2.0926
2026-02-24 21:56 | 70.682 | FALSE | TRUE | 0.036885 | 0.052157 | -3.5781 | -4.8183 | -0.2826 |  | 2026-02-24 19:27 | lower | TRUE | 1 | 70.7189 | FALSE | TRUE | 0.5647 | 2.5179 | 72.4895 | 11 | -0.2826 | -0.12708 | 0.14414 | -1.0789 | 0.88529 | Confirmed/Materialized Shift | 74.2601 | -2.0417 | Night | 202602 | 2026-02-24 | 2.0417
2026-02-24 22:11 | 70.682 | FALSE | TRUE | -0.22783 | -0.32337 | -3.5886 | -4.8318 | 0 |  | 2026-02-24 19:27 | none | FALSE | 1 | 70.4542 | FALSE | FALSE | 0.546 | 2.4549 | 72.3624 | 12 | 0 | -0.12708 | 0.14414 | 0.88163 | 0.95411 | Confirmed/Materialized Shift | 74.2706 | -1.7612 | Night | 202602 | 2026-02-24 | 1.7612
2026-02-24 22:26 | 70.3994 | FALSE | TRUE | -0.23064 | -0.32869 | -3.8742 | -5.2161 | -0.2826 |  | 2026-02-24 19:27 | none | FALSE | 0 | 70.1688 | FALSE | FALSE | 0.5184 | 2.4026 | 72.2212 | 13 | -0.2826 | -0.14121 | 0.14488 | -0.97592 | 1.0262 | Confirmed/Materialized Shift | 74.2736 | -1.7753 | Night | 202602 | 2026-02-24 | 1.7753
2026-02-24 22:41 | 70.3994 | FALSE | TRUE | -0.46783 | -0.66898 | -3.829 | -5.1584 | 0 |  | 2026-02-24 19:27 | none | FALSE | 0 | 69.9316 | FALSE | FALSE | 0.5043 | 2.3427 | 72.08 | 14 | 0 | -0.14121 | 0.14488 | 0.97468 | 1.0742 | Confirmed/Materialized Shift | 74.2284 | -1.5645 | Night | 202602 | 2026-02-24 | 1.5645
2026-02-24 22:56 | 70.1168 | FALSE | TRUE | -0.4394 | -0.63062 | -4.0551 | -5.4671 | -0.2826 |  | 2026-02-24 19:27 | none | FALSE | 0 | 69.6774 | FALSE | FALSE | 0.5073 | 2.2938 | 71.9246 | 15 | -0.2826 | -0.15534 | 0.14416 | -0.88276 | 1.1236 | Confirmed/Materialized Shift | 74.1719 | -1.6089 | Night | 202602 | 2026-02-24 | 1.6089
2026-02-24 23:11 | 69.836 | FALSE | TRUE | -0.42434 | -0.61134 | -4.2628 | -5.7529 | -0.2808 |  | 2026-02-24 19:27 | none | FALSE | 0 | 69.4117 | FALSE | FALSE | 0.5092 | 2.2528 | 71.7553 | 16 | -0.2808 | -0.16938 | 0.14189 | -0.78525 | 1.1718 | Confirmed/Materialized Shift | 74.0988 | -1.6379 | Night | 202602 | 2026-02-24 | 1.6379
2026-02-24 23:26 | 69.836 | FALSE | TRUE | -0.63617 | -0.91933 | -4.1359 | -5.5912 | 0 |  | 2026-02-24 19:27 | none | FALSE | 0 | 69.1998 | FALSE | FALSE | 0.4978 | 2.2066 | 71.5859 | 17 | 0 | -0.16938 | 0.14189 | 1.1937 | 1.193 | Confirmed/Materialized Shift | 73.9719 | -1.4668 | Night | 202602 | 2026-02-24 | 1.4668
2026-02-24 23:40 | 69.2708 | TRUE | TRUE | -0.35085 | -0.50906 | -4.5857 | -6.2089 | -0.5652 |  | 2026-02-24 19:27 | none | FALSE | 1 | 68.92 | FALSE | FALSE | 0.543 | 2.1793 | 71.3882 | 18 | -0.5652 | -0.19764 | 0.16133 | -2.2783 | 1.2341 | Confirmed/Materialized Shift | 73.8565 | -1.7157 | Night | 202602 | 2026-02-24 | 1.7157
2026-02-24 23:55 | 69.2708 | FALSE | TRUE | -0.56268 | -0.81894 | -4.4023 | -5.9754 | 0 |  | 2026-02-24 19:27 | none | FALSE | 1 | 68.7081 | FALSE | FALSE | 0.5317 | 2.146 | 71.1906 | 19 | 0 | -0.19764 | 0.16133 | 1.225 | 1.2412 | Confirmed/Materialized Shift | 73.6731 | -1.5467 | Night | 202602 | 2026-02-24 | 1.5467
2026-02-25 00:11 | 69.2708 | FALSE | TRUE | -0.70765 | -1.0321 | -4.152 | -5.6549 | 0 |  | 2026-02-24 19:27 | none | FALSE | 1 | 68.5631 | FALSE | FALSE | 0.5231 | 2.1096 | 70.9929 | 20 | 0 | -0.19764 | 0.16133 | 1.225 | 1.2149 | Confirmed/Materialized Shift | 73.4228 | -1.4175 | Night | 202602 | 2026-02-25 | 1.4175
2026-02-25 00:26 | 68.9882 | FALSE | TRUE | -0.59844 | -0.87504 | -4.2127 | -5.7549 | -0.2826 |  | 2026-02-24 19:27 | none | FALSE | 1 | 68.3898 | FALSE | FALSE | 0.5287 | 2.0807 | 70.7953 | 21 | -0.2826 | -0.19764 | 0.16133 | -0.52661 | 1.2028 | Confirmed/Materialized Shift | 73.2009 | -1.5025 | Night | 202602 | 2026-02-25 | 1.5025
2026-02-25 00:40 | 68.9882 | FALSE | TRUE | -0.70147 | -1.0272 | -3.9204 | -5.3772 | 0 |  | 2026-02-24 19:27 | none | FALSE | 1 | 68.2867 | FALSE | FALSE | 0.5214 | 2.0494 | 70.5977 | 22 | 0 | -0.19764 | 0.16133 | 1.225 | 1.1555 | Confirmed/Materialized Shift | 72.9086 | -1.3929 | Night | 202602 | 2026-02-25 | 1.3929
2026-02-25 00:55 | 68.7056 | FALSE | TRUE | -0.54959 | -0.80637 | -3.9384 | -5.4216 | -0.2826 |  | 2026-02-24 19:27 | none | FALSE | 1 | 68.156 | FALSE | FALSE | 0.5292 | 2.026 | 70.4 | 23 | -0.2826 | -0.19764 | 0.16133 | -0.52661 | 1.122 | Confirmed/Materialized Shift | 72.644 | -1.5102 | Night | 202602 | 2026-02-25 | 1.5102
2026-02-25 01:10 | 68.7056 | FALSE | TRUE | -0.65159 | -0.95746 | -3.6734 | -5.0753 | 0 |  | 2026-02-24 19:27 | none | FALSE | 1 | 68.054 | FALSE | FALSE | 0.5217 | 1.9998 | 70.2165 | 24 | 0 | -0.18351 | 0.16581 | 1.1067 | 1.0813 | Confirmed/Materialized Shift | 72.379 | -1.3974 | Night | 202602 | 2026-02-25 | 1.3974
2026-02-25 01:25 | 68.7056 | FALSE | TRUE | -0.73056 | -1.0748 | -3.4135 | -4.7331 | 0 |  | 2026-02-24 19:27 | none | FALSE | 1 | 67.975 | FALSE | FALSE | 0.5149 | 1.9716 | 70.047 | 25 | 0 | -0.16947 | 0.169 | 1.0028 | 1.036 | Confirmed/Materialized Shift | 72.1191 | -1.2948 | Night | 202602 | 2026-02-25 | 1.2948
2026-02-25 01:40 | 68.423 | FALSE | TRUE | -0.56321 | -0.82996 | -3.4724 | -4.8298 | -0.2826 |  | 2026-02-24 19:27 | none | FALSE | 1 | 67.8598 | FALSE | FALSE | 0.5247 | 1.9512 | 69.8776 | 26 | -0.2826 | -0.16947 | 0.169 | -0.66941 | 1.0089 | Confirmed/Materialized Shift | 71.8954 | -1.4418 | Night | 202602 | 2026-02-25 | 1.4418
2026-02-25 01:55 | 68.423 | FALSE | TRUE | -0.66051 | -0.97474 | -3.259 | -4.5465 | 0 |  | 2026-02-24 19:27 | none | FALSE | 1 | 67.7625 | FALSE | FALSE | 0.517 | 1.928 | 69.7222 | 27 | 0 | -0.15534 | 0.17085 | 0.90923 | 0.97987 | Confirmed/Materialized Shift | 71.682 | -1.3259 | Night | 202602 | 2026-02-25 | 1.3259
2026-02-25 02:10 | 68.1404 | FALSE | TRUE | -0.47406 | -0.70059 | -3.2988 | -4.6176 | -0.2826 |  | 2026-02-24 19:27 | none | FALSE | 0 | 67.6663 | FALSE | FALSE | 0.4998 | 1.9127 | 69.5528 | 28 | -0.2826 | -0.16947 | 0.169 | -0.66941 | 0.94322 | Confirmed/Materialized Shift | 71.4392 | -1.4974 | Night | 202602 | 2026-02-25 | 1.4974
2026-02-25 02:25 | 68.1404 | FALSE | TRUE | -0.55198 | -0.81669 | -3.066 | -4.3059 | 0 |  | 2026-02-24 19:27 | none | FALSE | 0 | 67.5884 | FALSE | FALSE | 0.4926 | 1.8946 | 69.3974 | 29 | 0 | -0.15534 | 0.17085 | 0.90923 | 0.90451 | Confirmed/Materialized Shift | 71.2064 | -1.3897 | Night | 202602 | 2026-02-25 | 1.3897
2026-02-25 02:39 | 68.1404 | FALSE | TRUE | -0.61744 | -0.91441 | -2.8491 | -4.0134 | 0 |  | 2026-02-24 19:27 | none | FALSE | 0 | 67.523 | FALSE | FALSE | 0.4858 | 1.8744 | 69.2562 | 30 | 0 | -0.14121 | 0.17145 | 0.8236 | 0.86663 | Confirmed/Materialized Shift | 70.9895 | -1.2875 | Night | 202602 | 2026-02-25 | 1.2875
2026-02-25 02:55 | 67.8596 | FALSE | TRUE | -0.44832 | -0.66505 | -2.9593 | -4.1787 | -0.2808 |  | 2026-02-24 19:27 | none | FALSE | 0 | 67.4113 | FALSE | FALSE | 0.4982 | 1.8615 | 69.1151 | 31 | -0.2808 | -0.14112 | 0.17138 | -0.81505 | 0.85191 | Confirmed/Materialized Shift | 70.8189 | -1.4737 | Night | 202602 | 2026-02-25 | 1.4737
2026-02-25 03:10 | 67.8596 | FALSE | TRUE | -0.50862 | -0.75517 | -2.7374 | -3.8775 | 0 |  | 2026-02-24 19:27 | none | FALSE | 0 | 67.351 | FALSE | FALSE | 0.4915 | 1.8462 | 68.974 | 32 | 0 | -0.14112 | 0.17138 | 0.82345 | 0.8115 | Confirmed/Materialized Shift | 70.597 | -1.3732 | Night | 202602 | 2026-02-25 | 1.3732
2026-02-25 03:25 | 67.8596 | FALSE | TRUE | -0.56177 | -0.83475 | -2.5366 | -3.6033 | 0 |  | 2026-02-24 19:27 | none | FALSE | 0 | 67.2978 | FALSE | FALSE | 0.485 | 1.8289 | 68.847 | 33 | 0 | -0.12699 | 0.17075 | 0.74373 | 0.77458 | Confirmed/Materialized Shift | 70.3962 | -1.2747 | Night | 202602 | 2026-02-25 | 1.2747
2026-02-25 03:39 | 67.8596 | FALSE | TRUE | -0.56434 | -0.8386 | -2.2851 | -3.2578 | 0 |  | 2026-02-24 19:27 | none | FALSE | 0 | 67.2953 | FALSE | FALSE | 0.4805 | 1.8106 | 68.72 | 34 | 0 | -0.12699 | 0.17075 | 0.74373 | 0.71237 | Confirmed/Materialized Shift | 70.1447 | -1.2078 | Night | 202602 | 2026-02-25 | 1.2078
2026-02-25 03:54 | 67.8596 | FALSE | TRUE | -0.56447 | -0.83879 | -2.0595 | -2.9456 | 0 |  | 2026-02-24 19:27 | none | FALSE | 0 | 67.2951 | FALSE | FALSE | 0.476 | 1.7915 | 68.6071 | 35 | 0 | -0.11286 | 0.16887 | 0.66831 | 0.656 | Confirmed/Materialized Shift | 69.9191 | -1.1395 | Night | 202602 | 2026-02-25 | 1.1395
2026-02-25 04:09 | 67.8596 | FALSE | TRUE | -0.56782 | -0.84382 | -1.8653 | -2.6752 | 0 |  | 2026-02-24 19:27 | none | FALSE | 0 | 67.2918 | FALSE | FALSE | 0.4711 | 1.7713 | 68.5083 | 36 | 0 | -0.09882 | 0.16582 | 0.59594 | 0.60827 | Confirmed/Materialized Shift | 69.7249 | -1.0665 | Night | 202602 | 2026-02-25 | 1.0665
2026-02-25 04:24 | 67.8596 | FALSE | TRUE | -0.52544 | -0.78034 | -1.6252 | -2.339 | 0 |  | 2026-02-24 19:27 | none | FALSE | 0 | 67.3342 | FALSE | FALSE | 0.4682 | 1.7511 | 68.4095 | 37 | 0 | -0.09882 | 0.16582 | 0.59594 | 0.53767 | Confirmed/Materialized Shift | 69.4848 | -1.0227 | Night | 202602 | 2026-02-25 | 1.0227
2026-02-25 04:39 | 67.577 | FALSE | TRUE | -0.30854 | -0.45867 | -1.8042 | -2.6004 | -0.2826 |  | 2026-02-24 19:27 | none | FALSE | 0 | 67.2685 | FALSE | FALSE | 0.4944 | 1.7423 | 68.3248 | 38 | -0.2826 | -0.08469 | 0.13273 | -1.4911 | 0.52818 | Confirmed/Materialized Shift | 69.3812 | -1.4158 | Night | 202602 | 2026-02-25 | 1.4158
2026-02-25 04:54 | 67.577 | FALSE | TRUE | -0.34436 | -0.51219 | -1.6706 | -2.4125 | 0 |  | 2026-02-24 19:27 | none | FALSE | 0 | 67.2326 | FALSE | FALSE | 0.4878 | 1.7313 | 68.2401 | 39 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.50374 | Confirmed/Materialized Shift | 69.2476 | -1.3164 | Night | 202602 | 2026-02-25 | 1.3164
2026-02-25 05:09 | 67.2944 | FALSE | TRUE | -0.12189 | -0.18145 | -1.8157 | -2.6272 | -0.2826 |  | 2026-02-24 19:27 | none | FALSE | 0 | 67.1725 | FALSE | FALSE | 0.5166 | 1.7318 | 68.1413 | 40 | -0.2826 | -0.09882 | 0.13817 | -1.3301 | 0.48439 | Confirmed/Materialized Shift | 69.1101 | -1.7484 | Night | 202602 | 2026-02-25 | 1.7484
2026-02-25 05:24 | 67.2944 | FALSE | TRUE | -0.19086 | -0.28443 | -1.7153 | -2.4856 | 0 |  | 2026-02-24 19:27 | none | FALSE | 0 | 67.1035 | FALSE | FALSE | 0.5066 | 1.7285 | 68.0566 | 41 | 0 | -0.08469 | 0.13273 | 0.63807 | 0.47654 | Confirmed/Materialized Shift | 69.0097 | -1.5995 | Night | 202602 | 2026-02-25 | 1.5995
2026-02-25 05:39 | 67.577 | TRUE | FALSE | -0.45876 | -0.68352 | -1.2769 | -1.8545 | 0.2826 |  |  | none | FALSE | 1 | 67.1182 | FALSE | FALSE | 0.0914 |  | 67.9861 | 0 | 0.2826 | -0.07056 | 0.15534 | 2.2735 | 0.43391 | Persistence ends | 68.8539 | -0.94271 | Night | 202602 | 2026-02-25 | 0.94271
2026-02-25 05:54 | 67.577 | FALSE | FALSE | -0.46342 | -0.6905 | -1.1687 | -1.7 | 0 |  |  | none | FALSE | 1 | 67.1136 | FALSE | FALSE | 0.0862 |  | 67.9296 | 0 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.40802 | Normal | 68.7457 | -0.86422 | Night | 202602 | 2026-02-25 | 0.86422
2026-02-25 06:09 | 67.577 | FALSE | FALSE | -0.44672 | -0.66546 | -1.0391 | -1.5144 | 0 |  |  | none | FALSE | 1 | 67.1303 | FALSE | FALSE | 0.0817 |  | 67.8732 | 0 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.37146 | Normal | 68.6161 | -0.79737 | Night | 202602 | 2026-02-25 | 0.79737
2026-02-25 06:24 | 67.577 | FALSE | FALSE | -0.40142 | -0.59756 | -0.88094 | -1.2868 | 0 |  |  | none | FALSE | 1 | 67.1756 | FALSE | FALSE | 0.0784 |  | 67.8168 | 0 | 0 | -0.05643 | 0.1477 | 0.38207 | 0.32059 | Normal | 68.4579 | -0.74788 | Night | 202602 | 2026-02-25 | 0.74788
2026-02-25 06:38 | 67.577 | FALSE | FALSE | -0.38418 | -0.57175 | -0.7791 | -1.1398 | 0 |  |  | none | FALSE | 1 | 67.1928 | FALSE | FALSE | 0.0738 |  | 67.7745 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.29082 | Normal | 68.3561 | -0.67898 | Night | 202602 | 2026-02-25 | 0.67898
2026-02-25 06:53 | 67.577 | FALSE | FALSE | -0.34527 | -0.51355 | -0.65559 | -0.96081 | 0 |  |  | none | FALSE | 1 | 67.2317 | FALSE | FALSE | 0.0699 |  | 67.7322 | 0 | 0 | -0.0423 | 0.13813 | 0.30624 | 0.25021 | Normal | 68.2326 | -0.62011 | Day | 202602 | 2026-02-25 | 0.62011
2026-02-25 07:08 | 67.577 | FALSE | FALSE | -0.33892 | -0.50405 | -0.5929 | -0.86973 | 0 |  |  | none | FALSE | 1 | 67.2381 | FALSE | FALSE | 0.0649 |  | 67.704 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.23295 | Normal | 68.1699 | -0.54513 | Day | 202602 | 2026-02-25 | 0.54513
2026-02-25 07:23 | 67.577 | FALSE | FALSE | -0.32193 | -0.47866 | -0.51957 | -0.76298 | 0 |  |  | none | FALSE | 1 | 67.2551 | FALSE | FALSE | 0.0599 |  | 67.6758 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.21037 | Normal | 68.0966 | -0.46974 | Day | 202602 | 2026-02-25 | 0.46974
2026-02-25 07:30 | 67.577 | FALSE | FALSE | -0.29032 | -0.43147 | -0.43162 | -0.63466 | 0 |  |  | none | FALSE | 1 | 67.2867 | FALSE | FALSE | 0.0547 |  | 67.6476 | 0 | 0 | -0.02817 | 0.12619 | 0.22323 | 0.18049 | Normal | 68.0086 | -0.39144 | Day | 202602 | 2026-02-25 | 0.39144
2026-02-25 07:45 | 67.8596 | TRUE | FALSE | -0.57292 | -0.85147 | -0.14902 | -0.21913 | 0.2826 |  |  | none | FALSE | 2 | 67.2867 | TRUE | FALSE | 0.1354 |  | 67.6476 | 0 | 0.2826 | 0 | 0.12967 | 2.1794 | 0.18049 | Normal | 68.0086 | 1.1743 | Day | 202602 | 2026-02-25 | 1.1743
2026-02-25 08:00 | 68.1404 | FALSE | FALSE | -0.89239 | -1.327 | 0.06503 | 0.095526 | 0.2808 |  | 2026-02-25 08:00 | upper | TRUE | 1 | 67.248 | FALSE | FALSE | 0.24 | 2.3144 | 67.6617 | 1 | 0.2808 | 0.01404 | 0.14407 | 1.8516 | 0.20684 | Extreme triggered | 68.0754 | 2.3144 | Day | 202602 | 2026-02-25 | 2.3144
2026-02-25 08:15 | 68.1404 | FALSE | FALSE | -0.92326 | -1.3735 | 0.0060849 | 0.0089308 | 0 |  | 2026-02-25 08:00 | upper | TRUE | 1 | 67.2171 | FALSE | FALSE | 0.278 | 2.1705 | 67.6757 | 2 | 0 | 0.01404 | 0.14407 | -0.097454 | 0.22929 | Extreme/elevated | 68.1343 | 2.0265 | Day | 202602 | 2026-02-25 | 2.0265
2026-02-25 08:30 | 68.1404 | FALSE | FALSE | -0.94843 | -1.4115 | -0.047174 | -0.069183 | 0 |  | 2026-02-25 08:00 | none | FALSE | 1 | 67.192 | FALSE | FALSE | 0.3207 | 2.0505 | 67.6898 | 3 | 0 | 0.01404 | 0.14407 | -0.097454 | 0.2489 | Persistent | 68.1876 | 1.8105 | Day | 202602 | 2026-02-25 | 1.8105
2026-02-25 08:45 | 68.423 | FALSE | FALSE | -1.298 | -1.9337 | 0.11212 | 0.16413 | 0.2826 |  | 2026-02-25 08:00 | upper | TRUE | 1 | 67.125 | FALSE | TRUE | 0.4157 | 2.1324 | 67.7179 | 4 | 0.2826 | 0.02817 | 0.15598 | 1.6311 | 0.29647 | Persistent | 68.3109 | 2.3782 | Day | 202602 | 2026-02-25 | 2.3782
2026-02-25 08:45 | 68.423 | FALSE | FALSE | -1.3467 | -2.0077 | 0.0070624 | 0.010323 | 0 |  | 2026-02-25 08:00 | upper | TRUE | 1 | 67.0763 | FALSE | TRUE | 0.449 | 2.1101 | 67.7461 | 5 | 0 | 0.02817 | 0.15598 | -0.18059 | 0.33491 | Persistent | 68.4159 | 2.0211 | Day | 202602 | 2026-02-25 | 2.0211
2026-02-25 09:00 | 68.7056 | FALSE | FALSE | -1.7123 | -2.556 | 0.12206 | 0.17797 | 0.2826 |  | 2026-02-25 08:00 | upper | TRUE | 1 | 66.9933 | FALSE | TRUE | 0.5252 | 2.1429 | 67.7884 | 6 | 0.2826 | 0.0423 | 0.16579 | 1.4494 | 0.39757 | Persistent | 68.5835 | 2.307 | Day | 202602 | 2026-02-25 | 2.307
2026-02-25 09:15 | 68.9882 | FALSE | TRUE | -2.0805 | -3.1095 | 0.17796 | 0.25862 | 0.2826 |  | 2026-02-25 08:00 | upper | TRUE | 1 | 66.9077 | FALSE | TRUE | 0.5868 | 2.176 | 67.859 | 7 | 0.2826 | 0.07056 | 0.15534 | 1.365 | 0.47564 | Confirmed/Materialized Shift | 68.8102 | 2.3741 | Day | 202602 | 2026-02-25 | 2.3741
2026-02-25 09:30 | 69.2708 | FALSE | TRUE | -2.4575 | -3.6781 | 0.19682 | 0.28495 | 0.2826 |  | 2026-02-25 08:00 | upper | TRUE | 1 | 66.8133 | FALSE | TRUE | 0.5851 | 2.1975 | 67.9437 | 8 | 0.2826 | 0.08469 | 0.16132 | 1.2268 | 0.56516 | Confirmed/Materialized Shift | 69.074 | 2.3483 | Day | 202602 | 2026-02-25 | 2.3483
2026-02-25 09:44 | 69.836 | TRUE | TRUE | -3.1345 | -4.6993 | 0.39604 | 0.57034 | 0.5652 |  | 2026-02-25 08:00 | upper | TRUE | 2 | 66.7015 | TRUE | TRUE | 0.629 | 2.2398 | 68.0707 | 9 | 0.5652 | 0.12708 | 0.17083 | 2.5646 | 0.68461 | Confirmed/Materialized Shift | 69.44 | 2.5785 | Day | 202602 | 2026-02-25 | 2.5785
2026-02-25 09:59 | 70.1168 | FALSE | TRUE | -3.5004 | -5.2545 | 0.30952 | 0.44339 | 0.2808 |  | 2026-02-25 08:00 | upper | TRUE | 1 | 66.6164 | FALSE | TRUE | 0.5878 | 2.2547 | 68.2119 | 10 | 0.2808 | 0.14112 | 0.17138 | 0.81505 | 0.79771 | Confirmed/Materialized Shift | 69.8073 | 2.388 | Day | 202602 | 2026-02-25 | 2.388
2026-02-25 10:14 | 70.682 | TRUE | TRUE | -4.2237 | -6.3554 | 0.40608 | 0.57783 | 0.5652 |  | 2026-02-25 08:00 | upper | TRUE | 2 | 66.4583 | TRUE | TRUE | 0.6188 | 2.2702 | 68.3671 | 11 | 0.5652 | 0.15525 | 0.19383 | 2.115 | 0.95441 | Confirmed/Materialized Shift | 70.2759 | 2.4255 | Day | 202602 | 2026-02-25 | 2.4255
2026-02-25 10:30 | 71.2472 | FALSE | TRUE | -4.9586 | -7.4803 | 0.43458 | 0.6137 | 0.5652 |  | 2026-02-25 08:00 | upper | TRUE | 2 | 66.2886 | FALSE | TRUE | 0.6161 | 2.2797 | 68.5506 | 12 | 0.5652 | 0.18351 | 0.21049 | 1.8133 | 1.131 | Confirmed/Materialized Shift | 70.8126 | 2.3842 | Day | 202602 | 2026-02-25 | 2.3842
2026-02-25 10:44 | 71.5298 | FALSE | TRUE | -5.3547 | -8.0917 | 0.20838 | 0.29217 | 0.2826 |  | 2026-02-25 08:00 | upper | TRUE | 2 | 66.1751 | FALSE | TRUE | 0.6013 | 2.2706 | 68.7483 | 13 | 0.2826 | 0.19764 | 0.20698 | 0.41047 | 1.2866 | Confirmed/Materialized Shift | 71.3214 | 2.162 | Day | 202602 | 2026-02-25 | 2.162
2026-02-25 10:59 | 72.095 | FALSE | TRUE | -6.0321 | -9.1309 | 0.20957 | 0.29153 | 0.5652 |  | 2026-02-25 08:00 | upper | TRUE | 2 | 66.0629 | FALSE | TRUE | 0.6001 | 2.2616 | 68.9742 | 14 | 0.5652 | 0.2259 | 0.21692 | 1.5641 | 1.4556 | Confirmed/Materialized Shift | 71.8854 | 2.144 | Day | 202602 | 2026-02-25 | 2.144
2026-02-25 11:14 | 72.3758 | FALSE | TRUE | -6.3645 | -9.6416 | -0.041138 | -0.056806 | 0.2808 |  | 2026-02-25 08:00 | none | FALSE | 2 | 66.0113 | FALSE | FALSE | 0.5888 | 2.2424 | 69.2141 | 15 | 0.2808 | 0.23994 | 0.21053 | 0.19409 | 1.6014 | Confirmed/Materialized Shift | 72.4169 | 1.9743 | Day | 202602 | 2026-02-25 | 1.9743